3484257 | BNMS MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-08-02 | AAA | 0.17 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-08-02 | AAA | 0.22 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-08-02 | AAA | 0.17 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-08-02 | AAA | 0.39 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-02 | AAA | 0.0069 | 0.0149 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-02 | AAA | 0.0071 | 0.0249 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-02 | AAA | 0.0068 | 0.1499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-02 | AAA | 0.12 | 1.4999 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-02 | AAA | 1 | 1.4999 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-02 | AAA | 7.6 | 0.4499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-02 | AAA | 1.2 | 9.4999 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-08-02 | AAA | 0.23 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-08-02 | AAA | 0.26 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-08-02 | AAA | 0.28 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-08-02 | AAA | 0.12 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-08-02 | AAA | 0.24 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-08-02 | AAA | 0.12 | 0.5499 |  |  | 1Q VOC (NO DETECTIONS IN THESE VOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-02 | AAA | 6.5 | 6.4999 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-02 | AAA | 0.95 | 0.6499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-02 | AAA | 0.57 | 2.4999 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-02 | AAA | 0.19 | 0.0749 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-02 | AAA | 1.5 | 0.6499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-02 | AAA | 0.23 | 0.1499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-02 | AAA | 0.86 | 0.2499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-02 | AAA | 0.012 | 0.1499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-02 | AAA | 0.28 | 0.9499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-02 | AAA | 0.16 | 0.1499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-02 | AAA | 0.26 | 0.2499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-02 | AAA | 0.006 | 0.0449 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-02 | AAA | 0.0052 | 0.0249 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-02 | AAA | 1.5 | 0.1499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-02 | AAA | 0.32 | 0.2499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-02 | AAA | 0.0063 | 0.1499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-02 | AAA | 0.096 | 0.0249 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-02 | AAA | 0.069 | 0.0449 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-02 | AAA | 0.11 | 0.1499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-02 | AAA | 0.0061 | 0.0249 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-02 | AAA | 0.0063 | 0.0149 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-02 | AAA | 0.053 | 0.2499 |  |  | 1Q SOC (NO DETECTIONS IN THESE SOCS)
3484257 | BNMS MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-08-02 | AAA | 2.2 |  |  |  | 1Q RADS
3484257 | BNMS MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-08-03 | AAA | 0.0048 |  |  |  | CY (TESTED SEP) STILL NEED MERCURY RESULT OR FOR MERCURY TO BE TESTED - 9/15/17 EM TO MELISA & AEL - DS/BB
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 72.36 | UG/L | 80.4999 | 2017-08-16 | L1 | 0.14 |  | 1 | 1.62 | LOT 18801 (HYPERLINKED 10/19/17 TO AR - BB)
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.86 | UG/L | 60.4999 | 2017-08-16 | L1 | 0.5 |  | 1 | 1.62 | LOT 18801 (HYPERLINKED 10/19/17 TO AR - BB)
3484257 | BNMS MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-09-28 | AAA | 5e-05 |  |  |  | MERCURY SEP
3484257 | BNMS MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.072 | MG/L | 0.0549 | 2017-09-28 | AAA | 0.0019 |  |  |  | MANGANESE RETEST DUE TO MCL (STILL OVER MCL) & FOAMING AGENTS RETESTED DUE TO Q QUALIFIER ON ORIGINAL RESULTS
3484257 | BNMS MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0.077 |  | 0.5499 | 2017-09-28 | AAA | 0.04 |  |  |  | MANGANESE RETEST DUE TO MCL (STILL OVER MCL) & FOAMING AGENTS RETESTED DUE TO Q QUALIFIER ON ORIGINAL RESULTS
3484257 | BNMS MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-11-15 | AAA | 0.19 | 0.0749 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-11-15 | AAA | 1.5 | 0.6499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-11-15 | AAA | 0.23 | 0.1499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-11-15 | AAA | 0.86 | 0.2499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-11-15 | AAA | 0.012 | 0.1499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-11-15 | AAA | 0.28 | 0.9499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-11-15 | AAA | 0.16 | 0.1499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-11-15 | AAA | 0.26 | 0.2499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-11-15 | AAA | 0.006 | 0.0449 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-11-15 | AAA | 0.0052 | 0.0249 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-11-15 | AAA | 1.5 | 0.1499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-11-15 | AAA | 0.32 | 0.2499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-11-15 | AAA | 0.0063 | 0.1499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-11-15 | AAA | 0.096 | 0.0249 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-11-15 | AAA | 0.069 | 0.0449 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-11-15 | AAA | 0.11 | 0.1499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-11-15 | AAA | 0.0061 | 0.0249 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-11-15 | AAA | 0.0063 | 0.0149 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-11-15 | AAA | 0.053 | 0.2499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-11-15 | AAA | 1.4 |  |  |  | 2Q RADS (PLACED IN FINAL CHEM HOLDING FOLDER 1-2-18 - BB)
3484257 | BNMS MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-11-15 | AAA | 0.8 | 1.4999 |  |  | 2Q RADS (PLACED IN FINAL CHEM HOLDING FOLDER 1-2-18 - BB)
3484257 | BNMS MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-11-15 | AAA | 0.28 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-11-15 | AAA | 0.32 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-11-15 | AAA | 0.28 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-11-15 | AAA | 0.44 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-11-15 | AAA | 0.46 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-11-15 | AAA | 0.26 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-11-15 | AAA | 0.2 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-11-15 | AAA | 0.18 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-11-15 | AAA | 0.28 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-11-15 | AAA | 0.36 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-11-15 | AAA | 0.39 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-11-15 | AAA | 0.23 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-11-15 | AAA | 0.26 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-15 | AAA | 0.28 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-11-15 | AAA | 0.12 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-15 | AAA | 0.24 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-11-15 | AAA | 0.12 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-11-15 | AAA | 0.17 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-11-15 | AAA | 0.22 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-11-15 | AAA | 0.17 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-11-15 | AAA | 0.39 | 0.5499 |  |  | 2Q VOC (NO DETECTIONS IN THESE RESULTS) PLACED IN FINAL CHEM HOLDNIG FOLDER 1-2-18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-11-15 | AAA | 0.0069 | 0.0149 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-11-15 | AAA | 0.0071 | 0.0249 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-11-15 | AAA | 0.0068 | 0.1499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-11-15 | AAA | 0.12 | 1.4999 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 1.3 | UG/L | 249.9999 | 2017-11-15 | AAA | 1 | 1.4999 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-11-15 | AAA | 7.6 | 0.4499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-11-15 | AAA | 1.8 | 9.4999 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-11-15 | AAA | 6.5 | 6.4999 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-11-15 | AAA | 0.95 | 0.6499 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-11-15 | AAA | 0.57 | 2.4999 |  |  | 2Q SOC (1QM DAL(J QUAL:METHOX MS 53% 2274 HEX MS 52% HEP MS 61%-BIASED LOW LCS OK MATHEMATICALLY THERE IS SUFFICIENT RECOV FOR ACCEPTANCE FOR EA.)FINAL REVISION RCVD FROM BRANDON AEL 12/29/17-BB/ATR
3484257 | BNMS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-11-22 | AAA | 0.12 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-22 | AAA | 0.24 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-11-22 | AAA | 0.12 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-11-22 | AAA | 0.17 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-11-22 | AAA | 0.22 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-11-22 | AAA | 0.17 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-11-22 | AAA | 0.39 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-11-22 | AAA | 0.28 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-11-22 | AAA | 0.32 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-11-22 | AAA | 0.28 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-11-22 | AAA | 0.44 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-11-22 | AAA | 0.46 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-11-22 | AAA | 0.26 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-11-22 | AAA | 0.2 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-11-22 | AAA | 0.18 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-11-22 | AAA | 0.28 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-11-22 | AAA | 0.36 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-11-22 | AAA | 0.39 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-11-22 | AAA | 0.23 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-11-22 | AAA | 0.26 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-22 | AAA | 0.28 | 0.5499 |  |  | EXTRA 2Q VOCS (ALREADY TESTED 11/17 PREVIOUSLY)
3484257 | BNMS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2017-11-28 | AAA | 0.051 |  |  |  | NN (US WTR) NN < 48 HRS HOLDING TIME - OK (PLACED IN FINAL CHEM HOLDING FOLDER 12/28/17 - BB)
3484257 | BNMS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-11-28 | AAA | 0.053 |  |  |  | NN (US WTR) NN < 48 HRS HOLDING TIME - OK (PLACED IN FINAL CHEM HOLDING FOLDER 12/28/17 - BB)
3484257 | BNMS MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-22 | AAA | 7.6 | 0.4499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-03-22 | AAA | 1.8 | 9.4999 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-22 | AAA | 6.5 | 6.4999 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-03-22 | AAA | 0.95 | 0.6499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-22 | AAA | 0.57 | 2.4999 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-03-22 | AAA | 0.19 | 0.0749 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-03-22 | AAA | 1.5 | 0.6499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-22 | AAA | 0.23 | 0.1499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-03-22 | AAA | 1 | 1.4999 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-03-22 | AAA | 0.13 | 1.4999 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-03-22 | AAA | 0.0073 | 0.1499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-03-22 | AAA | 0.0076 | 0.0249 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-03-22 | AAA | 0.0074 | 0.0149 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-22 | AAA | 0.86 | 0.2499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-03-22 | AAA | 0.057 | 0.2499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-22 | AAA | 0.0063 | 0.0149 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-22 | AAA | 0.0061 | 0.0249 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-03-22 | AAA | 0.013 | 0.1499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-03-22 | AAA | 0.28 | 0.9499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-03-22 | AAA | 0.16 | 0.1499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-03-22 | AAA | 0.26 | 0.2499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-03-22 | AAA | 0.0065 | 0.0449 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-03-22 | AAA | 0.0056 | 0.0249 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-22 | AAA | 1.5 | 0.1499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-22 | AAA | 0.32 | 0.2499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-03-22 | AAA | 0.0068 | 0.1499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-03-22 | AAA | 0.096 | 0.0249 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-22 | AAA | 0.069 | 0.0449 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-03-22 | AAA | 0.12 | 0.1499 |  |  | 3Q SOC (2QM DALAPON) (SMP# A1802293001) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-03-27 | AAA | 2 |  |  |  | GA E84025 IN PCI/L (SMP# 1802382001) & UR E82574 IN UG/L-UR CANNOT BE ENTD AS REPORTED (UR MUST BE REPORTED IN PCI/L TO BE ENTERED) BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-03-28 | AAA | 0.2 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-03-28 | AAA | 0.26 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-03-28 | AAA | 0.19 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-03-28 | AAA | 0.32 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-03-28 | AAA | 0.24 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-03-28 | AAA | 0.34 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-03-28 | AAA | 0.21 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-03-28 | AAA | 0.32 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-03-28 | AAA | 0.27 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-03-28 | AAA | 0.46 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-28 | AAA | 0.25 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-03-28 | AAA | 0.39 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-28 | AAA | 0.25 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-03-28 | AAA | 0.35 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-03-28 | AAA | 0.15 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-03-28 | AAA | 0.2 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-03-28 | AAA | 0.2 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-03-28 | AAA | 0.21 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2018-03-28 | AAA | 0.5 | 1.4999 |  |  | R226+R228 (SMP# A1802445001)
3484257 | BNMS MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-03-28 | AAA | 0.8 | 1.4999 |  |  | R226+R228 (SMP# A1802445001)
3484257 | BNMS MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-03-28 | AAA | 3 |  |  |  | GA (SMP# A1802445002) 3/18 RADS ALL PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-03-28 | AAA | 0.21 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-03-28 | AAA | 0.45 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-03-28 | AAA | 0.48 | 0.5499 |  |  | 3Q VOC (SMP# A1802445003) PLACED IN FINAL CHEM HOLDING FOLDER 4/26/18 - BB
3484257 | BNMS MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA | 0.28 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA | 0.39 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-15 | AAA | 0.28 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA | 0.44 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-15 | AAA | 0.46 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-15 | AAA | 0.26 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA | 0.2 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-15 | AAA | 0.18 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA | 0.28 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.36 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA | 0.39 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0.3 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.23 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA | 0.26 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.28 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA | 0.12 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.24 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA | 0.12 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA | 0.17 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-15 | AAA | 0.22 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-15 | AAA | 0.17 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA | 0.32 | 0.5499 |  |  | 4Q [CARBON TETRACHLORIDE 0.3 < RDL OF 0.5 NO DETECT_JMF] (1AM DUE 2019_VP
3484257 | BNMS MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-05-22 | AAA |  | 0.0149 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-05-22 | AAA |  |  |  |  | GA R226 R228 (UR IN UG/L CANNOT BE ENTERED - GA CAN SUB FOR UR)
3484257 | BNMS MOBILE HOME PARK | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2018-05-22 | AAA |  | 1.4999 |  |  | GA R226 R228 (UR IN UG/L CANNOT BE ENTERED - GA CAN SUB FOR UR)
3484257 | BNMS MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-05-22 | AAA |  | 1.4999 |  |  | GA R226 R228 (UR IN UG/L CANNOT BE ENTERED - GA CAN SUB FOR UR)
3484257 | BNMS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-22 | AAA |  |  |  |  | 2018 DONE
3484257 | BNMS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-22 | AAA |  |  |  |  | 2018 DONE
3484257 | BNMS MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.0149 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-05-22 | AAA |  | 1.4999 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-05-22 | AAA |  | 1.4999 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-05-22 | AAA |  | 0.4499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-05-22 | AAA |  | 9.4999 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-05-22 | AAA |  | 6.4999 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-05-22 | AAA |  | 0.6499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-05-22 | AAA |  | 2.4999 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-05-22 | AAA |  | 0.0749 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-05-22 | AAA |  | 0.6499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-05-22 | AAA |  | 0.9499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-05-22 | AAA |  | 0.0449 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-05-22 | AAA |  | 0.0449 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-05-22 | AAA |  | 0.1499 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 |  |  | 3QM DALAPON
3484257 | BNMS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-08-08 | AAA |  | 1.4999 |  |  | 4 QM DALAPON. MOVE TO ANNUAL TESTING. TEST 4TH QUARTER. VP
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 84.84 | UG/L | 60.4999 | 2018-11-21 | L1 |  |  |  | 1.2 | 2950-LOT 18801 / SUBCONTRACT LAB E84589 - MOVE TO QUARTLERY SAMPLING Q SAMPLING PLAN APPROVED 1/24/18
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 57.93 | UG/L | 80.4999 | 2018-11-21 | L1 |  |  |  | 1.2 | 2950-LOT 18801 / SUBCONTRACT LAB E84589 - MOVE TO QUARTLERY SAMPLING Q SAMPLING PLAN APPROVED 1/24/18
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 0 | UG/L | 60.4999 | 2018-12-27 | L1 | 0.89 |  | 2 | 0.5 | XXX LOT 18801 XXX-DO NOT COUNT-ENTD WITH "S" FOR INFO.PURPOSES-ONLY 11/18 RSLTS COUNT FOR COMPLIANCE-NOT ALLOWED TO TK 2ND SET OF ANNUAL OR TRIENNIAL RSLTS TO AVERAGE W/1ST SET TO TRY TO LOWER AVERAGE
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | S | 0 | UG/L | 80.4999 | 2018-12-27 | L1 | 0.56 |  | 2 | 0.5 | XXX LOT 18801 XXX-DO NOT COUNT-ENTD WITH "S" FOR INFO.PURPOSES-ONLY 11/18 RSLTS COUNT FOR COMPLIANCE-NOT ALLOWED TO TK 2ND SET OF ANNUAL OR TRIENNIAL RSLTS TO AVERAGE W/1ST SET TO TRY TO LOWER AVERAGE
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.08 | UG/L | 60.4999 | 2019-03-04 | L1 | 0.91 |  | 1 | 0.8 | 1QM LOT 18801 (HAA5/E84589
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 26.55 | UG/L | 80.4999 | 2019-03-04 | L1 | 0.39 |  | 1 | 0.8 | 1QM LOT 18801 (HAA5/E84589
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.47 | UG/L | 60.4999 | 2019-03-04 | L2 | 0.91 |  | 2 | 0.8 | 1QM LOT 18841 (HAA5/E84589)
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 17.54 | UG/L | 80.4999 | 2019-03-04 | L2 | 0.39 |  | 2 | 0.8 | 1QM LOT 18841 (HAA5/E84589)
3484257 | BNMS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-04-16 | AAA
3484257 | BNMS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-16 | AAA
3484257 | BNMS MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | D | 0 | UG/L | 7.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | D | 0 | UG/L | 149.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | D | 0 | UG/L | 3.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | D | 0 | UG/L | 249.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | D | 0 | UG/L | 3.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | D | 0 | UG/L | 5.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | D | 0 | UG/L | 5.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | D | 0 | UG/L | 149.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2990 | BENZENE | D | 0 | UG/L | 1.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2991 | TOLUENE | D | 0 | UG/L | 1499.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | D | 0 | UG/L | 749.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2996 | STYRENE | D | 0 | UG/L | 149.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | D | 0 | UG/L | 74.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | D | 0 | UG/L | 74.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | D | 0 | UG/L | 10499.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | D | 0 | UG/L | 5.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | D | 0 | UG/L | 649.9999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | D | 0 | UG/L | 75.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | D | 0 | UG/L | 1.4999 | 2019-04-17 | AAA |  | 0.5499 |  |  | 1 AM (2AM DUE 4-6/19)_VP
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.73 | UG/L | 60.4999 | 2019-06-11 | L1 |  |  | 1 |  | 2QM SUBCONTRACT LABS E84589 E82535
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 78.61 | UG/L | 80.4999 | 2019-06-11 | L1 |  |  | 1 |  | 2QM SUBCONTRACT LABS E84589 E82535
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 78.77 | UG/L | 80.4999 | 2019-06-11 | L2 |  |  |  | 2.06 | 2QM
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.77 | UG/L | 60.4999 | 2019-06-11 | L2 |  |  |  | 2.06 | 2QM
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 77.67 | UG/L | 80.4999 | 2019-09-03 | L2 |  |  | 2 | 0.8 | LOT 18841
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.28 | UG/L | 60.4999 | 2019-09-03 | L1 |  |  | 1 | 0.8 | LOT 18801
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 67.32 | UG/L | 80.4999 | 2019-09-03 | L1 |  |  | 1 | 0.8 | LOT 18801
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.96 | UG/L | 60.4999 | 2019-09-03 | L2 |  |  | 2 | 0.8 | LOT 18841
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 46.05 | UG/L | 80.4999 | 2019-12-05 | L1 | 0.39 |  | 1 | 0.7 | LOT 18801
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.46 | UG/L | 60.4999 | 2019-12-05 | L2 | 0.91 |  | 2 | 0.8 | LOT 18841
3484257 | BNMS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 50.74 | UG/L | 80.4999 | 2019-12-05 | L2 | 0.39 |  | 2 | 0.8 | LOT 18841
3484257 | BNMS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-12-05 | AAA |  | 1.4999
3484257 | BNMS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.52 | UG/L | 60.4999 | 2019-12-05 | L1 | 0.91 |  | 1 | 0.7 | LOT 18801
3484431 | OCOEE PINES (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28 | UG/L | 60.4999 | 2019-07-08 | L1 |  |  | 1 | 0.9 | 1315 DUSTY PINE DR
3484431 | OCOEE PINES (CONSEC) | DBP | 2950 | TOTAL THMS | D | 43.5 | UG/L | 80.4999 | 2019-07-08 | L1 |  |  | 1 | 0.9 | 1315 DUSTY PINE DR
3484431 | OCOEE PINES (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.3 | UG/L | 60.4999 | 2019-07-08 | L2 |  |  | 2 | 0.5 | 743 BIRCH HOLLOW DR
3484431 | OCOEE PINES (CONSEC) | DBP | 2950 | TOTAL THMS | D | 48.5 | UG/L | 80.4999 | 2019-07-08 | L2 |  |  | 2 | 0.5 | 743 BIRCH HOLLOW DR
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | AAA
3490090 | BAY LAKE ESTATES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-03-25 | AAA |  | 0.4499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-03-25 | AAA |  | 6.4999 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-03-25 | AAA |  | 0.0749 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-03-25 | AAA |  | 9.4999 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR 27 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-04-20 | AAA |  | 0.9499 |  |  | 3YR 2 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-04-20 | AAA |  | 2.4999 |  |  | 3YR 2 OF 29 SOCS
3490090 | BAY LAKE ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-04-27 | AAA |  | 0.0249 |  |  | 2AM/2931 (3AM/2931 DUE 2Q 2016>>EM 1/14/16 TO D. CROUCH WITH THIS RQRMNT-BB)
3490090 | BAY LAKE ESTATES | INOR | 1052 | SODIUM | N | 26.3 | MG/L | 160.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1094 | ASBESTOS | S | 0 | MF/L | 7.4999 | 2015-07-27 | AAA |  |  |  |  | POE/D (ASB. REPORTED WITH INORG-NOT FOR COMPLIANCE PURPOSES?METHOD EPA600/R-94/134 E83079 SUBCONTRACTED TO E86795)
3490090 | BAY LAKE ESTATES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | N | 0.11 | MG/L | 10.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1010 | BARIUM | N | 0.0053 | MG/L | 2.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1025 | FLUORIDE | N | 0.18 | MG/L | 4.0499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15 & 4/15) 3AM/2931 DUE 2Q 2016 (DEREK CROUCH TOHO)
3490090 | BAY LAKE ESTATES | SEC | 1017 | CHLORIDE | N | 29.5 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1022 | COPPER | N | 0.0006 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1025 | FLUORIDE | N | 0.18 | MG/L | 2.0499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1028 | IRON | N | 0.085 | MG/L | 0.3499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.5 | LN(10) |  | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 272 | MG/L | 500.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.3 | UG/L | 60.4999 | 2015-07-28 | L1 |  |  |  | 0.6 | 6820 BAYSHORE DR. (QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | D | 33.1 | UG/L | 80.4999 | 2015-07-28 | L1 |  |  |  | 0.6 | 6820 BAYSHORE DR. (QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3490090 | BAY LAKE ESTATES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490090 | BAY LAKE ESTATES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-09-29 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3490090 | BAY LAKE ESTATES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-09-29 | AAA |  |  |  |  | RADS DUE 2021
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | N | 0.32 | MG/L | 10.4999 | 2016-02-23 | AAA
3490090 | BAY LAKE ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2016-04-28 | AAA |  | 0.0249 |  |  | 3AM/2931 (EM 8/9/16 D. CROUCH TO STOP AM/2931 ? LAST 3 YRS -0-)
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.6 | UG/L | 60.4999 | 2016-07-27 | L1 |  |  |  | 1.8 | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | D | 40.9 | UG/L | 80.4999 | 2016-07-27 | L1 |  |  |  | 1.8 | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | AAA |  |  |  |  | J QUAL ACCEPTED FOR NITRITE
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | AAA |  |  |  |  | J QUAL ACCEPTED FOR NITRITE
3490090 | BAY LAKE ESTATES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-26 | AAA |  | 0.4499
3490090 | BAY LAKE ESTATES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-26 | AAA |  | 6.4999
3490090 | BAY LAKE ESTATES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 1.4999
3490090 | BAY LAKE ESTATES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-26 | AAA |  | 0.0149
3490090 | BAY LAKE ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 2.4999
3490090 | BAY LAKE ESTATES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-26 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-26 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-26 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-26 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-26 | AAA |  | 0.0449
3490090 | BAY LAKE ESTATES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-04-20 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-04-20 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-04-20 | AAA |  | 1.4999
3490090 | BAY LAKE ESTATES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-04-20 | AAA |  | 0.6499
3490090 | BAY LAKE ESTATES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-04-20 | AAA |  | 0.6499
3490090 | BAY LAKE ESTATES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-04-20 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-04-20 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-04-20 | AAA |  | 0.0449
3490090 | BAY LAKE ESTATES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-04-20 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-05-04 | AAA |  | 0.9499
3490090 | BAY LAKE ESTATES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1025 | FLUORIDE | N | 0.19 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1052 | SODIUM | N | 23.5 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1094 | ASBESTOS | N | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | SEC | 1002 | ALUMINUM | N | 0.0075 | MG/L | 0.2499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1017 | CHLORIDE | N | 26.9 | MG/L | 250.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1025 | FLUORIDE | N | 0.19 | MG/L | 2.0499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1028 | IRON | N | 0.071 | MG/L | 0.3499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1920 | ODOR THRESHOLD | N | 2 |  | 3.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.6 | LN(10) |  | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 241 | MG/L | 500.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1010 | BARIUM | N | 0 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1005 | ARSENIC | N | 0.0009 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | N | 0.035 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | D | 130 | UG/L | 80.4999 | 2018-07-23 | L1 |  |  |  | 0.6 | 2950 - 6820 BAYSHORE DR.- PLACED ON QTRLY MONITORING-SLB
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 73.8 | UG/L | 60.4999 | 2018-07-23 | L1 |  |  |  | 0.6 | 2950 - 6820 BAYSHORE DR.- PLACED ON QTRLY MONITORING-SLB
3490090 | BAY LAKE ESTATES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA
3490090 | BAY LAKE ESTATES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.5 | UG/L | 60.4999 | 2018-10-24 | L1 |  |  |  | 2.1 | 2950-6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | D | 47.3 | UG/L | 80.4999 | 2018-10-24 | L1 |  |  |  | 2.1 | 2950-6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | S | 68.8 | UG/L | 80.4999 | 2019-01-29 | L1 | 0.32 |  | 1 | 2 | ON QM/6820 BAYSHORE DR. (HLKD TO KC) [SAMPLED ONE DAY OUTSIDE DESIGNATED WEEK. PN DUE_JMF]
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 44.8 | UG/L | 60.4999 | 2019-01-29 | L1 | 0.48 |  | 1 | 2 | ON QM/6820 BAYSHORE DR. (HLKD TO KC) [SAMPLED ONE DAY OUTSIDE DESIGNATED WEEK. PN DUE_JMF]
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | D | 71.2 | UG/L | 80.4999 | 2019-04-26 | L1 |  |  | 1 | 1.8 | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.7 | UG/L | 60.4999 | 2019-04-26 | L1 |  |  | 1 | 1.8 | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49 | UG/L | 60.4999 | 2019-07-26 | L1 |  |  |  | 1.4 | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | D | 62.1 | UG/L | 80.4999 | 2019-07-26 | L1 |  |  |  | 1.4 | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | D | 58.7 | UG/L | 80.4999 | 2019-10-25 | L1 | 0.32 |  | 1 | 2.4 | HAA5 J QUALIFIED BIASED HIGH ACCEPTED_VP
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.1 | UG/L | 60.4999 | 2019-10-25 | L1 |  |  | 1 | 2.4 | HAA5 J QUALIFIED BIASED HIGH ACCEPTED_VP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | D | 60.4 | UG/L | 80.4999 | 2015-05-26 | L2 |  |  |  | 1.4 | (10/29/15 EW HAS 8/15 DBPS FOR PROCESSING) 115 WINDY DUNE CT. (ON R.M.-TEST 4TH WK MAY 2015 & 4TH WK AUG 2015-TK.BOTH SMPS @115 WINDY DUNE CT.)
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.2 | UG/L | 60.4999 | 2015-05-26 | L2 |  |  |  | 1.4 | (10/29/15 EW HAS 8/15 DBPS FOR PROCESSING) 115 WINDY DUNE CT. (ON R.M.-TEST 4TH WK MAY 2015 & 4TH WK AUG 2015-TK.BOTH SMPS @115 WINDY DUNE CT.)
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | D | 46.2 | UG/L | 80.4999 | 2015-08-27 | L2 |  |  |  | 0.7 | 115 WINDY DUNE CT. (9/15 DBF SUBMITTED - T<60 H<45) REMAIN ON R.M. (8/17 EW HAS 2ND QTR 2016 DBPS & ANN. DB REPORT FOR ENTRY BY EM ALREADY IN OCULUS-BB)
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.5 | UG/L | 60.4999 | 2015-08-27 | L2 |  |  |  | 0.7 | 115 WINDY DUNE CT. (9/15 DBF SUBMITTED - T<60 H<45) REMAIN ON R.M. (8/17 EW HAS 2ND QTR 2016 DBPS & ANN. DB REPORT FOR ENTRY BY EM ALREADY IN OCULUS-BB)
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | AAA
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | D | 45.4 | UG/L | 80.4999 | 2016-05-23 | L2 |  |  |  | 1.1 | ANN.T/H-SITE ADDRESS 5/16(MUST TEST 115 WINDY DUNE CT. SAME SITE DURING 4TH WEEK 8/16)RESET QTR FROM 2ND QTR TO 3RD QTR & BACK FOR SYS-MONIT LOCS AS DBPS TKN EA. YR.
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.2 | UG/L | 60.4999 | 2016-05-23 | L2 |  |  |  | 1.1 | ANN.T/H-SITE ADDRESS 5/16(MUST TEST 115 WINDY DUNE CT. SAME SITE DURING 4TH WEEK 8/16)RESET QTR FROM 2ND QTR TO 3RD QTR & BACK FOR SYS-MONIT LOCS AS DBPS TKN EA. YR.
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | D | 53 | UG/L | 80.4999 | 2016-08-30 | L2 |  |  |  | 1.4 | 115 WINDY DUNE CT.
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.9 | UG/L | 60.4999 | 2016-08-30 | L2 |  |  |  | 1.4 | 115 WINDY DUNE CT.
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | AAA
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 2905 | FOAMING AGENTS | N | 0.1 |  | 0.5499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1005 | ARSENIC | N | 0.0098 | MG/L | 0.0104 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1010 | BARIUM | N | 0.012 | MG/L | 2.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1025 | FLUORIDE | N | 0.18 | MG/L | 4.0499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1052 | SODIUM | N | 22.1 | MG/L | 160.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1017 | CHLORIDE | N | 21.8 | MG/L | 250.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1025 | FLUORIDE | N | 0.18 | MG/L | 2.0499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1028 | IRON | N | 0.033 | MG/L | 0.3499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1055 | SULFATE | N | 8.7 | MG/L | 250.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.1 | LN(10) |  | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 239 | MG/L | 500.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | AAA |  |  |  |  | BVL
3490184 | TOHO BUENAVENTURA LAKES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-06-02 | AAA |  |  |  |  | DUE 2023
3490184 | TOHO BUENAVENTURA LAKES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | AAA |  | 1.4999 |  |  | DUE 2023
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | S | 55 | UG/L | 80.4999 | 2017-08-25 | L2 | 0.32 |  | 1 | 1.8 | 115 WINDY DUNE CT(NO 2Q 2017 RSLTS 8/17 HAA5S HV Q QUALIFIERS-HAA5 OVR HOLDING TM ND DB RPRT)ISSUE PN FOR MSSD 2Q'17&FOR UNAC 3Q'17 T/H.2 SETS MAKE-UP TESTS THIS SITE NDD 4Q'17.HYPRLNKD 10/24/17>SB JF
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 24.4 | UG/L | 60.4999 | 2017-08-25 | L2 | 0.48 |  | 1 | 1.8 | 115 WINDY DUNE CT(NO 2Q 2017 RSLTS 8/17 HAA5S HV Q QUALIFIERS-HAA5 OVR HOLDING TM ND DB RPRT)ISSUE PN FOR MSSD 2Q'17&FOR UNAC 3Q'17 T/H.2 SETS MAKE-UP TESTS THIS SITE NDD 4Q'17.HYPRLNKD 10/24/17>SB JF
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-28 | AAA |  | 0.2499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-28 | AAA |  | 0.0149 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-28 | AAA |  | 0.9499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-28 | AAA |  | 0.1499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-28 | AAA |  | 0.2499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-28 | AAA |  | 0.0249 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-28 | AAA |  | 0.0449 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-28 | AAA |  | 0.1499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-28 | AAA |  | 0.2499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-28 | AAA |  | 0.1499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-28 | AAA |  | 0.0249 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-28 | AAA |  | 0.0449 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-28 | AAA |  | 0.1499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | AAA |  | 0.0249 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-28 | AAA |  | 0.0149 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-28 | AAA |  | 0.2499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-28 | AAA |  | 0.1499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | AAA |  | 0.0249 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-28 | AAA |  | 0.1499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-28 | AAA |  | 1.4999 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2031 | DALAPON | N | 1 | UG/L | 249.9999 | 2017-08-28 | AAA |  | 1.4999 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-28 | AAA |  | 0.4499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-28 | AAA |  | 9.4999 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-28 | AAA |  | 6.4999 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-28 | AAA |  | 0.6499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-28 | AAA |  | 2.4999 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-28 | AAA |  | 0.0749 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-28 | AAA |  | 0.6499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-28 | AAA |  | 0.1499 |  |  | DALAPON 1.0 = RDL 1.0 NOT OVER. QUARTERLY NOT REQ'D.
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | D | 47 | UG/L | 80.4999 | 2018-06-08 | L2 | 0.32 |  | 1 | 1.1
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.2 | UG/L | 60.4999 | 2018-06-08 | L2 | 0.48 |  | 1 | 1.1
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 27.9 | UG/L | 60.4999 | 2018-08-24 | L2 |  |  |  |  | REC'D 02/26/19 KAC
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | M | 49.5 | UG/L | 80.4999 | 2018-08-24 | L2 |  |  |  |  | REC'D 02/26/19 KAC
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.7 | UG/L | 60.4999 | 2019-05-24 | L2 | 0.48 |  | 1 | 1.6 | 115 WINDY DUNE
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | D | 50.8 | UG/L | 80.4999 | 2019-05-24 | L2 | 0.32 |  | 1 | 1.6 | 115 WINDY DUNE
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | D | 55.2 | UG/L | 80.4999 | 2019-08-27 | L2 |  |  | 1 | 1 | 115 WINDY DUNE CT.
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.6 | UG/L | 60.4999 | 2019-08-27 | L2 |  |  | 1 | 1 | 115 WINDY DUNE CT.
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 20 | UG/L | 80.4999 | 2015-07-13 | L1 |  |  |  | 0.8 | CAR WASH HOSEBIB (REMAIN ON ANNUAL SINCE H>30 T/H DUE @ 7/15/16) NOTE: 2014 T/H TKN 11/14 - LATE - DID NOT QUALIFY FOR R.M.) EM 9/7/16 TO LCRAN FOR CORRECT SMP# FOR PG1 FOR 7/7/16 T/H-IN OC
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.7 | UG/L | 60.4999 | 2015-07-13 | L1 |  |  |  | 0.8 | CAR WASH HOSEBIB (REMAIN ON ANNUAL SINCE H>30 T/H DUE @ 7/15/16) NOTE: 2014 T/H TKN 11/14 - LATE - DID NOT QUALIFY FOR R.M.) EM 9/7/16 TO LCRAN FOR CORRECT SMP# FOR PG1 FOR 7/7/16 T/H-IN OC
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-07-20 | AAA |  | 0.0149 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-07-20 | AAA |  | 0.0249 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-07-20 | AAA |  | 0.1499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-07-20 | AAA |  | 1.4999 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-07-20 | AAA |  | 1.4999 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-07-20 | AAA |  | 0.4499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-07-20 | AAA |  | 9.4999 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-07-20 | AAA |  | 6.4999 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-07-20 | AAA |  | 0.6499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-07-20 | AAA |  | 2.4999 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-07-20 | AAA |  | 0.0749 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 13.1 | UG/L | 6.4999 | 2015-07-20 | AAA |  | 0.6499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-07-20 | AAA |  | 0.1499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-07-20 | AAA |  | 0.2499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-07-20 | AAA |  | 0.1499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-07-20 | AAA |  | 0.9499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-07-20 | AAA |  | 0.1499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-07-20 | AAA |  | 0.2499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-07-20 | AAA |  | 0.0449 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-07-20 | AAA |  | 0.0249 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-07-20 | AAA |  | 0.1499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-07-20 | AAA |  | 0.2499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-07-20 | AAA |  | 0.1499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-07-20 | AAA |  | 0.0249 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-07-20 | AAA |  | 0.0449 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-07-20 | AAA |  | 0.1499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-07-20 | AAA |  | 0.0249 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-07-20 | AAA |  | 0.0149 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-07-20 | AAA |  | 0.2499 |  |  | 3YR SOC (1QM/2039 12/15 PHTHALATE 13.1 > MCL 7/15>EM 9/18/15 TO OWNER & L. CRANDALL) >>>>>12/21/15 EW HAS 11/15 PHTHALATE FOR PROCESSING
3490265 | COLONIAL MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-07-20 | AAA |  |  |  |  | RADS DUE 2021
3490265 | COLONIAL MOBILE HOME PARK | RAD | 4020 | RADIUM-226 | N | 1.7 | PCI/L | 3.4999 | 2015-07-20 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3490265 | COLONIAL MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-07-20 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.0091 | MG/L | 2.4999 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 20.2 | MG/L | 160.4999 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-20 | AAA |  |  |  |  | 15DON/16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 27 | MG/L | 250.4999 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1028 | IRON | N | 0.0853 | MG/L | 0.3499 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 1.15 | MG/L | 250.4999 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.0144 | MG/L | 5.4999 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1905 | COLOR | N | 10 | COLOR UNITS | 15.4999 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.08 | LN(10) |  | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 442 | MG/L | 500.4999 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-20 | AAA |  |  |  |  | NO MCL IN SECONDARIES
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-20 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-11-16 | AAA |  | 0.6499 |  |  | 1QM/2039 (2QM/2039 3/16) LES CRANDALL (***ORIG. HIT OVER MCL)
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2016-01-18 | AAA |  | 0.6499 |  |  | 2QM/2039 (3QM/2039 DUE 6/16 4QM/2039 DUE 9/16) **ORIG 7/15 HIT OVER MCL
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 5.48 | UG/L | 6.4999 | 2016-04-18 | AAA |  | 0.6499 |  |  | 3QM/2039 (4QM/2039 DUE 9/16) 6/16 RAA=4.645 (MCL=6). **ORIG 7/15 HIT OVER MCL (5/27/16 REFERRED TO WP JF NJH)
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 41.2 | UG/L | 80.4999 | 2016-07-07 | L1 | 0.5 |  | 1 | 1.1 | CAR WASH HOSEBIB (9/7/16 EM TO QTRLY T/H DUE TO HAA5 73.3 UG/L TO LES CRANDALL) ALL REVISIONS RCVD & IN OC
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 73.3 | UG/L | 60.4999 | 2016-07-07 | L1 | 0.5 |  | 1 | 1.1 | CAR WASH HOSEBIB (9/7/16 EM TO QTRLY T/H DUE TO HAA5 73.3 UG/L TO LES CRANDALL) ALL REVISIONS RCVD & IN OC
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2016-07-07 | AAA | 0.6 | 0.6499 |  |  | 4QM/2039 (9/16 9/16 RAA=1.37 MCL=6). LAST 4 2039 < MCL. STOP QM/2039. 1AM/2039 3Q'17>9/14/16 EM TO LES CRANDALL-BB. **ORIG 7/15 HIT OVER MCL (5/27/16 REFERRED TO WP JF NJH)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-07-07 | AAA | 0.2 |  |  |  | NN(IN OC)-16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-07-07 | AAA | 0.2 |  |  |  | NN(IN OC)-16:2QM/2039 3/16 - 2039 13.1 715 (>MCL)>EM 9/18/15>L.CRANDALL>PER 11/11/15 EM FR. L.CRANDALL HE IS TKNG 2039 "NXT WK"-BB T/H DUE @ 7/15/16 (LES CRANDALL)
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.4 | UG/L | 60.4999 | 2016-10-24 | L1 |  |  |  | 2 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 31.4 | UG/L | 80.4999 | 2016-10-24 | L1 |  |  |  | 2 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.5 | UG/L | 60.4999 | 2017-01-19 | L1 |  |  |  | 1.2 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 35.9 | UG/L | 80.4999 | 2017-01-19 | L1 |  |  |  | 1.2 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 50.9 | UG/L | 60.4999 | 2017-05-11 | L1 |  |  |  | 1.9 | CAR WASH HOSEBIB (RAA TTHM - 58.6; HAA5 39.5) - PAF OEL VALUE = 79.825 - NO REPORT REQUIRED (ATR) - REPEAT CALCULATIONS ON SPREADSHEET
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 126 | UG/L | 80.4999 | 2017-05-11 | L1 |  |  |  | 1.9 | CAR WASH HOSEBIB (RAA TTHM - 58.6; HAA5 39.5) - PAF OEL VALUE = 79.825 - NO REPORT REQUIRED (ATR) - REPEAT CALCULATIONS ON SPREADSHEET
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 47.4 | UG/L | 60.4999 | 2017-08-14 | L1 |  |  |  | 1.6 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 36.6 | UG/L | 80.4999 | 2017-08-14 | L1 |  |  |  | 1.6 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-08-14 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-08-14 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-11-20 | AAA |  | 0.6499
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | N | 7.12 | UG/L | 60.4999 | 2017-12-18 | L1
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | N | 7.5 | UG/L | 80.4999 | 2017-12-18 | L1
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 56.1 | UG/L | 80.4999 | 2018-02-12 | L1 |  |  |  | 3.1 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 57.7 | UG/L | 60.4999 | 2018-02-12 | L1 |  |  |  | 3.1 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-04-23 | AAA |  | 0.6499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-05-15 | AAA |  | 0.0249
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-05-15 | AAA |  | 0.1499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-05-15 | AAA |  | 6.4999
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-05-15 | AAA |  | 0.6499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA |  | 2.4999
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-05-15 | AAA |  | 0.0749
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-05-15 | AAA |  | 0.6499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-05-15 | AAA |  | 0.1499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-05-15 | AAA |  | 0.2499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-05-15 | AAA |  | 0.1499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-05-15 | AAA |  | 0.9499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.1499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-05-15 | AAA |  | 0.2499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-05-15 | AAA |  | 0.0449
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-05-15 | AAA |  | 0.0249
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.1499
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.7 | UG/L | 60.4999 | 2018-05-15 | L1 |  |  |  | 1.4 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 39.6 | UG/L | 80.4999 | 2018-05-15 | L1 |  |  |  | 1.4 | CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 1.4999
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA |  | 1.4999
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-05-15 | AAA |  | 0.4499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 9.4999
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-05-15 | AAA |  | 0.2499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.1499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-05-15 | AAA |  | 0.0249
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.0449
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-05-15 | AAA |  | 0.1499
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.0078 | MG/L | 2.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0.0035 | MG/L | 0.1499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 25.1 | MG/L | 160.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-05-15 | AAA |  | 0.0249
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-05-15 | AAA |  | 0.0149
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-05-15 | AAA |  | 0.2499
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 28.2 | MG/L | 250.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0.0066 | MG/L | 1.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1028 | IRON | N | 0.102 | MG/L | 0.3499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0.001 | MG/L | 0.1499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 1.21 | MG/L | 250.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.014 | MG/L | 5.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.31 | LN(10) |  | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 336 | MG/L | 500.4999 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0.202 |  | 0.5499 | 2018-05-15 | AAA
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-05-15 | AAA |  | 0.0149
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 4.63 | UG/L | 80.4999 | 2018-07-09 | L1 |  |  |  | 1.2 | 2950-CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.3 | UG/L | 60.4999 | 2018-07-09 | L1 |  |  |  | 1.2 | 2950-CAR WASH HOSEBIB
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.5 | UG/L | 60.4999 | 2018-10-15 | L1 |  |  |  | 0.4 | 2950-CAR WASH HOSEBIB (HAA5 LRAA = 29.55 TTHM LRAA 30.56) - REDUCED TO DUAL SAMPLE @ L1 IN 1ST Q. KAC EMAILED FOR NEW PLAN 2/7/9_JMF
3490265 | COLONIAL MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 21.9 | UG/L | 80.4999 | 2018-10-15 | L1 |  |  |  | 0.4 | 2950-CAR WASH HOSEBIB (HAA5 LRAA = 29.55 TTHM LRAA 30.56) - REDUCED TO DUAL SAMPLE @ L1 IN 1ST Q. KAC EMAILED FOR NEW PLAN 2/7/9_JMF
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-06-17 | AAA
3490265 | COLONIAL MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-06-17 | AAA
3490265 | COLONIAL MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2019-06-17 | AAA |  | 0.6499
3490293 | MILL CREEK RV RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-07-07 | AAA |  | 0.0149 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-07-07 | AAA |  | 0.0249 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-07-07 | AAA |  | 0.1499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-07-07 | AAA |  | 1.4999 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-07-07 | AAA |  | 1.4999 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-07-07 | AAA |  | 0.4499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-07-07 | AAA |  | 9.4999 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-07-07 | AAA |  | 0.1499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-07-07 | AAA |  | 0.0249 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-07-07 | AAA |  | 0.0449 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-07-07 | AAA |  | 0.1499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-07-07 | AAA |  | 0.0249 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-07-07 | AAA |  | 0.0149 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-07-07 | AAA |  | 0.2499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-07-07 | AAA |  | 6.4999 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-07-07 | AAA |  | 0.6499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-07-07 | AAA |  | 2.4999 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-07-07 | AAA |  | 0.0749 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-07-07 | AAA |  | 0.6499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-07-07 | AAA |  | 0.1499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-07-07 | AAA |  | 0.2499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-07-07 | AAA |  | 0.1499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-07-07 | AAA |  | 0.9499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-07-07 | AAA |  | 0.1499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-07-07 | AAA |  | 0.2499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-07-07 | AAA |  | 0.0449 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-07-07 | AAA |  | 0.0249 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-07-07 | AAA |  | 0.1499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-07-07 | AAA |  | 0.2499 |  |  | 3YR SOCS (NO DETECTIONS)- SOC WAIVER APPROVED. NEXT SAMPLE 2021
3490293 | MILL CREEK RV RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1010 | BARIUM | N | 0.0079 | MG/L | 2.4999 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1020 | CHROMIUM | N | 0.0005 | MG/L | 0.1499 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1025 | FLUORIDE | N | 0.27 | MG/L | 4.0499 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1030 | LEAD | N | 0.0003 | MG/L | 0.0154 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1052 | SODIUM | N | 14 | MG/L | 160.4999 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-07 | AAA |  |  |  |  | TOM FELTON NOW OPR 2/16 (6/24/16 EW HAS 3/16 NN FROM TOM FELTON BY EM)
3490293 | MILL CREEK RV RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1017 | CHLORIDE | N | 8.4 | MG/L | 250.4999 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1022 | COPPER | N | 0.0061 | MG/L | 1.4999 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1025 | FLUORIDE | N | 0.27 | MG/L | 2.0499 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1028 | IRON | N | 0.119 | MG/L | 0.3499 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1032 | MANGANESE | N | 0.0055 | MG/L | 0.0549 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1055 | SULFATE | N | 0.48 | MG/L | 250.4999 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1095 | ZINC | N | 0.0062 | MG/L | 5.4999 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.9 | LN(10) |  | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 180 | MG/L | 500.4999 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-07 | AAA |  |  |  |  | NO MCLS
3490293 | MILL CREEK RV RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-07 | AAA |  | 0.5499 |  |  | 3YR VOCS (NO DETECTIONS)
3490293 | MILL CREEK RV RESORT | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2015-07-13 | L1 |  |  |  | 0.3 | LOT 505 (QUALIFIES FOR R.M. - NEXT T/H DUE 2ND WEEK JULY 2018) <500
3490293 | MILL CREEK RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2015-07-13 | L1 |  |  |  | 0.3 | LOT 505 (QUALIFIES FOR R.M. - NEXT T/H DUE 2ND WEEK JULY 2018) <500
3490293 | MILL CREEK RV RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-03-02 | AAA |  |  |  |  | NN (TOM FELTON)
3490293 | MILL CREEK RV RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-03-02 | AAA |  |  |  |  | NN (TOM FELTON)
3490293 | MILL CREEK RV RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-10-26 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-10-26 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 214 | MG/L | 500.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1010 | BARIUM | N | 0.0068 | MG/L | 2.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1020 | CHROMIUM | N | 0.0026 | MG/L | 0.1499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1030 | LEAD | N | 0.001 | MG/L | 0.0154 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1052 | SODIUM | N | 18.4 | MG/L | 160.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1017 | CHLORIDE | N | 17.2 | MG/L | 250.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1022 | COPPER | N | 0.005 | MG/L | 1.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1028 | IRON | N | 0.0851 | MG/L | 0.3499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.31 | LN(10) |  | 2018-05-15 | AAA
3490293 | MILL CREEK RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.41 | UG/L | 60.4999 | 2018-07-11 | L1 |  |  |  | 0.4
3490293 | MILL CREEK RV RESORT | DBP | 2950 | TOTAL THMS | D | 0.85 | UG/L | 80.4999 | 2018-07-11 | L1 |  |  |  | 0.4
3490293 | MILL CREEK RV RESORT | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-09-30 | AAA |  | 3.4999 |  |  | DUE 2027
3490293 | MILL CREEK RV RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-09-30 | AAA |  |  |  |  | DUE 2027
3490293 | MILL CREEK RV RESORT | RAD | 4006 | COMBINED URANIUM | N | 0 | PCI/L | 20.4999 | 2018-09-30 | AAA |  | 0.667 |  |  | DUE 2027
3490293 | MILL CREEK RV RESORT | RAD | 4020 | RADIUM-226 | N | 0.4 | PCI/L | 3.4999 | 2018-09-30 | AAA |  | 1.4999 |  |  | DUE 2027
3490293 | MILL CREEK RV RESORT | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-09-30 | AAA |  | 1.4999 |  |  | DUE 2027
3490293 | MILL CREEK RV RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-09-10 | AAA
3490293 | MILL CREEK RV RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-09-10 | AAA
3490314 | CYPRESS COVE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-07-21 | AAA |  |  |  |  | NN (IN OC) 15:<3300>10/5/15 J.SCYPHERS RESAMPLING COL ODOR PH F.AG.SINCE OUT OF HOLD>MID-FLA SUBBED TO E84129) T/H 9/15>EM 9/28/15 EM TO JIM SCYPHERS & CC'D TO OWNERS RADS 2018 (JIM SCYPHERS)
3490314 | CYPRESS COVE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-21 | AAA |  |  |  |  | NN (IN OC) 15:<3300>10/5/15 J.SCYPHERS RESAMPLING COL ODOR PH F.AG.SINCE OUT OF HOLD>MID-FLA SUBBED TO E84129) T/H 9/15>EM 9/28/15 EM TO JIM SCYPHERS & CC'D TO OWNERS RADS 2018 (JIM SCYPHERS)
3490314 | CYPRESS COVE | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-08-25 | AAA |  | 1.4999 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-08-25 | AAA |  | 1.4999 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-08-25 | AAA |  | 0.4499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-08-25 | AAA |  | 9.4999 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-08-25 | AAA |  | 6.4999 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-08-25 | AAA |  | 0.6499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-08-25 | AAA |  | 2.4999 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-08-25 | AAA |  | 0.0749 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-08-25 | AAA |  | 0.6499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-08-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-08-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-08-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-08-25 | AAA |  | 0.9499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-08-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-08-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-08-25 | AAA |  | 0.0449 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-08-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-08-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-08-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-08-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-08-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-08-25 | AAA |  | 0.0449 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-08-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-08-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-08-25 | AAA |  | 0.0149 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-08-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1010 | BARIUM | N | 2 | MG/L | 2.4999 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1025 | FLUORIDE | N | 0.088 | MG/L | 4.0499 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1036 | NICKEL | N | 0.0008 | MG/L | 0.1499 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1052 | SODIUM | N | 7 | MG/L | 160.4999 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SEC | 1055 | SULFATE | N | 8.6 | MG/L | 250.4999 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 140 | MG/L | 500.4999 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0.39 | UG/L | 60.4999 | 2015-08-25 | L1 |  |  |  | 0.4 | WASTEWATER TREATMENT TAP (ON R.M. - NEXT T/H DUE JULY 2018)
3490314 | CYPRESS COVE | DBP | 2950 | TOTAL THMS | D | 1.6 | UG/L | 80.4999 | 2015-08-25 | L1 |  |  |  | 0.4 | WASTEWATER TREATMENT TAP (ON R.M. - NEXT T/H DUE JULY 2018)
3490314 | CYPRESS COVE | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-08-25 | AAA |  |  |  |  | NO MCLS (10/5/15 J. SCYPHERS RETESTING COLOR ODOR PH F. AGENTS SINCE OUT OF HOLD-BB)
3490314 | CYPRESS COVE | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SEC | 1017 | CHLORIDE | N | 8.3 | MG/L | 250.4999 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SEC | 1022 | COPPER | N | 0.0003 | MG/L | 1.4999 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-08-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SEC | 1025 | FLUORIDE | N | 0.088 | MG/L | 2.0499 | 2015-08-25 | AAA |  |  |  |  | 11/23 ASKED SCYPHERS TO HV MID-FLA LAB REPORT PH BY ITSELF- 8/15 COLOR ODOR AND FOAMING AGENTS OUT OF HOLD PER J. SCYPHERS - HE'S RESAMPLING. PH NOT REPORTED YET.
3490314 | CYPRESS COVE | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-08-25 | AAA |  | 0.0149 |  |  | 3YR SOC
3490314 | CYPRESS COVE | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-08-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3490314 | CYPRESS COVE | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3490314 | CYPRESS COVE | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.71 | LN(10) |  | 2015-10-08 | AAA |  |  |  |  | PH (1 OF 14 SECONDARIES) IN OC
3490314 | CYPRESS COVE | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-08 | AAA | 0.048 |  |  |  | COLOR ODOR F. AGENTS (3 OF 14 SECONDARIES) IN OC
3490314 | CYPRESS COVE | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-08 | AAA | 1 |  |  |  | COLOR ODOR F. AGENTS (3 OF 14 SECONDARIES) IN OC
3490314 | CYPRESS COVE | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-10-08 | AAA | 5 |  |  |  | COLOR ODOR F. AGENTS (3 OF 14 SECONDARIES) IN OC
3490314 | CYPRESS COVE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-11-15 | AAA
3490314 | CYPRESS COVE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-11-15 | AAA
3490314 | CYPRESS COVE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-11-15 | AAA
3490314 | CYPRESS COVE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-11-15 | AAA
3490314 | CYPRESS COVE | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-06-27 | AAA |  | 0.0449 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-06-27 | AAA |  | 0.0249 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-06-27 | AAA |  | 0.0249 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-06-27 | AAA |  | 0.0149 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-06-27 | AAA |  | 0.2499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.9 | PCI/L | 15.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/2019. DUE 2027
3490314 | CYPRESS COVE | RAD | 4006 | COMBINED URANIUM | N | 0 | PCI/L | 20.4999 | 2018-06-27 | AAA |  | 0.667 |  |  | RECEIVED 1/23/2019. DUE 2027
3490314 | CYPRESS COVE | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2018-06-27 | AAA |  | 1.4999 |  |  | RECEIVED 1/23/2019. DUE 2027
3490314 | CYPRESS COVE | RAD | 4030 | RADIUM-228 | N | 0.9 | PCI/L | 2.4999 | 2018-06-27 | AAA |  | 1.4999 |  |  | RECEIVED 1/23/2019. DUE 2027
3490314 | CYPRESS COVE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1015 | CADMIUM | N | 0.001 | MG/L | 0.0055 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1025 | FLUORIDE | N | 0.081 | MG/L | 4.0499 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1052 | SODIUM | N | 5.85 | MG/L | 160.4999 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-06-27 | AAA
3490314 | CYPRESS COVE | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1017 | CHLORIDE | N | 7.58 | MG/L | 250.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1022 | COPPER | N | 0.006 | MG/L | 1.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1025 | FLUORIDE | N | 0.081 | MG/L | 2.0499 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1032 | MANGANESE | N | 0.001 | MG/L | 0.0549 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1055 | SULFATE | N | 8.53 | MG/L | 250.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.17 | LN(10) |  | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 128 | MG/L | 500.4999 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-06-27 | AAA |  |  |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-06-27 | AAA |  | 0.0149 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-06-27 | AAA |  | 0.0249 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-06-27 | AAA |  | 0.1499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-06-27 | AAA |  | 1.4999 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-06-27 | AAA |  | 1.4999 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-06-27 | AAA |  | 0.4499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-06-27 | AAA |  | 9.4999 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-06-27 | AAA |  | 6.4999 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-06-27 | AAA |  | 0.6499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-06-27 | AAA |  | 2.4999 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-06-27 | AAA |  | 0.0749 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-06-27 | AAA |  | 0.6499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-06-27 | AAA |  | 0.1499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-06-27 | AAA |  | 0.2499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-06-27 | AAA |  | 0.1499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-06-27 | AAA |  | 0.9499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-06-27 | AAA |  | 0.1499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-06-27 | AAA |  | 0.2499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-06-27 | AAA |  | 0.0449 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-06-27 | AAA |  | 0.0249 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-06-27 | AAA |  | 0.1499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-06-27 | AAA |  | 0.2499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-06-27 | AAA |  | 0.1499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-06-27 | AAA |  | 0.1499 |  |  | RECEIVED 1/23/19
3490314 | CYPRESS COVE | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10 | UG/L | 60.4999 | 2018-07-18 | L1 |  |  | 18070610 | 0.3
3490314 | CYPRESS COVE | DBP | 2950 | TOTAL THMS | D | 36.5 | UG/L | 80.4999 | 2018-07-18 | L1 |  |  | 18070610 | 0.3
3490314 | CYPRESS COVE | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-07-18 | AAA |  | 0.5499
3490314 | CYPRESS COVE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-07-22 | AAA
3490314 | CYPRESS COVE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-07-22 | AAA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-01-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-01-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-01-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 53.9 | UG/L | 80.4999 | 2015-01-22 | DBP-4 |  |  |  | 1.7 | 145 EAST LAKESHORE KISS.(NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 51.4 | UG/L | 60.4999 | 2015-01-22 | DBP-4 |  |  |  | 1.7 | 145 EAST LAKESHORE KISS.(NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-01-22 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 36.1 | UG/L | 80.4999 | 2015-01-22 | DBP-3 |  |  |  | 2.1 | 120 SIMPSON RD. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 90.9 | UG/L | 60.4999 | 2015-01-22 | DBP-3 |  |  |  | 2.1 | 120 SIMPSON RD. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 51.7 | UG/L | 80.4999 | 2015-01-22 | DBP-2 |  |  |  | 1.2 | 1400 RIVIERA DR. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 63.4 | UG/L | 60.4999 | 2015-01-22 | DBP-2 |  |  |  | 1.2 | 1400 RIVIERA DR. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 45.4 | UG/L | 80.4999 | 2015-01-22 | DBP-6 |  |  |  | 1.5 | 2713 RISMEN CT. KISS.(NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 85 | UG/L | 60.4999 | 2015-01-22 | DBP-6 |  |  |  | 1.5 | 2713 RISMEN CT. KISS.(NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 46.3 | UG/L | 80.4999 | 2015-01-22 | DBP-1 |  |  |  | 1 | 3200 SERALAGO BLVD. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44 | UG/L | 60.4999 | 2015-01-22 | DBP-1 |  |  |  | 1 | 3200 SERALAGO BLVD. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41 | UG/L | 60.4999 | 2015-01-22 | DBP-5 |  |  |  | 0.9 | 1721 BRASSIE CT. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 40.6 | UG/L | 80.4999 | 2015-01-22 | DBP-5 |  |  |  | 0.9 | 1721 BRASSIE CT. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-01-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-01-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 1.1 | MG/L | 10.4999 | 2015-01-28 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-02-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-02-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-02-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-02-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-02-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-02-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.2 | UG/L | 60.4999 | 2015-02-27 | DBP-3 |  |  |  | 2.5 | 120 SIMPSON RD. KISS. (2 RSLTS 3/15 QTR) 3/15 LRAA/T=34.6125 LRAA/H=40.7125. NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 32.8 | UG/L | 80.4999 | 2015-02-27 | DBP-3 |  |  |  | 2.5 | 120 SIMPSON RD. KISS. (2 RSLTS 3/15 QTR) 3/15 LRAA/T=34.6125 LRAA/H=40.7125. NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 46.3 | UG/L | 80.4999 | 2015-02-27 | DBP-6 |  |  |  | 1.6 | (>100 000) 2713 RISMEN CT. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 49.3 | UG/L | 80.4999 | 2015-02-27 | DBP-2 |  |  |  | 1.4 | 1400 RIVIERA DR. KISS. (2 RSLTS 3/15 QTR) 3/15 LRAA/T=55.3 LRAA/H=56.3875. NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.3 | UG/L | 60.4999 | 2015-02-27 | DBP-2 |  |  |  | 1.4 | 1400 RIVIERA DR. KISS. (2 RSLTS 3/15 QTR) 3/15 LRAA/T=55.3 LRAA/H=56.3875. NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.9 | UG/L | 60.4999 | 2015-02-27 | DBP-6 |  |  |  | 1.6 | (>100 000) 2713 RISMEN CT. KISS. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-03-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-03-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-03-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-03-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-03-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-03-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-04-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-04-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-04-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36 | UG/L | 60.4999 | 2015-04-21 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS. (SYS. DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 62.4 | UG/L | 80.4999 | 2015-04-21 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS. (SYS. DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 62.5 | UG/L | 60.4999 | 2015-04-21 | DBP-2 |  |  |  | 0.8 | 1400 RIVIERA DR. KISS. (2 RSLTS 3/15 QTR) 6/15 LRAA/T=58.525 LRAA/H=63.6375) 6/15 HAA5 LRAA MCL VIOL NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 67.6 | UG/L | 80.4999 | 2015-04-21 | DBP-2 |  |  |  | 0.8 | 1400 RIVIERA DR. KISS. (2 RSLTS 3/15 QTR) 6/15 LRAA/T=58.525 LRAA/H=63.6375) 6/15 HAA5 LRAA MCL VIOL NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.1 | UG/L | 60.4999 | 2015-04-21 | DBP-3 |  |  |  | 1.3 | 120 SIMPSON RD. KISS. (2 RSLTS 3/15 QTR) SYS. DOES NOT QUALIFY FOR R.M. (NO T OR H OE EXC 6/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 43.7 | UG/L | 80.4999 | 2015-04-21 | DBP-3 |  |  |  | 1.3 | 120 SIMPSON RD. KISS. (2 RSLTS 3/15 QTR) SYS. DOES NOT QUALIFY FOR R.M. (NO T OR H OE EXC 6/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29 | UG/L | 60.4999 | 2015-04-21 | DBP-5 |  |  |  | 0.5 | 1721 BRASSIE CT. KISS. (SYS. DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55 | UG/L | 80.4999 | 2015-04-21 | DBP-4 |  |  |  | 0.9 | 145 EAST LAKESHORE KISS. (SYS. DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 54.8 | UG/L | 60.4999 | 2015-04-21 | DBP-6 |  |  |  | 0.8 | 2713 RISMEN CT. KISS.(SYS.DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15(7/29/15EM NOTIF TO WP JF ON 6/15 HAA5 LRAA MCL VIO AT 1400 RIVIERA DR. TOLD THEM THEY MAY BE ABLE TO HANDLE OPERATIONALLY.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 64.8 | UG/L | 80.4999 | 2015-04-21 | DBP-6 |  |  |  | 0.8 | 2713 RISMEN CT. KISS.(SYS.DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15(7/29/15EM NOTIF TO WP JF ON 6/15 HAA5 LRAA MCL VIO AT 1400 RIVIERA DR. TOLD THEM THEY MAY BE ABLE TO HANDLE OPERATIONALLY.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2015-04-21 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 49.7 | UG/L | 80.4999 | 2015-04-21 | DBP-5 |  |  |  | 0.5 | 1721 BRASSIE CT. KISS. (SYS. DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 51.9 | UG/L | 60.4999 | 2015-04-21 | DBP-4 |  |  |  | 0.9 | 145 EAST LAKESHORE KISS. (SYS. DOES NOT QUALIFY FOR R.M.) NO T OR H OE EXC 6/15
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-04-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-04-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-05-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-05-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-05-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-05-21 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-05-25 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-05-25 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-06-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-06-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2015-06-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-06-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-06-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-06-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-07-08 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-07-08 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-07-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-07-22 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-07-22 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-07-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.4 | UG/L | 60.4999 | 2015-07-24 | DBP-5 |  |  |  | 0.5 | 1721 BRASSIE CT. KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 30 | UG/L | 80.4999 | 2015-07-24 | DBP-5 |  |  |  | 0.5 | 1721 BRASSIE CT. KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.6 | UG/L | 60.4999 | 2015-07-24 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 43.2 | UG/L | 80.4999 | 2015-07-24 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 127 | UG/L | 60.4999 | 2015-07-24 | DBP-6 |  |  |  | 1.7 | (EM 10/9/15>JF WP FOR NEW LRAA H MCL VIOL FOR 9/15 QTR-RISMEN SITE-SNT APPRVD PN 10/9/15-30 DAYS ISSUANCE>AMBER)2713 RISMEN CT. KISS.(RETESTING W/IN QTR AT THIS SITE-DBP & DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 30.3 | UG/L | 80.4999 | 2015-07-24 | DBP-4 |  |  |  | 1.8 | 145 EAST LAKESHORE KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45.1 | UG/L | 60.4999 | 2015-07-24 | DBP-4 |  |  |  | 1.8 | 145 EAST LAKESHORE KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 23.6 | UG/L | 80.4999 | 2015-07-24 | DBP-3 |  |  |  | 1.9 | 120 SIMPSON RD. KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.1 | UG/L | 60.4999 | 2015-07-24 | DBP-3 |  |  |  | 1.9 | 120 SIMPSON RD. KISS. (DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 39.5 | UG/L | 80.4999 | 2015-07-24 | DBP-2 |  |  |  | 1.6 | 1400 RIVIERA DR. KISS. (RETESTING W/IN THE QTR AT THIS SITE - DBP TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 88 | UG/L | 60.4999 | 2015-07-24 | DBP-2 |  |  |  | 1.6 | 1400 RIVIERA DR. KISS. (RETESTING W/IN THE QTR AT THIS SITE - DBP TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 38.2 | UG/L | 80.4999 | 2015-07-24 | DBP-6 |  |  |  | 1.7 | (EM 10/9/15>JF WP FOR NEW LRAA H MCL VIOL FOR 9/15 QTR-RISMEN SITE-SNT APPRVD PN 10/9/15-30 DAYS ISSUANCE>AMBER)2713 RISMEN CT. KISS.(RETESTING W/IN QTR AT THIS SITE-DBP & DBF TO BE SENT BY 10/10/15)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-08-10 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-08-10 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-08-10 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-08-25 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-08-25 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-08-25 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 58.1 | UG/L | 60.4999 | 2015-09-03 | DBP-6 |  |  |  | 1.4 | 2713 RISMEN CT KISS(9/15LRAA/T=@45.5 LRAA/H=62.225)9/15QTR AVGOF2:T@33.9 H 92.55(NEW H MCL VIO>RISMEN9/15 QTR)APPRVD PN>10/9/15>AMBER>NWSPPR&MAIL-ISSUE30DAYS.9/15 H OE REPORT RCVD-2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 29.6 | UG/L | 80.4999 | 2015-09-03 | DBP-6 |  |  |  | 1.4 | 2713 RISMEN CT KISS(9/15LRAA/T=@45.5 LRAA/H=62.225)9/15QTR AVGOF2:T@33.9 H 92.55(NEW H MCL VIO>RISMEN9/15 QTR)APPRVD PN>10/9/15>AMBER>NWSPPR&MAIL-ISSUE30DAYS.9/15 H OE REPORT RCVD-2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 40.5 | UG/L | 80.4999 | 2015-09-03 | DBP-2 |  |  |  | 0.4 | 1400 RIVIERA DR. KISS. (9/15 LRAA/T=@51.2 LRAA/H=57.95) 9/15 QTR AVG OF 2: T@40 H 68.35 (NO MCL VIOL FOR RIVIERA FOR 9/15 QTR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.7 | UG/L | 60.4999 | 2015-09-03 | DBP-2 |  |  |  | 0.4 | 1400 RIVIERA DR. KISS. (9/15 LRAA/T=@51.2 LRAA/H=57.95) 9/15 QTR AVG OF 2: T@40 H 68.35 (NO MCL VIOL FOR RIVIERA FOR 9/15 QTR
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2015-09-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2015-09-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-09-07 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-09-21 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-09-21 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2015-09-21 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-07 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-10-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 91.1 | UG/L | 80.4999 | 2015-10-22 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.3 | UG/L | 60.4999 | 2015-10-22 | DBP-2 |  |  |  | 0.7 | 1400 RIVIERA DR. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF'S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 74.8 | UG/L | 80.4999 | 2015-10-22 | DBP-2 |  |  |  | 0.7 | 1400 RIVIERA DR. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF'S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.2 | UG/L | 60.4999 | 2015-10-22 | DBP-3 |  |  |  | 1.2 | 120 SIMPSON RD. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 62.2 | UG/L | 80.4999 | 2015-10-22 | DBP-3 |  |  |  | 1.2 | 120 SIMPSON RD. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.6 | UG/L | 60.4999 | 2015-10-22 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 71.8 | UG/L | 80.4999 | 2015-10-22 | DBP-5 |  |  |  | 0.5 | 1721 BRASSIE CT. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.9 | UG/L | 60.4999 | 2015-10-22 | DBP-5 |  |  |  | 0.5 | 1721 BRASSIE CT. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 72.8 | UG/L | 80.4999 | 2015-10-22 | DBP-6 |  |  |  | 0.8 | 2713 RISMEN CT. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF'S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. (12/15 LRAA/H-RISMEN=58.55 <MCL)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-10-22 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-22 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.4 | UG/L | 60.4999 | 2015-10-22 | DBP-6 |  |  |  | 0.8 | 2713 RISMEN CT. KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF'S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. (12/15 LRAA/H-RISMEN=58.55 <MCL)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44.8 | UG/L | 60.4999 | 2015-10-22 | DBP-4 |  |  |  | 0.6 | 145 EAST LAKESHORE KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 90.7 | UG/L | 80.4999 | 2015-10-22 | DBP-4 |  |  |  | 0.6 | 145 EAST LAKESHORE KISS. (WITH 12/15 DBF-NO LRAA MCLS SHOWN) JF?S EM 11/30/15>WP DLK BB: LOOKS LIKE THEY WENT UNDER MCL & CAN LET THEM GO FOR NOW. TO BB NOTIFY ALL IF OVER MCL AGAIN.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-11-06 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-11-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-11-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-11-25 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-11-25 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-11-25 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-12-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-12-07 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-12-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-12-27 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-12-29 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-12-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-01-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-01-06 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-01-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-01-22 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-01-23 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-01-25 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.7 | UG/L | 60.4999 | 2016-01-28 | DBP-1 |  |  |  | 1.7 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 48.2 | UG/L | 80.4999 | 2016-01-28 | DBP-5 |  |  |  | 0.8 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.2 | UG/L | 60.4999 | 2016-01-28 | DBP-5 |  |  |  | 0.8 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 35.7 | UG/L | 80.4999 | 2016-01-28 | DBP-1 |  |  |  | 1.7 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.2 | UG/L | 60.4999 | 2016-01-28 | DBP-2 |  |  |  | 1.1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 66.1 | UG/L | 80.4999 | 2016-01-28 | DBP-2 |  |  |  | 1.1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.5 | UG/L | 60.4999 | 2016-01-28 | DBP-3 |  |  |  | 1.8 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 38.9 | UG/L | 80.4999 | 2016-01-28 | DBP-3 |  |  |  | 1.8 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41.7 | UG/L | 60.4999 | 2016-01-28 | DBP-4 |  |  |  | 0.7 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 58.6 | UG/L | 80.4999 | 2016-01-28 | DBP-4 |  |  |  | 0.7 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.4 | UG/L | 60.4999 | 2016-01-28 | DBP-6 |  |  |  | 1.5 | 2713 RISMEN CT. KISS. (8/17/16 EW HAS 2Q 2016 DBPS FOR ENTRY IN PWS BY EMAIL ALREADY IN OCULUS)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 50.6 | UG/L | 80.4999 | 2016-01-28 | DBP-6 |  |  |  | 1.5 | 2713 RISMEN CT. KISS. (8/17/16 EW HAS 2Q 2016 DBPS FOR ENTRY IN PWS BY EMAIL ALREADY IN OCULUS)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-02-05 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-02-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-02-13 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA) NITRITE HAS A U J QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA) NITRITE HAS A U J QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-02-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-02-25 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-02-27 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-03-03 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-03-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-03-11 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-03-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-03-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-03-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-04-04 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-04-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-04-14 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-04-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-04-25 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-04-26 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.1 | UG/L | 60.4999 | 2016-04-27 | DBP-6 |  |  |  | 1.1 | 2713 RISMEN CT. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 53 | UG/L | 80.4999 | 2016-04-27 | DBP-6 |  |  |  | 1.1 | 2713 RISMEN CT. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 42.8 | UG/L | 80.4999 | 2016-04-27 | DBP-4 |  |  |  | 1.5 | 145 EAST LAKESHORE KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.8 | UG/L | 60.4999 | 2016-04-27 | DBP-4 |  |  |  | 1.5 | 145 EAST LAKESHORE KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.4 | UG/L | 60.4999 | 2016-04-27 | DBP-5 |  |  |  | 0.9 | 1721 BRASSIE CT. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 60 | UG/L | 80.4999 | 2016-04-27 | DBP-5 |  |  |  | 0.9 | 1721 BRASSIE CT. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.7 | UG/L | 60.4999 | 2016-04-27 | DBP-1 |  |  |  | 0.9 | 3200 SERALAGO BLVD. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 72.8 | UG/L | 80.4999 | 2016-04-27 | DBP-1 |  |  |  | 0.9 | 3200 SERALAGO BLVD. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.2 | UG/L | 60.4999 | 2016-04-27 | DBP-2 |  |  |  | 1.1 | 1400 RIVIERA DR. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 71.1 | UG/L | 80.4999 | 2016-04-27 | DBP-2 |  |  |  | 1.1 | 1400 RIVIERA DR. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18 | UG/L | 60.4999 | 2016-04-27 | DBP-3 |  |  |  | 1.6 | 120 SIMPSON RD. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 35 | UG/L | 80.4999 | 2016-04-27 | DBP-3 |  |  |  | 1.6 | 120 SIMPSON RD. KISS. (NO LRAA OR OE EXCEEDANCES 6/16 QTR 6/16 DBF W/RESULTS IN OC)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-05-06 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-05-07 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-05-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-05-19 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-05-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-05-26 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-06-03 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-06-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-06-09 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-06-23 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-06-27 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-06-27 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-07-08 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-07-08 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-07-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-07-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-07-23 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 25.5 | UG/L | 80.4999 | 2016-07-26 | DBP-4 |  |  |  | 0.5 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.1 | UG/L | 80.4999 | 2016-07-26 | DBP-5 |  |  |  | 0.8 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 49.9 | UG/L | 80.4999 | 2016-07-26 | DBP-6 |  |  |  | 0.6 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.9 | UG/L | 60.4999 | 2016-07-26 | DBP-6 |  |  |  | 0.6 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.4 | UG/L | 60.4999 | 2016-07-26 | DBP-5 |  |  |  | 0.8 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.7 | UG/L | 60.4999 | 2016-07-26 | DBP-4 |  |  |  | 0.5 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 30.2 | UG/L | 80.4999 | 2016-07-26 | DBP-3 |  |  |  | 1.4 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20 | UG/L | 60.4999 | 2016-07-26 | DBP-3 |  |  |  | 1.4 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 52.7 | UG/L | 80.4999 | 2016-07-26 | DBP-2 |  |  |  | 0.5 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.7 | UG/L | 60.4999 | 2016-07-26 | DBP-2 |  |  |  | 0.5 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 29.2 | UG/L | 80.4999 | 2016-07-26 | DBP-1 |  |  |  | 1.5 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11 | UG/L | 60.4999 | 2016-07-26 | DBP-1 |  |  |  | 1.5 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-07-29 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-08-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-08-11 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-08-11 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-08-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-08-27 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-09-06 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-09-06 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-09-07 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-09-19 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-09-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2016-09-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-10-03 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-10-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-10-11 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 64.1 | UG/L | 80.4999 | 2016-10-24 | DBP-6 |  |  |  | 1.9 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33 | UG/L | 60.4999 | 2016-10-24 | DBP-6 |  |  |  | 1.9 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.5 | UG/L | 60.4999 | 2016-10-24 | DBP-5 |  |  |  | 0.7 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 51.8 | UG/L | 80.4999 | 2016-10-24 | DBP-5 |  |  |  | 0.7 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.9 | UG/L | 60.4999 | 2016-10-24 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 95.2 | UG/L | 80.4999 | 2016-10-24 | DBP-1 |  |  |  | 0.6 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.1 | UG/L | 60.4999 | 2016-10-24 | DBP-2 |  |  |  | 1.7 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 65.3 | UG/L | 80.4999 | 2016-10-24 | DBP-2 |  |  |  | 1.7 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42 | UG/L | 60.4999 | 2016-10-24 | DBP-3 |  |  |  | 2.4 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 42.2 | UG/L | 80.4999 | 2016-10-24 | DBP-3 |  |  |  | 2.4 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.3 | UG/L | 60.4999 | 2016-10-24 | DBP-4 |  |  |  | 1.9 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.4 | UG/L | 80.4999 | 2016-10-24 | DBP-4 |  |  |  | 1.9 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-10-25 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2016-10-26 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-10-26 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2016-11-08 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-11-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-11-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-11-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.3 | LN(10) |  | 2016-11-25 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-11-30 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-12-05 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.3 | LN(10) |  | 2016-12-08 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-12-08 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-12-16 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-12-23 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.3 | LN(10) |  | 2016-12-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27 | UG/L | 60.4999 | 2017-01-30 | DBP-4 |  |  |  | 1.2 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.7 | UG/L | 60.4999 | 2017-01-30 | DBP-5 |  |  |  | 1 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 61.4 | UG/L | 80.4999 | 2017-01-30 | DBP-6 |  |  |  | 1.6 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.7 | UG/L | 60.4999 | 2017-01-30 | DBP-1 |  |  |  | 0.7 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 67.7 | UG/L | 80.4999 | 2017-01-30 | DBP-1 |  |  |  | 0.7 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.9 | UG/L | 60.4999 | 2017-01-30 | DBP-2 |  |  |  | 1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 68.9 | UG/L | 80.4999 | 2017-01-30 | DBP-2 |  |  |  | 1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.2 | UG/L | 60.4999 | 2017-01-30 | DBP-6 |  |  |  | 1.6 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 46.1 | UG/L | 80.4999 | 2017-01-30 | DBP-4 |  |  |  | 1.2 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 47.6 | UG/L | 80.4999 | 2017-01-30 | DBP-5 |  |  |  | 1 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 42.1 | UG/L | 80.4999 | 2017-01-30 | DBP-3 |  |  |  | 2.5 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.9 | UG/L | 60.4999 | 2017-01-30 | DBP-3 |  |  |  | 2.5 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP5 |  | 0.5499 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 39.6 | UG/L | 80.4999 | 2017-04-27 | DBP-3 |  |  |  | 1.6 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.9 | UG/L | 60.4999 | 2017-04-27 | DBP-4 |  |  |  | 1.4 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 52.2 | UG/L | 80.4999 | 2017-04-27 | DBP-4 |  |  |  | 1.4 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.6 | UG/L | 60.4999 | 2017-04-27 | DBP-6 |  |  |  | 1.4 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 54.3 | UG/L | 80.4999 | 2017-04-27 | DBP-6 |  |  |  | 1.4 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.7 | UG/L | 60.4999 | 2017-04-27 | DBP-5 |  |  |  | 0.7 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.8 | UG/L | 80.4999 | 2017-04-27 | DBP-5 |  |  |  | 0.7 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.6 | UG/L | 60.4999 | 2017-04-27 | DBP-1 |  |  |  | 2.1 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 13.5 | UG/L | 80.4999 | 2017-04-27 | DBP-1 |  |  |  | 2.1 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.6 | UG/L | 60.4999 | 2017-04-27 | DBP-2 |  |  |  | 1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 73.6 | UG/L | 80.4999 | 2017-04-27 | DBP-2 |  |  |  | 1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.9 | UG/L | 60.4999 | 2017-04-27 | DBP-3 |  |  |  | 1.6 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1017 | CHLORIDE | N | 10.1 | MG/L | 250.4999 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1022 | COPPER | N | 0.0014 | MG/L | 1.4999 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1025 | FLUORIDE | N | 0.63 | MG/L | 2.0499 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1055 | SULFATE | N | 7.4 | MG/L | 250.4999 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.2 | LN(10) |  | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 151 | MG/L | 500.4999 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP1 |  |  |  |  | PH. HAD A Q QUALIFER IN IT. REDONE AND HAD 8.2
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1005 | ARSENIC | N | 0.0009 | MG/L | 0.0104 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1010 | BARIUM | N | 0 | MG/L | 2.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1025 | FLUORIDE | N | 0.071 | MG/L | 4.0499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1052 | SODIUM | N | 5.6 | MG/L | 160.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1017 | CHLORIDE | N | 8.3 | MG/L | 250.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1022 | COPPER | N | 0.0018 | MG/L | 1.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1025 | FLUORIDE | N | 0.071 | MG/L | 2.0499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1055 | SULFATE | N | 9.2 | MG/L | 250.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 119 | MG/L | 500.4999 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1005 | ARSENIC | N | 0.0007 | MG/L | 0.0104 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1010 | BARIUM | N | 0.013 | MG/L | 2.4999 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1052 | SODIUM | N | 9.5 | MG/L | 160.4999 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1010 | BARIUM | N | 0.017 | MG/L | 2.4999 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1025 | FLUORIDE | N | 0.17 | MG/L | 4.0499 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1052 | SODIUM | N | 11.3 | MG/L | 160.4999 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1017 | CHLORIDE | N | 12.9 | MG/L | 250.4999 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 158 | MG/L | 500.4999 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.1 | LN(10) |  | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1920 | ODOR THRESHOLD | N | 4 |  | 3.4999 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1055 | SULFATE | N | 12.4 | MG/L | 250.4999 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1025 | FLUORIDE | N | 0.17 | MG/L | 2.0499 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1022 | COPPER | N | 0.0016 | MG/L | 1.4999 | 2017-04-29 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-06-02 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | WTP3 |  | 1.4999 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4030 | RADIUM-228 | N | 0.74 | PCI/L | 2.4999 | 2017-06-02 | WTP5 |  | 1.4999 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-06-02 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | WTP1 |  | 1.4999 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-06-02 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 7.9 | LN(10) |  | 2017-06-27 | 1425 E 192
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 7.8 | LN(10) |  | 2017-06-27 | 5216 BROKEN ARROW
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 7.9 | LN(10) |  | 2017-06-27 | 3230 SMOKE SIGNAL
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 8.1 | LN(10) |  | 2017-06-27 | 3210 PEACE PIPE
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 8.1 | LN(10) |  | 2017-06-27 | 3132 PINTO DR
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 8.2 | LN(10) |  | 2017-06-27 | 5324 MICCO ST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 7.5 | LN(10) |  | 2017-06-27 | 1319 ASTRO LAKE DR
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 7.8 | LN(10) |  | 2017-06-27 | 4015 W VOE ST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 7.8 | LN(10) |  | 2017-06-27 | 2007 HIDDENDALE CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | D | 7.6 | LN(10) |  | 2017-06-27 | 2661 MILL RUN BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 42.1 | UG/L | 80.4999 | 2017-07-28 | DBP-3 |  |  |  | 1.7 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.5 | UG/L | 60.4999 | 2017-07-28 | DBP-4 |  |  |  | 1.4 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 69.8 | UG/L | 80.4999 | 2017-07-28 | DBP-4 |  |  |  | 1.4 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.2 | UG/L | 60.4999 | 2017-07-28 | DBP-6 |  |  |  | 1.4 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 62.7 | UG/L | 80.4999 | 2017-07-28 | DBP-6 |  |  |  | 1.4 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.3 | UG/L | 60.4999 | 2017-07-28 | DBP-3 |  |  |  | 1.7 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 81.8 | UG/L | 80.4999 | 2017-07-28 | DBP-2 |  |  |  | 1.2 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.6 | UG/L | 60.4999 | 2017-07-28 | DBP-2 |  |  |  | 1.2 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 59.5 | UG/L | 80.4999 | 2017-07-28 | DBP-1 |  |  |  | 1.5 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.4 | UG/L | 60.4999 | 2017-07-28 | DBP-1 |  |  |  | 1.5 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.6 | UG/L | 60.4999 | 2017-07-28 | DBP-5 |  |  |  | 1 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 77.7 | UG/L | 80.4999 | 2017-07-28 | DBP-5 |  |  |  | 1 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP3 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-28 | WTP3 |  | 0.0449 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP3 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-28 | WTP3 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-28 | WTP3 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-28 | WTP3 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP3 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP5 |  | 0.0149
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP5 |  | 0.0249
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-28 | WTP5 |  | 0.1499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-28 | WTP5 |  | 1.4999
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-28 | WTP5 |  | 1.4999
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-28 | WTP5 |  | 0.4499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-28 | WTP5 |  | 9.4999
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-28 | WTP5 |  | 6.4999
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-28 | WTP5 |  | 0.6499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-28 | WTP5 |  | 2.4999
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-28 | WTP5 |  | 0.0749
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-28 | WTP5 |  | 0.6499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-28 | WTP5 |  | 0.1499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-28 | WTP5 |  | 0.2499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-28 | WTP5 |  | 0.1499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-28 | WTP5 |  | 0.9499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-28 | WTP5 |  | 0.1499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-28 | WTP3 |  | 0.0449 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-28 | WTP3 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP3 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-28 | WTP3 |  | 0.0149 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP3 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP5 |  | 0.2499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-28 | WTP5 |  | 0.0449
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP5 |  | 0.0249
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-28 | WTP5 |  | 0.1499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-28 | WTP5 |  | 0.2499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-28 | WTP5 |  | 0.1499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP5 |  | 0.0249
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-28 | WTP5 |  | 0.0449
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-28 | WTP5 |  | 0.1499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP5 |  | 0.0249
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-28 | WTP5 |  | 0.0149
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP5 |  | 0.2499
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP1 |  | 0.0149 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP1 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-28 | WTP1 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-28 | WTP1 |  | 1.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-28 | WTP1 |  | 1.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-28 | WTP1 |  | 0.4499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-28 | WTP1 |  | 9.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-28 | WTP1 |  | 6.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-28 | WTP1 |  | 0.6499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-28 | WTP1 |  | 2.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-28 | WTP1 |  | 0.0749 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-28 | WTP1 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-28 | WTP1 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-28 | WTP1 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-28 | WTP1 |  | 0.9499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-28 | WTP1 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP1 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-28 | WTP1 |  | 0.0449 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP1 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-28 | WTP1 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-28 | WTP1 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-28 | WTP1 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP1 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-28 | WTP1 |  | 0.0449 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-28 | WTP1 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP1 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-28 | WTP1 |  | 0.0149 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP1 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-28 | WTP3 |  | 0.0149 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-28 | WTP3 |  | 0.0249 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-28 | WTP3 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-28 | WTP3 |  | 1.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-28 | WTP3 |  | 1.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-28 | WTP3 |  | 0.4499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-28 | WTP3 |  | 9.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-28 | WTP3 |  | 6.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-28 | WTP3 |  | 0.6499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-28 | WTP3 |  | 2.4999 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-28 | WTP3 |  | 0.0749 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-28 | WTP3 |  | 0.6499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-28 | WTP3 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-28 | WTP3 |  | 0.2499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-28 | WTP3 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-28 | WTP3 |  | 0.9499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-28 | WTP3 |  | 0.1499 |  |  | NO DIOXIN DONE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 61.5 | UG/L | 80.4999 | 2017-10-25 | DBP-2
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.6 | UG/L | 60.4999 | 2017-10-25 | DBP-3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 35.7 | UG/L | 80.4999 | 2017-10-25 | DBP-3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.8 | UG/L | 60.4999 | 2017-10-25 | DBP-4
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 66.7 | UG/L | 80.4999 | 2017-10-25 | DBP-4
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.1 | UG/L | 60.4999 | 2017-10-25 | DBP-6
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 60.5 | UG/L | 80.4999 | 2017-10-25 | DBP-6
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.1 | UG/L | 60.4999 | 2017-10-25 | DBP-5 |  |  |  |  | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36 | UG/L | 60.4999 | 2017-10-25 | DBP-2
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 58.1 | UG/L | 80.4999 | 2017-10-25 | DBP-1 |  |  |  |  | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.1 | UG/L | 60.4999 | 2017-10-25 | DBP-1 |  |  |  |  | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 58 | UG/L | 80.4999 | 2017-10-25 | DBP-5 |  |  |  |  | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-01-10 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-01-10 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-10 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-01-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-01-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.1 | UG/L | 60.4999 | 2018-01-30 | DBP-5 |  |  |  | 1.1 | 1721 BRASSIE CT. KISS. DIBROMAOACETIC ACID HAS A RESULT OF U J
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.3 | UG/L | 60.4999 | 2018-01-30 | DBP-1 |  |  |  | 0.9 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 52.3 | UG/L | 80.4999 | 2018-01-30 | DBP-1 |  |  |  | 0.9 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.3 | UG/L | 60.4999 | 2018-01-30 | DBP-2 |  |  |  | 1.2 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 57.6 | UG/L | 80.4999 | 2018-01-30 | DBP-2 |  |  |  | 1.2 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 48.3 | UG/L | 80.4999 | 2018-01-30 | DBP-5 |  |  |  | 1.1 | 1721 BRASSIE CT. KISS. DIBROMAOACETIC ACID HAS A RESULT OF U J
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 36 | UG/L | 80.4999 | 2018-01-30 | DBP-3 |  |  |  | 1.9 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.9 | UG/L | 60.4999 | 2018-01-30 | DBP-4 |  |  |  | 1.1 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 35.7 | UG/L | 80.4999 | 2018-01-30 | DBP-4 |  |  |  | 1.1 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.6 | UG/L | 60.4999 | 2018-01-30 | DBP-6 |  |  |  | 1.3 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.3 | UG/L | 80.4999 | 2018-01-30 | DBP-6 |  |  |  | 1.3 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.7 | UG/L | 60.4999 | 2018-01-30 | DBP-3 |  |  |  | 1.9 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-02-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-02-09 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-02-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-26 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-26 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-02-26 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-03-09 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-03-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-03-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-03-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-03-23 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-03-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-04-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-04-09 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 52.7 | UG/L | 80.4999 | 2018-04-24 | DBP-6 | 0.32 |  | D | 1.9 | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.8 | UG/L | 60.4999 | 2018-04-24 | DBP-6 | 0.48 |  | D | 1.9 | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 43.4 | UG/L | 80.4999 | 2018-04-24 | DBP-4 | 0.32 |  | 5 | 1.9 | 145 E LAKESHORE BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.3 | UG/L | 60.4999 | 2018-04-24 | DBP-4 | 0.48 |  | 5 | 1.9 | 145 E LAKESHORE BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 32.8 | UG/L | 80.4999 | 2018-04-24 | DBP-3 | 0.32 |  | 4 | 1.8 | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.3 | UG/L | 60.4999 | 2018-04-24 | DBP-3 | 0.48 |  | 4 | 1.8 | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 62.4 | UG/L | 80.4999 | 2018-04-24 | DBP-2 | 0.62 |  | 3 | 1.2 | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44.4 | UG/L | 60.4999 | 2018-04-24 | DBP-2 | 0.48 |  | 3 | 1.2 | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 21 | UG/L | 80.4999 | 2018-04-24 | DBP-1 | 0.32 |  | 2 | 1.6 | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.1 | UG/L | 60.4999 | 2018-04-24 | DBP-1 | 0.48 |  | 2 | 1.6 | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 56.6 | UG/L | 80.4999 | 2018-04-24 | DBP-5 | 0.32 |  | 1 | 0.9 | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.6 | UG/L | 60.4999 | 2018-04-24 | DBP-5 | 0.48 |  | 1 | 0.9 | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-04-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-04-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-10 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-05-10 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-05-10 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-05-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-05-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-06-08 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-06-08 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-06-25 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-06-25 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-25 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-09 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-09 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-07-09 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-25 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-25 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-07-25 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 66.8 | UG/L | 80.4999 | 2018-07-26 | DBP-6 | 0.32 |  | 6 | 1.6 | 2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 73 | UG/L | 80.4999 | 2018-07-26 | DBP-2 | 0.32 |  | 3 | 1 | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.7 | UG/L | 60.4999 | 2018-07-26 | DBP-3 | 0.48 |  | 4 | 1.6 | 120 SIMPSON
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 43.3 | UG/L | 80.4999 | 2018-07-26 | DBP-3 | 0.32 |  | 4 | 1.6 | 120 SIMPSON
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.5 | UG/L | 60.4999 | 2018-07-26 | DBP-6 | 0.48 |  | 6 | 1.6 | 2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 49.3 | UG/L | 80.4999 | 2018-07-26 | DBP-4 | 0.32 |  | 5 | 0.9 | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.3 | UG/L | 60.4999 | 2018-07-26 | DBP-4 | 0.48 |  | 5 | 0.9 | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41.2 | UG/L | 60.4999 | 2018-07-26 | DBP-2 | 0.48 |  | 3 | 1 | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 69.3 | UG/L | 80.4999 | 2018-07-27 | DBP-5 | 0.32 |  | 1 | 0.5 | 1721 BRASSIE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.8 | UG/L | 80.4999 | 2018-07-27 | DBP-1 | 0.32 |  | 2 | 1 | 3200 SERALAGO
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.6 | UG/L | 60.4999 | 2018-07-27 | DBP-5 | 0.48 |  | 1 | 0.5 | 1721 BRASSIE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.8 | UG/L | 60.4999 | 2018-07-27 | DBP-1 | 0.48 |  | 2 | 1 | 3200 SERALAGO
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-08-09 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-08-09 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-08-09 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-08-27 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-08-27 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-08-27 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-09-07 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-09-07 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-09-07 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-09-24 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-09-24 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-09-24 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-10-09 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-10-09 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-10-09 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55 | UG/L | 80.4999 | 2018-10-23 | DBP-5 |  |  |  | 0.6 | 2950-1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35 | UG/L | 60.4999 | 2018-10-23 | DBP-1 |  |  |  | 0.4 | 2950-3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 63.3 | UG/L | 80.4999 | 2018-10-23 | DBP-1 |  |  |  | 0.4 | 2950-3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.6 | UG/L | 60.4999 | 2018-10-23 | DBP-2 |  |  |  | 1.1 | 2950-1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 42.3 | UG/L | 80.4999 | 2018-10-23 | DBP-2 |  |  |  | 1.1 | 2950-1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.5 | UG/L | 60.4999 | 2018-10-23 | DBP-3 |  |  |  | 2.1 | 2950-120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 33.2 | UG/L | 80.4999 | 2018-10-23 | DBP-3 |  |  |  | 2.1 | 2950-120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.9 | UG/L | 60.4999 | 2018-10-23 | DBP-4 |  |  |  | 1 | 2950-145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.3 | UG/L | 60.4999 | 2018-10-23 | DBP-5 |  |  |  | 0.6 | 2950-1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 54.8 | UG/L | 80.4999 | 2018-10-23 | DBP-6 |  |  |  | 1.2 | 2950-2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 57.9 | UG/L | 80.4999 | 2018-10-23 | DBP-4 |  |  |  | 1 | 2950-145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.3 | UG/L | 60.4999 | 2018-10-23 | DBP-6 |  |  |  | 1.2 | 2950-2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-10-25 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-10-25 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-10-25 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-09 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-09 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-09 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-26 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-11-26 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-26 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-10 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-12-10 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-12-10 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-26 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-26 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-12-26 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-01-10 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-01-10 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-10 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-01-24 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-24 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-01-24 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 15.3 | UG/L | 80.4999 | 2019-01-28 | DBP-1 | 0.32 |  | 2 | 1.7 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.7 | UG/L | 60.4999 | 2019-01-28 | DBP-6 | 0.48 |  | 6 | 1.2 | 2713 RISMEN CT. KISS. (HLKD) 1ST QTR 2019 DISINF BYP RPRT RCVD W/RSLTS
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 54 | UG/L | 80.4999 | 2019-01-28 | DBP-6 | 0.32 |  | 6 | 1.2 | 2713 RISMEN CT. KISS. (HLKD) 1ST QTR 2019 DISINF BYP RPRT RCVD W/RSLTS
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.5 | UG/L | 60.4999 | 2019-01-28 | DBP-1 | 0.48 |  | 2 | 1.7 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 53.4 | UG/L | 80.4999 | 2019-01-28 | DBP-4 | 0.32 |  | 5 | 1.3 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.6 | UG/L | 60.4999 | 2019-01-28 | DBP-2 | 0.48 |  | 3 | 1.1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 34.3 | UG/L | 80.4999 | 2019-01-28 | DBP-3 | 0.32 |  | 4 | 1.8 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.9 | UG/L | 60.4999 | 2019-01-28 | DBP-3 | 0.48 |  | 4 | 1.8 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 45.9 | UG/L | 80.4999 | 2019-01-28 | DBP-5 | 0.32 |  | 1 | 1.4 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.5 | UG/L | 60.4999 | 2019-01-28 | DBP-5 | 0.48 |  | 1 | 1.4 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.8 | UG/L | 80.4999 | 2019-01-28 | DBP-2 | 0.32 |  | 3 | 1.1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.1 | UG/L | 60.4999 | 2019-01-28 | DBP-4 | 0.48 |  | 5 | 1.3 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-08 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-02-09 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-11 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-02-26 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-26 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-02-26 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-09 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-03-09 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-11 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-03-23 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-03-25 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-03-29 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-04-09 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-09 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-04-09 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-04-24 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-04-24 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-04-24 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.1 | UG/L | 60.4999 | 2019-04-26 | DBP-1 |  |  | 2 | 0.9 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 60.8 | UG/L | 80.4999 | 2019-04-26 | DBP-1 |  |  | 2 | 0.9 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 62.5 | UG/L | 80.4999 | 2019-04-26 | DBP-6 |  |  | 6 | 1.4 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 53.4 | UG/L | 80.4999 | 2019-04-26 | DBP-5 |  |  | 1 | 0.7 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.7 | UG/L | 60.4999 | 2019-04-26 | DBP-5 |  |  | 1 | 0.7 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.6 | UG/L | 60.4999 | 2019-04-26 | DBP-4 |  |  | 5 | 1.5 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.2 | UG/L | 60.4999 | 2019-04-26 | DBP-6 |  |  | 6 | 1.4 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 75.7 | UG/L | 80.4999 | 2019-04-26 | DBP-4 |  |  | 5 | 1.5 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 40.7 | UG/L | 80.4999 | 2019-04-26 | DBP-3 |  |  | 4 | 2 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.1 | UG/L | 60.4999 | 2019-04-26 | DBP-2 |  |  | 3 | 1.1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 50.6 | UG/L | 80.4999 | 2019-04-26 | DBP-2 |  |  | 3 | 1.1 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.5 | UG/L | 60.4999 | 2019-04-26 | DBP-3 |  |  | 4 | 2 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-10 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-05-10 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-10 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-05-24 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-24 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-24 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-06-08 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-06-08 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-06-08 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-06-25 | WTP3 |  |  |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-06-25 | WTP5 |  |  |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-25 | WTP1 |  |  |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-07-02 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-07-05 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-07-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-07-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-07-18 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-07-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.1 | UG/L | 60.4999 | 2019-07-24 | DBP-4 |  |  | 5 | 1.9 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.2 | UG/L | 60.4999 | 2019-07-24 | DBP-1 |  |  | 2 | 1 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36 | UG/L | 60.4999 | 2019-07-24 | DBP-6 |  |  | 1 |  | 2713 RISMEN CT (DBP-6) (REPLACED 2750 RISMENT CT. ON 1-24-13 PRIOR DATA IS FROM 2720 RISMEN)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 34.4 | UG/L | 80.4999 | 2019-07-24 | DBP-4 |  |  | 5 | 1.9 | 145 EAST LAKESHORE KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 60.6 | UG/L | 80.4999 | 2019-07-24 | DBP-6 |  |  | 6 | 1.5 | 2713 RISMEN CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.7 | UG/L | 80.4999 | 2019-07-24 | DBP-5 |  |  | 1 | 1 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38 | UG/L | 60.4999 | 2019-07-24 | DBP-5 |  |  | 1 | 1 | 1721 BRASSIE CT. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 44.2 | UG/L | 80.4999 | 2019-07-24 | DBP-1 |  |  | 2 | 1 | 3200 SERALAGO BLVD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.2 | UG/L | 60.4999 | 2019-07-24 | DBP-2 |  |  | 3 | 0.6 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 72.8 | UG/L | 80.4999 | 2019-07-24 | DBP-2 |  |  | 3 | 0.6 | 1400 RIVIERA DR. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.2 | UG/L | 60.4999 | 2019-07-24 | DBP-3 |  |  | 4 | 1.8 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 37 | UG/L | 80.4999 | 2019-07-24 | DBP-3 |  |  | 4 | 1.8 | 120 SIMPSON RD. KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-08-05 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-08-05 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-08-05 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-08-14 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-08-20 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-08-27 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-09-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-09-07 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-09-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-09-17 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-09-20 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-09-27 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-10-02 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-10-03 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-10-04 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-10-21 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-10-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-10-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.9 | UG/L | 60.4999 | 2019-10-24 | DBP-4 | 0.9 |  | 5 | 1.9 | 145 E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 54.8 | UG/L | 80.4999 | 2019-10-24 | DBP-4 | 0.32 |  | 5 | 1.9 | 145 E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.9 | UG/L | 60.4999 | 2019-10-24 | DBP-6 | 0.9 |  | 6 | 1.7 | 2713 RISMEN CR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 55.7 | UG/L | 80.4999 | 2019-10-24 | DBP-6 | 0.32 |  | 6 | 1.7 | 2713 RISMEN CR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.6 | UG/L | 60.4999 | 2019-10-24 | DBP-5 | 0.9 |  | 1 | 1.1 | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 56.4 | UG/L | 80.4999 | 2019-10-24 | DBP-5 | 0.32 |  | 1 | 1.1 | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.1 | UG/L | 60.4999 | 2019-10-24 | DBP-1 | 0.9 |  | 2 | 1.5 | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 27.8 | UG/L | 80.4999 | 2019-10-24 | DBP-1 | 0.32 |  | 2 | 1.5 | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41.7 | UG/L | 60.4999 | 2019-10-24 | DBP-2 | 0.9 |  | 3 | 1.2 | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 56.5 | UG/L | 80.4999 | 2019-10-24 | DBP-2 | 0.32 |  | 3 | 1.2 | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.3 | UG/L | 60.4999 | 2019-10-24 | DBP-3 | 0.9 |  | 4 | 2.1 | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | D | 34.1 | UG/L | 80.4999 | 2019-10-24 | DBP-3 | 0.32 |  | 4 | 2.1 | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-11-01 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-11-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-11-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-11-15 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-11-21 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-11-26 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-12-03 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-12-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-12-12 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-12-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-12-23 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-12-27 | WTP3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 15.92 | UG/L | 80.4999 | 2015-08-13 | L1 |  |  |  | 0.3 | NORTH PAVILION (QUALIFIES FOR R.M. - NEXT T/H DUE @ 8/13/18) <500
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.36 | UG/L | 60.4999 | 2015-08-13 | L1 |  |  |  | 0.3 | NORTH PAVILION (QUALIFIES FOR R.M. - NEXT T/H DUE @ 8/13/18) <500
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-10-19 | AAA |  | 6.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-10-19 | AAA |  | 0.6499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-10-19 | AAA |  | 2.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-10-19 | AAA |  | 0.0749 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-10-19 | AAA |  | 0.6499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-10-19 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-10-19 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0.023 | UG/L | 54.9999 | 2015-10-19 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-10-19 | AAA |  | 0.9499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-10-19 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-10-19 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-10-19 | AAA |  | 0.0449 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-10-19 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-10-19 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-10-19 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-10-19 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-10-19 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-10-19 | AAA |  | 0.0449 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-10-19 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-10-19 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-10-19 | AAA |  | 0.0149 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-10-19 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-10-19 | AAA |  |  |  |  | DUE 2021
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-19 | AAA |  | 1.4999 |  |  | DUE 2021
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.9 | LN(10) |  | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 340 | MG/L | 500.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.0077 | MG/L | 2.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.23 | MG/L | 4.0499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 47 | MG/L | 160.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 65 | MG/L | 250.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.23 | MG/L | 2.0499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0008 | MG/L | 0.0549 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 5.7 | MG/L | 250.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.021 | MG/L | 5.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-10-19 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-19 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-10-19 | AAA |  | 0.0149 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-10-19 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-10-19 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-10-19 | AAA |  | 1.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 3 | UG/L | 249.9999 | 2015-10-19 | AAA |  | 1.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-10-19 | AAA |  | 0.4499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-10-19 | AAA |  | 9.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC+1QM/DAL (DAL 3.0) 2QM/DAL 3/16>TKN PER ABWTR 3/31/16 EM 11/12/15>ABWTR & OWNER. CHEM 2042 HEX... 0.023 (<RDL OF 0.1 NO QM NDD)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-03-17 | AAA |  | 1.4999 |  |  | 2QM/DAL (3QM/DAL 6/16) 8/17 EW HAS 6/16 DALAPON FOR ENTRY IN PWS ALREADY IN OCULUS-BB
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-06-30 | AAA |  | 1.4999 |  |  | 3QM/DAL
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-09-26 | AAA |  | 1.4999
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-20 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-12-20 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-12-27 | AAA | 1 | 1.4999 |  |  | RCVD 2-10-17 (1ST AM SAMPLE 4TH Q 2017 AND 2018 IF NO DETECTS GO TO TRIENNIAL_JMF)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2017-11-10 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-11-10 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-12-11 | AAA |  | 1.4999
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2018-02-21 | AAA |  |  |  |  | ANALYSIS TIME 11:12
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-21 | AAA |  |  |  |  | ANALYSIS TIME 11:12
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.3 | MG/L | 4.0499 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 31 | MG/L | 160.4999 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-21 | AAA |  |  |  |  | NN ANALYSIS TIME 10:41
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 280 | MG/L | 500.4999 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 48 | MG/L | 250.4999 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0.0072 | MG/L | 1.4999 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.3 | MG/L | 2.0499 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 14 | MG/L | 250.4999 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.16 | LN(10) |  | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0.042 |  | 0.5499 | 2018-02-21 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 57.77 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.91 |  | 1 | 0.7 | RETURN TO AM SAMPLE AUGUST ANNUALLY_JMF
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 77.79 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.39 |  | 1 | 0.7 | RETURN TO AM SAMPLE AUGUST ANNUALLY_JMF
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 3.2 | UG/L | 249.9999 | 2018-11-27 | AAA | 0.9 | 1.4999 |  |  | DALAPON 3.2 (HLKD 1-11-19)
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1041 | NITRITE | D | 0 | MG/L | 1.4999 | 2019-04-23 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | INOR | 1040 | NITRATE | D | 0.46 | MG/L | 10.4999 | 2019-04-23 | AAA
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.41 | UG/L | 60.4999 | 2019-08-22 | L1 |  |  |  | 0.73 | NORTH PAVILION
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 79.98 | UG/L | 80.4999 | 2019-08-22 | L1 |  |  |  | 0.73 | NORTH PAVILION
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-10-28 | AAA |  | 1.4999
3490816 | GREAT OAK R.V. RESORT | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-09-24 | AAA |  | 1.4999 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-09-24 | AAA |  | 0.4499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-09-24 | AAA |  | 9.4999 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-09-24 | AAA |  | 6.4999 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-09-24 | AAA |  | 0.6499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-09-24 | AAA |  | 2.4999 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-09-24 | AAA |  | 0.0749 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-09-24 | AAA |  | 0.6499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-09-24 | AAA |  | 0.1499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-09-24 | AAA |  | 0.2499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-09-24 | AAA |  | 0.1499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-09-24 | AAA |  | 0.9499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-09-24 | AAA |  | 0.1499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-09-24 | AAA |  | 0.2499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-09-24 | AAA |  | 0.0449 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-09-24 | AAA |  | 0.0249 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-09-24 | AAA |  | 0.1499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-09-24 | AAA |  | 0.2499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-09-24 | AAA |  | 0.1499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-09-24 | AAA |  | 0.0249 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-09-24 | AAA |  | 0.0449 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-09-24 | AAA |  | 0.1499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-09-24 | AAA |  | 0.0249 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-09-24 | AAA |  | 0.0149 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-09-24 | AAA |  | 0.2499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2063 | DIOXIN (NG/L) | N | 0 | NG/L | 0.0349 | 2015-09-24 | AAA |  | 0.0055 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1010 | BARIUM | N | 0.012 | MG/L | 2.4999 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1025 | FLUORIDE | N | 0.092 | MG/L | 4.0499 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1030 | LEAD | N | 0.0001 | MG/L | 0.0154 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1052 | SODIUM | N | 6.3 | MG/L | 160.4999 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-09-24 | AAA |  |  |  |  | (NO MCLS) 15DON/16:NN>>12/6/16 MIKE POWERS INDICATED BY EMAIL THAT HE WILL SAMPLE "NEXT WEEK" FOR NN-BB RADS 2021 (MIKE POWERS)
3490816 | GREAT OAK R.V. RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1017 | CHLORIDE | N | 9.8 | MG/L | 250.4999 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.7 | PCI/L | 15.4999 | 2015-09-24 | AAA |  |  |  |  | RADS DUE 2021
3490816 | GREAT OAK R.V. RESORT | RAD | 4020 | RADIUM-226 | N | 0.8 | PCI/L | 3.4999 | 2015-09-24 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3490816 | GREAT OAK R.V. RESORT | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-09-24 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3490816 | GREAT OAK R.V. RESORT | SEC | 1025 | FLUORIDE | N | 0.092 | MG/L | 2.0499 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1055 | SULFATE | N | 6.5 | MG/L | 250.4999 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.19 | LN(10) |  | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 120 | MG/L | 500.4999 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-09-24 | AAA |  |  |  |  | NO MCLS
3490816 | GREAT OAK R.V. RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2955 | TOT XYLENE | N | 0.42 | UG/L | 10499.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-09-24 | AAA |  | 0.5499 |  |  | 3YR VOC (XY. 0.42 - DOES NOT EXCEED 0.5 - NO QM NEEDED)
3490816 | GREAT OAK R.V. RESORT | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-09-24 | AAA |  | 0.0149 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-09-24 | AAA |  | 0.0249 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-09-24 | AAA |  | 0.1499 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-09-24 | AAA |  | 1.4999 |  |  | 3YR SOC (DIOXIN REVISED - ENTERED BUT NOT RQRD FOR THIS SYSTEM SINCE IT'S A GROUNDWATER SYSTEM)
3490816 | GREAT OAK R.V. RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.17 | UG/L | 60.4999 | 2015-09-24 | L1 |  |  |  | 1.2 | LOT A-26 (REMAIN ON R.M. - NEXT T/H DUE SEPT. 2018) <500
3490816 | GREAT OAK R.V. RESORT | DBP | 2950 | TOTAL THMS | D | 24.35 | UG/L | 80.4999 | 2015-09-24 | L1 |  |  |  | 1.2 | LOT A-26 (REMAIN ON R.M. - NEXT T/H DUE SEPT. 2018) <500
3490816 | GREAT OAK R.V. RESORT | INOR | 1040 | NITRATE | N | 0.111 | MG/L | 10.4999 | 2016-12-14 | AAA |  |  |  |  | 2016 NN OK
3490816 | GREAT OAK R.V. RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-14 | AAA |  |  |  |  | 2016 NN OK
3490816 | GREAT OAK R.V. RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-12-20 | AAA |  |  |  |  | LATE REPORTING SUBMISSION
3490816 | GREAT OAK R.V. RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-12-20 | AAA |  |  |  |  | LATE REPORTING SUBMISSION
3490816 | GREAT OAK R.V. RESORT | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-09-27 | AAA |  | 0.2499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2063 | DIOXIN (NG/L) | N | 0 | NG/L | 0.0349 | 2018-09-27 | AAA |  | 0.0055 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-09-27 | AAA |  | 0.0449 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-09-27 | AAA |  | 0.0249 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-09-27 | AAA |  | 0.1499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2955 | TOT XYLENE | N | 0.1 | UG/L | 10499.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-09-27 | AAA |  | 0.2499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-09-27 | AAA |  | 0.1499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-09-27 | AAA |  | 0.0249 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-09-27 | AAA |  | 0.0449 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-09-27 | AAA |  | 0.1499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-09-27 | AAA |  | 0.0249 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-09-27 | AAA |  | 0.0149 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-09-27 | AAA |  | 0.2499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.4 | PCI/L | 15.4999 | 2018-09-27 | AAA |  |  |  |  | DUE 2024
3490816 | GREAT OAK R.V. RESORT | RAD | 4020 | RADIUM-226 | N | 1.2 | PCI/L | 3.4999 | 2018-09-27 | AAA |  | 1.4999 |  |  | DUE 2024
3490816 | GREAT OAK R.V. RESORT | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-09-27 | AAA |  | 1.4999 |  |  | DUE 2024
3490816 | GREAT OAK R.V. RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-09-27 | AAA |  | 0.5499 |  |  | TOT XYL = 0.1 < 0.5 DO NOT NEED QM_JMF
3490816 | GREAT OAK R.V. RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1010 | BARIUM | N | 0.011 | MG/L | 2.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1025 | FLUORIDE | N | 0.16 | MG/L | 4.0499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1030 | LEAD | N | 0.0001 | MG/L | 0.0154 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1052 | SODIUM | N | 7.1 | MG/L | 160.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1017 | CHLORIDE | N | 11 | MG/L | 250.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1025 | FLUORIDE | N | 0.16 | MG/L | 2.0499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1055 | SULFATE | N | 8.5 | MG/L | 250.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.2 | LN(10) |  | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 120 | MG/L | 500.4999 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-09-27 | AAA
3490816 | GREAT OAK R.V. RESORT | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-09-27 | AAA |  | 0.0149 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-09-27 | AAA |  | 0.0249 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-09-27 | AAA |  | 0.1499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-09-27 | AAA |  | 1.4999 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-09-27 | AAA |  | 1.4999 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-09-27 | AAA |  | 0.4499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-09-27 | AAA |  | 9.4999 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-09-27 | AAA |  | 6.4999 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-09-27 | AAA |  | 0.6499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-09-27 | AAA |  | 2.4999 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-09-27 | AAA |  | 0.0749 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-09-27 | AAA |  | 0.6499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-09-27 | AAA |  | 0.1499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-09-27 | AAA |  | 0.2499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-09-27 | AAA |  | 0.1499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-09-27 | AAA |  | 0.9499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490816 | GREAT OAK R.V. RESORT | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-09-27 | AAA |  | 0.1499 |  |  | QUALIFIED DATA ACCEPTED_JMF
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | D | 17.14 | UG/L | 80.4999 | 2015-09-09 | L1 |  |  |  | 0.5 | ON R.M.-BIBB @ WWTP(REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) <500
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.17 | UG/L | 60.4999 | 2015-09-09 | L1 |  |  |  | 0.5 | ON R.M.-BIBB @ WWTP(REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) <500
3490986 | PLEASANT HILL VILLAGE | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 1.4999 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-10-08 | AAA |  | 1.4999 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-10-08 | AAA |  | 0.4499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 9.4999 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-10-08 | AAA |  | 6.4999 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-10-08 | AAA |  | 0.6499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-10-08 | AAA |  | 2.4999 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-10-08 | AAA |  | 0.0749 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-10-08 | AAA |  | 0.6499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-10-08 | AAA |  | 0.1499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-10-08 | AAA |  | 0.2499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-10-08 | AAA |  | 0.1499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-10-08 | AAA |  | 0.9499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.1499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-10-08 | AAA |  | 0.2499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-10-08 | AAA |  | 0.0449 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-10-08 | AAA |  | 0.1499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-10-08 | AAA |  | 0.2499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.1499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.0449 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-10-08 | AAA |  | 0.1499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-10-08 | AAA |  | 0.0149 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-10-08 | AAA |  | 0.2499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1017 | CHLORIDE | N | 8.6 | MG/L | 250.4999 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1025 | FLUORIDE | N | 0.28 | MG/L | 2.0499 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1028 | IRON | N | 0.2 | MG/L | 0.3499 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1032 | MANGANESE | N | 0.0067 | MG/L | 0.0549 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1055 | SULFATE | N | 33 | MG/L | 250.4999 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.1 | PCI/L | 15.4999 | 2015-10-08 | AAA |  |  |  |  | DUE 2021
3490986 | PLEASANT HILL VILLAGE | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-08 | AAA |  | 1.4999 |  |  | DUE 2021
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1010 | BARIUM | N | 0.025 | MG/L | 2.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1020 | CHROMIUM | N | 0.0007 | MG/L | 0.1499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1025 | FLUORIDE | N | 0.28 | MG/L | 4.0499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1052 | SODIUM | N | 5.9 | MG/L | 160.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3490986 | PLEASANT HILL VILLAGE | SEC | 1095 | ZINC | N | 0.12 | MG/L | 5.4999 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1905 | COLOR | N | 15 | COLOR UNITS | 15.4999 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 170 | MG/L | 500.4999 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-08 | AAA
3490986 | PLEASANT HILL VILLAGE | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 0.5499
3490986 | PLEASANT HILL VILLAGE | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-10-08 | AAA |  | 0.0149 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-10-08 | AAA |  | 0.1499 |  |  | MISSED 2018
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-21 | AAA |  |  |  |  | NITRATE 5.3 IS > HALF MCL OF 10. GO TO QUARTERLY_JMF
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 5.3 | MG/L | 10.4999 | 2016-12-21 | AAA |  |  |  |  | NITRATE 5.3 IS > HALF MCL OF 10. GO TO QUARTERLY_JMF
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-25 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-25 | AAA |  |  |  |  | MAKEUPS FOR MISSED 1ST QUARTER 2017 SAMPLING. - MBB
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-25 | AAA |  |  |  |  | MAKEUPS FOR MISSED 1ST QUARTER 2017 SAMPLING. - MBB
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-25 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-08-22 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-08-22 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-11-28 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-11-28 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1052 | SODIUM | N | 15.8 | MG/L | 160.4999 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1010 | BARIUM | N | 0.025 | MG/L | 2.4999 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1025 | FLUORIDE | N | 0.25 | MG/L | 4.0499 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-01 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1920 | ODOR THRESHOLD | N | 3 |  | 3.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 183 | MG/L | 500.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | N | 2.7 | UG/L | 10499.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499 |  |  | RCVD 1/15/19. TOT XYLENE 2.7 - MISSED 2ND 3RD AND 4TH Q TOT XYLENE. BEGIN QM_JMF
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1010 | BARIUM | N | 0.025 | MG/L | 2.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1025 | FLUORIDE | N | 0.25 | MG/L | 4.0499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1052 | SODIUM | N | 15.8 | MG/L | 160.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1017 | CHLORIDE | N | 15.6 | MG/L | 250.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1025 | FLUORIDE | N | 0.25 | MG/L | 2.0499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1028 | IRON | N | 0.041 | MG/L | 0.3499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1032 | MANGANESE | N | 0.0034 | MG/L | 0.0549 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1055 | SULFATE | N | 32.3 | MG/L | 250.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-02-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-04-24 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-04-24 | AAA
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | D | 39.3 | UG/L | 80.4999 | 2018-09-25 | L1 |  |  | 1 | 1.4 | HAA5 > 45UG/L. RETURN TO AM DURING 3RD QUARTER_JMF
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 58.6 | UG/L | 60.4999 | 2018-09-25 | L1 |  |  | 1 | 1.4 | HAA5 > 45UG/L. RETURN TO AM DURING 3RD QUARTER_JMF
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-10-23 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-10-23 | AAA
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-02-14 | AAA |  | 0.5499 |  |  | 1QM TOT XYLENE (2QM DUE 4-6/19)_VP. MISSING Q2 INPUT Q3 11/4/19. NEED DX WHEN Q2 REC GC
3490986 | PLEASANT HILL VILLAGE | SOC | 2326 | PENTACHLOROPHENOL | S | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.0449 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | S | 0 | UG/L | 0.5499 | 2019-02-14 | AAA |  | 0.1499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2931 | DIBROMOCHLOROPROPANE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2946 | ETHYLENE DIBROMIDE | S | 0 | UG/L | 0.0249 | 2019-02-14 | AAA |  | 0.0149 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2959 | CHLORDANE | S | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2005 | ENDRIN | S | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.0149 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2010 | LINDANE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2015 | METHOXYCLOR | S | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2020 | TOXAPHENE | S | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 1.4999 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2031 | DALAPON | S | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 1.4999 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2032 | DIQUAT | S | 0 | UG/L | 24.9999 | 2019-02-14 | AAA |  | 0.4499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2033 | ENDOTHALL | S | 0 | UG/L | 149.9999 | 2019-02-14 | AAA |  | 9.4999 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2034 | GLYPHOSATE | S | 0 | UG/L | 749.9999 | 2019-02-14 | AAA |  | 6.4999 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | S | 0 | UG/L | 449.9999 | 2019-02-14 | AAA |  | 0.6499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2036 | OXAMYL (VYDATE) | S | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 2.4999 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2037 | SIMAZINE | S | 0 | UG/L | 4.4999 | 2019-02-14 | AAA |  | 0.0749 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | S | 0 | UG/L | 6.4999 | 2019-02-14 | AAA |  | 0.6499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2040 | PICLORAM | S | 0 | UG/L | 549.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2041 | DINOSEB | S | 0 | UG/L | 7.4999 | 2019-02-14 | AAA |  | 0.2499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | S | 0 | UG/L | 54.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2046 | CARBOFURAN | S | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.9499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2050 | ATRAZINE | S | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 0.1499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2051 | ALACHLOR (LASSO) | S | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2065 | HEPTACHLOR | S | 0 | UG/L | 0.4499 | 2019-02-14 | AAA |  | 0.0449 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2067 | HEPTACHLOR EPOXIDE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2105 | 2 4-D | S | 0 | UG/L | 74.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2110 | 2 4 5-TP (Silvex) | S | 0 | UG/L | 54.9999 | 2019-02-14 | AAA |  | 0.2499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2274 | HEXACHLOROBENZENE | S | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.1499 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2306 | BENZO(A)PYRENE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-08-27 | AAA | 0.25 | 0.5499 |  |  | 2QM (3QM DUE 10-12/2019) ; QM/XY (RCVD 10-30-19)._VP [10-12/2019 3QM MISSED RESTART Q SAMPLING_VPU]
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-08-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-08-27 | AAA
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | S | 21.5 | UG/L | 80.4999 | 2019-11-19 | L1 | 0.32 |  | 1 | 0.6 | MAKUP SAMPLES. MISSED 3Q19 RETURN TO ROUTINE 2 LOCATIONS ANNUALLY_VPU
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 13.6 | UG/L | 60.4999 | 2019-11-19 | L1 | 0.9 |  | 1 | 0.6 | MAKUP SAMPLES. MISSED 3Q19 RETURN TO ROUTINE 2 LOCATIONS ANNUALLY_VPU
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-07 | AAA |  |  |  |  | NEW OPR TOM FELTON 6/10/16. EM 6/10/16 FOR QTRLY BACTES (1R 1D) & 2016 NN (POE/D). BB (8/5/16 EW HAS 7/16 NN - JAX WILL LATER INSERT INTO OCULUS)
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | N | 0.02 | MG/L | 10.4999 | 2015-07-07 | AAA |  |  |  |  | NEW OPR TOM FELTON 6/10/16. EM 6/10/16 FOR QTRLY BACTES (1R 1D) & 2016 NN (POE/D). BB (8/5/16 EW HAS 7/16 NN - JAX WILL LATER INSERT INTO OCULUS)
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | N | 0.3 | MG/L | 10.4999 | 2016-07-06 | AAA |  |  |  |  | 16 DONE (TOM FELTON) 9/12/16 EM WITH 8/16 N/C > COMMUNITY SCHEDULE ATTACHED SENT TO TOM FELTON & C MACEACHERN. BB
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-07-06 | AAA |  |  |  |  | 16 DONE (TOM FELTON) 9/12/16 EM WITH 8/16 N/C > COMMUNITY SCHEDULE ATTACHED SENT TO TOM FELTON & C MACEACHERN. BB
3491002 | KISSIMMEE RV PARK | RAD | 4020 | RADIUM-226 | N | 1.97 | PCI/L | 3.4999 | 2016-11-02 | AAA | 0.11 | 1.4999 |  |  | 1Q RADS(2/9/17 GA REVISED & R226 ADDED BY LAB. ORIG. GA OF 9.94 U INVALID. GA ACTUALLY 9.94 WITH MDL OF 2.5. R226 ANALYZED FROM SAME SAMPLE DUE TO GA > 5 PCI/L) ORIG. INCORRECT GA+R228 RCVD 12/7/16.
3491002 | KISSIMMEE RV PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 9.94 | PCI/L | 15.4999 | 2016-11-02 | AAA | 2.5 |  |  |  | 1Q RADS(2/9/17 GA REVISED & R226 ADDED BY LAB. ORIG. GA OF 9.94 U INVALID. GA ACTUALLY 9.94 WITH MDL OF 2.5. R226 ANALYZED FROM SAME SAMPLE DUE TO GA > 5 PCI/L) ORIG. INCORRECT GA+R228 RCVD 12/7/16.
3491002 | KISSIMMEE RV PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2016-11-02 | AAA | 0.7 | 1.4999 |  |  | 1Q RADS(2/9/17 GA REVISED & R226 ADDED BY LAB. ORIG. GA OF 9.94 U INVALID. GA ACTUALLY 9.94 WITH MDL OF 2.5. R226 ANALYZED FROM SAME SAMPLE DUE TO GA > 5 PCI/L) ORIG. INCORRECT GA+R228 RCVD 12/7/16.
3491002 | KISSIMMEE RV PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1025 | FLUORIDE | N | 0.16 | MG/L | 4.0499 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1045 | SELENIUM | N | 0.0013 | MG/L | 0.0549 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1052 | SODIUM | N | 9.9 | MG/L | 160.4999 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1017 | CHLORIDE | N | 16.2 | MG/L | 250.4999 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1022 | COPPER | N | 0.0071 | MG/L | 1.4999 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1025 | FLUORIDE | N | 0.15 | MG/L | 2.0499 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1055 | SULFATE | N | 20.9 | MG/L | 250.4999 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 5.8 | LN(10) |  | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 192 | MG/L | 500.4999 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2016-11-02 | AAA |  |  |  |  | Q DATA QUALIFIERS FOR COLOR PH FOAMING AGENTS
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-11-02 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2016-11-02 | AAA |  | 0.0149 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2016-11-02 | AAA |  | 0.0249 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2016-11-02 | AAA |  | 0.1499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2016-11-02 | AAA |  | 1.4999 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-11-02 | AAA |  | 1.4999 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2016-11-02 | AAA |  | 0.4499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2016-11-02 | AAA |  | 9.4999 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2016-11-02 | AAA |  | 6.4999 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2016-11-02 | AAA |  | 0.6499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2016-11-02 | AAA |  | 2.4999 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2016-11-02 | AAA |  | 0.0749 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2016-11-02 | AAA |  | 0.6499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2016-11-02 | AAA |  | 0.1499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2016-11-02 | AAA |  | 0.2499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2016-11-02 | AAA |  | 0.1499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2016-11-02 | AAA |  | 0.9499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2016-11-02 | AAA |  | 0.1499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2016-11-02 | AAA |  | 0.2499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2016-11-02 | AAA |  | 0.0449 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2016-11-02 | AAA |  | 0.0249 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2016-11-02 | AAA |  | 0.1499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2016-11-02 | AAA |  | 0.2499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2016-11-02 | AAA |  | 0.1499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2016-11-02 | AAA |  | 0.0249 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2016-11-02 | AAA |  | 0.0449 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2016-11-02 | AAA |  | 0.1499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2016-11-02 | AAA |  | 0.0249 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2016-11-02 | AAA |  | 0.0149 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2016-11-02 | AAA |  | 0.2499 |  |  | DIQUAT J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | N | 1.7 | MG/L | 10.4999 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1005 | ARSENIC | N | 0.0011 | MG/L | 0.0104 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | INOR | 1010 | BARIUM | N | 0.025 | MG/L | 2.4999 | 2016-11-02 | AAA |  |  |  |  | ARSENIC SELENIUM J DATA Q.
3491002 | KISSIMMEE RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.3 | UG/L | 60.4999 | 2016-12-21 | L1 |  |  |  | 1 | WWTF HOSE BIB; SAMPLE AGAIN 3RD Q 2017 IF RESULTS ARE LOW CAN BE REDUCED - PAF
3491002 | KISSIMMEE RV PARK | DBP | 2950 | TOTAL THMS | D | 19 | UG/L | 80.4999 | 2016-12-21 | L1 |  |  |  | 1 | WWTF HOSE BIB; SAMPLE AGAIN 3RD Q 2017 IF RESULTS ARE LOW CAN BE REDUCED - PAF
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2016-12-28 | AAA |  | 0.2499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2016-12-28 | AAA |  | 0.2499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2016-12-28 | AAA |  | 0.1499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2016-12-28 | AAA |  | 0.1499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0.91 | UG/L | 6.4999 | 2016-12-28 | AAA |  | 0.6499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2016-12-28 | AAA |  | 0.0749 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2016-12-28 | AAA |  | 0.6499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2016-12-28 | AAA |  | 1.4999 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2016-12-28 | AAA |  | 0.1499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2016-12-28 | AAA |  | 0.0249 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2016-12-28 | AAA |  | 0.0149 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2016-12-28 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2016-12-28 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2016-12-28 | AAA |  |  |  |  | Q DATA QUALIFIER
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2016-12-28 | AAA |  | 0.1499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2016-12-28 | AAA |  | 0.0249 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2016-12-28 | AAA |  | 0.1499 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2016-12-28 | AAA |  | 0.0249 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2016-12-28 | AAA |  | 0.0449 |  |  | INCOMPLETE MISSING 13 CONTAMINATES DI(2-ETHYLHEXYL)PHTHALATE DETECT (1QM)
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-23 | AAA |  | 6.4999
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-23 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-23 | AAA |  | 2.4999
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-03-23 | AAA |  | 0.0749
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-23 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-23 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-23 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-23 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-23 | AAA |  | 0.9499
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-23 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-23 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-23 | AAA |  | 0.0449
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-23 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-23 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-23 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-23 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-03-23 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-23 | AAA |  | 0.0449
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-23 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-23 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-23 | AAA |  | 0.0149
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-23 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-23 | AAA |  | 0.0149
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-23 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-23 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | AAA |  | 1.4999
3491002 | KISSIMMEE RV PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-23 | AAA |  | 1.4999
3491002 | KISSIMMEE RV PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-23 | AAA |  | 0.4499
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-23 | AAA |  | 9.4999
3491002 | KISSIMMEE RV PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-03-25 | AAA |  | 1.4999
3491002 | KISSIMMEE RV PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-03-25 | AAA
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-06-21 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-06-21 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-06-21 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-06-21 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-06-21 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-06-21 | AAA |  | 0.0449
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-06-21 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-06-21 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-06-21 | AAA |  | 0.0149
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-06-21 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-06-21 | AAA |  | 0.0449
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-06-21 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-06-21 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-06-21 | AAA |  | 0.9499
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-06-21 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-06-21 | AAA |  | 0.2499
3491002 | KISSIMMEE RV PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-06-21 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-06-21 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-06-21 | AAA |  | 0.0149
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-06-21 | AAA |  | 0.0249
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-06-21 | AAA |  | 0.1499
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-06-21 | AAA |  | 1.4999
3491002 | KISSIMMEE RV PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-06-21 | AAA |  | 1.4999
3491002 | KISSIMMEE RV PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-06-21 | AAA |  | 0.4499
3491002 | KISSIMMEE RV PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-06-21 | AAA |  | 9.4999
3491002 | KISSIMMEE RV PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-06-21 | AAA |  | 6.4999
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-06-21 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-06-21 | AAA |  | 2.4999
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-06-21 | AAA |  | 0.0749
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-06-21 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-23 | AAA |  | 1.4999 |  |  | 3QM AFTER BEING UPGRADED
3491002 | KISSIMMEE RV PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-06-23 | AAA |  |  |  |  | 3QM AFTER BEING UPGRADED
3491002 | KISSIMMEE RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2017-08-30 | L1 |  |  |  |  | MOVED TO TRIANNUAL STARTING 3RD QTR 2018-SLB
3491002 | KISSIMMEE RV PARK | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2017-08-30 | L1 |  |  |  |  | MOVED TO TRIANNUAL STARTING 3RD QTR 2018-SLB
3491002 | KISSIMMEE RV PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-09-26 | AAA | 1.3 |  |  |  | 4QM AFTER BEING UPGRADED (10/26/17 HYPRLNKD TO SB/JF-BB) [SAMPLE GA AND 228 IN 2021]-9 YR PLAN
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-09-26 | AAA | 0.01 | 0.2499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-09-26 | AAA | 0.2 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-09-26 | AAA | 0.5 | 0.5499 |  |  | 4Q VOC (4 QTRS SPLIT AMONG 2 COMPLIANCE PERIODS 2016-2017 GO TO ANNUAL 2017-2018-2019) 1ST AN. 2017 2ND AN. 2018 3RD AN. 2019 (4Q VOC CAN USUALLY DOUBLE AS 1ST AN. VOC) 10/26/17 HYPRLNKD TO SB&JF-BB.
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-09-26 | AAA | 0.01 | 0.0149 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-09-26 | AAA | 0.01 | 0.0249 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-09-26 | AAA | 0.05 | 0.1499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-09-26 | AAA | 0.5 | 1.4999 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-09-26 | AAA | 0.1 | 1.4999 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-09-26 | AAA | 0.4 | 0.4499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-09-26 | AAA | 9 | 9.4999 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-09-26 | AAA | 6 | 6.4999 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 7.77 | UG/L | 449.9999 | 2017-09-26 | AAA | 0.6 | 0.6499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-09-26 | AAA | 2 | 2.4999 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-09-26 | AAA | 0.07 | 0.0749 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-09-26 | AAA | 0.6 | 0.6499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-09-26 | AAA | 0.1 | 0.1499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-09-26 | AAA | 0.2 | 0.2499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-09-26 | AAA | 0.1 | 0.1499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-09-26 | AAA | 0.9 | 0.9499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-09-26 | AAA | 0.1 | 0.1499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-09-26 | AAA | 0.2 | 0.2499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-09-26 | AAA | 0.01 | 0.0449 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-09-26 | AAA | 0.01 | 0.0249 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-09-26 | AAA | 0.1 | 0.1499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-09-26 | AAA | 0.2 | 0.2499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-09-26 | AAA | 0.1 | 0.1499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-09-26 | AAA | 0.02 | 0.0249 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-09-26 | AAA | 0.04 | 0.0449 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-09-26 | AAA | 0.1 | 0.1499 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-09-26 | AAA | 0.02 | 0.0249 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-09-26 | AAA | 0.01 | 0.0149 |  |  | 4Q SOC(ANALYSIS DATES REVISED FOR DBCP&EDB-OK)10/26/17 HYPRLNKD TO SB/JF-BB. 10/29/17 2035 ADIPATE 7.77 QTRLY TESTING RQRD. 12/16 2039 PHTHALATE 0.91 QTRLY PHTHALATE ENDS ANNUAL PHTHALATE BEGINS 4Q.
3491002 | KISSIMMEE RV PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-09-26 | AAA | 0.7 | 1.4999 |  |  | 4QM AFTER BEING UPGRADED (10/26/17 HYPRLNKD TO SB/JF-BB) [SAMPLE GA AND 228 IN 2021]-9 YR PLAN
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-10-26 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-10-26 | AAA
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-02-09 | AAA |  | 0.6499 |  |  | START OF QTRLY SAMPLING FOR ADIPATE- 2018
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-06-19 | AAA | 0.6 | 0.6499
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-06-19 | AAA | 0.6 | 0.6499
3491002 | KISSIMMEE RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28 | UG/L | 60.4999 | 2018-09-17 | L1 |  |  |  | 1.2 | WWTF HOSE BIB
3491002 | KISSIMMEE RV PARK | DBP | 2950 | TOTAL THMS | D | 17.8 | UG/L | 80.4999 | 2018-09-17 | L1 |  |  |  | 1.2 | WWTF HOSE BIB
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-09-21 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1010 | BARIUM | N | 0.0144 | MG/L | 2.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1020 | CHROMIUM | N | 0.0011 | MG/L | 0.1499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1052 | SODIUM | N | 14.7 | MG/L | 160.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SEC | 1017 | CHLORIDE | N | 21.1 | MG/L | 250.4999 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.17 | LN(10) |  | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 176 | MG/L | 500.4999 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-10-29 | AAA |  | 0.2499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-10-29 | AAA |  | 0.1499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-10-29 | AAA |  | 0.9499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.1499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-10-29 | AAA |  | 0.2499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-10-29 | AAA |  | 0.0449 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.1499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-10-29 | AAA |  | 0.2499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.1499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.0449 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-10-29 | AAA |  | 0.1499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-10-29 | AAA |  | 0.0149 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-10-29 | AAA |  | 0.2499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1028 | IRON | N | 0.0385 | MG/L | 0.3499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1055 | SULFATE | N | 3.2 | MG/L | 250.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.17 | LN(10) |  | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 176 | MG/L | 500.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499 |  |  | SAMPLE 3 ANNUAL IN 2018 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-10-29 | AAA |  | 0.0149 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-10-29 | AAA |  | 0.1499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 1.4999 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 1.4999 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-10-29 | AAA |  | 0.4499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 9.4999 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-10-29 | AAA |  | 6.4999 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-10-29 | AAA |  | 0.6499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 2.4999 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-10-29 | AAA |  | 0.0749 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-10-29 | AAA |  | 0.6499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-10-29 | AAA |  | 0.1499 |  |  | 1ST AM FOR PHTALATE SAMPLE 4TH Q 2019 2020
3491002 | KISSIMMEE RV PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1028 | IRON | N | 0.0385 | MG/L | 0.3499 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1055 | SULFATE | N | 3.2 | MG/L | 250.4999 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-10-29 | AAA |  |  |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1017 | CHLORIDE | N | 21.1 | MG/L | 250.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-01 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-04-01 | AAA
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2019-09-24 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-09-24 | AAA |  | 0.5499
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2019-10-21 | AAA | 0.6 | 0.6499 |  |  | 2AM/2039 PHTHALATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-01-09 | L5 |  |  |  |  | 1/15 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-02-06 | L5 |  |  |  |  | 2/15 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-03-13 | L5 |  |  |  |  | 3/15 BROMATE - SW WP (3/15 BROMATE RAA IN OC 3/15 RAA = -0- 3/15 QTR AVG = -0-)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 2 | UG/L | 10.4999 | 2015-04-03 | L5 |  |  |  | 2 | 4/15 BROMATE - SW WP (PER 11/20/14 EM FROM AMBER TOHO WL. GO ON R.M. 2 SITES ANNUALLY EMERALD 4/23/15 & BALI 7/22/15 PER DEP EM 10/22/14)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 22.9 | UG/L | 80.4999 | 2015-04-21 | L1 |  |  |  | 1.6 | 2600 EMERALD ISLAND (ON R.M. 4/15 EMERALD SITE BALI SITE TO BE TESTED @ 7/22/15) 6/15 DBF IN OC W/RSLTS
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13 | UG/L | 60.4999 | 2015-04-21 | L1 |  |  |  | 1.6 | 2600 EMERALD ISLAND (ON R.M. 4/15 EMERALD SITE BALI SITE TO BE TESTED @ 7/22/15) 6/15 DBF IN OC W/RSLTS
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-05-01 | L5 |  |  |  |  | 5/15 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-06-05 | L5 |  |  |  |  | 6/15 BROMATE -SW WP (6/15 BROMATE RAA IN OC 6/15 RAA/BROMATE = 0.16 PER REPORT 6/15 QTR AVG/BROMATE=0.66)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-07-02 | L5 |  |  |  |  | 7/15 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.9 | UG/L | 60.4999 | 2015-07-24 | L2 |  |  |  | 1.4 | ON R.M.-17627 BALI BLVD. (TEST T/H 7/22/15-R.M) ? DBPS DONE FOR 2015 9/15 DBF W/RSLTS (R.M. IN 2016: TEST 4/23/16 AT 2600 EMERALD ISLAND TEST 7/22/16 AT 17627 BALI BLVD.)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 8.47 | UG/L | 80.4999 | 2015-07-24 | L2 |  |  |  | 1.4 | ON R.M.-17627 BALI BLVD. (TEST T/H 7/22/15-R.M) ? DBPS DONE FOR 2015 9/15 DBF W/RSLTS (R.M. IN 2016: TEST 4/23/16 AT 2600 EMERALD ISLAND TEST 7/22/16 AT 17627 BALI BLVD.)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-08-07 | L5 |  |  |  |  | 8/15 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-09-03 | L5 |  |  |  |  | 9/15 BROMATE - SW WP (9/15 RAA/BROMATE = 0.16 PER REPORT IN OCULUS)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-10-02 | L5 |  |  |  |  | 10/15 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-11-06 | L5 |  |  |  |  | 11/15 BROMATE - SW WP ***12/21/15 EW HAS 12/15 BROMATE FOR PROCESSING BY EMAIL)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-12-04 | L5 |  |  |  |  | 12/15 BROMATE - SW WP (12/15 BROMATE RAA IN OC 1/15-12/15 RAA=0.16 PER REPORT)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-01-08 | L5 |  |  |  |  | 1/16 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-02-05 | L5 |  |  |  |  | 2/16 BROMATE ? SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0.12 | MG/L | 10.4999 | 2016-02-23 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-03-04 | L5 |  |  |  |  | 3/16 BROMATE - SW WP (3/16 BROMATE RAA IN OC = -0-) (5/11 EW HAS 4/16 BROMATE)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-04-08 | L5 |  |  |  |  | 4/16 BROMATE - SW WP (7/29 EW HAS 6/16 BROMATE BY EM-NEED 5/16 BROMATE)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.3 | UG/L | 60.4999 | 2016-04-28 | L1 |  |  |  | 1.9 | ANNUAL T/H-2600 EMERALD ISLAND(TEST T/H 4/23/15) (R.M.) **FOR 2ND TEST IN YEAR TEST 17627 BALI BLVD. DUAL T/H ON OR NEAR 7/22/16.
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 22 | UG/L | 80.4999 | 2016-04-28 | L1 |  |  |  | 1.9 | ANNUAL T/H-2600 EMERALD ISLAND(TEST T/H 4/23/15) (R.M.) **FOR 2ND TEST IN YEAR TEST 17627 BALI BLVD. DUAL T/H ON OR NEAR 7/22/16.
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-05-06 | L5 |  |  |  |  | 5/16 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-06-03 | L5 |  |  |  |  | 6/16 BROMATE - SW WP (6/16 BROMATE RAA = -0- IN OC) 8/17 EW HAS 2ND QTR DBPS & DB REPORT FOR ENTRY ALREADY IN OCULUS
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-07-08 | L5 | 1.6 |  | 1 | 0 | 7/16 BROMATE - SW WP (C.R. NOT RQRD FOR BROMATE)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.2 | UG/L | 60.4999 | 2016-07-26 | L2 |  |  |  | 1.5 | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 28.9 | UG/L | 80.4999 | 2016-07-26 | L2 |  |  |  | 1.5 | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | S | 0 | UG/L | 10.4999 | 2016-08-05 | L5 | 79.8 |  |  |  | 8/16 BROMATE - SW WP; RESULT IS 79.8 U. LAB MDL IS 79.8 UG/L WHICH IS HIGHER THAN THE REG. MRL OF 5.0 UG/L. SAMPLES ARE INVALID. SYSTEM WILL DO PN. - PAF
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | S | 0 | UG/L | 10.4999 | 2016-09-02 | L5 |  |  |  |  | 9/16 BROMATE - SW WP;RESULT IS 8.0 UG/L QUALIFIER U LAB MDL IS 8.0 UG/L WHICH IS HIGHER THAN THE REG.MRL OF 5.0 UG/L. SMPLS ARE INVALID. SYS.WILL DO PN. - PAF(DEREK SENDING 10/16 PG 1 BROM REVISION)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-10-13 | L5 |  |  |  |  | BROMATE - SW WP ADDITIONAL FOR AUGUST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-10-14 | L5 |  |  |  |  | 10/16 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-11-10 | L5 |  |  |  |  | 11/16 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-01-13 | L5 |  |  |  |  | 01/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-02-03 | L5 |  |  |  |  | 02/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0.94 | MG/L | 10.4999 | 2017-02-27 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP3
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | WTP3
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-04-07 | L5 |  |  |  |  | 04/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.8 | UG/L | 60.4999 | 2017-04-27 | L1 |  |  |  | 1.3 | 2600 EMERALD ISLAND(TEST T/H 4/23/15)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 22.7 | UG/L | 80.4999 | 2017-04-27 | L1 |  |  |  | 1.3 | 2600 EMERALD ISLAND(TEST T/H 4/23/15)
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 163 | MG/L | 500.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1010 | BARIUM | N | 0.026 | MG/L | 2.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1025 | FLUORIDE | N | 0.57 | MG/L | 4.0499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1052 | SODIUM | N | 6.8 | MG/L | 160.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1017 | CHLORIDE | N | 8.6 | MG/L | 250.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1022 | COPPER | N | 0.0081 | MG/L | 1.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1025 | FLUORIDE | N | 0.57 | MG/L | 2.0499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1055 | SULFATE | N | 51.6 | MG/L | 250.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1920 | ODOR THRESHOLD | N | 3 |  | 3.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 194 | MG/L | 500.4999 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0.95 | MG/L | 10.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1005 | ARSENIC | N | 0.0005 | MG/L | 0.0104 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1010 | BARIUM | N | 0.015 | MG/L | 2.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1025 | FLUORIDE | N | 0.72 | MG/L | 4.0499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1030 | LEAD | N | 0.01 | MG/L | 0.0154 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1052 | SODIUM | N | 7.9 | MG/L | 160.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1017 | CHLORIDE | N | 12.4 | MG/L | 250.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1022 | COPPER | N | 0.0061 | MG/L | 1.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1025 | FLUORIDE | N | 0.72 | MG/L | 2.0499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1055 | SULFATE | N | 14 | MG/L | 250.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2017-04-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-05-05 | L5 |  |  |  |  | 05/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-06-01 | L5 |  |  |  |  | 06/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 4.43 | PCI/L | 15.4999 | 2017-06-02 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | WTP1 |  | 1.4999 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | WTP3 |  | 1.4999 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-06-02 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-07-07 | L5 |  |  |  |  | 07/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 21.1 | UG/L | 80.4999 | 2017-07-28 | L2 |  |  |  | 1.9 | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.4 | UG/L | 60.4999 | 2017-07-28 | L2 |  |  |  | 1.9 | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-08-04 | L5 |  |  |  |  | 08/17 BROMATE - SW WP (9/17 BROMATE RAA RCVD & HYPERLINKED TO SB/JF 10/9/17 - BB)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-29 | WTP1 |  | 6.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-29 | WTP1 |  | 9.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP1 |  | 2.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-29 | WTP1 |  | 0.0749
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-29 | WTP1 |  | 0.6499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-29 | WTP1 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-29 | WTP1 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP1 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP1 |  | 0.9499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP1 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP1 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-29 | WTP1 |  | 0.0449
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-29 | WTP1 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP1 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP1 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP1 |  | 0.0449
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-29 | WTP1 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-29 | WTP1 |  | 0.0149
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP1 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP3 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP3 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP3 |  | 0.0449
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-29 | WTP3 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-29 | WTP3 |  | 0.0149
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP3 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP3 |  | 0.0149
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP3 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP3 |  | 1.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP3 |  | 1.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-29 | WTP3 |  | 0.4499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-29 | WTP3 |  | 9.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-29 | WTP3 |  | 6.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-29 | WTP3 |  | 0.6499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP3 |  | 2.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-29 | WTP3 |  | 0.0749
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-29 | WTP3 |  | 0.6499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-29 | WTP3 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-29 | WTP3 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP3 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP3 |  | 0.9499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP3 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP3 |  | 0.2499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-29 | WTP3 |  | 0.0449
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-29 | WTP3 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP1 |  | 0.0149
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP1 |  | 0.1499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP1 |  | 1.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP1 |  | 1.4999
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-29 | WTP1 |  | 0.4499
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-29 | WTP1 |  | 0.6499
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-09-07 | L5 | 0.64 |  | 1 |  | 9/17 BROMATE - SW WP (9/17 BROMATE & 9/17 BROMATE RAA BOTH HYPERLINKED 10/9/17 TO SB & JF - BB)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-10-06 | L5 |  |  |  |  | 10/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-11-03 | L5 |  |  |  |  | 11/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-12-01 | L5 |  |  |  |  | 12/17 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-01-05 | L5 |  |  |  |  | 1/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-02-02 | L5 |  |  |  |  | 2/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0.87 | MG/L | 10.4999 | 2018-02-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP1 |  |  |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP3 |  |  |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-03-02 | L5 |  |  |  |  | 3/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-04-06 | L5 |  |  |  |  | 4/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 22.5 | UG/L | 80.4999 | 2018-04-23 | L1 | 0.32 |  | 1 | 1.5 | 2600 EMERALD ISLAND
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.8 | UG/L | 60.4999 | 2018-04-23 | L1 | 0.48 |  | 1 | 1.5 | 2600 EMERALD ISLAND
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-05-04 | L5 |  |  |  |  | 5/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-06-01 | L5 |  |  |  |  | 6/18 BROMATE - SW WP (6/18 BROMATE RAA RCVD & HLKD TO SB - BB)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-07-06 | L5 |  |  |  |  | 07/2018 BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.6 | UG/L | 60.4999 | 2018-07-26 | L2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 36.3 | UG/L | 80.4999 | 2018-07-26 | L2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-08-03 | L5 |  |  |  |  | 08/2018 BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-09-07 | L5
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-10-05 | L5 | 3.2 |  | 1 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-11-02 | L5 |  |  |  |  | 11/2018 BROMATE - SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0.92 | UG/L | 10.4999 | 2018-12-07 | L5 | 0.64 |  |  |  | BROMATE (12/18 BROMATE RAA RCVD & HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-01-04 | L5 | 0.64 |  | 1 |  | 1/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-02-01 | L5 | 0.64 |  | 1 |  | 2/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0.56 | MG/L | 10.4999 | 2019-02-28 | WTP1
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP1
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | WTP3
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-03-01 | L5 | 0.64 |  | 1 |  | 3/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-04-05 | L5 |  |  | 1 |  | 2019-04 BROMATE - SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 29.3 | UG/L | 80.4999 | 2019-04-26 | L1 |  |  | 1 | 1.5 | 2600 EMERALD ISLAND(TEST T/H 4/23/15)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.6 | UG/L | 60.4999 | 2019-04-26 | L1 |  |  | 1 | 1.5 | 2600 EMERALD ISLAND(TEST T/H 4/23/15)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-05-03 | L5 |  |  |  |  | 2019-05 SOUTHWEST POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-06-07 | L5 | 0.64 |  | 1 |  | 6/19 BROMATE - SW WP (HLKD) 6/19 BROMATE RAA RCVD (HLKD SEP)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 5.1 | UG/L | 10.4999 | 2019-07-05 | L5 |  |  | 1 |  | 07/2019 BROMATE - SOUTHWEST POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | D | 36 | UG/L | 80.4999 | 2019-07-25 | L2 |  |  | 1 | 1.3 | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.4 | UG/L | 60.4999 | 2019-07-25 | L2 |  |  | 1 | 1.3 | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-08-02 | L5 |  |  | 1 |  | 2019-08 BROMATE / SOUTHWEST POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-09-06 | L5 |  |  |  |  | 2019 09 - BROMATE / SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-10-04 | L5 | 0.64 |  | 1 |  | BROMATE - SW POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-11-01 | L5 | 0.64 |  | 1 |  | 11/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | D | 0 | UG/L | 10.4999 | 2019-12-06 | L5 | 0.64 |  | 1 |  | BROMATE LRAA = 0.05
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 94.6 | UG/L | 80.4999 | 2015-08-26 | L1 |  |  |  | 0.7 | GUARD SHACK (START QM/T+H - TTHMS 94.6 UG/L > MCL OF 80 UG/L) EM 9/29/15 TO BIOMETRICS & OWNER
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.8 | UG/L | 60.4999 | 2015-08-26 | L1 |  |  |  | 0.7 | GUARD SHACK (START QM/T+H - TTHMS 94.6 UG/L > MCL OF 80 UG/L) EM 9/29/15 TO BIOMETRICS & OWNER
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-09-18 | AAA |  | 0.6499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-09-18 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-09-18 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-09-18 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-09-18 | AAA |  | 0.9499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-09-18 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-09-18 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-09-18 | AAA |  | 0.0449 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-09-18 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-09-18 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-09-18 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-09-18 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-09-18 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-09-18 | AAA |  | 0.0449 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-09-18 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-09-18 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-09-18 | AAA |  | 0.0149 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-09-18 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | N | 0.078 | MG/L | 10.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1010 | BARIUM | N | 0.012 | MG/L | 2.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1025 | FLUORIDE | N | 0.22 | MG/L | 4.0499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1052 | SODIUM | N | 32.4 | MG/L | 160.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (3 ODOR RECS RCVD-ALL OK) 1/26/16 EM & 2/26/16 EM FOR 3 ODOR RECS TO BIOMETRICS
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1017 | CHLORIDE | N | 35.8 | MG/L | 250.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1022 | COPPER | N | 0.0031 | MG/L | 1.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1025 | FLUORIDE | N | 0.22 | MG/L | 2.0499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1028 | IRON | N | 0.046 | MG/L | 0.3499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1055 | SULFATE | N | 3.5 | MG/L | 250.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1920 | ODOR THRESHOLD | N | 4 |  | 3.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.4 | LN(10) |  | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 313 | MG/L | 500.4999 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 2905 | FOAMING AGENTS | N | 0.06 |  | 0.5499 | 2015-09-18 | AAA |  |  |  |  | ODOR 4 T.O.N. (ND. 3 ODOR RECS) EM 1/26/16 & EM REMINDER 2/26/16 FOR 3 ODOR RECS TO BIOMETRICS - BB
3491077 | BOGGY CREEK RESORT AND RV PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-09-18 | AAA |  |  |  |  | RADS DUE 2021
3491077 | BOGGY CREEK RESORT AND RV PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-09-18 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-09-18 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL BDL)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-09-18 | AAA |  | 0.0149 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-09-18 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-09-18 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-09-18 | AAA |  | 1.4999 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2031 | DALAPON | N | 1.1 | UG/L | 249.9999 | 2015-09-18 | AAA |  | 1.4999 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-09-18 | AAA |  | 0.4499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-09-18 | AAA |  | 9.4999 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-09-18 | AAA |  | 6.4999 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-09-18 | AAA |  | 0.6499 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-09-18 | AAA |  | 2.4999 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-09-18 | AAA |  | 0.0749 |  |  | 3YR SOC (DALAPON 1.1 - NO QM RQRD DOES NOT EXCEED RDL OF 1 = 1.4999)
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.6 | UG/L | 60.4999 | 2015-10-22 | L1 |  |  |  | 0.2 | (4/28 EW HAS 1/16 DBPS JUST RCVD 4/28/16 FROM BIOMETRICS FOR 1ST TM) 2QM-GUARD SHACK (3QM/T+H 1/16-IT'S SCHEDULED 1/26/16 WEEK PER JESSICA) 12/15 LRAA/T=50.4 LRAA/H=17.85) CONT. QM/DBPS
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 107 | UG/L | 80.4999 | 2015-10-22 | L1 |  |  |  | 0.2 | (4/28 EW HAS 1/16 DBPS JUST RCVD 4/28/16 FROM BIOMETRICS FOR 1ST TM) 2QM-GUARD SHACK (3QM/T+H 1/16-IT'S SCHEDULED 1/26/16 WEEK PER JESSICA) 12/15 LRAA/T=50.4 LRAA/H=17.85) CONT. QM/DBPS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | D | 7.3 | LN(10) |  | 2015-12-20 | DIST |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | N | 170 | MG/L | 0 | 2015-12-20 | AAA |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1930 | TOTAL DISSOLVED SOLIDS | D | 260 | MG/L |  | 2015-12-20 | DIST |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 22 |  |  | 2015-12-20 | DIST |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | D | 210 | MG/L |  | 2015-12-20 | DIST |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | N | 7.3 | LN(10) |  | 2015-12-20 | AAA |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | N | 210 | MG/L |  | 2015-12-20 | AAA |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22 |  |  | 2015-12-20 | AAA |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1930 | TOTAL DISSOLVED SOLIDS | N | 260 | MG/L |  | 2015-12-20 | AAA |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | D | 170 | MG/L | 0 | 2015-12-20 | DIST |  |  |  |  | 1ST ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 22 |  |  | 2015-12-30 | DIST |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | D | 210 | MG/L |  | 2015-12-30 | DIST |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | D | 7.3 | LN(10) |  | 2015-12-30 | DIST |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | D | 180 | MG/L | 0 | 2015-12-30 | DIST |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23 |  |  | 2015-12-30 | AAA |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | N | 210 | MG/L |  | 2015-12-30 | AAA |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-12-30 | AAA |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | N | 180 | MG/L | 0 | 2015-12-30 | AAA |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1930 | TOTAL DISSOLVED SOLIDS | D | 260 | MG/L |  | 2015-12-30 | DIST |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1930 | TOTAL DISSOLVED SOLIDS | N | 260 | MG/L |  | 2015-12-30 | AAA |  |  |  |  | 2ND ROUND WQP DUE TO 2015 AL EXCEEDANCE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 99.9 | UG/L | 80.4999 | 2016-01-27 | L1 |  |  |  | 0.8 | GUARD SHACK (3/16 LRAA/T=75.375 LRAA/H=29.175) 3/16 OE VALUE/T = 100.35 (ND. OE REPORT>EM 4/28/16 TO BIOMETRICS & OWNER
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45.3 | UG/L | 60.4999 | 2016-01-27 | L1 |  |  |  | 0.8 | GUARD SHACK (3/16 LRAA/T=75.375 LRAA/H=29.175) 3/16 OE VALUE/T = 100.35 (ND. OE REPORT>EM 4/28/16 TO BIOMETRICS & OWNER
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2016-01-31 | AAA |  |  |  |  | 1/31 ODOR -0-
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2016-02-01 | AAA |  |  |  |  | 2/1 ODOR -0-
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2016-02-02 | AAA |  |  |  |  | 2/2 ODOR -0- (ALL 3 ODOR RECHECKS -0- NOTHING ELSE NEEDED) ODOR A.D. REVISION RCVD & IN OC
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | N | 0.085 | MG/L | 10.4999 | 2016-04-26 | AAA |  |  |  |  | ABSOLUTE WATER IS OPERATING IT AGAIN AS OF 8/17/16. BB
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.5 | UG/L | 60.4999 | 2016-04-26 | L1 |  |  |  | 0.7 | ALSO IS ADDNG CORROSION CON>PB+CU)GUARD SHACK (6/16 LRAA/T=106.375 LRAA/H=39.8) ND. PN>EM 5/10/16 TO BIOMETRICS OWNER. 5/10/16 REFERRAL TO WP & JF. 5/17/16 MTG HELD TO DISCUSS CA/TTHMS PER JF. BB
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-04-26 | AAA |  |  |  |  | ABSOLUTE WATER IS OPERATING IT AGAIN AS OF 8/17/16. BB
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 124 | UG/L | 80.4999 | 2016-04-26 | L1 |  |  |  | 0.7 | ALSO IS ADDNG CORROSION CON>PB+CU)GUARD SHACK (6/16 LRAA/T=106.375 LRAA/H=39.8) ND. PN>EM 5/10/16 TO BIOMETRICS OWNER. 5/10/16 REFERRAL TO WP & JF. 5/17/16 MTG HELD TO DISCUSS CA/TTHMS PER JF. BB
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 114 | UG/L | 60.4999 | 2016-07-27 | L1 |  |  |  | 1 | (8/25 OPERATIONAL T/H IN OC-PN ISSUED 9/2)GUARD SHACK(9/16 LRAA/T=118.475 LRAA/H=59.35)NXT QTR HAA5 MAY GO OVER MCL.BIOMETRICS LOCKED OUT AS OF 8/12/16(?)PER JESSICA 8/26/16 EM.SEE C-E 8/29 PWS ENTRY
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 143 | UG/L | 80.4999 | 2016-07-27 | L1 |  |  |  | 1 | (8/25 OPERATIONAL T/H IN OC-PN ISSUED 9/2)GUARD SHACK(9/16 LRAA/T=118.475 LRAA/H=59.35)NXT QTR HAA5 MAY GO OVER MCL.BIOMETRICS LOCKED OUT AS OF 8/12/16(?)PER JESSICA 8/26/16 EM.SEE C-E 8/29 PWS ENTRY
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.61 | UG/L | 60.4999 | 2016-12-19 | L2 |  |  |  | 1.3 | MANAGERS HOUSE-MAXIMUM RESIDENCE IS THE LOCATION ON THE DBP REPORT.
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 25.41 | UG/L | 80.4999 | 2016-12-19 | L2 |  |  |  | 1.3 | MANAGERS HOUSE-MAXIMUM RESIDENCE IS THE LOCATION ON THE DBP REPORT.
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-27 | AAA | 0.053 |  |  |  | 16 DONE (RCVD 2/10/17) DARYL RIGDON ABSOLUTE WATER (ALREADY HAD 4/16 NN RESULTS ENTERED - THESE ARE EXTRA)
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | N | 0.27 | MG/L | 10.4999 | 2016-12-27 | AAA | 0.051 |  |  |  | 16 DONE (RCVD 2/10/17) DARYL RIGDON ABSOLUTE WATER (ALREADY HAD 4/16 NN RESULTS ENTERED - THESE ARE EXTRA)
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.4 | UG/L | 60.4999 | 2017-03-28 | L2 |  |  |  | 1.8 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 33.75 | UG/L | 80.4999 | 2017-03-28 | L2 |  |  |  | 1.8 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | N | 0.19 | MG/L | 10.4999 | 2017-07-12 | AAA | 0.051 |  |  |  | NN (KENT SCHWING) PG 1 SIGNED AS RQRD - ALL OK (IN FINAL CHEM HOLDING FOLDER 9/19/17)
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-07-12 | AAA | 0.053 |  |  |  | NN (KENT SCHWING) PG 1 SIGNED AS RQRD - ALL OK (IN FINAL CHEM HOLDING FOLDER 9/19/17)
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 66.81 | UG/L | 60.4999 | 2017-07-28 | L2 |  |  | 1 | 2.2 | MISSED 2Q START 4 CONSEC QS AGAIN. CONTINUE ISSUING PN FOR LRAA AT GUARD SHACK UNTIL 4Q AT MANAGERS HOUSE_JMF
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 149.35 | UG/L | 80.4999 | 2017-07-28 | L2 |  |  | 1 | 2.2 | MISSED 2Q START 4 CONSEC QS AGAIN. CONTINUE ISSUING PN FOR LRAA AT GUARD SHACK UNTIL 4Q AT MANAGERS HOUSE_JMF
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | D | 0.19 | MG/L | 10.4999 | 2017-11-10 | AAA |  |  |  |  | *EXTRA SAMPLE TAKEN SLB
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | D | 0.16 | MG/L | 1.4999 | 2017-11-10 | AAA |  |  |  |  | *EXTRA SAMPLE TAKEN SLB
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-12-11 | AAA |  |  |  |  | *EXTRA SAMPLES TAKEN**
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | N | 0.19 | MG/L | 10.4999 | 2017-12-11 | AAA |  |  |  |  | *EXTRA SAMPLES TAKEN**
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.09 | UG/L | 60.4999 | 2017-12-13 | L2 |  |  |  | 1.23 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 70.16 | UG/L | 80.4999 | 2017-12-13 | L2 |  |  |  | 1.23 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 65.35 | UG/L | 80.4999 | 2018-02-21 | L2 |  |  |  | 1.08 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.51 | UG/L | 60.4999 | 2018-02-21 | L2 |  |  |  | 1.08 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-21 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | N | 0.18 | MG/L | 10.4999 | 2018-02-21 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.26 | UG/L | 60.4999 | 2018-05-23 | L2 |  |  |  | 0.88 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 88.06 | UG/L | 80.4999 | 2018-05-23 | L2 |  |  |  | 0.88 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.02 | UG/L | 60.4999 | 2018-08-10 | L2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 50.8 | UG/L | 80.4999 | 2018-08-10 | L2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 27.46 | UG/L | 80.4999 | 2018-11-12 | L2 |  |  |  | 0.93 | 2950-MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.43 | UG/L | 60.4999 | 2018-11-12 | L2 |  |  |  | 0.93 | 2950-MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | D | 0.24 | MG/L | 10.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | D | 0 | MG/L | 1.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1005 | ARSENIC | D | 0 | MG/L | 0.0104 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1010 | BARIUM | D | 0.012 | MG/L | 2.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1015 | CADMIUM | D | 0 | MG/L | 0.0055 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1020 | CHROMIUM | D | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1024 | CYANIDE | D | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1025 | FLUORIDE | D | 0.24 | MG/L | 4.0499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1030 | LEAD | D | 0 | MG/L | 0.0154 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1035 | MERCURY | D | 0.0001 | MG/L | 0.0024 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1036 | NICKEL | D | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1045 | SELENIUM | D | 0 | MG/L | 0.0549 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1052 | SODIUM | D | 35 | MG/L | 160.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1074 | ANTIMONY | D | 0 | MG/L | 0.0065 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1075 | BERYLLIUM | D | 0 | MG/L | 0.0045 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1085 | THALLIUM | D | 0 | MG/L | 0.0025 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1002 | ALUMINUM | D | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1017 | CHLORIDE | D | 36 | MG/L | 250.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1022 | COPPER | D | 0.0051 | MG/L | 1.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1025 | FLUORIDE | D | 0.24 | MG/L | 2.0499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1028 | IRON | D | 0 | MG/L | 0.3499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1032 | MANGANESE | D | 0 | MG/L | 0.0549 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1050 | SILVER | D | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1055 | SULFATE | D | 5 | MG/L | 250.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1095 | ZINC | D | 0.1 | MG/L | 5.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1905 | COLOR | D | 5 | COLOR UNITS | 15.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1920 | ODOR THRESHOLD | D | 0 |  | 3.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | D | 7.93 | LN(10) |  | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | D | 360 | MG/L | 500.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 2905 | FOAMING AGENTS | D | 0.056 |  | 0.5499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | D | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | D | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2955 | TOT XYLENE | D | 0 | UG/L | 10499.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2964 | DICHLOROMETHANE | D | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | D | 0 | UG/L | 649.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2969 | P-DICHLOROBENZENE | D | 0 | UG/L | 75.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2976 | VINYL CHLORIDE | D | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2977 | 1 1-DICHLOROETHENE | D | 0 | UG/L | 7.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | D | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2980 | 1 2-DICHLOROETHANE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | D | 0 | UG/L | 249.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | D | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2984 | TRICHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | D | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2989 | CHLOROBENZENE | D | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2990 | BENZENE | D | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2991 | TOLUENE | D | 0 | UG/L | 1499.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2992 | ETHYLBENZENE | D | 0 | UG/L | 749.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2996 | STYRENE | D | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.28 | UG/L | 60.4999 | 2019-02-13 | L2 | 0.91 |  | 1 | 0.81 | MANAGER'S HOUSE (HLKD TO KC JF-BB)
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 36.42 | UG/L | 80.4999 | 2019-02-13 | L2 | 0.39 |  | 1 | 0.81 | MANAGER'S HOUSE (HLKD TO KC JF-BB)
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-22 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | N | 0.51 | MG/L | 10.4999 | 2019-04-22 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.53 | UG/L | 60.4999 | 2019-05-10 | L2 |  |  |  | 0.87 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 66.22 | UG/L | 80.4999 | 2019-05-10 | L2 |  |  |  | 0.87 | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 64.52 | UG/L | 80.4999 | 2019-08-12 | L2 |  |  |  | 0.96 | MANAGERS HOUSE [LRAA TTHM=48.655 HAA5=19.74]
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.71 | UG/L | 60.4999 | 2019-08-12 | L2 |  |  |  | 0.96 | MANAGERS HOUSE [LRAA TTHM=48.655 HAA5=19.74]
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | D | 54.64 | UG/L | 80.4999 | 2019-11-14 | L2 |  |  |  | 0.72 | MANAGERS HOUSE [LRAA TTHM=55.45; HAA5= 19.17] TEST BOTH ANNUALLY 2Q_VP
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.15 | UG/L | 60.4999 | 2019-11-14 | L2 |  |  |  | 0.72 | MANAGERS HOUSE [LRAA TTHM=55.45; HAA5= 19.17] TEST BOTH ANNUALLY 2Q_VP
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.56 | UG/L | 60.4999 | 2015-09-10 | L1 |  |  |  | 0.5 | 805 PARKWAY EAST (REMAIN ON R.M. ? NEXT T/H DUE @ 9/10/18) <500
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | D | 56.57 | UG/L | 80.4999 | 2015-09-10 | L1 |  |  |  | 0.5 | 805 PARKWAY EAST (REMAIN ON R.M. ? NEXT T/H DUE @ 9/10/18) <500
3491298 | SHELTER COVE RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1025 | FLUORIDE | N | 0.18 | MG/L | 4.0499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1052 | SODIUM | N | 31 | MG/L | 160.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1017 | CHLORIDE | N | 32 | MG/L | 250.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1022 | COPPER | N | 0.032 | MG/L | 1.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1025 | FLUORIDE | N | 0.18 | MG/L | 2.0499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1028 | IRON | N | 0.04 | MG/L | 0.3499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1032 | MANGANESE | N | 0.0042 | MG/L | 0.0549 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1055 | SULFATE | N | 3.1 | MG/L | 250.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1095 | ZINC | N | 0.0085 | MG/L | 5.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.7 | LN(10) |  | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 320 | MG/L | 500.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-10-13 | AAA |  | 0.0149
3491298 | SHELTER COVE RESORT | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491298 | SHELTER COVE RESORT | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-10-13 | AAA |  | 0.1499
3491298 | SHELTER COVE RESORT | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 1.4999
3491298 | SHELTER COVE RESORT | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-10-13 | AAA |  | 1.4999
3491298 | SHELTER COVE RESORT | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-10-13 | AAA |  | 0.4499
3491298 | SHELTER COVE RESORT | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 9.4999
3491298 | SHELTER COVE RESORT | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-10-13 | AAA |  | 6.4999
3491298 | SHELTER COVE RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-10-13 | AAA |  | 0.6499
3491298 | SHELTER COVE RESORT | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-10-13 | AAA |  | 2.4999
3491298 | SHELTER COVE RESORT | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-10-13 | AAA |  | 0.0749
3491298 | SHELTER COVE RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491298 | SHELTER COVE RESORT | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-10-13 | AAA |  | 0.1499
3491298 | SHELTER COVE RESORT | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-10-13 | AAA |  | 0.2499
3491298 | SHELTER COVE RESORT | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.1499
3491298 | SHELTER COVE RESORT | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491298 | SHELTER COVE RESORT | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.0449
3491298 | SHELTER COVE RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-10-13 | AAA |  | 0.1499
3491298 | SHELTER COVE RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491298 | SHELTER COVE RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-10-13 | AAA |  | 0.0149
3491298 | SHELTER COVE RESORT | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-10-13 | AAA |  | 0.2499
3491298 | SHELTER COVE RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-10-13 | AAA |  |  |  |  | DUE 2021
3491298 | SHELTER COVE RESORT | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-13 | AAA |  | 1.4999 |  |  | DUE 2021
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-10-13 | AAA
3491298 | SHELTER COVE RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-10-13 | AAA |  | 0.6499
3491298 | SHELTER COVE RESORT | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-10-13 | AAA |  | 0.1499
3491298 | SHELTER COVE RESORT | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-10-13 | AAA |  | 0.2499
3491298 | SHELTER COVE RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-10-13 | AAA |  | 0.1499
3491298 | SHELTER COVE RESORT | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-10-13 | AAA |  | 0.9499
3491298 | SHELTER COVE RESORT | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.1499
3491298 | SHELTER COVE RESORT | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-10-13 | AAA |  | 0.2499
3491298 | SHELTER COVE RESORT | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-10-13 | AAA |  | 0.0449
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-12-20 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-20 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-11-10 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-11-10 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2018-02-20 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-20 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.12 | LN(10) |  | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 270 | MG/L | 500.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 2905 | FOAMING AGENTS | N | 0.064 |  | 0.5499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1010 | BARIUM | N | 0.0048 | MG/L | 2.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1025 | FLUORIDE | N | 0.28 | MG/L | 4.0499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1052 | SODIUM | N | 21 | MG/L | 160.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1017 | CHLORIDE | N | 27 | MG/L | 250.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1025 | FLUORIDE | N | 0.28 | MG/L | 2.0499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1028 | IRON | N | 0.13 | MG/L | 0.3499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1032 | MANGANESE | N | 0.0044 | MG/L | 0.0549 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1055 | SULFATE | N | 3.1 | MG/L | 250.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 53.75 | UG/L | 60.4999 | 2018-08-14 | L1 | 0.91 |  | 1 | 0.2 | RETURN TO ROUTINE ANNUAL MONITORING DURING 3RD Q_JMF
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | D | 72.04 | UG/L | 80.4999 | 2018-08-14 | L1 | 0.39 |  | 1 | 0.2 | RETURN TO ROUTINE ANNUAL MONITORING DURING 3RD Q_JMF
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-23 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | N | 0.46 | MG/L | 10.4999 | 2019-04-23 | AAA
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | D | 157.87 | UG/L | 80.4999 | 2019-08-22 | L1 |  |  | 1 |  | 805 PARKWAY EAST EXCEEDANCE PLACE ON QUARTERLY_JB
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.77 | UG/L | 60.4999 | 2019-08-22 | L1 |  |  | 1 |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 1.5 | UG/L | 60.4999 | 2019-11-20 | L1 | 0.91 |  | 1 | 0.78 | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | D | 12.99 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.39 |  | 1 | 0.78 | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.37 | UG/L | 60.4999 | 2019-11-20 | L2 | 0.91 |  | 2 | 0.89 | 392 PINE ISLAND
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | D | 67.83 | UG/L | 80.4999 | 2019-11-20 | L2 | 0.39 |  | 2 | 0.89 | 392 PINE ISLAND
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-01-07 | WTP4 |  | 0.6499 |  |  | 2QM/ADIPATE & PHTHALATE (3QM/2035+2039-WP4 DUE 6/15) >>>6/12/15 EM TO ADA FOR F.PAGES FOR 4/15 2039 & 2035 - WP4 - BB (CC'D FLOWERS)
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-01-07 | WTP4 |  | 0.6499 |  |  | 2QM/ADIPATE & PHTHALATE (3QM/2035+2039-WP4 DUE 6/15) >>>6/12/15 EM TO ADA FOR F.PAGES FOR 4/15 2039 & 2035 - WP4 - BB (CC'D FLOWERS)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 21 | UG/L | 80.4999 | 2015-02-16 | L4 |  |  |  | 0.8 | (6/12/15 EM SNT TO ADA ASKING FOR REVISED 2ND QTR 2015 DBF-EW HAS 5/20/15 T/H RSLTS&DBF-NO LRAA OR OE MCLS) 803 MASSACHUSETTS AVE. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.6 | UG/L | 60.4999 | 2015-02-16 | L4 |  |  |  | 0.8 | (6/12/15 EM SNT TO ADA ASKING FOR REVISED 2ND QTR 2015 DBF-EW HAS 5/20/15 T/H RSLTS&DBF-NO LRAA OR OE MCLS) 803 MASSACHUSETTS AVE. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 21.6 | UG/L | 80.4999 | 2015-02-16 | L3 |  |  |  | 0.6 | 3600 CANOE CREEK RD. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.8 | UG/L | 60.4999 | 2015-02-16 | L3 |  |  |  | 0.6 | 3600 CANOE CREEK RD. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 22.9 | UG/L | 80.4999 | 2015-02-16 | L2 |  |  |  | 2.4 | 4805 DOC DR. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.5 | UG/L | 60.4999 | 2015-02-16 | L2 |  |  |  | 2.4 | 4805 DOC DR. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 25.2 | UG/L | 80.4999 | 2015-02-16 | L1 |  |  |  | 2.6 | 5371 MAJESTIC ISLAND CIR. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.1 | UG/L | 60.4999 | 2015-02-16 | L1 |  |  |  | 2.6 | 5371 MAJESTIC ISLAND CIR. (NO LRAA MCLS VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-04-06 | WTP4 | 0.6 | 0.6499 |  |  | 3QM/ADIPATE & PHTHALATE (4QM/2035+2039-WP4 DUE 9/15) IN OC >>>6/17/15 EM RMNDR TO ADA FOR 4QM 9/15 2039 & 2035 - WP4 - BB
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-04-06 | WTP4 | 0.6 | 0.6499 |  |  | 3QM/ADIPATE & PHTHALATE (4QM/2035+2039-WP4 DUE 9/15) IN OC >>>6/17/15 EM RMNDR TO ADA FOR 4QM 9/15 2039 & 2035 - WP4 - BB
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.9 | UG/L | 60.4999 | 2015-05-20 | L2 |  |  |  | 1.2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45.1 | UG/L | 60.4999 | 2015-05-20 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 40.4 | UG/L | 80.4999 | 2015-05-20 | L4 |  |  |  | 0.8 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 39.4 | UG/L | 80.4999 | 2015-05-20 | L2 |  |  |  | 1.2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 47.1 | UG/L | 60.4999 | 2015-05-20 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 57.6 | UG/L | 80.4999 | 2015-05-20 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.9 | UG/L | 60.4999 | 2015-05-20 | L4 |  |  |  | 0.8 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 62.4 | UG/L | 80.4999 | 2015-05-20 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-01 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-07-01 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-01 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-07-01 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-01 | WTP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-07-01 | WTP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-07-01 | WTP4 |  | 0.6499 |  |  | 4QM/ADIPATE & PHTHALATE - WP4 (1AM/2035+2039-WP4 1Q 2016>EM TO ADA 7/23/15 W/RQRMNT)
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-07-01 | WTP4 |  | 0.6499 |  |  | 4QM/ADIPATE & PHTHALATE - WP4 (1AM/2035+2039-WP4 1Q 2016>EM TO ADA 7/23/15 W/RQRMNT)
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-07-01 | WTP4 |  | 0.0249 |  |  | 4QM/ADIPATE & PHTHALATE - WP4 (1AM/2035+2039-WP4 1Q 2016>EM TO ADA 7/23/15 W/RQRMNT)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 21.6 | UG/L | 80.4999 | 2015-08-19 | L4 |  |  |  | 1.6 | (12/22/15 EW HAS 11/15 DBPS WITH 12/15 QTR DBF FOR PROCESSING) 803 MASSACHUSETTS AVE. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.4 | UG/L | 60.4999 | 2015-08-19 | L4 |  |  |  | 1.6 | (12/22/15 EW HAS 11/15 DBPS WITH 12/15 QTR DBF FOR PROCESSING) 803 MASSACHUSETTS AVE. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 31.2 | UG/L | 80.4999 | 2015-08-19 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 25.1 | UG/L | 80.4999 | 2015-08-19 | L2 |  |  |  | 1.6 | 4805 DOC DR. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.4 | UG/L | 60.4999 | 2015-08-19 | L2 |  |  |  | 1.6 | 4805 DOC DR. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 39.4 | UG/L | 80.4999 | 2015-08-19 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.4 | UG/L | 60.4999 | 2015-08-19 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.1 | UG/L | 60.4999 | 2015-08-19 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD. (NO LRAA MCLS OR OE EXCEEDANCES) 9/15 DBF WITH RESLTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.3 | UG/L | 60.4999 | 2015-11-17 | L4 |  |  |  | 2.5 | 803 MASSACHUSETTS AVE. (CONT. TO TEST QUARTERLY FOR T/H - DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 33.6 | UG/L | 80.4999 | 2015-11-17 | L4 |  |  |  | 2.5 | 803 MASSACHUSETTS AVE. (CONT. TO TEST QUARTERLY FOR T/H - DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 1.11 | UG/L | 60.4999 | 2015-11-17 | L1 |  |  |  | 1.9 | 5371 MAJESTIC ISLAND CIR. (CONT. TO TEST QUARTERLY FOR T/H ? DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 44.8 | UG/L | 80.4999 | 2015-11-17 | L1 |  |  |  | 1.9 | 5371 MAJESTIC ISLAND CIR. (CONT. TO TEST QUARTERLY FOR T/H ? DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.8 | UG/L | 60.4999 | 2015-11-17 | L2 |  |  |  | 2.4 | 4805 DOC DR. (CONT. TO TEST QUARTERLY FOR T/H ? DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.8 | UG/L | 80.4999 | 2015-11-17 | L2 |  |  |  | 2.4 | 4805 DOC DR. (CONT. TO TEST QUARTERLY FOR T/H ? DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.75 | UG/L | 60.4999 | 2015-11-17 | L3 |  |  |  | 2.9 | 3600 CANOE CREEK RD. (CONT. TO TEST QUARTERLY FOR T/H ? DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 29.4 | UG/L | 80.4999 | 2015-11-17 | L3 |  |  |  | 2.9 | 3600 CANOE CREEK RD. (CONT. TO TEST QUARTERLY FOR T/H ? DOES NOT QUALIFY FOR R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 5.3 | UG/L | 6.4999 | 2016-01-04 | WTP4 |  | 0.6499 |  |  | 1AM/2035+2039-WP4 1Q 2016 (2AM/2035+2039-WP4 1Q 2017)
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2016-01-04 | WTP4 |  | 0.6499 |  |  | 1AM/2035+2039-WP4 1Q 2016 (2AM/2035+2039-WP4 1Q 2017)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 34.1 | UG/L | 80.4999 | 2016-02-17 | L2 |  |  |  | 1.5 | 4805 DOC DR. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.2 | UG/L | 60.4999 | 2016-02-17 | L4 |  |  |  | 2 | (7/6 EW HAS 5/16 DBPS & DB REPORT>7/6EM TO ADA FOR DB REPORT REVISION-MINOR) 803 MASSACHUSETTS AVE. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 38.2 | UG/L | 80.4999 | 2016-02-17 | L3 |  |  |  | 1.5 | 3600 CANOE CREEK RD. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 52.4 | UG/L | 60.4999 | 2016-02-17 | L3 |  |  |  | 1.5 | 3600 CANOE CREEK RD. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49.1 | UG/L | 60.4999 | 2016-02-17 | L2 |  |  |  | 1.5 | 4805 DOC DR. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 33 | UG/L | 80.4999 | 2016-02-17 | L1 |  |  |  | 1.3 | 5371 MAJESTIC ISLAND CIR. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 63.7 | UG/L | 60.4999 | 2016-02-17 | L1 |  |  |  | 1.3 | 5371 MAJESTIC ISLAND CIR. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 28.9 | UG/L | 80.4999 | 2016-02-17 | L4 |  |  |  | 2 | (7/6 EW HAS 5/16 DBPS & DB REPORT>7/6EM TO ADA FOR DB REPORT REVISION-MINOR) 803 MASSACHUSETTS AVE. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES 3/16 QTR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 24.7 | UG/L | 80.4999 | 2016-05-19 | L2 |  |  |  | 1.4 | 4805 DOC DR. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.2 | UG/L | 60.4999 | 2016-05-19 | L2 |  |  |  | 1.4 | 4805 DOC DR. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.4 | UG/L | 60.4999 | 2016-05-19 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 34.3 | UG/L | 80.4999 | 2016-05-19 | L4 |  |  |  | 2 | 803 MASSACHUSETTS AVE. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.1 | UG/L | 60.4999 | 2016-05-19 | L4 |  |  |  | 2 | 803 MASSACHUSETTS AVE. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50 | UG/L | 80.4999 | 2016-05-19 | L3 |  |  |  | 1.2 | 3600 CANOE CREEK RD. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30 | UG/L | 60.4999 | 2016-05-19 | L3 |  |  |  | 1.2 | 3600 CANOE CREEK RD. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.7 | UG/L | 80.4999 | 2016-05-19 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR. (6/16 DB SHOWS LRAAS ARE = 40 T & < 30 H 3Q & 4Q L1 HIGHEST SINGLE RSLTS SO FAR-MAYBE WAIT UNTIL END OF YR TO GO TO R.M.)
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-07-07 | WTP4 | 0.2 |  |  |  | WP4 (NN-3 WPS IN OC)
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-07-07 | WTP4 | 0.2 |  |  |  | WP4 (NN-3 WPS IN OC)
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-07-07 | WTP2 | 0.2 |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-07-07 | WTP2 | 0.2 |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-07-07 | WTP1 | 0.2 |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-07-07 | WTP1 | 0.2 |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.5 | UG/L | 80.4999 | 2016-08-17 | L2 |  |  |  | 1.6 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.8 | UG/L | 60.4999 | 2016-08-17 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.2 | UG/L | 60.4999 | 2016-08-17 | L4 |  |  |  | 2 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 34.1 | UG/L | 80.4999 | 2016-08-17 | L4 |  |  |  | 2 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.6 | UG/L | 60.4999 | 2016-08-17 | L2 |  |  |  | 1.6 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 53.3 | UG/L | 80.4999 | 2016-08-17 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.3 | UG/L | 60.4999 | 2016-08-17 | L1 |  |  |  | 1.2 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48 | UG/L | 80.4999 | 2016-08-17 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.8 | UG/L | 60.4999 | 2016-11-16 | L3 |  |  |  | 1.8 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.1 | UG/L | 80.4999 | 2016-11-16 | L3 |  |  |  | 1.8 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.8 | UG/L | 60.4999 | 2016-11-16 | L4 |  |  |  | 1.4 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 27.4 | UG/L | 80.4999 | 2016-11-16 | L4 |  |  |  | 1.4 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 30.3 | UG/L | 80.4999 | 2016-11-16 | L2 |  |  |  | 1.2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.7 | UG/L | 60.4999 | 2016-11-16 | L2 |  |  |  | 1.2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.4 | UG/L | 80.4999 | 2016-11-16 | L1 |  |  |  | 1 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 46.5 | UG/L | 60.4999 | 2016-11-16 | L1 |  |  |  | 1 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-01-06 | WTP4 | 0.6 | 0.6499 |  |  | 2AM/2035+2039-WP4 1Q 2017 (3AM/2035+2039-WP4 1Q 2018) SHOULD BE FROM POE/D - MARKED RAW (AT WELL) BUT ALSO HAS WTP4 ON SAMPLE LOCATION LINE
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-01-06 | WTP4 | 0.6 | 0.6499 |  |  | 2AM/2035+2039-WP4 1Q 2017 (3AM/2035+2039-WP4 1Q 2018) SHOULD BE FROM POE/D - MARKED RAW (AT WELL) BUT ALSO HAS WTP4 ON SAMPLE LOCATION LINE
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.8 | UG/L | 60.4999 | 2017-02-16 | L4 |  |  |  | 2.7 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 47.1 | UG/L | 80.4999 | 2017-02-16 | L4 |  |  |  | 2.7 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.6 | UG/L | 60.4999 | 2017-02-16 | L1 |  |  |  | 1.6 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 58.5 | UG/L | 80.4999 | 2017-02-16 | L1 |  |  |  | 1.6 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.3 | UG/L | 60.4999 | 2017-02-16 | L2 |  |  |  | 3.3 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 53.3 | UG/L | 80.4999 | 2017-02-16 | L2 |  |  |  | 3.3 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.2 | UG/L | 60.4999 | 2017-02-16 | L3 |  |  |  | 2.5 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48.2 | UG/L | 80.4999 | 2017-02-16 | L3 |  |  |  | 2.5 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | N | 1.3 | PCI/L | 3.4999 | 2017-02-23 | WTP1 |  | 1.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-23 | WTP1 |  | 1.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 95.8 | MG/L | 250.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP1 |  | 0.0149 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-23 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP1 |  | 1.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP1 |  | 1.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-23 | WTP1 |  | 0.4499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP1 |  | 9.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-23 | WTP1 |  | 6.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-23 | WTP1 |  | 0.6499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP1 |  | 2.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-23 | WTP1 |  | 0.0749 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-23 | WTP1 |  | 0.6499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-23 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-23 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-23 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-23 | WTP1 |  | 0.9499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-23 | WTP1 |  | 0.0449 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-23 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP1 |  | 0.0449 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-23 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-23 | WTP1 |  | 0.0149 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | N | 1.5 | PCI/L | 3.4999 | 2017-02-23 | WTP4 |  | 1.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-23 | WTP4 |  | 1.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | N | 1.3 | PCI/L | 3.4999 | 2017-02-23 | WTP2 |  | 1.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-23 | WTP2 |  | 1.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP2 |  | 0.0149 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-23 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP2 |  | 1.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP2 |  | 1.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-23 | WTP2 |  | 0.4499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP2 |  | 9.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-23 | WTP2 |  | 6.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-23 | WTP2 |  | 0.6499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP2 |  | 2.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-23 | WTP2 |  | 0.0749 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-23 | WTP2 |  | 0.6499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-23 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-23 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-23 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-23 | WTP2 |  | 0.9499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-23 | WTP2 |  | 0.0449 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-23 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP2 |  | 0.0449 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-23 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-23 | WTP2 |  | 0.0149 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.456 | MG/L | 10.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.0182 | MG/L | 2.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 53.5 | MG/L | 160.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0.0027 | MG/L | 1.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0.0481 | MG/L | 0.3499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 34.2 | MG/L | 250.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.02 | LN(10) |  | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 352 | MG/L | 500.4999 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-23 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP1 |  | 0.5499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-23 | WTP4 |  | 0.9499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-23 | WTP4 |  | 0.0449 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-23 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP4 |  | 0.0449 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-23 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-23 | WTP4 |  | 0.0149 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.0139 | MG/L | 2.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.799 | MG/L | 4.0499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 25.9 | MG/L | 160.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 45.9 | MG/L | 250.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0.0023 | MG/L | 1.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.799 | MG/L | 2.0499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 6.14 | MG/L | 250.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0.0262 | MG/L | 5.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.98 | LN(10) |  | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 196 | MG/L | 500.4999 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-23 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.0137 | MG/L | 2.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-23 | WTP2 |  | 0.5499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.875 | MG/L | 4.0499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0.0055 | MG/L | 0.1499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 25.2 | MG/L | 160.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 43.8 | MG/L | 250.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.875 | MG/L | 2.0499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0.148 | MG/L | 0.3499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 6.07 | MG/L | 250.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.94 | LN(10) |  | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 186 | MG/L | 500.4999 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-23 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP4 |  | 0.5499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-23 | WTP4 |  | 0.0149 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-23 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-23 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-23 | WTP4 |  | 1.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP4 |  | 1.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-23 | WTP4 |  | 0.4499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-23 | WTP4 |  | 9.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-23 | WTP4 |  | 6.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-23 | WTP4 |  | 0.6499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-23 | WTP4 |  | 2.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-23 | WTP4 |  | 0.0749 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-23 | WTP4 |  | 0.6499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-23 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-23 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-23 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.6 | UG/L | 60.4999 | 2017-05-12 | L1 |  |  |  | 1 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 29.4 | UG/L | 80.4999 | 2017-05-12 | L4 |  |  |  | 2.2 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.1 | UG/L | 60.4999 | 2017-05-12 | L4 |  |  |  | 2.2 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 27.4 | UG/L | 80.4999 | 2017-05-12 | L3 |  |  |  | 3 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.8 | UG/L | 60.4999 | 2017-05-12 | L3 |  |  |  | 3 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 47.6 | UG/L | 80.4999 | 2017-05-12 | L2 |  |  |  | 2.2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.6 | UG/L | 60.4999 | 2017-05-12 | L2 |  |  |  | 2.2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 61.1 | UG/L | 80.4999 | 2017-05-12 | L1 |  |  |  | 1 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP2 | 0.1 | 1.4999 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-17 | WTP2 | 0.4 | 0.4499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-17 | WTP2 | 9 | 9.4999 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-17 | WTP2 | 6 | 6.4999 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-17 | WTP2 | 0.6 | 0.6499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP2 | 2 | 2.4999 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-17 | WTP2 | 0.07 | 0.0749 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-17 | WTP2 | 0.6 | 0.6499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-17 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-17 | WTP2 | 0.01 | 0.0149 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP2 | 0.01 | 0.2499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP4 | 0.01 | 0.0149 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP4 | 0.01 | 0.0249 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP4 | 0.05 | 0.1499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP4 | 0.5 | 1.4999 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP4 | 0.1 | 1.4999 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-17 | WTP4 | 0.4 | 0.4499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-17 | WTP4 | 9 | 9.4999 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-17 | WTP4 | 6 | 6.4999 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-17 | WTP4 | 0.6 | 0.6499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP4 | 2 | 2.4999 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-17 | WTP4 | 0.07 | 0.0749 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-17 | WTP4 | 0.6 | 0.6499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-17 | WTP4 | 0.1 | 0.1499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-17 | WTP4 | 0.2 | 0.2499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP4 | 0.1 | 0.1499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP4 | 0.9 | 0.9499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP4 | 0.1 | 0.1499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP4 | 0.2 | 0.2499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-17 | WTP4 | 0.01 | 0.0449 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP4 | 0.01 | 0.0249 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-17 | WTP4 | 0.1 | 0.1499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP4 | 0.2 | 0.2499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP4 | 0.1 | 0.1499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP4 | 0.02 | 0.0249 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP4 | 0.04 | 0.0449 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-17 | WTP4 | 0.1 | 0.1499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP4 | 0.02 | 0.0249 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-17 | WTP4 | 0.01 | 0.0149 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP4 | 0.01 | 0.2499 |  |  | 2Q SOCWP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP1 | 0.01 | 0.0149 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP1 | 0.01 | 0.0249 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP1 | 0.05 | 0.1499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP1 | 0.5 | 1.4999 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP1 | 0.1 | 1.4999 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-17 | WTP1 | 0.4 | 0.4499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-17 | WTP1 | 9 | 9.4999 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-17 | WTP1 | 6 | 6.4999 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-17 | WTP1 | 0.6 | 0.6499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP1 | 2 | 2.4999 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-17 | WTP1 | 0.07 | 0.0749 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-17 | WTP1 | 0.6 | 0.6499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-17 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-17 | WTP1 | 0.2 | 0.2499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP1 | 0.9 | 0.9499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP1 | 0.2 | 0.2499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-17 | WTP1 | 0.01 | 0.0449 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP1 | 0.01 | 0.0249 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-17 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP1 | 0.2 | 0.2499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP1 | 0.02 | 0.0249 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP1 | 0.04 | 0.0449 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-17 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP1 | 0.02 | 0.0249 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-17 | WTP1 | 0.01 | 0.0149 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP1 | 0.01 | 0.2499 |  |  | 2Q SOC/WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP2 | 0.01 | 0.0149 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP2 | 0.01 | 0.0249 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP2 | 0.05 | 0.1499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP2 | 0.5 | 1.4999 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-17 | WTP2 | 0.2 | 0.2499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP2 | 0.9 | 0.9499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP2 | 0.2 | 0.2499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-17 | WTP2 | 0.01 | 0.0449 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP2 | 0.01 | 0.0249 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-17 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP2 | 0.2 | 0.2499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP2 | 0.02 | 0.0249 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP2 | 0.04 | 0.0449 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-17 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP2 | 0.02 | 0.0249 |  |  | 2Q SOC/WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-07-26 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-07-26 | WTP4 |  | 0.9499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-07-26 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-07-26 | WTP4 |  | 0.0449 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-07-26 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-07-26 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-07-26 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-07-26 | WTP1 |  | 0.0449 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-07-26 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-07-26 | WTP1 |  | 0.0149 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP1 |  | 0.0149 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-07-26 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-07-26 | WTP1 |  | 1.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-07-26 | WTP1 |  | 1.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-07-26 | WTP1 |  | 0.4499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-07-26 | WTP1 |  | 9.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-07-26 | WTP1 |  | 6.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-07-26 | WTP1 |  | 0.6499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-07-26 | WTP1 |  | 2.4999 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-07-26 | WTP1 |  | 0.0749 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-07-26 | WTP1 |  | 0.6499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-07-26 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-07-26 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-07-26 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-07-26 | WTP4 |  | 0.0449 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-07-26 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-07-26 | WTP4 |  | 0.0149 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-07-26 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-07-26 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-07-26 | WTP1 |  | 0.9499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-07-26 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-07-26 | WTP1 |  | 0.0449 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP1 |  | 0.0249 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-07-26 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-07-26 | WTP1 |  | 0.2499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-07-26 | WTP1 |  | 0.1499 |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-07-26 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-07-26 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP2 |  | 0.0149 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-07-26 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-07-26 | WTP2 |  | 1.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-07-26 | WTP2 |  | 1.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-07-26 | WTP2 |  | 0.4499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-07-26 | WTP2 |  | 9.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-07-26 | WTP2 |  | 6.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-07-26 | WTP2 |  | 0.6499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-07-26 | WTP2 |  | 2.4999 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-07-26 | WTP2 |  | 0.0749 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-07-26 | WTP2 |  | 0.6499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-07-26 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-07-26 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-07-26 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-07-26 | WTP2 |  | 0.9499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-07-26 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-07-26 | WTP2 |  | 0.0449 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-07-26 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-07-26 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-07-26 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-07-26 | WTP2 |  | 0.0449 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-07-26 | WTP2 |  | 0.1499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP2 |  | 0.0249 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-07-26 | WTP2 |  | 0.0149 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP2 |  | 0.2499 |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-07-26 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-07-26 | WTP4 |  |  |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-07-26 | WTP4 |  | 0.0149 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-07-26 | WTP4 |  | 0.0249 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-07-26 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-07-26 | WTP4 |  | 1.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-07-26 | WTP4 |  | 1.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-07-26 | WTP4 |  | 0.4499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-07-26 | WTP4 |  | 9.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-07-26 | WTP4 |  | 6.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-07-26 | WTP4 |  | 0.6499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-07-26 | WTP4 |  | 2.4999 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-07-26 | WTP4 |  | 0.0749 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-07-26 | WTP4 |  | 0.6499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-07-26 | WTP4 |  | 0.1499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-07-26 | WTP4 |  | 0.2499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.8 | UG/L | 60.4999 | 2017-08-16 | L2 |  |  |  | 2.3 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.9 | UG/L | 60.4999 | 2017-08-16 | L4 |  |  |  | 1.8 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.5 | UG/L | 60.4999 | 2017-08-16 | L1 |  |  |  | 0.5 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 49.4 | UG/L | 80.4999 | 2017-08-16 | L1 |  |  |  | 0.5 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.9 | UG/L | 80.4999 | 2017-08-16 | L4 |  |  |  | 1.8 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.8 | UG/L | 80.4999 | 2017-08-16 | L2 |  |  |  | 2.3 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.9 | UG/L | 60.4999 | 2017-08-16 | L3 |  |  |  | 1 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48 | UG/L | 80.4999 | 2017-08-16 | L3 |  |  |  | 1 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 92.6 | UG/L | 60.4999 | 2017-11-20 | L4 |  |  |  | 1.8 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 145 | UG/L | 80.4999 | 2017-11-20 | L3 |  |  |  | 2.1 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 129 | UG/L | 60.4999 | 2017-11-20 | L3 |  |  |  | 2.1 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 106 | UG/L | 80.4999 | 2017-11-20 | L2 |  |  |  | 1.6 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 104 | UG/L | 60.4999 | 2017-11-20 | L2 |  |  |  | 1.6 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 73.2 | UG/L | 80.4999 | 2017-11-20 | L1 |  |  |  | 0.9 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 141 | UG/L | 60.4999 | 2017-11-20 | L1 |  |  |  | 0.9 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 100 | UG/L | 80.4999 | 2017-11-20 | L4 |  |  |  | 1.8 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-01-01 | WTP4 |  | 0.6499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-01-01 | WTP4 |  | 0.6499 |  |  | WP4
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 45.2 | UG/L | 80.4999 | 2018-02-19 | L3 |  |  |  | 1.5 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 28.1 | UG/L | 80.4999 | 2018-02-19 | L1 |  |  |  | 1.5 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.4 | UG/L | 60.4999 | 2018-02-19 | L2 |  |  |  | 2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 31.2 | UG/L | 80.4999 | 2018-02-19 | L2 |  |  |  | 2 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.1 | UG/L | 60.4999 | 2018-02-19 | L3 |  |  |  | 1.5 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.2 | UG/L | 60.4999 | 2018-02-19 | L4 |  |  |  | 1.4 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 29.9 | UG/L | 80.4999 | 2018-02-19 | L4 |  |  |  | 1.4 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.33 | UG/L | 60.4999 | 2018-02-19 | L1 |  |  |  | 1.5 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 28.3 | UG/L | 80.4999 | 2018-05-15 | L1 |  |  |  | 1.3 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.7 | UG/L | 60.4999 | 2018-05-15 | L1 |  |  |  | 1.3 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 29 | UG/L | 80.4999 | 2018-05-15 | L4 |  |  |  | 1.7 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.2 | UG/L | 60.4999 | 2018-05-15 | L4 |  |  |  | 1.7 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 25.7 | UG/L | 80.4999 | 2018-05-15 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.6 | UG/L | 60.4999 | 2018-05-15 | L3 |  |  |  | 1.6 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 55.9 | UG/L | 80.4999 | 2018-05-15 | L2 |  |  |  | 1.5 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.9 | UG/L | 60.4999 | 2018-05-15 | L2 |  |  |  | 1.5 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 32.1 | UG/L | 80.4999 | 2018-08-15 | L3 | 0.5 |  | 3 | 1.4 | 3600 CANOE CREEK
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21 | UG/L | 60.4999 | 2018-08-15 | L4 | 0.5 |  | 4 | 2.1 | 803 MASSACHUSSETTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 25.2 | UG/L | 80.4999 | 2018-08-15 | L4 | 0.5 |  | 4 | 2.1 | 803 MASSACHUSSETTS
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.7 | UG/L | 60.4999 | 2018-08-15 | L3 | 0.5 |  | 3 | 1.4 | 3600 CANOE CREEK
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 34.5 | UG/L | 80.4999 | 2018-08-15 | L2 | 0.5 |  | 2 | 2.9 | 4805 DOC DR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.8 | UG/L | 60.4999 | 2018-08-15 | L2 | 0.5 |  | 2 | 2.9 | 4805 DOC DR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.5 | UG/L | 60.4999 | 2018-08-15 | L1 | 0.5 |  | 1 | 0.7 | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 13.9 | UG/L | 80.4999 | 2018-08-15 | L1 | 0.5 |  | 1 | 0.7 | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.4 | UG/L | 80.4999 | 2018-11-15 | L4 |  |  | 4 | 2.2 | 2950-803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.2 | UG/L | 60.4999 | 2018-11-15 | L4 |  |  | 4 | 2.2 | 2950-803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.1 | UG/L | 80.4999 | 2018-11-15 | L3 |  |  | 3 | 1.8 | 2950-3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22 | UG/L | 60.4999 | 2018-11-15 | L3 |  |  | 3 | 1.8 | 2950-3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 29.5 | UG/L | 80.4999 | 2018-11-15 | L2 |  |  | 2 | 1.9 | 2950-4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.6 | UG/L | 60.4999 | 2018-11-15 | L2 |  |  | 2 | 1.9 | 2950-4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.6 | UG/L | 60.4999 | 2018-11-15 | L1 |  |  | 1 | 1.6 | 2950-5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 28.2 | UG/L | 80.4999 | 2018-11-15 | L1 |  |  | 1 | 1.6 | 2950-5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | S | 0 | MG/L | 10.4999 | 2019-01-17 | WTP4 |  |  |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | S | 0 | MG/L | 1.4999 | 2019-01-17 | WTP2 |  |  |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19_KAC
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | S | 0 | MG/L | 10.4999 | 2019-01-17 | WTP2 |  |  |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19_KAC
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | S | 0 | MG/L | 1.4999 | 2019-01-17 | WTP1 |  |  |  |  | MISSED SAMPLING. RCVD 01/28/19_KAC
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | S | 0 | MG/L | 10.4999 | 2019-01-17 | WTP1 |  |  |  |  | MISSED SAMPLING. RCVD 01/28/19_KAC
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | S | 0 | MG/L | 1.4999 | 2019-01-17 | WTP4 |  |  |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-01-17 | WTP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-01-17 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-01-17 | WTP2 |  |  |  |  | WP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-01-17 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-01-17 | WTP1 |  |  |  |  | WP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-01-17 | WTP4
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-12 | WTP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-12 | WTP1
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-12 | WTP4 | 0.2 |  |  |  | WP4 (RCVD 2/19 WP4 NN ON 6/28/19--BB OTHER 2 WP'S 2/19 NN RCVD EARLIER)
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-12 | WTP2
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-12 | WTP4 | 0.2 |  |  |  | WP4 (RCVD 2/19 WP4 NN ON 6/28/19--BB OTHER 2 WP'S 2/19 NN RCVD EARLIER)
3491373 | ST. CLOUD CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-12 | WTP2
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.6 | UG/L | 60.4999 | 2019-02-20 | L4 | 1 |  | 4 | 2.2 | 803 MASS AVE
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 37 | UG/L | 80.4999 | 2019-02-20 | L4 | 0.5 |  | 4 | 2.2 | 803 MASS AVE
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 35 | UG/L | 80.4999 | 2019-02-20 | L3 | 0.5 |  | 3 | 0.8 | 3600 CANOE CREEK
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.4 | UG/L | 60.4999 | 2019-02-20 | L3 | 1 |  | 3 | 0.8 | 3600 CANOE CREEK
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 38.7 | UG/L | 80.4999 | 2019-02-20 | L2 | 0.5 |  | 2 | 2.3 | 4805 DOC DR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.2 | UG/L | 60.4999 | 2019-02-20 | L2 | 1 |  | 2 | 2.3 | 4805 DOC DR
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 35.7 | UG/L | 80.4999 | 2019-02-20 | L1 | 0.5 |  | 1 | 1 | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34 | UG/L | 60.4999 | 2019-02-20 | L1 | 1 |  | 1 | 1 | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 67.5 | UG/L | 60.4999 | 2019-05-21 | L1 |  |  | 1 | 1 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 50.3 | UG/L | 60.4999 | 2019-05-21 | L2 |  |  | 2 | 1.3 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 81.1 | UG/L | 80.4999 | 2019-05-21 | L1 |  |  | 1 | 1 | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 46.7 | UG/L | 60.4999 | 2019-05-21 | L3 |  |  | 3 | 1.8 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 68.4 | UG/L | 80.4999 | 2019-05-21 | L2 |  |  | 2 | 1.3 | 4805 DOC DR.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 63.1 | UG/L | 80.4999 | 2019-05-21 | L4 |  |  | 4 | 1.5 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49.4 | UG/L | 60.4999 | 2019-05-21 | L4 |  |  | 4 | 1.5 | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 54 | UG/L | 80.4999 | 2019-05-21 | L3 |  |  | 3 | 1.8 | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 76.9 | UG/L | 80.4999 | 2019-08-15 | L4 |  |  | 4 | 0.7 | 803 MASSACHUSETTS AVE. H LRAA = 47.8 T LRAA = 55.1
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 73.2 | UG/L | 80.4999 | 2019-08-15 | L3 |  |  | 3 | 1.4 | 3600 CANOE CREEK RD. H LRAA = 46.4 T LRAA = 49.6
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 84.5 | UG/L | 60.4999 | 2019-08-15 | L3 |  |  | 3 | 1.4 | 3600 CANOE CREEK RD. H LRAA = 46.4 T LRAA = 49.6
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 74.7 | UG/L | 80.4999 | 2019-08-15 | L2 |  |  | 2 | 2.7 | 4805 DOC DR. H LRAA = 42.6 T LRAA = 52.8
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 81.1 | UG/L | 60.4999 | 2019-08-15 | L2 |  |  | 2 | 2.7 | 4805 DOC DR. H LRAA = 42.6 T LRAA = 52.8
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 57.6 | UG/L | 80.4999 | 2019-08-15 | L1 |  |  | 1 | 1.2 | 5371 MAJESTIC ISLAND CIR. H LRAA = 43.3 T LRAA = 50.65
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.1 | UG/L | 60.4999 | 2019-08-15 | L1 |  |  | 1 | 1.2 | 5371 MAJESTIC ISLAND CIR. H LRAA = 43.3 T LRAA = 50.65
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 83.8 | UG/L | 60.4999 | 2019-08-15 | L4 |  |  | 4 | 0.7 | 803 MASSACHUSETTS AVE. H LRAA = 47.8 T LRAA = 55.1
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.9 | UG/L | 80.4999 | 2019-11-20 | L3 | 0.5 |  | 3 | 1.5 | 3600 CANOE CREEK [LRAA TTHM=53.28; HAA5=50.13]
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.9 | UG/L | 60.4999 | 2019-11-20 | L3 | 1 |  | 3 | 1.5 | 3600 CANOE CREEK [LRAA TTHM=53.28; HAA5=50.13]
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37 | UG/L | 60.4999 | 2019-11-20 | L2 | 1 |  | 2 | 1.4 | 4805 DOC DR [LRAA TTHM=74.7 ; HAA5=48.9]
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 74.2 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.5 |  | 1 | 0.7 | 5371 MAJESTIC ISLAND [LRAA TTHM=62.15; HAA5=49.55]
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.6 | UG/L | 60.4999 | 2019-11-20 | L1 | 1 |  | 1 | 0.7 | 5371 MAJESTIC ISLAND [LRAA TTHM=62.15; HAA5=49.55]
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 66 | UG/L | 80.4999 | 2019-11-20 | L4 | 0.5 |  | 4 | 1.2 | 803 MASSACHUSETTS [LRAA TTHM= 60.75; HAA5=49.55]
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.4 | UG/L | 60.4999 | 2019-11-20 | L4 | 1 |  | 4 | 1.2 | 803 MASSACHUSETTS [LRAA TTHM= 60.75; HAA5=49.55]
3491373 | ST. CLOUD CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 117 | UG/L | 80.4999 | 2019-11-20 | L2 | 0.5 |  | 2 | 1.4 | 4805 DOC DR [LRAA TTHM=74.7 ; HAA5=48.9]
3491702 | FLORIDIAN SANDALWOOD MHC | DBP | 2950 | TOTAL THMS | D | 27.35 | UG/L | 80.4999 | 2015-07-27 | L1 |  |  |  | 0.7 | ANN. T/H-BOAT RAMP (<500 QUALIFIES FOR R.M. TEST AGAIN @ 7/23/18 1 DUAL SMP)
3491702 | FLORIDIAN SANDALWOOD MHC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.24 | UG/L | 60.4999 | 2015-07-27 | L1 |  |  |  | 0.7 | ANN. T/H-BOAT RAMP (<500 QUALIFIES FOR R.M. TEST AGAIN @ 7/23/18 1 DUAL SMP)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1017 | CHLORIDE | N | 63 | MG/L | 250.4999 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1025 | FLUORIDE | N | 0.16 | MG/L | 2.0499 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1028 | IRON | N | 0.041 | MG/L | 0.3499 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1032 | MANGANESE | N | 0.0008 | MG/L | 0.0549 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1055 | SULFATE | N | 62 | MG/L | 250.4999 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1095 | ZINC | N | 0.01 | MG/L | 5.4999 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-11-03 | AAA |  | 0.0149 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-11-03 | AAA |  | 0.0249 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-11-03 | AAA |  | 0.1499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-11-03 | AAA |  | 1.4999 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-11-03 | AAA |  | 1.4999 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-11-03 | AAA |  | 0.4499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-11-03 | AAA |  | 9.4999 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-11-03 | AAA |  | 6.4999 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-11-03 | AAA |  | 0.6499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-11-03 | AAA |  | 2.4999 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-11-03 | AAA |  | 0.0749 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-11-03 | AAA |  | 0.6499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-11-03 | AAA |  | 0.1499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-11-03 | AAA |  | 0.2499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-11-03 | AAA |  | 0.1499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-11-03 | AAA |  | 0.9499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-11-03 | AAA |  | 0.1499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-11-03 | AAA |  | 0.2499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-11-03 | AAA |  | 0.0449 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-11-03 | AAA |  | 0.0249 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-11-03 | AAA |  | 0.1499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-11-03 | AAA |  | 0.2499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-11-03 | AAA |  | 0.1499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-11-03 | AAA |  | 0.0249 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-11-03 | AAA |  | 0.0449 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-11-03 | AAA |  | 0.1499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-11-03 | AAA |  | 0.0249 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-11-03 | AAA |  | 0.0149 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-11-03 | AAA |  | 0.2499 |  |  | 3YR SOC- SOC WAIVER APPROVED. NEXT SAMPLE IN 2021
3491702 | FLORIDIAN SANDALWOOD MHC | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 9 | PCI/L | 15.4999 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION ON RESULTS PAGE (RADS DUE 2018)
3491702 | FLORIDIAN SANDALWOOD MHC | RAD | 4020 | RADIUM-226 | N | 1.2 | PCI/L | 3.4999 | 2015-11-03 | AAA |  | 1.4999 |  |  | ND. R1 REVISION ON RESULTS PAGE (RADS DUE 2018)
3491702 | FLORIDIAN SANDALWOOD MHC | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-11-03 | AAA |  | 1.4999 |  |  | ND. R1 REVISION ON RESULTS PAGE (RADS DUE 2018)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1025 | FLUORIDE | N | 0.16 | MG/L | 4.0499 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1052 | SODIUM | N | 37 | MG/L | 160.4999 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 410 | MG/L | 500.4999 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-11-03 | AAA |  | 0.5499 |  |  | 3YR VOC
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-11-03 | AAA |  |  |  |  | ND. R1 REVISION FOR RADS RSLTS NO MCLS (J QUAL: NO2 88/90% MS/MSD FL 89/88% MS/MSD ALL SUFFIC. FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-11-03 | AAA |  |  |  |  | NO MCLS J QUAL: FL 89/88% MS/MSD SULF 89/89% MS/MSD ALL SUFFIC FOR ACCEPTANCE ALL LCS OK)
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-12-14 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-14 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-18 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-05-18 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1028 | IRON | N | 2.06 | MG/L | 0.3499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1040 | NITRATE | N | 0.282 | MG/L | 10.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1010 | BARIUM | N | 0.0095 | MG/L | 2.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1020 | CHROMIUM | N | 0.0029 | MG/L | 0.1499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1052 | SODIUM | N | 43.6 | MG/L | 160.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1017 | CHLORIDE | N | 68.7 | MG/L | 250.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1022 | COPPER | N | 0.0197 | MG/L | 1.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1055 | SULFATE | N | 75.6 | MG/L | 250.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1095 | ZINC | N | 0.0945 | MG/L | 5.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.61 | LN(10) |  | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 408 | MG/L | 500.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-15 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN SANDALWOOD MHC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 53.4 | UG/L | 60.4999 | 2018-08-09 | L1 | 0.5 |  | 1 | 0.5 | BOAT RAMP (T>60 H>45 RETURN TO ROUTINE ANNUAL DBP TESTING) HLKD TO SB
3491702 | FLORIDIAN SANDALWOOD MHC | DBP | 2950 | TOTAL THMS | D | 61.3 | UG/L | 80.4999 | 2018-08-09 | L1 | 0.5 |  | 1 | 0.5 | BOAT RAMP (T>60 H>45 RETURN TO ROUTINE ANNUAL DBP TESTING) HLKD TO SB
3491702 | FLORIDIAN SANDALWOOD MHC | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.65 | PCI/L | 15.4999 | 2018-12-26 | AAA |  |  |  |  | DUE 2024
3491702 | FLORIDIAN SANDALWOOD MHC | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-12-26 | AAA |  | 1.4999 |  |  | DUE 2024
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-08-27 | AAA
3491702 | FLORIDIAN SANDALWOOD MHC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.1 | UG/L | 60.4999 | 2019-08-27 | L1 | 0.9 |  | 1 | 0.2 | BOAT RAMP (RCVD 11/7/19) HLKD (*****TTHMS > MCL*****) QTRLY TESTING NEEDED FOR BOTH T/H
3491702 | FLORIDIAN SANDALWOOD MHC | DBP | 2950 | TOTAL THMS | D | 84.3 | UG/L | 80.4999 | 2019-08-27 | L1 | 0.32 |  | 1 | 0.2 | BOAT RAMP (RCVD 11/7/19) HLKD (*****TTHMS > MCL*****) QTRLY TESTING NEEDED FOR BOTH T/H
3491702 | FLORIDIAN SANDALWOOD MHC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-08-27 | AAA
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.9 | UG/L | 60.4999 | 2015-09-10 | L1 |  |  |  | 0.4 | ON R.M.-LOT #47 (REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) <500
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 16.14 | UG/L | 80.4999 | 2015-09-10 | L1 |  |  |  | 0.4 | ON R.M.-LOT #47 (REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) <500
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-10-13 | AAA |  | 0.1499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-10-13 | AAA |  | 0.2499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.1499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.0449
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-10-13 | AAA |  | 0.1499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-10-13 | AAA |  | 0.0149
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-10-13 | AAA |  | 0.2499
3491726 | SHARP'S MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-10-13 | AAA |  |  |  |  | DUE 2021
3491726 | SHARP'S MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-13 | AAA |  | 1.4999 |  |  | DUE 2021
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-10-13 | AAA |  | 0.0149
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.16 | MG/L | 10.4999 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.19 | MG/L | 4.0499 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 31 | MG/L | 160.4999 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-10-13 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 32 | MG/L | 250.4999 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.19 | MG/L | 2.0499 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1028 | IRON | N | 0.039 | MG/L | 0.3499 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0041 | MG/L | 0.0549 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 3.1 | MG/L | 250.4999 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.0023 | MG/L | 5.4999 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.8 | LN(10) |  | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 350 | MG/L | 500.4999 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-13 | AAA
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-10-13 | AAA |  | 0.1499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 1.4999
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-10-13 | AAA |  | 1.4999
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-10-13 | AAA |  | 0.4499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-10-13 | AAA |  | 9.4999
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-10-13 | AAA |  | 6.4999
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-10-13 | AAA |  | 0.6499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-10-13 | AAA |  | 2.4999
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-10-13 | AAA |  | 0.0749
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-10-13 | AAA |  | 0.6499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-10-13 | AAA |  | 0.1499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-10-13 | AAA |  | 0.2499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-10-13 | AAA |  | 0.1499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-10-13 | AAA |  | 0.9499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-10-13 | AAA |  | 0.1499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-10-13 | AAA |  | 0.2499
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-10-13 | AAA |  | 0.0449
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-10-13 | AAA |  | 0.0249
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-20 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-12-20 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-11-10 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-11-10 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0.068 |  | 0.5499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.011 | MG/L | 2.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.22 | MG/L | 4.0499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 25 | MG/L | 160.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 29 | MG/L | 250.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0.0038 | MG/L | 1.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.22 | MG/L | 2.0499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.003 | MG/L | 0.0549 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 2.9 | MG/L | 250.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.04 | MG/L | 5.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.68 | LN(10) |  | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 340 | MG/L | 500.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-20 | AAA |  |  |  |  | RESULTS ACCEPTED WITH J4 QUALIFER- QAQC ACCEPTABLE_SLB
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.16 | MG/L | 10.4999 | 2018-02-20 | AAA |  |  |  |  | RESULTS ACCEPTED WITH J4 QUALIFER- QAQC ACCEPTABLE_SLB
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.54 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.91 |  | 1 | 0.7
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 49.3 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.39 |  | 1 | 0.7
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-17 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.46 | MG/L | 10.4999 | 2019-04-17 | AAA
3491904 | KING'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.47 | UG/L | 60.4999 | 2015-09-09 | L1 |  |  |  | 0.5 | ON R.M.-LOT #18 (REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) <500
3491904 | KING'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 22.54 | UG/L | 80.4999 | 2015-09-09 | L1 |  |  |  | 0.5 | ON R.M.-LOT #18 (REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) <500
3491904 | KING'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-10-08 | AAA |  | 0.0149
3491904 | KING'S MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249
3491904 | KING'S MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-10-08 | AAA |  | 0.1499
3491904 | KING'S MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 1.4999
3491904 | KING'S MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-10-08 | AAA |  | 1.4999
3491904 | KING'S MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-10-08 | AAA |  | 0.4499
3491904 | KING'S MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 9.4999
3491904 | KING'S MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-10-08 | AAA |  | 6.4999
3491904 | KING'S MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-10-08 | AAA |  | 0.6499
3491904 | KING'S MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-10-08 | AAA |  | 2.4999
3491904 | KING'S MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-10-08 | AAA |  | 0.0749
3491904 | KING'S MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-10-08 | AAA |  | 0.6499
3491904 | KING'S MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-10-08 | AAA |  | 0.1499
3491904 | KING'S MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-10-08 | AAA |  | 0.2499
3491904 | KING'S MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-10-08 | AAA |  | 0.1499
3491904 | KING'S MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-10-08 | AAA |  | 0.9499
3491904 | KING'S MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.1499
3491904 | KING'S MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-10-08 | AAA |  | 0.2499
3491904 | KING'S MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-10-08 | AAA |  | 0.0449
3491904 | KING'S MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249
3491904 | KING'S MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-10-08 | AAA |  | 0.1499
3491904 | KING'S MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-10-08 | AAA |  | 0.2499
3491904 | KING'S MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.1499
3491904 | KING'S MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249
3491904 | KING'S MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-10-08 | AAA |  | 0.0449
3491904 | KING'S MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-10-08 | AAA |  | 0.1499
3491904 | KING'S MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-10-08 | AAA |  | 0.0249
3491904 | KING'S MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-10-08 | AAA |  | 0.0149
3491904 | KING'S MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-10-08 | AAA |  | 0.2499
3491904 | KING'S MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.2 | PCI/L | 15.4999 | 2015-10-08 | AAA |  |  |  |  | RADS DUE 2021
3491904 | KING'S MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-08 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.019 | MG/L | 2.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.18 | MG/L | 4.0499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 8.7 | MG/L | 160.4999 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-10-08 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (RADS TESTED)
3491904 | KING'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 13 | MG/L | 250.4999 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0.0083 | MG/L | 1.4999 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.18 | MG/L | 2.0499 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1028 | IRON | N | 0.096 | MG/L | 0.3499 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0028 | MG/L | 0.0549 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 11 | MG/L | 250.4999 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.043 | MG/L | 5.4999 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.5 | LN(10) |  | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 190 | MG/L | 500.4999 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-08 | AAA
3491904 | KING'S MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-08 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-21 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-12-21 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-10-19 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-10-19 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-03-05 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-03-05 | AAA
3491904 | KING'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 3.13 | UG/L | 80.4999 | 2018-08-08 | L1 | 0.39 |  | 1 | 0.35
3491904 | KING'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.78 | UG/L | 60.4999 | 2018-08-08 | L1 | 0.91 |  | 1 | 0.35
3491904 | KING'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | D | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | D | 0 | UG/L | 649.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | D | 0 | UG/L | 75.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | D | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | D | 0 | UG/L | 7.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | D | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | D | 0 | UG/L | 249.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | D | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | D | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | D | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2990 | BENZENE | D | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | D | 0 | UG/L | 1499.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | D | 0 | UG/L | 749.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2996 | STYRENE | D | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | D | 0.19 | MG/L | 10.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | D | 0 | MG/L | 1.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | D | 0 | MG/L | 0.0104 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1010 | BARIUM | D | 0.02 | MG/L | 2.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | D | 0 | MG/L | 0.0055 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | D | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | D | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | D | 0 | MG/L | 4.0499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1030 | LEAD | D | 0 | MG/L | 0.0154 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1035 | MERCURY | D | 0 | MG/L | 0.0024 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1036 | NICKEL | D | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | D | 0 | MG/L | 0.0549 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1052 | SODIUM | D | 13 | MG/L | 160.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | D | 0 | MG/L | 0.0065 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | D | 0 | MG/L | 0.0045 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | D | 0 | MG/L | 0.0025 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1028 | IRON | N | 0.033 | MG/L | 0.3499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0023 | MG/L | 0.0549 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 10 | MG/L | 250.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.033 | MG/L | 5.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.5 | LN(10) |  | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 170 | MG/L | 500.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 17 | MG/L | 250.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | D | 0 | UG/L | 10499.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | D | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | D | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0.0055 | MG/L | 1.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-23 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.46 | MG/L | 10.4999 | 2019-04-23 | AAA
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.9 | UG/L | 60.4999 | 2015-01-22 | L1 | 0.5 |  | 1 | 0.8 | 3203 WHISPERWIND DR(3/15 LRAA/T=62.1625(12/14QTR HAS 2 RSLTS) LRAA/H=37.8625 UG/L)OE VALUES 10/13TO3/15 QTR HV NVR EXCDD THE MCL(S) EVEN THO 9/14&12/14 LRAAS/T>MCL(ST.CLOUD'S CORR.ACTION>3/16/15EM>OC)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 26.4 | UG/L | 80.4999 | 2015-01-22 | L1 | 0.5 |  | 1 | 0.8 | 3203 WHISPERWIND DR(3/15 LRAA/T=62.1625(12/14QTR HAS 2 RSLTS) LRAA/H=37.8625 UG/L)OE VALUES 10/13TO3/15 QTR HV NVR EXCDD THE MCL(S) EVEN THO 9/14&12/14 LRAAS/T>MCL(ST.CLOUD'S CORR.ACTION>3/16/15EM>OC)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.2 | UG/L | 60.4999 | 2015-04-21 | L1 |  |  |  | 0.5 | 3203 WHISPERWIND DR. (12/14 QTR HAS 2 RSLTS) 6/15 LRAA/T=55.6875 LRAA/H=35.5875. T<60 H<45. CAN STOP QM/T+H - NEXT ANNUAL T/H DUE 9/15
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 31.2 | UG/L | 80.4999 | 2015-04-21 | L1 |  |  |  | 0.5 | 3203 WHISPERWIND DR. (12/14 QTR HAS 2 RSLTS) 6/15 LRAA/T=55.6875 LRAA/H=35.5875. T<60 H<45. CAN STOP QM/T+H - NEXT ANNUAL T/H DUE 9/15
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.96 | UG/L | 60.4999 | 2015-07-24 | L1 |  |  |  | 0.8 | ANNUAL T/H-3203 WHISPERWIND DR. (QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 20.3 | UG/L | 80.4999 | 2015-07-24 | L1 |  |  |  | 0.8 | ANNUAL T/H-3203 WHISPERWIND DR. (QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.8 | UG/L | 60.4999 | 2015-10-22 | L1 |  |  |  | 0.8 | EXTRA T/H-3203 WHISPERWIND DR. (QUALIFIED FOR R.M. AFTER 7/15 TESTS & STILL QUALIFIES FOR ANNUAL SINCE T<60 H<45 NEXT T/H DUE @ 7/23/18 TRIENNIAL)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 46.6 | UG/L | 80.4999 | 2015-10-22 | L1 |  |  |  | 0.8 | EXTRA T/H-3203 WHISPERWIND DR. (QUALIFIED FOR R.M. AFTER 7/15 TESTS & STILL QUALIFIES FOR ANNUAL SINCE T<60 H<45 NEXT T/H DUE @ 7/23/18 TRIENNIAL)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.3 | UG/L | 60.4999 | 2016-01-27 | L1 |  |  |  | 1.4 | (8/17/16 EW HAS EXTRA 4/27/16 DBPS FOR ENTRY BY EM ALREADY IN OCULUS) 3203 WHISPERWIND DR. (STILL QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 28.5 | UG/L | 80.4999 | 2016-01-27 | L1 |  |  |  | 1.4 | (8/17/16 EW HAS EXTRA 4/27/16 DBPS FOR ENTRY BY EM ALREADY IN OCULUS) 3203 WHISPERWIND DR. (STILL QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.2 | UG/L | 60.4999 | 2016-04-27 | L1 |  |  |  | 1.1 | 3203 WHISPERWIND DR. (STILL QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 38.5 | UG/L | 80.4999 | 2016-04-27 | L1 |  |  |  | 1.1 | 3203 WHISPERWIND DR. (STILL QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 46.5 | UG/L | 80.4999 | 2016-07-27 | L1 |  |  |  | 0.8 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.8 | UG/L | 60.4999 | 2016-07-27 | L1 |  |  |  | 0.8 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30 | UG/L | 60.4999 | 2016-10-24 | L1 |  |  |  | 0.6 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 62.3 | UG/L | 80.4999 | 2016-10-24 | L1 |  |  |  | 0.6 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 40.4 | UG/L | 80.4999 | 2017-03-01 | L1 |  |  |  | 1.4 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17 | UG/L | 60.4999 | 2017-03-01 | L1 |  |  |  | 1.4 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.2 | UG/L | 60.4999 | 2018-07-24 | L1 |  |  |  | 0.8 | 2950 - 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 97.1 | UG/L | 80.4999 | 2018-07-24 | L1 |  |  |  | 0.8 | 2950 - 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.2 | UG/L | 60.4999 | 2018-10-24 | L1 |  |  |  | 1.5 | 2950-3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 43.1 | UG/L | 80.4999 | 2018-10-24 | L1 |  |  |  | 1.5 | 2950-3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 6.5 | UG/L | 60.4999 | 2019-01-29 | L1 |  |  | 1 | 1.7 | SAMPLED OUTSIDE TIMEFRAME (1/22 - 1/28) ON PLAN. SURROGATE RECOVERY OUTSIDE RANGE. RESAMPLE REQUIRED_JMF
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | S | 67.5 | UG/L | 80.4999 | 2019-01-29 | L1 |  |  | 1 | 1.7 | SAMPLED OUTSIDE TIMEFRAME (1/22 - 1/28) ON PLAN. SURROGATE RECOVERY OUTSIDE RANGE. RESAMPLE REQUIRED_JMF
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.1 | UG/L | 60.4999 | 2019-02-22 | L1 |  |  | 1 | 1.2 | RESAMPLE FROM JANUARY TESTS WITH QUALIFIERS_JMF
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 77.2 | UG/L | 80.4999 | 2019-02-22 | L1 |  |  | 1 | 1.2 | RESAMPLE FROM JANUARY TESTS WITH QUALIFIERS_JMF
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 72 | UG/L | 80.4999 | 2019-04-26 | L1 |  |  |  | 1.4 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.6 | UG/L | 60.4999 | 2019-04-26 | L1 |  |  |  | 1.4 | 3203 WHISPERWIND DR.
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 127 | UG/L | 80.4999 | 2019-07-26 | L1 |  |  |  | 0.6 | 3203 WHISPERWIND DR. TTHMS LRAA = 79.8 HAA5 LRAA = 31.4 (1QM OVER LRAA) [1/19 SAMPLES QUALIFIED DO NOT COUNT TOWARDS CALCULATION]_VP
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 62.9 | UG/L | 60.4999 | 2019-07-26 | L1 |  |  |  | 0.6 | 3203 WHISPERWIND DR. TTHMS LRAA = 79.8 HAA5 LRAA = 31.4 (1QM OVER LRAA) [1/19 SAMPLES QUALIFIED DO NOT COUNT TOWARDS CALCULATION]_VP
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.2 | UG/L | 60.4999 | 2019-10-26 | L1 |  |  |  | 1 | 3203 WHISPERWIND DR. [LRAA TTHM=93.1; HAA5=37.95]. (2QM OVER LRAA) CONTINUE Q SAMPLING_VP
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 96.2 | UG/L | 80.4999 | 2019-10-26 | L1 |  |  |  | 1 | 3203 WHISPERWIND DR. [LRAA TTHM=93.1; HAA5=37.95]. (2QM OVER LRAA) CONTINUE Q SAMPLING_VP
3494313 | WHISPERING PINES MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.4 | UG/L | 60.4999 | 2015-09-09 | L1 |  |  |  | 0.5 | ON R.M.-1729 GRAND CYPRESS AVE. (REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) POP. 465
3494313 | WHISPERING PINES MHP | DBP | 2950 | TOTAL THMS | D | 21.59 | UG/L | 80.4999 | 2015-09-09 | L1 |  |  |  | 0.5 | ON R.M.-1729 GRAND CYPRESS AVE. (REMAIN ON R.M. - NEXT T/H DUE @ 9/10/18) POP. 465
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1010 | BARIUM | N | 0.0066 | MG/L | 2.4999 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1025 | FLUORIDE | N | 0.18 | MG/L | 4.0499 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1052 | SODIUM | N | 46 | MG/L | 160.4999 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1017 | CHLORIDE | N | 66 | MG/L | 250.4999 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1025 | FLUORIDE | N | 0.18 | MG/L | 2.0499 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1032 | MANGANESE | N | 0.0006 | MG/L | 0.0549 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.9 | LN(10) |  | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 340 | MG/L | 500.4999 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-11-11 | AAA |  | 0.5499 |  |  | 3YR VOC
3494313 | WHISPERING PINES MHP | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-11-11 | AAA |  | 0.0149 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-11-11 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-11-11 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-11-11 | AAA |  | 1.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | N | 3.2 | UG/L | 249.9999 | 2015-11-11 | AAA |  | 1.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-11-11 | AAA |  | 0.4499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-11-11 | AAA |  | 9.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-11-11 | AAA |  | 6.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-11-11 | AAA |  | 0.6499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-11-11 | AAA |  | 2.4999 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-11-11 | AAA |  | 0.0749 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-11-11 | AAA |  | 0.6499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-11-11 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-11-11 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0.032 | UG/L | 54.9999 | 2015-11-11 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-11-11 | AAA |  | 0.9499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-11-11 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1055 | SULFATE | N | 5.7 | MG/L | 250.4999 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SEC | 1095 | ZINC | N | 0.0073 | MG/L | 5.4999 | 2015-11-11 | AAA |  |  |  |  | NO MCL
3494313 | WHISPERING PINES MHP | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-11-11 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-11-11 | AAA |  | 0.0449 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-11-11 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-11-11 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-11-11 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-11-11 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-11-11 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-11-11 | AAA |  | 0.0449 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-11-11 | AAA |  | 0.1499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-11-11 | AAA |  | 0.0249 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-11-11 | AAA |  | 0.0149 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-11-11 | AAA |  | 0.2499 |  |  | (EM 4/28/16 FOR 6/16 QTR DALAPON TO ABWTR) 3YR SOC (DAL 3.2 > RDL OF 1 2QM/DAL 3/16 QM RQRD>EM 1/15/16>ABWTR) 2042 HEX... 0.032 DOES NOT NEED QM - 0.032 < RDL OF 0.1
3494313 | WHISPERING PINES MHP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2 | PCI/L | 15.4999 | 2015-11-11 | AAA |  |  |  |  | RADS DUE 2021
3494313 | WHISPERING PINES MHP | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-11-11 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | N | 0.15 | MG/L | 10.4999 | 2015-11-11 | AAA |  |  |  |  | 15DON(NO MCL)16:2QM/DAL 3/16 NN NEXT T/H @ 9/10/18 (R.M.) ABSOLUTE WATER)
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-03-17 | AAA |  | 1.4999 |  |  | 2QM/DAL (3QM/DAL 6/16) 7/18/16 EW HAS 6/16 DAL BY EM FOR PROCESSING
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-06-30 | AAA |  | 1.4999 |  |  | 3QM/DAL (4QM/DAL DUE 9/16) EM 7/18/16 TO D. RIGDON FOR REMINDER OF 9/16 QTR TESTING
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-09-26 | AAA |  | 1.4999
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-12-21 | AAA
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-21 | AAA
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-12-27 | AAA | 1 | 1.4999 |  |  | RCVD 2-10-17
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-10-19 | AAA
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-10-19 | AAA
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-10-31 | AAA |  | 1.4999
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-21 | AAA
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-21 | AAA
3494313 | WHISPERING PINES MHP | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-06-25 | AAA | 0.46 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-06-25 | AAA | 0.006 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-06-25 | AAA | 5e-05 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-06-25 | AAA | 0.00024 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1025 | FLUORIDE | N | 0.24 | MG/L | 4.0499 | 2018-06-25 | AAA | 0.075 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-06-25 | AAA | 0.0048 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-06-25 | AAA | 0.0016 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-06-25 | AAA | 0.00045 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1052 | SODIUM | N | 6.8 | MG/L | 160.4999 | 2018-06-25 | AAA | 0.34 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-06-25 | AAA | 0.00011 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-06-25 | AAA | 0.0004 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-06-25 | AAA | 6e-05 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-06-25 | AAA | 0.028 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1017 | CHLORIDE | N | 10 | MG/L | 250.4999 | 2018-06-25 | AAA | 0.78 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-06-25 | AAA | 0.0032 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1025 | FLUORIDE | N | 0.24 | MG/L | 2.0499 | 2018-06-25 | AAA | 0.075 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-06-25 | AAA | 0.1 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1032 | MANGANESE | N | 0.0025 | MG/L | 0.0549 | 2018-06-25 | AAA | 0.0019 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-06-25 | AAA | 0.0001 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1055 | SULFATE | N | 44 | MG/L | 250.4999 | 2018-06-25 | AAA | 0.52 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-06-25 | AAA | 0.033 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-06-25 | AAA | 5 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-06-25 | AAA | 1 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.32 | LN(10) |  | 2018-06-25 | AAA |  |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 170 | MG/L | 500.4999 | 2018-06-25 | AAA | 10 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-06-25 | AAA | 0.04 |  |  |  | 53076/CHL FL SULF COL OD PH TDS E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-06-25 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-06-25 | AAA | 0.32 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-06-25 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-06-25 | AAA | 0.44 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-06-25 | AAA | 0.00058 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-06-25 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-06-25 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-06-25 | AAA | 0.18 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-06-25 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.36 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-06-25 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.23 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-06-25 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-06-25 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.24 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-06-25 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-06-25 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-06-25 | AAA | 0.22 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-06-25 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-06-25 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-06-25 | AAA | 0.051 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | N | 0.24 | MG/L | 1.4999 | 2018-06-25 | AAA | 0.053 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-06-25 | AAA | 8e-05 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | INOR | 1010 | BARIUM | N | 0.021 | MG/L | 2.4999 | 2018-06-25 | AAA | 0.00083 |  |  |  | E53076/NN FL E84589/CY HG
3494313 | WHISPERING PINES MHP | DBP | 2950 | TOTAL THMS | D | 23.48 | UG/L | 80.4999 | 2018-08-08 | L1 | 0.39 |  | 1 | 1.1
3494313 | WHISPERING PINES MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.57 | UG/L | 60.4999 | 2018-08-08 | L1 | 0.91 |  | 1 | 1.1
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | D | 0 | UG/L | 249.9999 | 2018-11-27 | AAA |  | 1.4999
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-16 | AAA
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-04-16 | AAA
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-11-19 | AAA |  | 1.4999
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | E | 0 | UG/L | 1.4999 | 2015-09-09 | AAA |  | 0.1499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | E | 0 | UG/L | 0.2499 | 2015-09-09 | AAA |  | 0.0249 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | E | 0 | UG/L | 1.4999 | 2015-09-09 | AAA |  | 0.0449 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | E | 0 | UG/L | 0.5499 | 2015-09-09 | AAA |  | 0.1499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | E | 0 | UG/L | 0.2499 | 2015-09-09 | AAA |  | 0.0249 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | E | 0 | UG/L | 0.0249 | 2015-09-09 | AAA |  | 0.0149 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | E | 0 | UG/L | 2.4999 | 2015-09-09 | AAA |  | 0.2499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0.0021 | MG/L | 0.0154 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0.001 | MG/L | 0.1499 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0.0009 | MG/L | 0.0549 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 36 | MG/L | 160.4999 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0.0019 | MG/L | 0.0065 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0.0004 | MG/L | 0.0045 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 43 | MG/L | 250.4999 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0.027 | MG/L | 1.4999 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.15 | MG/L | 2.0499 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1028 | IRON | N | 0.16 | MG/L | 0.3499 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0017 | MG/L | 0.0549 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.06 | MG/L | 5.4999 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.2 | LN(10) |  | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 230 | MG/L | 500.4999 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0.18 |  | 0.5499 | 2015-09-09 | AAA |  |  |  |  | NO MCLS
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-09-09 | AAA |  |  |  |  | RADS DUE AGAIN 2021
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-09-09 | AAA |  | 1.4999 |  |  | RADS DUE AGAIN 2021
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | E | 0 | UG/L | 74.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | E | 0 | UG/L | 74.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | E | 0 | UG/L | 10499.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | E | 0 | UG/L | 5.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | E | 0 | UG/L | 649.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | E | 0 | UG/L | 75.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | E | 0 | UG/L | 1.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | E | 0 | UG/L | 7.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | E | 0 | UG/L | 149.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | E | 0 | UG/L | 3.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | E | 0 | UG/L | 249.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | E | 0 | UG/L | 3.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | E | 0 | UG/L | 5.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | E | 0 | UG/L | 3.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | E | 0 | UG/L | 5.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | E | 0 | UG/L | 3.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | E | 0 | UG/L | 149.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24 | UG/L | 60.4999 | 2015-09-09 | L1 |  |  |  | 1.6 | L-1 (TRAILER #1) (REMAIN ON R.M. - NEXT T/H DUE @ 9/1/18) <500
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 23.2 | UG/L | 80.4999 | 2015-09-09 | L1 |  |  |  | 1.6 | L-1 (TRAILER #1) (REMAIN ON R.M. - NEXT T/H DUE @ 9/1/18) <500
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-09-09 | AAA | 0.02 | 0.0249 |  |  | BENZO(A)PYRENE W/O COMPOSITING - FROM ORIG SAMPLE (CAN USE THIS ONE RATHER THAN COMPOSITE FOR COMPLIANCE - BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | E | 0 | UG/L | 1.4999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | E | 0 | UG/L | 1499.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | E | 0 | UG/L | 749.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | E | 0 | UG/L | 149.9999 | 2015-09-09 | AAA |  | 0.5499 |  |  | 3YR VOC (COMPOSITED W/LAUREL MHP 6531052)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | E | 0 | UG/L | 2.4999 | 2015-09-09 | AAA |  | 0.0149 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | E | 0 | UG/L | 0.2499 | 2015-09-09 | AAA |  | 0.0249 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | E | 0 | UG/L | 44.9999 | 2015-09-09 | AAA |  | 0.1499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | E | 0 | UG/L | 3.4999 | 2015-09-09 | AAA |  | 1.4999 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | E | 0 | UG/L | 249.9999 | 2015-09-09 | AAA |  | 1.4999 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | E | 0 | UG/L | 24.9999 | 2015-09-09 | AAA |  | 0.4499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | E | 0 | UG/L | 149.9999 | 2015-09-09 | AAA |  | 9.4999 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | E | 0 | UG/L | 749.9999 | 2015-09-09 | AAA |  | 6.4999 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | E | 0 | UG/L | 449.9999 | 2015-09-09 | AAA |  | 0.6499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | E | 0 | UG/L | 249.9999 | 2015-09-09 | AAA |  | 2.4999 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | E | 0 | UG/L | 4.4999 | 2015-09-09 | AAA |  | 0.0749 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | E | 0 | UG/L | 6.4999 | 2015-09-09 | AAA |  | 0.6499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | E | 0 | UG/L | 549.9999 | 2015-09-09 | AAA |  | 0.1499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | E | 0 | UG/L | 7.4999 | 2015-09-09 | AAA |  | 0.2499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | E | 0 | UG/L | 54.9999 | 2015-09-09 | AAA |  | 0.1499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | E | 0 | UG/L | 44.9999 | 2015-09-09 | AAA |  | 0.9499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | E | 0 | UG/L | 3.4999 | 2015-09-09 | AAA |  | 0.1499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | E | 0 | UG/L | 2.4999 | 2015-09-09 | AAA |  | 0.2499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | E | 0 | UG/L | 0.4499 | 2015-09-09 | AAA |  | 0.0449 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.29 | MG/L | 10.4999 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0.03 | MG/L | 1.4999 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.0094 | MG/L | 2.4999 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0.0025 | MG/L | 0.1499 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.15 | MG/L | 4.0499 | 2015-09-09 | AAA |  |  |  |  | (5/12 EW HAS 2/16 NN) NO MCLS (BIOMETRICS OPR EFFEC. 4/12/16>SNT 2016 MONIT SCHEDULE 5/10/16-BB US WTR OPR 4/1/16-4/11/16 & TOOK 4/16 BAC PREV. OPR 3/16 & FOR YEARS LARRY SCOTT TRI-FLA. WTR. BB)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | E | 0 | UG/L | 0.2499 | 2015-09-09 | AAA |  | 0.0249 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | E | 0 | UG/L | 74.9999 | 2015-09-09 | AAA |  | 0.1499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | E | 0 | UG/L | 54.9999 | 2015-09-09 | AAA |  | 0.2499 |  |  | 3YR SOC (COMPOSITED W/LAUREL MHP 6531052) BENZO HAS J5 QUALIFIER (J5 MS BENZO ONLY 11% RECOVERY-HAVE TEST RESULT W/O COMPOSITING ALSO ENT'D SEPARATELY FOR BENZO-BOTH ARE BELOW DETECTION LIMITS)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-22 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-22 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-25 | AAA |  | 0.0249
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-25 | AAA |  | 0.1499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-25 | AAA |  | 0.2499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-25 | AAA |  | 0.1499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-25 | AAA |  | 0.0249
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-25 | AAA |  | 0.0449
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-25 | AAA |  | 0.1499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-25 | AAA |  | 0.0249
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-25 | AAA |  | 0.0149
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-25 | AAA |  | 0.2499
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-04-25 | AAA
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-04-25 | AAA |  | 1.4999
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-25 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0.012 | UG/L | 2.4999 | 2017-04-25 | AAA |  | 0.0149
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-25 | AAA |  | 0.0249
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-25 | AAA |  | 0.1499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-25 | AAA |  | 1.4999
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-25 | AAA |  | 1.4999
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-25 | AAA |  | 0.4499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-25 | AAA |  | 9.4999
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-25 | AAA |  | 6.4999
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-25 | AAA |  | 0.6499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-25 | AAA |  | 2.4999
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-25 | AAA |  | 0.0749
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-25 | AAA |  | 0.6499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-25 | AAA |  | 0.1499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-25 | AAA |  | 0.2499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-25 | AAA |  | 0.1499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-25 | AAA |  | 0.9499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-25 | AAA |  | 0.1499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-25 | AAA |  | 0.2499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-25 | AAA |  | 0.0449
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 11.7 | UG/L | 80.4999 | 2017-06-27 | L1 |  |  |  | 1 | L-1 (TRAILER #1)
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.5 | UG/L | 60.4999 | 2017-06-27 | L1 |  |  |  | 1 | L-1 (TRAILER #1)
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-06-27 | AAA |  |  |  |  | REVISION NEEDED
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-06-27 | AAA |  |  |  |  | REVISION NEEDED
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-07-25 | AAA |  | 0.0149 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-07-25 | AAA |  | 0.0249 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-07-25 | AAA |  | 0.1499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-07-25 | AAA |  | 1.4999 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-07-25 | AAA |  | 1.4999 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-07-25 | AAA |  | 0.4499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-07-25 | AAA |  | 9.4999 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-07-25 | AAA |  | 6.4999 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-07-25 | AAA |  | 0.6499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-07-25 | AAA |  | 2.4999 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-07-25 | AAA |  | 0.0749 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-07-25 | AAA |  | 0.6499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-07-25 | AAA |  | 0.1499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-07-25 | AAA |  | 0.2499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-07-25 | AAA |  | 0.1499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-07-25 | AAA |  | 0.9499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-07-25 | AAA |  | 0.1499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-07-25 | AAA |  | 0.2499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-07-25 | AAA |  | 0.0449 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-07-25 | AAA |  | 0.0249 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-07-25 | AAA |  | 0.1499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-07-25 | AAA |  | 0.2499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-07-25 | AAA |  | 0.1499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-07-25 | AAA |  | 0.0249 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-07-25 | AAA |  | 0.0449 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-07-25 | AAA |  | 0.1499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-07-25 | AAA |  | 0.0249 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-07-25 | AAA |  | 0.0149 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-07-25 | AAA |  | 0.2499 |  |  | 2040 PICLORAM U J DATA QUALIFIER; % RECOVERY 131. BIASED HIGH. THE RESULTS ARE ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-07-25 | AAA
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-07-25 | AAA |  | 1.4999
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-07-25 | AAA |  | 0.5499 |  |  | 2964 DICHLOROMETHANE UJ DATA QUALIFIER % RECOVERY IS 165 & 149. BIASED HIGH. RESULTS ACCEPTABLE - MBB
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-10-19 | AAA |  | 0.0149 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-10-19 | AAA |  | 0.0249 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-10-19 | AAA |  | 0.1499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-10-19 | AAA |  | 1.4999 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-10-19 | AAA |  | 0.4499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-10-19 | AAA |  | 6.4999 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-10-19 | AAA |  | 0.6499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-10-19 | AAA |  | 2.4999 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-10-19 | AAA |  | 0.0749 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-10-19 | AAA |  | 0.6499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-10-19 | AAA |  | 0.1499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-10-19 | AAA |  | 0.9499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-10-19 | AAA |  | 0.1499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-10-19 | AAA |  | 0.2499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-10-19 | AAA |  | 0.0449 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-10-19 | AAA |  | 0.0249 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-10-19 | AAA |  | 0.1499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-10-19 | AAA |  | 0.0249 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-10-19 | AAA |  | 0.1499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-10-19 | AAA |  | 0.0249 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-10-19 | AAA |  | 0.0149 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-10-19 | AAA |  | 0.2499 |  |  | ENDOTHALL DALAPON PICLORAM DINOSEB 2 4-D 2 4 5-TP PENTACHLOROPHENOL MS/MSD 0% NOT ACCEPTED. BEGIN 1QM IN 1ST Q 2018 FOR THESE. THE REST WILL HAVE 4QM IN 1STQ 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-10-19 | AAA |  |  |  |  | 3QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-10-19 | AAA |  | 1.4999 |  |  | 3QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-10-19 | AAA |  | 0.5499 |  |  | 3RD QM AFTER NEW WELL. SAMPLE 1ST Q 2018_JMF
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.13 | MG/L | 4.0499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 13 | MG/L | 160.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 12.6 | MG/L | 250.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 107 | MG/L | 500.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 3.2 | MG/L | 250.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0029 | MG/L | 0.0549 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.13 | MG/L | 2.0499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1028 | IRON | N | 0.13 | MG/L | 0.3499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.0449 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-03-27 | AAA |  | 0.1499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-03-27 | AAA |  |  |  |  | DUE 2024_JMF
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-03-27 | AAA |  | 1.4999 |  |  | DUE 2024_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-03-27 | AAA |  | 9.4999 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-27 | AAA |  | 0.0149 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.0149 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 1.4999 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 1.4999 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-27 | AAA |  | 0.4499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-27 | AAA |  | 6.4999 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-03-27 | AAA |  | 0.6499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 2.4999 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-03-27 | AAA |  | 0.0749 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-03-27 | AAA |  | 0.6499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.9499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 0.1499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-03-27 | AAA |  | 0.0449 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.2499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.1499 |  |  | 1QM[2QM 4-6/18] ETHOXYCLOR ENDOTHALL SIMAZINE CARBOFURAN DIBROMOCHLOROPROPANE ETHYLENE DIBROMIDE HAVE RESULTS OF U J BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.0149 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-05-22 | AAA |  | 0.9499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-05-22 | AAA |  | 1.4999 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-05-22 | AAA |  | 1.4999 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-05-22 | AAA |  | 0.4499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-05-22 | AAA |  | 9.4999 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-05-22 | AAA |  | 6.4999 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-05-22 | AAA |  | 0.6499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-05-22 | AAA |  | 0.0749 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-05-22 | AAA |  | 0.6499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-05-22 | AAA |  | 0.0449 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-05-22 | AAA |  | 0.1499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-05-22 | AAA |  | 0.0449 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-05-22 | AAA |  | 0.1499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.2499 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-05-22 | AAA |  | 2.4999 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 |  |  | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | M | 8.2 | UG/L | 80.4999 | 2018-09-25 | L1 |  |  |  |  | RECV'D 02/14/19_KAC
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 9.9 | UG/L | 60.4999 | 2018-09-25 | L1 |  |  |  |  | RECV'D 02/14/19_KAC
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-09-25 | AAA |  | 0.6499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-09-25 | AAA |  | 0.0149 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-09-25 | AAA |  | 0.0149 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-09-25 | AAA |  | 0.1499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-09-25 | AAA |  | 1.4999 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-09-25 | AAA |  | 1.4999 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-09-25 | AAA |  | 0.4499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-09-25 | AAA |  | 9.4999 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-09-25 | AAA |  | 6.4999 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-09-25 | AAA |  | 0.6499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-09-25 | AAA |  | 2.4999 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-09-25 | AAA |  | 0.0749 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-09-25 | AAA |  | 0.2499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-09-25 | AAA |  | 0.1499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-09-25 | AAA |  | 0.2499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-09-25 | AAA |  | 0.1499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-09-25 | AAA |  | 0.9499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-09-25 | AAA |  | 0.1499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-09-25 | AAA |  | 0.2499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-09-25 | AAA |  | 0.0449 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-09-25 | AAA |  | 0.1499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-09-25 | AAA |  | 0.2499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-09-25 | AAA |  | 0.1499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-09-25 | AAA |  | 0.0449 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-09-25 | AAA |  | 0.1499 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 |  |  | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-12-26 | AAA |  | 0.0749 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-12-26 | AAA |  | 0.6499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-12-26 | AAA |  | 0.1499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-12-26 | AAA |  | 2.4999 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-12-26 | AAA |  | 0.6499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-12-26 | AAA |  | 6.4999 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-12-26 | AAA |  | 9.4999 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-12-26 | AAA |  | 0.4499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-12-26 | AAA |  | 1.4999 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-12-26 | AAA |  | 1.4999 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-12-26 | AAA |  | 0.1499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-12-26 | AAA |  | 0.0149 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-12-26 | AAA |  | 0.2499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-12-26 | AAA |  | 0.0149 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-12-26 | AAA |  | 0.1499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-12-26 | AAA |  | 0.0449 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-12-26 | AAA |  | 0.1499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-12-26 | AAA |  | 0.2499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-12-26 | AAA |  | 0.1499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-12-26 | AAA |  | 0.2499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-12-26 | AAA |  | 0.1499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-12-26 | AAA |  | 0.9499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-12-26 | AAA |  | 0.1499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-12-26 | AAA |  | 0.2499 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-12-26 | AAA |  | 0.0449 |  |  | 4QM [CAN MOVE TO "T" MISISNG 2Q18SAMPLES RCVD 8/8/19 NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | S | 0 | UG/L | 54.9999 | 2019-02-14 | AAA |  | 0.2499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | S | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.1499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | S | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.0449 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | S | 0 | UG/L | 0.5499 | 2019-02-14 | AAA |  | 0.1499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | S | 0 | UG/L | 0.0249 | 2019-02-14 | AAA |  | 0.0149 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | S | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | S | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 2.4999 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | S | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.0149 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | S | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | S | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 1.4999 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | S | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 1.4999 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | S | 0 | UG/L | 24.9999 | 2019-02-14 | AAA |  | 0.4499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | S | 0 | UG/L | 149.9999 | 2019-02-14 | AAA |  | 9.4999 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | S | 0 | UG/L | 749.9999 | 2019-02-14 | AAA |  | 6.4999 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | S | 0 | UG/L | 449.9999 | 2019-02-14 | AAA |  | 0.6499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | S | 0 | UG/L | 4.4999 | 2019-02-14 | AAA |  | 0.0749 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | S | 0 | UG/L | 6.4999 | 2019-02-14 | AAA |  | 0.6499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | S | 0 | UG/L | 549.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | S | 0 | UG/L | 7.4999 | 2019-02-14 | AAA |  | 0.2499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | S | 0 | UG/L | 54.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | S | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.9499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | S | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 0.1499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | S | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | S | 0 | UG/L | 0.4499 | 2019-02-14 | AAA |  | 0.0449 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | S | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2 4-D | S | 0 | UG/L | 74.9999 | 2019-02-14 | AAA |  | 0.1499 |  |  | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-08-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-08-27 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-13 | AAA | 0.2 |  |  |  | NN FL (IN OC) 32QM/FL AFT.MCL(FL 2.81)ENT'D AS BOTH PRIM.&SEC(1/15 RAA/FL=2.725 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 & 2/19/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-13 | AAA | 0.2 |  |  |  | NN FL (IN OC) 32QM/FL AFT.MCL(FL 2.81)ENT'D AS BOTH PRIM.&SEC(1/15 RAA/FL=2.725 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 & 2/19/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.81 | MG/L | 4.0499 | 2015-01-13 | AAA | 0.2 |  |  |  | NN FL (IN OC) 32QM/FL AFT.MCL(FL 2.81)ENT'D AS BOTH PRIM.&SEC(1/15 RAA/FL=2.725 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 & 2/19/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.81 | MG/L | 2.0499 | 2015-01-13 | AAA | 0.2 |  |  |  | FL (IN OC) 32QM/FL AFT.MCL(FL 2.81)ENT'D AS BOTH PRIM.&SEC(1/15 RAA/FL=2.725 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.82 | MG/L | 4.0499 | 2015-04-13 | AAA |  |  |  |  | 33QM/FL AFT.MCL(FL 2.82)ENT'D AS BOTH PRIM.&SEC(6/15 RAA/FL=2.7475 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.82 | MG/L | 2.0499 | 2015-04-13 | AAA |  |  |  |  | 33QM/FL AFT.MCL(FL 2.82)ENT'D AS BOTH PRIM.&SEC(6/15 RAA/FL=2.7475 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.81 | MG/L | 4.0499 | 2015-07-07 | AAA | 0.2 |  |  |  | 34QM/FL AFT.MCL(FL 2.81)ENT'D AS BOTH PRIM.&SEC(7/15 RAA/FL=2.78 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.81 | MG/L | 2.0499 | 2015-07-07 | AAA | 0.2 |  |  |  | 34QM/FL AFT.MCL(FL 2.81)ENT'D AS BOTH PRIM.&SEC(7/15 RAA/FL=2.78 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.1 | UG/L | 60.4999 | 2015-08-21 | L1 |  |  |  | 1.2 | LOT 64 BREEZEWAY COURT (TTHMS 94.3 2QM/T+H 12/15>EM 10/19/15 TO US WTR & OWNER) <500 PSD 3RD WEEK AUGUST NORMALLY
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 94.3 | UG/L | 80.4999 | 2015-08-21 | L1 |  |  |  | 1.2 | LOT 64 BREEZEWAY COURT (TTHMS 94.3 2QM/T+H 12/15>EM 10/19/15 TO US WTR & OWNER) <500 PSD 3RD WEEK AUGUST NORMALLY
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 85.2 | UG/L | 80.4999 | 2015-11-18 | L1 |  |  |  | 0.45 | LOT 64 BREEZEWAY COURT (AFTER 2 QTRS LRAA/T=44.875 LRAA/H=16.4) 3/22 EW HAS 2/16 DBPS
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.5 | UG/L | 60.4999 | 2015-11-18 | L1 |  |  |  | 0.45 | LOT 64 BREEZEWAY COURT (AFTER 2 QTRS LRAA/T=44.875 LRAA/H=16.4) 3/22 EW HAS 2/16 DBPS
3494318 | LAKE MARIAN SHORES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0.73 | UG/L | 10499.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.92 | MG/L | 2.0499 | 2015-11-24 | AAA |  |  |  |  | 35QM/FL AFT.MCL(FL 2.92)ENT'D AS BOTH PRIM.&SEC(11/15 RAA/FL=X.XX MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.92 | MG/L | 4.0499 | 2015-11-24 | AAA |  |  |  |  | 35QM/FL AFT.MCL(FL 2.92)ENT'D AS BOTH PRIM.&SEC(11/15 RAA/FL=X.XX MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-11-24 | AAA |  | 0.5499 |  |  | 3YR VOC+2QM/XY 3/16 (XY 0.73 UG/L) EM 12/30/15 TO US WTR FOR QM/XYLENES
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.92 | MG/L | 4.0499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 270 | MG/L | 500.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.83 | LN(10) |  | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1055 | SULFATE | N | 1.23 | MG/L | 250.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1028 | IRON | N | 0.0118 | MG/L | 0.3499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.92 | MG/L | 2.0499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1017 | CHLORIDE | N | 42.1 | MG/L | 250.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1010 | BARIUM | N | 0.0152 | MG/L | 2.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1052 | SODIUM | N | 18.3 | MG/L | 160.4999 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-12-08 | AAA |  |  |  |  | EX. 35QM/FL AFT.MCL(2 FL EA. 2.92)ENT'D AS BOTH PRIM.&SEC(12/15 RAA/FL=2.84 MG/L)PN TO BE DONE ANNUALLY-PN FOR 2015 ALREADY ISSUED 2/17/15 FOR THE 1/15 FL SINGLE SAMPLE MCL VIOL.
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.82 | MG/L | 4.0499 | 2016-02-11 | AAA |  |  |  |  | FLUORIDE (ALL OK)
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.82 | MG/L | 2.0499 | 2016-02-11 | AAA |  |  |  |  | FLUORIDE (ALL OK)
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-02-18 | AAA |  | 0.5499 |  |  | 2QM/XY (3QM/XY 6/16 4QM/XY 9/16)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 2.73 | UG/L | 80.4999 | 2016-02-18 | L1 |  |  |  | 0.9 | LOT 64 BREEZEWAY COURT (AFTER 3 QTRS LRAA/T=XXXX LRAA/H=XXXXX) NO MCLS OR OE EXCEEDANCES 3/16 QTR
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.09 | UG/L | 60.4999 | 2016-02-18 | L1 |  |  |  | 0.9 | LOT 64 BREEZEWAY COURT (AFTER 3 QTRS LRAA/T=XXXX LRAA/H=XXXXX) NO MCLS OR OE EXCEEDANCES 3/16 QTR
3494318 | LAKE MARIAN SHORES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.9 | MG/L | 2.0499 | 2016-05-25 | AAA | 0.2 |  |  |  | FLUORIDE 2.90 - ALL REVISIONS RCVD. (NOTE: 8/17 ASKED FOR MELISA US WTR & CJ SILVA TO ADD SECONDARIES FLUORIDE TO REPORT-CJ SILVA EM WENT NOWHERE - MELISA SAID SHE SENT RQST TO LAB ON 8/17/16.)
3494318 | LAKE MARIAN SHORES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.32 | UG/L | 60.4999 | 2016-05-25 | L1 |  |  |  | 0.92 | LOT 64 BREEZEWAY COURT (AFTER 4 QTRS 6/16 LRAA/T=47.29 LRAA/H=20.2525) T<60 H<45. MAY STOP QM/T+H. NO MCLS OR OE EXCEEDANCES 6/16 QTR
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 6.93 | UG/L | 80.4999 | 2016-05-25 | L1 |  |  |  | 0.92 | LOT 64 BREEZEWAY COURT (AFTER 4 QTRS 6/16 LRAA/T=47.29 LRAA/H=20.2525) T<60 H<45. MAY STOP QM/T+H. NO MCLS OR OE EXCEEDANCES 6/16 QTR
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.9 | MG/L | 4.0499 | 2016-05-25 | AAA |  |  |  |  | 5/16 FL ADDED TO SECONDARIES PAGE AS RQRD (IN OC) 9/30/16 EM RQSTED SECONDARIES FL BE ADDED TO 9/7/16 REPORT IN OC TO ROBERT FLWRS LAB - BB
3494318 | LAKE MARIAN SHORES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-05-25 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 9/16) SECONDARY FLUORIDE ADDED TO LAB REPORT BY FLOWERS LAB. BB (CHRIS SILVA IS CURRENT SAMPLER)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 50.2 | UG/L | 80.4999 | 2016-08-22 | L1 | 0.5 |  | 1 | 0.9 | ON ANN. T/H - LOT 64 BREEZEWAY COURT (T>40 H>30) REMAIN ON ANN. T/H DUE 8/17 (SAMPLER CHRIS SILVA)
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.9 | UG/L | 60.4999 | 2016-08-22 | L1 | 0.5 |  | 1 | 0.9 | ON ANN. T/H - LOT 64 BREEZEWAY COURT (T>40 H>30) REMAIN ON ANN. T/H DUE 8/17 (SAMPLER CHRIS SILVA)
3494318 | LAKE MARIAN SHORES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.89 | MG/L | 2.0499 | 2016-09-07 | AAA |  |  |  |  | FL 2.89
3494318 | LAKE MARIAN SHORES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-09-07 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-09-07 | AAA |  |  |  |  | NN FL 2.89
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-09-07 | AAA |  |  |  |  | NN FL 2.89
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.89 | MG/L | 4.0499 | 2016-09-07 | AAA |  |  |  |  | NN FL 2.89
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.73 | MG/L | 4.0499 | 2016-11-17 | AAA
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-11-25 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-15 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.85 | MG/L | 4.0499 | 2017-02-15 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.85 | MG/L | 2.0499 | 2017-02-15 | AAA |  |  |  |  | ANNUAL PN FOR FLOURIDE MCL RECIEVED 5/9/2017 - MBB
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.89 | MG/L | 2.0499 | 2017-04-25 | AAA | 0.2 |  |  |  | FL 2.89
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.89 | MG/L | 4.0499 | 2017-04-25 | AAA | 0.2 |  |  |  | FL 2.89
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.92 | MG/L | 4.0499 | 2017-07-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.92 | MG/L | 2.0499 | 2017-07-24 | AAA
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.52 | UG/L | 60.4999 | 2017-08-17 | L1 |  |  |  | 0.3 | LOT 64 BREEZEWAY COURT
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 6.86 | UG/L | 80.4999 | 2017-08-17 | L1 |  |  |  | 0.3 | LOT 64 BREEZEWAY COURT
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.79 | MG/L | 2.0499 | 2017-11-15 | AAA |  |  |  |  | FLUORIDE IS OVER MDL BUT NOT MCL- NO PN NEEDED.
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-11-15 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | S | 0 |  |  | 2017-11-15 | AAA |  |  |  |  | TOC AFTER FILTER AT ENTRY POINT FOR INFORMATIONAL PURPOSES
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | N | 0.2 | MG/L | 1.4999 | 2017-11-30 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-11-30 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | N | 3.3 |  |  | 2018-03-15 | AAA |  |  |  |  | TOC AFTER FILTER AT ENTRY POINT FOR INFORMATIONAL PURPOSES
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.4 | MG/L | 4.0499 | 2018-03-15 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 310 | MG/L | 500.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.2 | PCI/L | 15.4999 | 2018-05-24 | AAA |  |  |  |  | DUE 2024
3494318 | LAKE MARIAN SHORES | RAD | 4030 | RADIUM-228 | N | 0.7 | PCI/L | 2.4999 | 2018-05-24 | AAA |  | 1.4999 |  |  | DUE 2024
3494318 | LAKE MARIAN SHORES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | N | 0.18 | MG/L | 10.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.6 | MG/L | 4.0499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1005 | ARSENIC | N | 0.0015 | MG/L | 0.0104 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1010 | BARIUM | N | 0.026 | MG/L | 2.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1030 | LEAD | N | 0.0002 | MG/L | 0.0154 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1052 | SODIUM | N | 21 | MG/L | 160.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1074 | ANTIMONY | N | 0.0004 | MG/L | 0.0065 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1022 | COPPER | N | 0.0049 | MG/L | 1.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1017 | CHLORIDE | N | 39 | MG/L | 250.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.6 | MG/L | 2.0499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1055 | SULFATE | N | 3.7 | MG/L | 250.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.73 | LN(10) |  | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.5 | MG/L | 4.0499 | 2018-07-23 | AAA | 0.075 |  |  |  | FLUORIDE 2.5 MG/L
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.5 | MG/L | 2.0499 | 2018-07-23 | AAA | 0.075 |  |  |  | FLUORIDE 2.5 MG/L
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 142.3 | UG/L | 60.4999 | 2018-08-10 | L1 |  |  |  | 1.3 | 2950-LOT 64 BREEZEWAY COURT HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 152.28 | UG/L | 80.4999 | 2018-08-10 | L1 |  |  |  | 1.3 | 2950-LOT 64 BREEZEWAY COURT HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.7 | MG/L | 4.0499 | 2018-10-25 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | N | 3.4 |  |  | 2018-10-25 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.7 | MG/L | 2.0499 | 2018-10-25 | AAA
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-10-25 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E84589
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49.88 | UG/L | 60.4999 | 2018-11-20 | L1 | 0.91 |  | 1 | 0.55 | LOT 64 BREEZEWAY CT. OST (HLKD 12/28/18)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 64.39 | UG/L | 80.4999 | 2018-11-20 | L1 | 0.56 |  | 1 | 0.55 | LOT 64 BREEZEWAY CT. OST (HLKD 12/28/18)
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | N | 3.9 |  |  | 2018-12-04 | AAA |  |  |  |  | FLOURIDE CONTINUE TO ISSUE ANNUAL PN. SLB
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.6 | MG/L | 2.0499 | 2018-12-04 | AAA |  |  |  |  | FLOURIDE CONTINUE TO ISSUE ANNUAL PN. SLB
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.5 | MG/L | 2.0499 | 2019-01-02 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.6 | MG/L | 4.0499 | 2019-01-02 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | D | 2.6 | MG/L | 2.0499 | 2019-02-05 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | D | 2.6 | MG/L | 4.0499 | 2019-02-05 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | D | 2.6 | MG/L | 4.0499 | 2019-02-05 | AAA
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 104.66 | UG/L | 80.4999 | 2019-02-19 | L1 | 0.39 |  | 1 | 0.58 | LOT 64 BREEZEWAY CT [HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)]_JMF
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 74.77 | UG/L | 60.4999 | 2019-02-19 | L1 | 0.91 |  | 1 | 0.58 | LOT 64 BREEZEWAY CT [HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)]_JMF
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | D | 2.4 | MG/L | 4.0499 | 2019-03-08 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | D | 2.4 | MG/L | 2.0499 | 2019-03-08 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.4 | MG/L | 2.0499 | 2019-04-04 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.4 | MG/L | 4.0499 | 2019-04-04 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | N | 3.6 |  |  | 2019-04-19 | AAA |  |  |  |  | TOC AFTER FILTER AT ENTRY POINT FOR INFORMATIONAL PURPOSES
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | D | 0.57 | MG/L | 4.0499 | 2019-05-08 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | N | 4.2 |  |  | 2019-05-09 | AAA |  |  |  |  | TOC AFTER FILTER AT ENTRY POINT FOR INFORMATIONAL PURPOSES
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.8 | UG/L | 60.4999 | 2019-05-20 | L1 |  |  |  | 0.46 | LOT 64 BREEZEWAY COURT [HAA5 LRAA = 74.69; TTHM LRAA =91.37 ]_VP
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 44.16 | UG/L | 80.4999 | 2019-05-20 | L1 |  |  |  | 0.46 | LOT 64 BREEZEWAY COURT [HAA5 LRAA = 74.69; TTHM LRAA =91.37 ]_VP
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 23.3 | UG/L | 80.4999 | 2019-08-20 | L1 |  |  | 1 | 5.2 | LOT 64 BREEZEWAY COURT
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.99 | UG/L | 60.4999 | 2019-08-20 | L1 |  |  | 1 | 5.2 | LOT 64 BREEZEWAY COURT
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-10-09 | AAA | 0.25
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | N | 2.8 | MG/L | 2.0499 | 2019-10-09 | AAA | 0.15 |  |  |  | FLOURIDE
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-10-09 | AAA | 0.28 | 0.5499 |  |  | XYLENES
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | N | 0.46 | MG/L | 10.4999 | 2019-10-09 | AAA | 0.1
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | N | 2.8 | MG/L | 4.0499 | 2019-10-09 | AAA | 0.15
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.25 | UG/L | 60.4999 | 2019-11-20 | L1 | 0.91 |  | 1 | 0.7
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | D | 12.64 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.39 |  | 1 | 0.7
3494359 | HYATT FARMS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | E | 0 | UG/L | 149.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2980 | 1 2-DICHLOROETHANE | E | 0 | UG/L | 3.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | E | 0 | UG/L | 249.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2982 | CARBON TETRACHLORIDE | E | 0 | UG/L | 3.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2983 | 1 2-DICHLOROPROPANE | E | 0 | UG/L | 5.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2984 | TRICHLOROETHYLENE | E | 0 | UG/L | 3.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | E | 0 | UG/L | 5.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2987 | TETRACHLOROETHYLENE | E | 0 | UG/L | 3.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2989 | CHLOROBENZENE | E | 0 | UG/L | 149.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2990 | BENZENE | E | 0 | UG/L | 1.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | E | 0 | UG/L | 1499.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2992 | ETHYLBENZENE | E | 0 | UG/L | 749.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2996 | STYRENE | E | 0 | UG/L | 149.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2005 | ENDRIN | E | 0 | UG/L | 2.4999 | 2015-01-22 | AAA |  | 0.0149 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2010 | LINDANE | E | 0 | UG/L | 0.2499 | 2015-01-22 | AAA |  | 0.0249 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2015 | METHOXYCLOR | E | 0 | UG/L | 44.9999 | 2015-01-22 | AAA |  | 0.1499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2020 | TOXAPHENE | E | 0 | UG/L | 3.4999 | 2015-01-22 | AAA |  | 1.4999 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2031 | DALAPON | E | 0 | UG/L | 249.9999 | 2015-01-22 | AAA |  | 1.4999 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2032 | DIQUAT | E | 0 | UG/L | 24.9999 | 2015-01-22 | AAA |  | 0.4499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2041 | DINOSEB | E | 0 | UG/L | 7.4999 | 2015-01-22 | AAA |  | 0.2499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | E | 0 | UG/L | 54.9999 | 2015-01-22 | AAA |  | 0.1499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2046 | CARBOFURAN | E | 0 | UG/L | 44.9999 | 2015-01-22 | AAA |  | 0.9499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2050 | ATRAZINE | E | 0 | UG/L | 3.4999 | 2015-01-22 | AAA |  | 0.1499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2051 | ALACHLOR (LASSO) | E | 0 | UG/L | 2.4999 | 2015-01-22 | AAA |  | 0.2499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2065 | HEPTACHLOR | E | 0 | UG/L | 0.4499 | 2015-01-22 | AAA |  | 0.0449 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2067 | HEPTACHLOR EPOXIDE | E | 0 | UG/L | 0.2499 | 2015-01-22 | AAA |  | 0.0249 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2105 | 2 4-D | E | 0 | UG/L | 74.9999 | 2015-01-22 | AAA |  | 0.1499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2110 | 2 4 5-TP (Silvex) | E | 0 | UG/L | 54.9999 | 2015-01-22 | AAA |  | 0.2499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2274 | HEXACHLOROBENZENE | E | 0 | UG/L | 1.4999 | 2015-01-22 | AAA |  | 0.1499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2306 | BENZO(A)PYRENE | E | 0 | UG/L | 0.2499 | 2015-01-22 | AAA |  | 0.0249 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2326 | PENTACHLOROPHENOL | E | 0 | UG/L | 1.4999 | 2015-01-22 | AAA |  | 0.0449 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | E | 0 | UG/L | 0.5499 | 2015-01-22 | AAA |  | 0.1499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2931 | DIBROMOCHLOROPROPANE | E | 0 | UG/L | 0.2499 | 2015-01-22 | AAA |  | 0.0249 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2946 | ETHYLENE DIBROMIDE | E | 0 | UG/L | 0.0249 | 2015-01-22 | AAA |  | 0.0149 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2959 | CHLORDANE | E | 0 | UG/L | 2.4999 | 2015-01-22 | AAA |  | 0.2499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2033 | ENDOTHALL | E | 0 | UG/L | 149.9999 | 2015-01-22 | AAA |  | 9.4999 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2034 | GLYPHOSATE | E | 0 | UG/L | 749.9999 | 2015-01-22 | AAA |  | 6.4999 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | E | 0 | UG/L | 449.9999 | 2015-01-22 | AAA |  | 0.6499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2036 | OXAMYL (VYDATE) | E | 0 | UG/L | 249.9999 | 2015-01-22 | AAA |  | 2.4999 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2037 | SIMAZINE | E | 0 | UG/L | 4.4999 | 2015-01-22 | AAA |  | 0.0749 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | E | 0 | UG/L | 6.4999 | 2015-01-22 | AAA |  | 0.6499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | SOC | 2040 | PICLORAM | E | 0 | UG/L | 549.9999 | 2015-01-22 | AAA |  | 0.1499 |  |  | 3YR SOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | N | 0.03 | MG/L | 10.4999 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1005 | ARSENIC | N | 0.002 | MG/L | 0.0104 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1010 | BARIUM | N | 0.05 | MG/L | 2.4999 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1020 | CHROMIUM | N | 0.0092 | MG/L | 0.1499 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1025 | FLUORIDE | N | 0.94 | MG/L | 4.0499 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1036 | NICKEL | N | 0.001 | MG/L | 0.1499 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1045 | SELENIUM | N | 0.0059 | MG/L | 0.0549 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1052 | SODIUM | N | 65 | MG/L | 160.4999 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-01-22 | AAA |  |  |  |  | 15DON/16:NN RADS 2018 (LARRY SCOTT)
3494359 | HYATT FARMS | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1017 | CHLORIDE | N | 89 | MG/L | 250.4999 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1022 | COPPER | N | 0.0077 | MG/L | 1.4999 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1025 | FLUORIDE | N | 0.94 | MG/L | 2.0499 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1055 | SULFATE | N | 14 | MG/L | 250.4999 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1095 | ZINC | N | 0.0065 | MG/L | 5.4999 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.6 | LN(10) |  | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 300 | MG/L | 500.4999 | 2015-01-22 | AAA
3494359 | HYATT FARMS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-01-22 | AAA
3494359 | HYATT FARMS | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 4 | PCI/L | 15.4999 | 2015-01-22 | AAA |  |  |  |  | RADS DUE 2021
3494359 | HYATT FARMS | RAD | 4030 | RADIUM-228 | N | 0.7 | PCI/L | 2.4999 | 2015-01-22 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3494359 | HYATT FARMS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | E | 0 | UG/L | 74.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | E | 0 | UG/L | 74.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2955 | TOT XYLENE | E | 0 | UG/L | 10499.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2964 | DICHLOROMETHANE | E | 0 | UG/L | 5.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2968 | 1 2-DICHLOROBENZENE | E | 0 | UG/L | 649.9999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2969 | P-DICHLOROBENZENE | E | 0 | UG/L | 75.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2976 | VINYL CHLORIDE | E | 0 | UG/L | 1.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | VOC | 2977 | 1 1-DICHLOROETHENE | E | 0 | UG/L | 7.4999 | 2015-01-22 | AAA |  | 0.5499 |  |  | 3YR VOCS (COMPOSITE/HYATT FARMS & THREE LAKES)
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | D | 48.4 | UG/L | 80.4999 | 2015-07-27 | L1 |  |  |  | 1.5 | L-1 RED HOUSE (<500 REMAIN ON R.M. SINCE T<60 H<45) NEXT T/H DUE @ 9/1/18
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2015-07-27 | L1 |  |  |  | 1.5 | L-1 RED HOUSE (<500 REMAIN ON R.M. SINCE T<60 H<45) NEXT T/H DUE @ 9/1/18
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-11 | AAA
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-05-11 | AAA
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-15 | AAA
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-03-15 | AAA
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | D | 72.9 | UG/L | 80.4999 | 2018-09-21 | L1 | 0.5 |  | 1 | 2.5 | RED HOUSE (T>60 MUST TEST ROUTINE - ANNUALLY - IN 2019 HLKD TO SB)
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.3 | UG/L | 60.4999 | 2018-09-21 | L1 | 0.5 |  | 1 | 2.5 | RED HOUSE (T>60 MUST TEST ROUTINE - ANNUALLY - IN 2019 HLKD TO SB)
3494359 | HYATT FARMS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | N | 1.64 | UG/L | 1499.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-11-30 | AAA |  | 0.0249
3494359 | HYATT FARMS | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-11-30 | AAA |  | 0.0749
3494359 | HYATT FARMS | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-11-30 | AAA |  | 0.9499
3494359 | HYATT FARMS | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-11-30 | AAA |  | 0.0149
3494359 | HYATT FARMS | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-11-30 | AAA |  | 0.0249
3494359 | HYATT FARMS | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SEC | 1055 | SULFATE | N | 17.4 | MG/L | 250.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1095 | ZINC | N | 0.076 | MG/L | 5.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1920 | ODOR THRESHOLD | N | 2 |  | 3.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.83 | LN(10) |  | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 408 | MG/L | 500.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1002 | ALUMINUM | N | 0.027 | MG/L | 0.2499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1017 | CHLORIDE | N | 119 | MG/L | 250.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1022 | COPPER | N | 0.025 | MG/L | 1.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1025 | FLUORIDE | N | 0.855 | MG/L | 2.0499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1032 | MANGANESE | N | 0.001 | MG/L | 0.0549 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | N | 0.048 | MG/L | 10.4999 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1010 | BARIUM | N | 0.047 | MG/L | 2.4999 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1025 | FLUORIDE | N | 0.855 | MG/L | 4.0499 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1030 | LEAD | N | 0.001 | MG/L | 0.0154 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1052 | SODIUM | N | 49.5 | MG/L | 160.4999 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | N | 0.01 | MG/L | 0.0065 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-11-30 | AAA |  |  |  |  | ANTIMONY OVER MCL BEGIN QM_JMF
3494359 | HYATT FARMS | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 1.4999
3494359 | HYATT FARMS | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-11-30 | AAA |  | 1.4999
3494359 | HYATT FARMS | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-11-30 | AAA |  | 0.4499
3494359 | HYATT FARMS | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 9.4999
3494359 | HYATT FARMS | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-11-30 | AAA |  | 6.4999
3494359 | HYATT FARMS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-11-30 | AAA |  | 0.6499
3494359 | HYATT FARMS | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-11-30 | AAA |  | 2.4999
3494359 | HYATT FARMS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-11-30 | AAA |  | 0.6499
3494359 | HYATT FARMS | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-11-30 | AAA |  | 0.2499
3494359 | HYATT FARMS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-11-30 | AAA |  | 0.2499
3494359 | HYATT FARMS | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-11-30 | AAA |  | 0.0449
3494359 | HYATT FARMS | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-11-30 | AAA |  | 0.2499
3494359 | HYATT FARMS | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-11-30 | AAA |  | 0.5499 |  |  | 3 YR VOC OK. TOLUENE DETECT BEGIN QM. SYSTEM MISSED 1ST Q 2019 BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2019-02-13 | AAA |  |  |  |  | 1ST QUARTER ANTIMONY_KAC
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | AAA |  |  |  |  | 2019 NN SAMPLES_KAC
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-26 | AAA |  |  |  |  | 2019 NN SAMPLES_KAC
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2019-05-01 | AAA |  |  |  |  | 2QM (3QM DUE 7-9/19)
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-05-15 | AAA |  | 0.5499 |  |  | 1QM <MCL (2QM DUE 7-9/19)
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2019-08-28 | AAA |  |  |  |  | 3QM (4QM DUE 10-12/19)
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-08-28 | AAA |  | 0.5499 |  |  | 2QM (3QM DUE 10-12/19)
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | D | 43.6 | UG/L | 80.4999 | 2019-09-04 | L1 |  |  | 1 | 0.5 | L-1 RED HOUSE
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.5 | UG/L | 60.4999 | 2019-09-04 | L1 |  |  | 1 | 0.5 | L-1 RED HOUSE
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2019-11-11 | AAA |  |  |  |  | 4QM. 4 CONSEC. QUARTERS UNDETECTED. TEST WITH OTHER INORGANICS IN 2021_VP
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-11-11 | AAA |  | 0.5499 |  |  | 3 QM (4QM DUE 1-3/20)
3494399 | DEER PARK | DBP | 2950 | TOTAL THMS | D | 0.68 | UG/L | 80.4999 | 2015-09-03 | L1 |  |  |  | 0.3
3494399 | DEER PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 1.62 | UG/L | 60.4999 | 2015-09-03 | L1 |  |  |  | 0.3
3494399 | DEER PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1052 | SODIUM | N | 44.2 | MG/L | 160.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1017 | CHLORIDE | N | 94.2 | MG/L | 250.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1028 | IRON | N | 0.1 | MG/L | 0.3499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1032 | MANGANESE | N | 0.0213 | MG/L | 0.0549 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1055 | SULFATE | N | 8.88 | MG/L | 250.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1095 | ZINC | N | 0.0271 | MG/L | 5.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.58 | LN(10) |  | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 482 | MG/L | 500.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-10-29 | AAA |  | 0.0149 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-10-29 | AAA |  | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-10-29 | AAA |  | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-10-29 | AAA |  | 1.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-10-29 | AAA |  | 1.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-10-29 | AAA |  | 0.4499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-10-29 | AAA |  | 9.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-10-29 | AAA |  | 6.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-10-29 | AAA |  | 0.6499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-10-29 | AAA |  | 2.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-10-29 | AAA |  | 0.0749 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-10-29 | AAA |  | 0.6499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-10-29 | AAA |  | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-10-29 | AAA |  | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-10-29 | AAA |  | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-10-29 | AAA |  | 0.9499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-10-29 | AAA |  | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-10-29 | AAA |  | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-10-29 | AAA |  | 0.0449 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-10-29 | AAA |  | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-10-29 | AAA |  | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-10-29 | AAA |  | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-10-29 | AAA |  | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-10-29 | AAA |  | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-10-29 | AAA |  | 0.0449 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-10-29 | AAA |  | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-10-29 | AAA |  | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-10-29 | AAA |  | 0.0149 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-10-29 | AAA |  | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1010 | BARIUM | N | 0.0407 | MG/L | 2.4999 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2015-10-29 | AAA |  |  |  |  | NO MCLS
3494399 | DEER PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-11-22 | AAA
3494399 | DEER PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-11-22 | AAA
3494399 | DEER PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-12-18 | AAA
3494399 | DEER PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-12-18 | AAA
3494399 | DEER PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.04 | 0.0449 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-07-16 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-07-16 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-07-16 | AAA | 0.01 | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-07-16 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-07-16 | AAA | 0.05 | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 1.4999 |  |  | 3YR SOC
3494399 | DEER PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-07-16 | AAA | 0.001 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-07-16 | AAA | 0.005 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-07-16 | AAA | 0.2 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-07-16 | AAA | 0.001 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-07-16 | AAA | 2e-05 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-07-16 | AAA | 0.001 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-07-16 | AAA | 0.002 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1052 | SODIUM | N | 42.8 | MG/L | 160.4999 | 2018-07-16 | AAA | 0.5 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-07-16 | AAA | 0.001 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-07-16 | AAA | 0.0005 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-07-16 | AAA | 0.001 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | D | 4.1 | PCI/L | 15.4999 | 2018-07-16 | AAA |  |  |  |  | RADS DUE 2024
3494399 | DEER PARK | RAD | 4020 | RADIUM-226 | D | 0.8 | PCI/L | 3.4999 | 2018-07-16 | AAA |  | 1.4999 |  |  | RADS DUE 2024
3494399 | DEER PARK | RAD | 4030 | RADIUM-228 | D | 0.9 | PCI/L | 2.4999 | 2018-07-16 | AAA |  | 1.4999 |  |  | RADS DUE 2024
3494399 | DEER PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-07-16 | AAA | 0.02 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1017 | CHLORIDE | N | 80.7 | MG/L | 250.4999 | 2018-07-16 | AAA | 0.4 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1022 | COPPER | N | 0.0069 | MG/L | 1.4999 | 2018-07-16 | AAA | 0.001 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-07-16 | AAA | 0.2 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1028 | IRON | N | 0.102 | MG/L | 0.3499 | 2018-07-16 | AAA | 0.01 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1032 | MANGANESE | N | 0.0206 | MG/L | 0.0549 | 2018-07-16 | AAA | 0.01 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-07-16 | AAA | 0.0005 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1055 | SULFATE | N | 8.28 | MG/L | 250.4999 | 2018-07-16 | AAA | 1 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1095 | ZINC | N | 0.0195 | MG/L | 5.4999 | 2018-07-16 | AAA | 0.01 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-07-16 | AAA | 5 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-07-16 | AAA | 1 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.81 | LN(10) |  | 2018-07-16 | AAA | 0.01 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 506 | MG/L | 500.4999 | 2018-07-16 | AAA | 2.5 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-07-16 | AAA | 0.2 |  |  |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-07-16 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3494399 | DEER PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-07-16 | AAA | 0.1 | 1.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-07-16 | AAA | 0.4 | 0.4499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 9 | 9.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-07-16 | AAA | 6 | 6.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-07-16 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-07-16 | AAA | 2 | 2.4999 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-07-16 | AAA | 0.07 | 0.0749 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-07-16 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-07-16 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-07-16 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-07-16 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-07-16 | AAA | 0.9 | 0.9499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-07-16 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-07-16 | AAA | 0.01 | 0.0449 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-07-16 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-07-16 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3494399 | DEER PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-07-16 | AAA | 0.2 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-07-16 | AAA | 0.2 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-07-16 | AAA | 0.001 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1010 | BARIUM | N | 0.0429 | MG/L | 2.4999 | 2018-07-16 | AAA | 0.002 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-07-16 | AAA | 0.001 |  |  |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3494399 | DEER PARK | DBP | 2950 | TOTAL THMS | D | 31.7 | UG/L | 80.4999 | 2018-09-25 | L1
3494399 | DEER PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.7 | UG/L | 60.4999 | 2018-09-25 | L1
3494399 | DEER PARK | INOR | 1040 | NITRATE | N | 0.2 | MG/L | 10.4999 | 2019-12-12 | AAA | 0.2
3494399 | DEER PARK | INOR | 1041 | NITRITE | N | 0.2 | MG/L | 1.4999 | 2019-12-12 | AAA | 0.2
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-01-07 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-01-07 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-01-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-01-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2 | MG/L |  | 2015-02-04 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2 | MG/L |  | 2015-02-04 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-02-04 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-02-04 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-02-18 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2 | MG/L |  | 2015-02-18 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2.1 | MG/L |  | 2015-03-03 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-03-03 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-03-18 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-03-18 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-03-31 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-03-31 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2 | MG/L |  | 2015-04-14 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-04-14 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-04-30 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-04-30 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-05-13 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-05-13 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-05-29 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-05-29 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-06-09 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-06-09 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-06-23 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2.1 | MG/L |  | 2015-06-23 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-07-08 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-07-08 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2.1 | MG/L |  | 2015-07-23 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-07-23 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.9 | UG/L | 60.4999 | 2015-07-27 | L2 |  |  |  | 0.8 | ANN. T/H - 2801 DEERFIELD ST. (PHASE 3 EOL) (>500 QUALIFIES FOR R.M. TEST AT 2801 DEERFIELD ST. 1 SITE ONLY @ 7/23/16) R.M. IS ANNUAL FOR >500
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 11.7 | UG/L | 80.4999 | 2015-07-27 | L1 |  |  |  | 0.6 | ANN. T/H - 5221 HAMMOCK POINTE CT. (>500 QUALIFIES FOR R.M. TEST AT 2801 DEERFIELD ST. 1 SITE ONLY @ 7/23/16) R.M. IS ANNUAL FOR >500
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.05 | UG/L | 60.4999 | 2015-07-27 | L1 |  |  |  | 0.6 | ANN. T/H - 5221 HAMMOCK POINTE CT. (>500 QUALIFIES FOR R.M. TEST AT 2801 DEERFIELD ST. 1 SITE ONLY @ 7/23/16) R.M. IS ANNUAL FOR >500
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 13.92 | UG/L | 80.4999 | 2015-07-27 | L2 |  |  |  | 0.8 | ANN. T/H - 2801 DEERFIELD ST. (PHASE 3 EOL) (>500 QUALIFIES FOR R.M. TEST AT 2801 DEERFIELD ST. 1 SITE ONLY @ 7/23/16) R.M. IS ANNUAL FOR >500
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-08-04 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-08-04 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-08-18 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-08-18 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2.2 | MG/L |  | 2015-09-03 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-09-03 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-09-17 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-09-17 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-09-29 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-09-29 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1017 | CHLORIDE | N | 67 | MG/L | 250.4999 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1025 | FLUORIDE | N | 0.25 | MG/L | 2.0499 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1055 | SULFATE | N | 5.8 | MG/L | 250.4999 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1095 | ZINC | N | 0.016 | MG/L | 5.4999 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.9 | LN(10) |  | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 340 | MG/L | 500.4999 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-06 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-06 | AAA |  | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-10-06 | AAA |  | 0.0149 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-10-06 | AAA |  | 2.4999 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-10-06 | AAA |  | 0.0749 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-10-06 | AAA |  | 0.6499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-10-06 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-10-06 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-10-06 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-10-06 | AAA |  | 0.9499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-10-06 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-10-06 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-10-06 | AAA |  | 0.0449 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-10-06 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-10-06 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-10-06 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-10-06 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-10-06 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-10-06 | AAA |  | 0.0449 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-10-06 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-10-06 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-10-06 | AAA |  | 0.0149 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-10-06 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-10-06 | AAA |  |  |  |  | DUE 2021
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-06 | AAA |  | 1.4999 |  |  | DUE 2021
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-10-06 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-10-06 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-10-06 | AAA |  | 1.4999 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-10-06 | AAA |  | 1.4999 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-10-06 | AAA |  | 0.4499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-10-06 | AAA |  | 9.4999 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-10-06 | AAA |  | 6.4999 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-10-06 | AAA |  | 0.6499 |  |  | 3YR 27 OF 29 SOC (RETESTS NEEDED FOR OXAMYL & CARBOFURAN DUE TO ONLY 24 & 0% RECOVERY IN THE MS SMPL LCS OK EM 11/12/15>ABWTR) TOLD ABWTR PN IS NOT RQRD FOR OX & CARBO FOR 2015 IN 1/15/16 EM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1010 | BARIUM | N | 0.0074 | MG/L | 2.4999 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1025 | FLUORIDE | N | 0.25 | MG/L | 4.0499 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1052 | SODIUM | N | 47 | MG/L | 160.4999 | 2015-10-06 | AAA |  |  |  |  | NO MCLS (RADS TSTD) CY MS/MSD 67/68%-SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2 | MG/L |  | 2015-10-13 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2015-10-13 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-10-29 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-10-29 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-11-10 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-11-10 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-11-17 | AAA |  | 2.4999 |  |  | 3YR 2 OF 29 SOC (OX 0% RECOV MS & CARBO 7% RECOV MS LCS OK) THIS IS ALREADY A RETEST OF OX ONLY 24% RECOV MS & CARBO ONLY 0% RECOV MS FROM 10/6/15 (NOT ENT?D)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-11-17 | AAA |  | 0.9499 |  |  | 3YR 2 OF 29 SOC (OX 0% RECOV MS & CARBO 7% RECOV MS LCS OK) THIS IS ALREADY A RETEST OF OX ONLY 24% RECOV MS & CARBO ONLY 0% RECOV MS FROM 10/6/15 (NOT ENT?D)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2 | MG/L |  | 2015-11-24 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-11-24 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7 | LN(10) |  | 2015-12-10 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-12-10 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1044 | ORTHOPHOSPHATE | N | 2 | MG/L |  | 2015-12-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | WQP | 1924 | pH (FIELD) | N | 7.1 | LN(10) |  | 2015-12-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2016-01-26 | AAA |  | 0.9499 |  |  | RETESTS FOR 2015 OX & CARBO (OK ? NO QUALIFIERS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2016-01-26 | AAA |  | 2.4999 |  |  | RETESTS FOR 2015 OX & CARBO (OK ? NO QUALIFIERS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.37 | UG/L | 60.4999 | 2016-07-22 | L2 |  |  |  | 1 | 2801 DEERFIELD ST. (PHASE 3 EOL) Q QUALIFIER
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 9.21 | UG/L | 80.4999 | 2016-07-22 | L2 |  |  |  | 1 | 2801 DEERFIELD ST. (PHASE 3 EOL) Q QUALIFIER
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0.94 | UG/L | 60.4999 | 2016-07-22 | L1 | 0.2 |  | 1 | 1.3 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 4.68 | UG/L | 80.4999 | 2016-07-22 | L1 | 0.82 |  | 1 | 1.3 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-27 | AAA | 0.053 |  |  |  | RCVD 2-10-17 (ABSOLUTE WATER)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | N | 0.26 | MG/L | 10.4999 | 2016-12-27 | AAA | 0.051 |  |  |  | RCVD 2-10-17 (ABSOLUTE WATER)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 88.49 | UG/L | 80.4999 | 2017-07-19 | L2 | 0.14 |  | 2 | 1 | 2801 DEERFIELD ST. (HYPERLINKED) L2 SITE HAS T>80 START QTRLY TESTING BOTH T/H BOTH SITES
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 69.1 | UG/L | 80.4999 | 2017-07-19 | L1 | 0.14 |  | 1 | 1.2 | 5221 HAMMOCK POINT (SITE REVISED ON LAB REPORT AS RQRD) HYPERLINKED - L2 SITE HAS T>80 (START QTRLY TESTING)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.25 | UG/L | 60.4999 | 2017-07-19 | L2 | 0.5 |  | 2 | 1 | 2801 DEERFIELD ST. (HYPERLINKED) L2 SITE HAS T>80 START QTRLY TESTING BOTH T/H BOTH SITES
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 53.1 | UG/L | 60.4999 | 2017-07-19 | L1 | 0.5 |  | 1 | 1.2 | 5221 HAMMOCK POINT (SITE REVISED ON LAB REPORT AS RQRD) HYPERLINKED - L2 SITE HAS T>80 (START QTRLY TESTING)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | N | 0.19 | MG/L | 10.4999 | 2017-11-10 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-11-10 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 103.17 | UG/L | 80.4999 | 2017-12-13 | L1 |  |  |  |  | STILL ON QUARTERLY MONITORING-RESULTS NOT OVER OEL OR LRAA YET. SLB
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 64.35 | UG/L | 60.4999 | 2017-12-13 | L1 |  |  |  |  | STILL ON QUARTERLY MONITORING-RESULTS NOT OVER OEL OR LRAA YET. SLB
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 165.79 | UG/L | 80.4999 | 2017-12-13 | L2 |  |  |  |  | OEL RESULTS ARE 105 AND OVER THE MCL-FACILITY HAS 90 DAYS TO SUBMITT OE REPORT FOR SITE LOCATION 2 2801 DEERFIELD. LRAA IS NOT OVER
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 90.14 | UG/L | 60.4999 | 2017-12-13 | L2 |  |  |  |  | OEL RESULTS ARE 105 AND OVER THE MCL-FACILITY HAS 90 DAYS TO SUBMITT OE REPORT FOR SITE LOCATION 2 2801 DEERFIELD. LRAA IS NOT OVER
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.35 | UG/L | 60.4999 | 2018-02-02 | L2 |  |  |  | 1.02 | 2801 DEERFIELD ST. (PHASE 3 EOL). LRAA FOR TTHMS = 89.375. PWS DID NOT GENERATE VIO. MANUALLY ENTERED 10/19/18. SYSTEM UNDER LFCO AND 3RD Q RESULTS ARE BELOW MCL. JMF
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 103.22 | UG/L | 80.4999 | 2018-02-02 | L2 |  |  |  | 1.02 | 2801 DEERFIELD ST. (PHASE 3 EOL). LRAA FOR TTHMS = 89.375. PWS DID NOT GENERATE VIO. MANUALLY ENTERED 10/19/18. SYSTEM UNDER LFCO AND 3RD Q RESULTS ARE BELOW MCL. JMF
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-21 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | N | 0.15 | MG/L | 10.4999 | 2018-02-21 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 54.39 | UG/L | 60.4999 | 2018-02-21 | L1 |  |  |  | 0.98 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 84.31 | UG/L | 80.4999 | 2018-02-21 | L1 |  |  |  | 0.98 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-23 | AAA | 0.18 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.36 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-23 | AAA | 0.39 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.23 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-23 | AAA | 0.26 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-23 | AAA | 0.12 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.24 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-23 | AAA | 0.12 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-23 | AAA | 0.17 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-23 | AAA | 0.22 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-23 | AAA | 0.17 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-23 | AAA | 0.39 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | N | 0.16 | MG/L | 10.4999 | 2018-05-23 | AAA | 0.051
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-23 | AAA | 0.053
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-05-23 | AAA | 8e-05
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1010 | BARIUM | N | 0.0077 | MG/L | 2.4999 | 2018-05-23 | AAA | 0.00083
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-23 | AAA | 0.00045
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-05-23 | AAA | 0.0016
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-23 | AAA | 0.0048
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1025 | FLUORIDE | N | 0.26 | MG/L | 4.0499 | 2018-05-23 | AAA | 0.075
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-23 | AAA | 0.00024
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-23 | AAA | 5e-05
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-23 | AAA | 0.006
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-23 | AAA | 0.00058
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1052 | SODIUM | N | 30 | MG/L | 160.4999 | 2018-05-23 | AAA | 0.34
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-23 | AAA | 0.00011
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-23 | AAA | 0.0004
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-23 | AAA | 6e-05
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-23 | AAA | 0.028
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1017 | CHLORIDE | N | 40 | MG/L | 250.4999 | 2018-05-23 | AAA | 0.78
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-05-23 | AAA | 0.0032
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1025 | FLUORIDE | N | 0.26 | MG/L | 2.0499 | 2018-05-23 | AAA | 0.075
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-05-23 | AAA | 0.1
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1032 | MANGANESE | N | 0.0022 | MG/L | 0.0549 | 2018-05-23 | AAA | 0.0019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-23 | AAA | 0.0001
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1055 | SULFATE | N | 9.3 | MG/L | 250.4999 | 2018-05-23 | AAA | 0.52
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-05-23 | AAA | 0.033
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1905 | COLOR | N | 15 | COLOR UNITS | 15.4999 | 2018-05-23 | AAA | 5
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2018-05-23 | AAA | 1
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.87 | LN(10) |  | 2018-05-23 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 240 | MG/L | 500.4999 | 2018-05-23 | AAA | 10
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-23 | AAA | 0.04
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-23 | AAA | 0.32 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-23 | AAA | 0.44 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-23 | AAA | 0.46 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 38.76 | UG/L | 80.4999 | 2018-05-23 | L1 |  |  |  | 0.83 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-23 | AAA | 0.26 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-23 | AAA | 0.2 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 138.5 | UG/L | 80.4999 | 2018-05-23 | L2 |  |  |  | 0.76 | 2801 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.57 | UG/L | 60.4999 | 2018-05-23 | L1 |  |  |  | 0.83 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 50.38 | UG/L | 60.4999 | 2018-05-23 | L2 |  |  |  | 0.76 | 2801 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 63.4 | UG/L | 80.4999 | 2018-07-24 | L2 | 0.14 |  | 2 | 0.98 | 2801 DEERFIELD ST. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.69 | UG/L | 60.4999 | 2018-07-24 | L1 | 0.91 |  | 1 | 0.87 | 5221 HAMMOCK POINTE CT. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.03 | UG/L | 60.4999 | 2018-07-24 | L2 | 0.91 |  | 2 | 0.98 | 2801 DEERFIELD ST. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 35.76 | UG/L | 80.4999 | 2018-07-24 | L1 | 0.14 |  | 1 | 0.87 | 5221 HAMMOCK POINTE CT. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 77.55 | UG/L | 60.4999 | 2018-10-24 | L2 |  |  |  | 1.01 | 2950-2801 DEERFIELD ST. (PHASE 3 EOL) / SUBCONTRACT LAB E84589 (HAA5 OEL = 63.3775; LRAA = 48.89. TTHM OEL = 132.48; LRAA = 117.28)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 164 | UG/L | 80.4999 | 2018-10-24 | L2 |  |  |  | 1.01 | 2950-2801 DEERFIELD ST. (PHASE 3 EOL) / SUBCONTRACT LAB E84589 (HAA5 OEL = 63.3775; LRAA = 48.89. TTHM OEL = 132.48; LRAA = 117.28)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 84.75 | UG/L | 60.4999 | 2018-10-24 | L1 |  |  |  | 1.23 | 2950-5221 HAMMOCK POINTE CT. / SUBCONTRACT LAB E84589 (HAA5 LRAA = 47.085 UG/L; TTHM LRAA = 49.205)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 37.99 | UG/L | 80.4999 | 2018-10-24 | L1 |  |  |  | 1.23 | 2950-5221 HAMMOCK POINTE CT. / SUBCONTRACT LAB E84589 (HAA5 LRAA = 47.085 UG/L; TTHM LRAA = 49.205)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.12 | UG/L | 60.4999 | 2019-01-23 | L2 |  |  |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 95.73 | UG/L | 80.4999 | 2019-01-23 | L1 |  |  |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.34 | UG/L | 60.4999 | 2019-01-23 | L1 |  |  |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 80.84 | UG/L | 80.4999 | 2019-01-23 | L2 |  |  |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.16 | UG/L | 60.4999 | 2019-04-22 | L1 |  |  |  | 0.97 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | N | 0.26 | MG/L | 10.4999 | 2019-04-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 178.62 | UG/L | 80.4999 | 2019-04-22 | L1 |  |  |  | 0.97 | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 52.54 | UG/L | 60.4999 | 2019-04-22 | L2 |  |  |  | 0.89 | 2801 DEERFIELD ST. (PHASE 3 EOL) TTHM LRAA = 99.1; H5 = 54.6
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-04-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 88.14 | UG/L | 80.4999 | 2019-04-22 | L2 |  |  |  | 0.89 | 2801 DEERFIELD ST. (PHASE 3 EOL) TTHM LRAA = 99.1; H5 = 54.6
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 81.09 | UG/L | 80.4999 | 2019-07-24 | L2 | 0.39 |  | 2 | 0.74 | 2801 DEERFIELD [TTHM LRAA = 103.5; HAA5 LRAA = 52.105 (<60 MCL)]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41.21 | UG/L | 60.4999 | 2019-07-24 | L2 | 0.91 |  | 2 | 0.74 | 2801 DEERFIELD [TTHM LRAA = 103.5; HAA5 LRAA = 52.105 (<60 MCL)]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44.81 | UG/L | 60.4999 | 2019-07-24 | L1 |  |  | 1 | 0.63 | 5221 HAMMOCK POINTE CT. [LRAA TTHM = 97.65; LRAA HAA5 = 46.52 (<60)] CONTINUE ON QUARTERLY_VP
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 78.26 | UG/L | 80.4999 | 2019-07-24 | L1 |  |  | 1 | 0.63 | 5221 HAMMOCK POINTE CT. [LRAA TTHM = 97.65; LRAA HAA5 = 46.52 (<60)] CONTINUE ON QUARTERLY_VP
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 4.29 | UG/L | 80.4999 | 2019-10-23 | L2 | 0.39 |  | 1 | 0.81 | 2801 DEERFIELD ST
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.8 | UG/L | 60.4999 | 2019-10-23 | L1 | 0.91 |  | 2 | 0.9 | 5221 HAMMOCK POINTE LRAA TTHM=41.6225 HAA5=23.58
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | D | 2.85 | UG/L | 80.4999 | 2019-10-23 | L1 | 0.39 |  | 2 | 0.9 | 5221 HAMMOCK POINTE LRAA TTHM=41.6225 HAA5=23.58
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.5 | UG/L | 60.4999 | 2019-10-23 | L2 | 0.91 |  | 1 | 0.81 | 2801 DEERFIELD ST
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | AAA
3494416 | HIDDEN GLEN | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-03-25 | AAA |  | 0.4499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-03-25 | AAA |  | 9.4999 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-03-25 | AAA |  | 6.4999 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-03-25 | AAA |  | 2.4999 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-03-25 | AAA |  | 0.0749 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-03-25 | AAA |  | 0.9499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOCS (OXAMYL J-QUALIFIED RESULT ACCEPTABLE)
3494416 | HIDDEN GLEN | SEC | 1017 | CHLORIDE | N | 8.3 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1022 | COPPER | N | 0.0026 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1025 | FLUORIDE | N | 0.078 | MG/L | 2.0499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1028 | IRON | N | 0.1 | MG/L | 0.3499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | N | 0.092 | MG/L | 10.4999 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1010 | BARIUM | N | 0.011 | MG/L | 2.4999 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1025 | FLUORIDE | N | 0.078 | MG/L | 4.0499 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | SEC | 1032 | MANGANESE | N | 0.0034 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.8 | LN(10) |  | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 159 | MG/L | 500.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | INOR | 1052 | SODIUM | N | 6.3 | MG/L | 160.4999 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-27 | AAA |  |  |  |  | CYANIDE-J QUAL MS 64% RECOVERY (LCS PASSED) - SUFFICENT RECOVERY FOR ACCEPTANCE-WOULD NOT EXCEED MCL AT 100% RECOVERY. NO MCLS. 15: VOCS (SOCS TSTD 3/15) RADS 2018 (DEREK CROUCH TOHO)
3494416 | HIDDEN GLEN | INOR | 1094 | ASBESTOS | S | 0 | MF/L | 7.4999 | 2015-07-27 | AAA |  |  |  |  | POE/D (ASB. REPORTED WITH INORG-NOT FOR COMPLIANCE PURPOSES-METHOD EPA600/R-94/134 E83079 SUBCONTRACTED TO E86795)
3494416 | HIDDEN GLEN | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494416 | HIDDEN GLEN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.3 | UG/L | 60.4999 | 2015-07-28 | L1 |  |  |  | 0.5 | 6624 IVY MIST (QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3494416 | HIDDEN GLEN | DBP | 2950 | TOTAL THMS | D | 23.9 | UG/L | 80.4999 | 2015-07-28 | L1 |  |  |  | 0.5 | 6624 IVY MIST (QUALIFIES FOR R.M. - NEXT T/H DUE @ 7/23/18 TRIENNIAL) <500 (T<40 H<30)
3494416 | HIDDEN GLEN | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | AAA
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | AAA
3494416 | HIDDEN GLEN | DBP | 2950 | TOTAL THMS | D | 26.6 | UG/L | 80.4999 | 2016-07-26 | L1 |  |  |  | 1.4 | 6624 IVY MIST
3494416 | HIDDEN GLEN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.4 | UG/L | 60.4999 | 2016-07-26 | L1 |  |  |  | 1.4 | 6624 IVY MIST
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | AAA
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | AAA
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | AAA
3494416 | HIDDEN GLEN | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.9499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-03-27 | AAA |  | 0.6499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-03-27 | AAA |  | 0.0749 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 2.4999 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-03-27 | AAA |  | 0.6499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-27 | AAA |  | 6.4999 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-03-27 | AAA |  | 9.4999 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-27 | AAA |  | 0.4499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 1.4999 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 1.4999 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.0149 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-27 | AAA |  | 0.0149 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-03-27 | AAA |  | 0.1499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.0449 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2063 | DIOXIN (NG/L) | N | 0 | NG/L | 0.0349 | 2018-03-27 | AAA |  | 0.0055 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-03-27 | AAA |  | 0.0449 |  |  | ACCEPTED J QUALIFERS FOR CARBOFURAN ENDRIN METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | INOR | 1005 | ARSENIC | N | 0.0006 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1025 | FLUORIDE | N | 0.087 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1052 | SODIUM | N | 6.4 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1094 | ASBESTOS | N | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1017 | CHLORIDE | N | 8.6 | MG/L | 250.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1022 | COPPER | N | 0.0034 | MG/L | 1.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1025 | FLUORIDE | N | 0.087 | MG/L | 2.0499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1028 | IRON | N | 0.089 | MG/L | 0.3499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1032 | MANGANESE | N | 0.0036 | MG/L | 0.0549 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1095 | ZINC | N | 0.095 | MG/L | 5.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1920 | ODOR THRESHOLD | N | 2 |  | 3.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.9 | LN(10) |  | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 162 | MG/L | 500.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.1 | UG/L | 60.4999 | 2018-07-24 | L1 | 0.48 |  | 1 | 1.5 | T<60 H<45 CAN STAY ON REDUCED_JMF
3494416 | HIDDEN GLEN | DBP | 2950 | TOTAL THMS | D | 55.9 | UG/L | 80.4999 | 2018-07-24 | L1 | 0.32 |  | 1 | 1.5 | T<60 H<45 CAN STAY ON REDUCED_JMF
3494416 | HIDDEN GLEN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA |  |  |  |  | DUE 2024
3494416 | HIDDEN GLEN | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999 |  |  | DUE 2024
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | N | 2.1 | UG/L | 249.9999 | 2015-01-28 | AAA |  | 1.4999 |  |  | 2AM/DAL 1Q'15 (3AM/DAL 1Q'16 2AM/DBCP DUE 2Q'15>>PUT IN 2015 MONIT SCHEDULE) EM REMINDER ON DBCP SENT 2/19/15 TO D. CROUCH. BB (THIS DAL IN OC)
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-03-25 | AAA |  | 0.0749 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-03-25 | AAA |  | 6.4999 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-03-25 | AAA |  | 9.4999 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-03-25 | AAA |  | 0.4499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | N | 2.8 | UG/L | 249.9999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR 27 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-04-20 | AAA |  | 0.9499 |  |  | 3YR 2 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-04-20 | AAA |  | 2.4999 |  |  | 3YR 2 OF 29 SOCS
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-04-27 | AAA |  | 0.5499 |  |  | 2AM/XY (3AM/XY DUE 2Q'16) PUT IN 2016 MONIT. SCHEDULE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-04-27 | AAA |  | 0.0249 |  |  | 2AM/DBCP (3AM/DBCP DUE 2Q'16 3AM/DAL 1Q'16) EM 1/14/16 REMINDER FOR 3AM/DBCP & 3AM/DAL
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1094 | ASBESTOS | S | 0 | MF/L | 7.4999 | 2015-07-27 | AAA |  |  |  |  | POE/D (ASB. REPORTED WITH INORG-NOT FOR COMPLIANCE PURPOSES-METHOD EPA600/R-94/134 E83079 SUBCONTRACTED TO E86795)
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1052 | SODIUM | N | 11.8 | MG/L | 160.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1025 | FLUORIDE | N | 0.68 | MG/L | 4.0499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1010 | BARIUM | N | 0.017 | MG/L | 2.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | N | 0.029 | MG/L | 10.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 165 | MG/L | 500.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.8 | LN(10) |  | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1055 | SULFATE | N | 8.5 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1025 | FLUORIDE | N | 0.68 | MG/L | 2.0499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1017 | CHLORIDE | N | 13.5 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1022 | COPPER | N | 0.0039 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (3AM/XY DUE 2Q'16)>>>PUT THIS IN THE 2016 MONIT. SCHEDULE>>EM 1/14/16 TO D. CROUCH AS REMINDER FOR 3AM/XY
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41.8 | UG/L | 60.4999 | 2015-09-03 | L2 |  |  |  | 0.7 | ANN. T/H - 3645 LATE MORNING CIRCLE (REMAIN ON ANNUAL T/H - NEXT T/H TESTS DUE 1ST WEEK 9/16 AT BOTH SITES) H>30 (POP. 3 070)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 38.9 | UG/L | 80.4999 | 2015-09-03 | L2 |  |  |  | 0.7 | ANN. T/H - 3645 LATE MORNING CIRCLE (REMAIN ON ANNUAL T/H - NEXT T/H TESTS DUE 1ST WEEK 9/16 AT BOTH SITES) H>30 (POP. 3 070)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 40.4 | UG/L | 80.4999 | 2015-09-03 | L1 |  |  |  | 0.7 | ANN. T/H - 3854 WOOD THRUSH DR. (REMAIN ON ANNUAL T/H - NEXT T/H TESTS DUE 1ST WEEK 9/16 AT BOTH SITES) H>30 (POP. 3 070)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.1 | UG/L | 60.4999 | 2015-09-03 | L1 |  |  |  | 0.7 | ANN. T/H - 3854 WOOD THRUSH DR. (REMAIN ON ANNUAL T/H - NEXT T/H TESTS DUE 1ST WEEK 9/16 AT BOTH SITES) H>30 (POP. 3 070)
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-09-29 | AAA |  |  |  |  | RADS DUE 2021
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-09-29 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | N | 1.4 | UG/L | 249.9999 | 2016-01-29 | AAA |  | 1.4999 |  |  | 3AM/DAL 1Q'16 (4AM/DAL 1Q'17>PUT THIS IN 2017 MONIT. SCHEDULE) KEEP ON AM DUE TO DETECTIONS
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2016-04-28 | AAA |  | 0.0249
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-04-28 | AAA |  | 0.5499 |  |  | 3AM/XY (8/9/16 EM TO D. CROUCH TO STOP AM/XYLENES ? LAST 3 YEARS -0-)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.8 | UG/L | 60.4999 | 2016-09-01 | L2 |  |  |  | 0.8 | 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 71.7 | UG/L | 80.4999 | 2016-09-01 | L2 |  |  |  | 0.8 | 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 76.7 | UG/L | 80.4999 | 2016-09-01 | L1 |  |  |  | 1 | 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.8 | UG/L | 60.4999 | 2016-09-01 | L1 |  |  |  | 1 | 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | N | 1.9 | UG/L | 249.9999 | 2017-03-29 | AAA |  | 1.4999
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.5 | UG/L | 60.4999 | 2017-09-07 | L2 | 0.48 |  | 2 | 1 | ANN. T/H-3645 LATE MORNING CIRCLE (HYPERLINKED TO SB & JF 10/26/17 - BB)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 68.4 | UG/L | 80.4999 | 2017-09-07 | L2 | 0.32 |  | 2 | 1 | ANN. T/H-3645 LATE MORNING CIRCLE (HYPERLINKED TO SB & JF 10/26/17 - BB)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 62.2 | UG/L | 80.4999 | 2017-09-07 | L1 | 0.32 |  | 1 | 1.3 | ANN. T/H-3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.7 | UG/L | 60.4999 | 2017-09-07 | L1 | 0.48 |  | 1 | 1.3 | ANN. T/H-3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | N | 1.4 | UG/L | 249.9999 | 2018-03-23 | AAA |  | 1.4999
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-03-27 | AAA |  | 0.6499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-03-27 | AAA |  | 0.0749 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 2.4999 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-03-27 | AAA |  | 0.6499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-27 | AAA |  | 6.4999 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-03-27 | AAA |  | 9.4999 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-27 | AAA |  | 0.4499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | N | 2.3 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 1.4999 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 1.4999 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.0149 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-27 | AAA |  | 0.0149 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-03-27 | AAA |  | 0.1499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.0449 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.2499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-27 | AAA |  | 0.1499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-03-27 | AAA |  | 0.0449 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2063 | DIOXIN (NG/L) | N | 0 | NG/L | 0.0349 | 2018-03-27 | AAA |  | 0.0055 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.9499 |  |  | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN METHOXYCHLOR SIMAZINE HECACHLOROCYCLOPENTADINENE AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1005 | ARSENIC | N | 0.0006 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1010 | BARIUM | N | 0.017 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1025 | FLUORIDE | N | 0.44 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1052 | SODIUM | N | 12.2 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1094 | ASBESTOS | N | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1002 | ALUMINUM | N | 0.0064 | MG/L | 0.2499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1017 | CHLORIDE | N | 13.7 | MG/L | 250.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1022 | COPPER | N | 0.0011 | MG/L | 1.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1025 | FLUORIDE | N | 0.44 | MG/L | 2.0499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1028 | IRON | N | 0.021 | MG/L | 0.3499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1055 | SULFATE | N | 10.3 | MG/L | 250.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1920 | ODOR THRESHOLD | N | 3 |  | 3.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 157 | MG/L | 500.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 58.5 | UG/L | 80.4999 | 2018-09-07 | L2 |  |  | 1 | 1.2 | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 57.7 | UG/L | 80.4999 | 2018-09-07 | L1 |  |  | 2 | 1.1 | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.4 | UG/L | 60.4999 | 2018-09-07 | L1 |  |  | 2 | 1.1 | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.3 | UG/L | 60.4999 | 2018-09-07 | L2 |  |  | 1 | 1.2 | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | N | 2.5 | UG/L | 249.9999 | 2019-06-21 | AAA |  | 1.4999 |  |  | MAKE-UP FOR MISSING 1ST Q ANNUAL DALAPON. CONTINUE SAMPLING ANNUALLY DURING THE 1ST Q_JMF
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 66.5 | UG/L | 60.4999 | 2019-09-05 | L2 | 0.9 |  | 1 | 0.4 | 3645 LATE MORNING CIRCLE; QUARTERLY MONITORING TRIGGERED 09/05/19 - Q MONITORING SHOULD START IN DECEMBER_JB
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 111 | UG/L | 80.4999 | 2019-09-05 | L2 | 0.32 |  | 1 | 0.4 | 3645 LATE MORNING CIRCLE; QUARTERLY MONITORING TRIGGERED 09/05/19 - Q MONITORING SHOULD START IN DECEMBER_JB
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.2 | UG/L | 60.4999 | 2019-09-05 | L1 | 0.9 |  | 2 | 1.1 | 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 68.7 | UG/L | 80.4999 | 2019-09-05 | L1 | 0.32 |  | 2 | 1.1 | 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.1 | UG/L | 60.4999 | 2019-12-23 | L1 | 0.9 |  | 2 | 0.8 | 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 55.2 | UG/L | 80.4999 | 2019-12-23 | L2 | 0.32 |  | 1 | 0.9 | 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.9 | UG/L | 60.4999 | 2019-12-23 | L2 | 0.9 |  | 1 | 0.9 | 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | D | 63.4 | UG/L | 80.4999 | 2019-12-23 | L1 | 0.32 |  | 2 | 0.8 | 3854 WOOD THRUSH DR.
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | AAA
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | N | 0.077 | MG/L | 10.4999 | 2015-01-28 | AAA
3494427 | HARMONY CDD | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-03-25 | AAA |  | 0.0449 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-03-25 | AAA |  | 0.9499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-03-25 | AAA |  | 0.2499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-03-25 | AAA |  | 0.0749 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-03-25 | AAA |  | 2.4999 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-03-25 | AAA |  | 0.6499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-03-25 | AAA |  | 6.4999 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-03-25 | AAA |  | 9.4999 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-03-25 | AAA |  | 0.4499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-03-25 | AAA |  | 1.4999 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-03-25 | AAA |  | 0.1499 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-03-25 | AAA |  | 0.0149 |  |  | 3YR SOC
3494427 | HARMONY CDD | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-03-25 | AAA |  | 0.0249 |  |  | 3YR SOC
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.6 | UG/L | 60.4999 | 2015-07-24 | L1 |  |  |  | 1.2 | 3351 SCHOOL HOUSE RD. (HAA5S 73.2 UG/L 7/15 1 SITE - BEGIN QM/T+H UFN @ BOTH SITES) 9/10/15 COVER PAGE W/RSLTS ACKNOWLEDGES QM/T+H & EM 9/10/15>AMBER TOHO. REVISED STG2 PLAN RCVD (IN OC).
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 6.89 | UG/L | 80.4999 | 2015-07-24 | L1 |  |  |  | 1.2 | 3351 SCHOOL HOUSE RD. (HAA5S 73.2 UG/L 7/15 1 SITE - BEGIN QM/T+H UFN @ BOTH SITES) 9/10/15 COVER PAGE W/RSLTS ACKNOWLEDGES QM/T+H & EM 9/10/15>AMBER TOHO. REVISED STG2 PLAN RCVD (IN OC).
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 5.24 | UG/L | 80.4999 | 2015-07-24 | L2 |  |  |  | 2.4 | 3315 BRACKENFERN DR. (HAA5S 73.2 UG/L 7/15 1 SITE - BEGIN QM/T+H UFN @ BOTH SITES) 9/10/15 COVER PAGE W/RSLTS ACKNOWLEDGES QM/T+H & EM 9/10/15>AMBER TOHO. REVISED STG2 PLAN RCVD (IN OC).
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 73.2 | UG/L | 60.4999 | 2015-07-24 | L2 |  |  |  | 2.4 | 3315 BRACKENFERN DR. (HAA5S 73.2 UG/L 7/15 1 SITE - BEGIN QM/T+H UFN @ BOTH SITES) 9/10/15 COVER PAGE W/RSLTS ACKNOWLEDGES QM/T+H & EM 9/10/15>AMBER TOHO. REVISED STG2 PLAN RCVD (IN OC).
3494427 | HARMONY CDD | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1052 | SODIUM | N | 73.7 | MG/L | 160.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1025 | FLUORIDE | N | 0.22 | MG/L | 4.0499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1020 | CHROMIUM | N | 0.003 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1010 | BARIUM | N | 0.011 | MG/L | 2.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | N | 0.035 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | N | 0.18 | MG/L | 10.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 446 | MG/L | 500.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.1 | LN(10) |  | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1055 | SULFATE | N | 19.5 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1028 | IRON | N | 0.085 | MG/L | 0.3499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1025 | FLUORIDE | N | 0.22 | MG/L | 2.0499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1022 | COPPER | N | 0.0026 | MG/L | 1.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1017 | CHLORIDE | N | 121 | MG/L | 250.4999 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | SEC | 1002 | ALUMINUM | N | 0.0082 | MG/L | 0.2499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS
3494427 | HARMONY CDD | INOR | 1094 | ASBESTOS | S | 0 | MF/L | 7.4999 | 2015-07-27 | AAA |  |  |  |  | POE/D (ASB. REPORTED WITH INORG-NOT FOR COMPLIANCE PURPOSES-METHOD EPA600/R-94/134 E83079 SUBCONTRACTED TO E86795)
3494427 | HARMONY CDD | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-07-27 | AAA |  |  |  |  | NO MCLS-15: RADS VOCS (SOCS TSTD 3/15) DEREK CROUCH TOHO
3494427 | HARMONY CDD | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-26 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3494427 | HARMONY CDD | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-09-29 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3494427 | HARMONY CDD | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-09-29 | AAA |  |  |  |  | RADS DUE 2021
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.5 | UG/L | 60.4999 | 2015-10-23 | L2 |  |  |  | 2.2 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 18.5 | UG/L | 80.4999 | 2015-10-23 | L2 |  |  |  | 2.2 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.4 | UG/L | 60.4999 | 2015-10-23 | L1 |  |  |  | 0.5 | 3351 SCHOOL HOUSE RD. (AFT. 2 QTRS NOT OVER MCL FOR HAA5 FOR EITHER SITE)
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 16.9 | UG/L | 80.4999 | 2015-10-23 | L1 |  |  |  | 0.5 | 3351 SCHOOL HOUSE RD. (AFT. 2 QTRS NOT OVER MCL FOR HAA5 FOR EITHER SITE)
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 12.9 | UG/L | 80.4999 | 2016-01-27 | L1 |  |  |  | 2.6 | 3351 SCHOOL HOUSE RD. (SITE REVISION RCVD FOR 3351 SCHOOL HOUSE RD. FOR 4/16 T/H - SITE ADDRESS MATCHES C OF C & NOW THE PAGE 1 IS CORRECTED) ORIG & REVISION IN OCULUS
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.4 | UG/L | 60.4999 | 2016-01-27 | L2 |  |  |  | 2.8 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 9 | UG/L | 80.4999 | 2016-01-27 | L2 |  |  |  | 2.8 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.1 | UG/L | 60.4999 | 2016-01-27 | L1 |  |  |  | 2.6 | 3351 SCHOOL HOUSE RD. (SITE REVISION RCVD FOR 3351 SCHOOL HOUSE RD. FOR 4/16 T/H - SITE ADDRESS MATCHES C OF C & NOW THE PAGE 1 IS CORRECTED) ORIG & REVISION IN OCULUS
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | N | 0.1 | MG/L | 10.4999 | 2016-02-23 | AAA
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | AAA
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 4.2 | UG/L | 80.4999 | 2016-04-28 | L2 |  |  |  | 3.6 | 3315 BRACKENFERN DR. (NO LRAA OR OE EXCEEDANCES MAY GO TO ROUTINE TESTING 7-9/16 AS LONG AS SITE REVISION RCVD FOR SCHOOL HOUSE SITE) 4/16 T/H SITE REVISION RCVD 8/17/16
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 4.4 | UG/L | 80.4999 | 2016-04-28 | L1 |  |  |  | 2.7 | 3351 SCHOOL HOUSE RD. (NO LRAA OR OE EXCEEDANCES MAY GO TO ROUTINE TESTING 7-9/16 AS LONG AS SITE REVISION RCVD FOR SCHOOL HOUSE SITE) 4/16 T/H SITE REVISION RCVD 8/17/16
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.3 | UG/L | 60.4999 | 2016-04-28 | L1 |  |  |  | 2.7 | 3351 SCHOOL HOUSE RD. (NO LRAA OR OE EXCEEDANCES MAY GO TO ROUTINE TESTING 7-9/16 AS LONG AS SITE REVISION RCVD FOR SCHOOL HOUSE SITE) 4/16 T/H SITE REVISION RCVD 8/17/16
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.1 | UG/L | 60.4999 | 2016-04-28 | L2 |  |  |  | 3.6 | 3315 BRACKENFERN DR. (NO LRAA OR OE EXCEEDANCES MAY GO TO ROUTINE TESTING 7-9/16 AS LONG AS SITE REVISION RCVD FOR SCHOOL HOUSE SITE) 4/16 T/H SITE REVISION RCVD 8/17/16
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 8 | UG/L | 80.4999 | 2016-07-27 | L1 |  |  |  | 2.7 | 3351 SCHOOL HOUSE RD.
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.9 | UG/L | 60.4999 | 2016-07-27 | L2 |  |  |  | 2.7 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 4.6 | UG/L | 80.4999 | 2016-07-27 | L2 |  |  |  | 2.7 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9 | UG/L | 60.4999 | 2016-07-27 | L1 |  |  |  | 2.7 | 3351 SCHOOL HOUSE RD.
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.4 | UG/L | 60.4999 | 2016-10-24 | L1 |  |  |  | 0.8 | 3351 SCHOOL HOUSE RD.
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.6 | UG/L | 60.4999 | 2016-10-24 | L2 |  |  |  | 1.8 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 18.3 | UG/L | 80.4999 | 2016-10-24 | L2 |  |  |  | 1.8 | 3315 BRACKENFERN DR.
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 22.1 | UG/L | 80.4999 | 2016-10-24 | L1 |  |  |  | 0.8 | 3351 SCHOOL HOUSE RD.
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | N | 0.073 | MG/L | 10.4999 | 2017-02-27 | AAA |  |  |  |  | NITRATE HAS J DATA QUALIFIER
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | AAA |  |  |  |  | NITRATE HAS J DATA QUALIFIER
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 12.2 | UG/L | 80.4999 | 2017-07-28 | L1 |  |  |  | 0.9 | 3351 SCHOOL HOUSE RD.
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.6 | UG/L | 60.4999 | 2017-07-28 | L1 |  |  |  | 0.9 | 3351 SCHOOL HOUSE RD.
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | N | 0.079 | MG/L | 10.4999 | 2018-02-28 | AAA
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3494427 | HARMONY CDD | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-26 | AAA |  | 0.2499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-03-26 | AAA |  | 0.9499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-03-26 | AAA |  | 0.0749 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-03-26 | AAA |  | 9.4999 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-03-26 | AAA |  | 0.1499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-03-26 | AAA |  | 0.2499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-26 | AAA |  | 0.0149 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-03-26 | AAA |  | 0.1499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-26 | AAA |  | 0.0449 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-03-26 | AAA |  | 0.1499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-26 | AAA |  | 0.1499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-03-26 | AAA |  | 0.0449 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2063 | DIOXIN (NG/L) | N | 0 | NG/L | 0.0349 | 2018-03-26 | AAA |  | 0.0055 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-03-26 | AAA |  | 0.2499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-03-26 | AAA |  | 0.1499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-03-26 | AAA |  | 0.1499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-26 | AAA |  | 0.2499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-03-26 | AAA |  | 0.0149 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-03-26 | AAA |  | 1.4999 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 1.4999 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-26 | AAA |  | 0.4499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-26 | AAA |  | 6.4999 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-03-26 | AAA |  | 0.6499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 2.4999 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-03-26 | AAA |  | 0.6499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-26 | AAA |  | 0.1499 |  |  | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1025 | FLUORIDE | N | 0.25 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1052 | SODIUM | N | 61.4 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1094 | ASBESTOS | N | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1017 | CHLORIDE | N | 99.4 | MG/L | 250.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1025 | FLUORIDE | N | 0.25 | MG/L | 2.0499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1028 | IRON | N | 0.076 | MG/L | 0.3499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1055 | SULFATE | N | 15.4 | MG/L | 250.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1920 | ODOR THRESHOLD | N | 3 |  | 3.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.2 | LN(10) |  | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 392 | MG/L | 500.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1010 | BARIUM | N | 0.0088 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1005 | ARSENIC | N | 0.001 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | N | 0.079 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.5 | UG/L | 60.4999 | 2018-07-23 | L1 | 0.48 |  | 1 | 2.3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 4.5 | UG/L | 80.4999 | 2018-07-23 | L1 | 0.32 |  | 1 | 2.3
3494427 | HARMONY CDD | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA |  |  |  |  | DUE 2024
3494427 | HARMONY CDD | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999 |  |  | DUE 2024
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | N | 0.028 | MG/L | 10.4999 | 2019-02-28 | AAA
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.1 | UG/L | 60.4999 | 2019-07-30 | L1 |  |  | 1 | 1 | 3351 SCHOOL HOUSE RD.
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | D | 14.4 | UG/L | 80.4999 | 2019-07-30 | L1 |  |  | 1 | 1 | 3351 SCHOOL HOUSE RD.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.34 | UG/L | 60.4999 | 2015-07-08 | L1 |  |  |  | 1.39 | (SNT 9/30 EM TO GRAHAM)ON ANN. R.M.@ 1 SITE-CELEBRATION H.S.(REMAIN ON R.M.-NEXT TEST DUE @ 7/10/16 AT CELEBRATION H.S.)EM 6/7/16 RMNDR FOR T/H DUE TO BE SMPLD 7/10/16 TO GRAHAM GARY SEVERN TRENT. BB
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | D | 18.6 | UG/L | 80.4999 | 2015-07-08 | L1 |  |  |  | 1.39 | (SNT 9/30 EM TO GRAHAM)ON ANN. R.M.@ 1 SITE-CELEBRATION H.S.(REMAIN ON R.M.-NEXT TEST DUE @ 7/10/16 AT CELEBRATION H.S.)EM 6/7/16 RMNDR FOR T/H DUE TO BE SMPLD 7/10/16 TO GRAHAM GARY SEVERN TRENT. BB
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | D | 13.7 | UG/L | 80.4999 | 2016-10-27 | L1 |  |  |  | 1.3 | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.1 | UG/L | 60.4999 | 2016-10-27 | L1 |  |  |  | 1.3 | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.78 | UG/L | 60.4999 | 2017-07-06 | L1 |  |  |  | 1.25 | (7/18 DBPS HLKD - NO FORMAT PAGES RCVD - ONLY BACKGROUND PAGES)
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | D | 28.7 | UG/L | 80.4999 | 2017-07-06 | L1 |  |  |  | 1.25 | (7/18 DBPS HLKD - NO FORMAT PAGES RCVD - ONLY BACKGROUND PAGES)
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | D | 14.8 | UG/L | 80.4999 | 2018-07-11 | L1 |  |  |  |  | 2950-CELEBRATION H.S. L.S. / SUBCONTRACT LAB E87610
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 1.6 | UG/L | 60.4999 | 2018-07-11 | L1 |  |  |  |  | 2950-CELEBRATION H.S. L.S. / SUBCONTRACT LAB E87610
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2019-09-06 | L1 |  |  |  | 1.3 | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | D | 17.19 | UG/L | 80.4999 | 2019-09-06 | L1 |  |  |  | 1.3 | CELEBRATION H.S. L.S.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-01-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-01-06 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 2.1 | MG/L |  | 2015-01-08 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-01-08 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.9 | MG/L |  | 2015-01-21 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-01-21 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-01-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-01-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 1.4 | MG/L | 10.4999 | 2015-01-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2015-02-05 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-02-05 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-02-06 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-02-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2015-02-19 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-02-19 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.1 | UG/L | 60.4999 | 2015-02-23 | L1 |  |  |  | 1.5 | 4738 ASHURST STREET KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 36.1 | UG/L | 80.4999 | 2015-02-23 | L1 |  |  |  | 1.5 | 4738 ASHURST STREET KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14 | UG/L | 60.4999 | 2015-02-23 | L3 |  |  |  | 1.3 | 2942 EVANS DR. KISSIMMEE(SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 28.5 | UG/L | 80.4999 | 2015-02-23 | L3 |  |  |  | 1.3 | 2942 EVANS DR. KISSIMMEE(SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.7 | UG/L | 60.4999 | 2015-02-23 | L4 |  |  |  | 1.6 | 5508 WILLOW BEND TR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 37.9 | UG/L | 80.4999 | 2015-02-23 | L2 |  |  |  | 1.5 | 3543 BEAU CHENE DR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 35.7 | UG/L | 80.4999 | 2015-02-23 | L4 |  |  |  | 1.6 | 5508 WILLOW BEND TR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18 | UG/L | 60.4999 | 2015-02-23 | L2 |  |  |  | 1.5 | 3543 BEAU CHENE DR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) LRAAS & OE VALUES ALL < MCLS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-02-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-02-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-03-05 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 7.8 | MG/L |  | 2015-03-05 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-03-06 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-03-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-03-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-03-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2015-03-27 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-03-27 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-04-06 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-04-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-04-09 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.7 | MG/L |  | 2015-04-09 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.7 | MG/L |  | 2015-04-23 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-04-23 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-04-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-04-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-05-06 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-05-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2015-05-07 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-05-07 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 7.9 | MG/L |  | 2015-05-21 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-05-21 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-05-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-05-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.1 | UG/L | 60.4999 | 2015-05-26 | L4 |  |  |  | 1.5 | 5508 WILLOW BEND TR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) >>>10/29/15 EW HAS 8/15 T/H FOR PROCESSING
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 64.1 | UG/L | 80.4999 | 2015-05-26 | L4 |  |  |  | 1.5 | 5508 WILLOW BEND TR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.) >>>10/29/15 EW HAS 8/15 T/H FOR PROCESSING
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 45.5 | UG/L | 80.4999 | 2015-05-26 | L3 |  |  |  | 2.1 | 2942 EVANS DR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.5 | UG/L | 60.4999 | 2015-05-26 | L3 |  |  |  | 2.1 | 2942 EVANS DR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 66.3 | UG/L | 80.4999 | 2015-05-26 | L1 |  |  |  | 1.5 | 4738 ASHURST STREET KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.8 | UG/L | 60.4999 | 2015-05-26 | L1 |  |  |  | 1.5 | 4738 ASHURST STREET KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 67.2 | UG/L | 80.4999 | 2015-05-26 | L2 |  |  |  | 1.3 | 3543 BEAU CHENE DR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.3 | UG/L | 60.4999 | 2015-05-26 | L2 |  |  |  | 1.3 | 3543 BEAU CHENE DR. KISSIMMEE (SYSTEM DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-06-06 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-06-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 2.1 | MG/L |  | 2015-06-11 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-06-11 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-06-23 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2015-06-23 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-06-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-06-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-07-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-07-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-07-17 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2015-07-17 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-07-21 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-07-21 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-07-31 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2015-07-31 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2015-08-05 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-08-05 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-08-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-08-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2015-08-20 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-08-20 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-08-21 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-08-21 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 58.6 | UG/L | 80.4999 | 2015-08-27 | L2 |  |  |  | 0.7 | 3543 BEAU CHENE DR. KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 47.6 | UG/L | 80.4999 | 2015-08-27 | L1 |  |  |  | 1.2 | 4738 ASHURST STREET KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.7 | UG/L | 60.4999 | 2015-08-27 | L3 |  |  |  | 1.8 | 2942 EVANS DR. KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 31.2 | UG/L | 80.4999 | 2015-08-27 | L3 |  |  |  | 1.8 | 2942 EVANS DR. KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.5 | UG/L | 60.4999 | 2015-08-27 | L2 |  |  |  | 0.7 | 3543 BEAU CHENE DR. KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 49.7 | UG/L | 80.4999 | 2015-08-27 | L4 |  |  |  | 1 | (1/26/16 EW HAS 11/15 DBPS WITH DBF BY EM) 5508 WILLOW BEND TR. KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.2 | UG/L | 60.4999 | 2015-08-27 | L4 |  |  |  | 1 | (1/26/16 EW HAS 11/15 DBPS WITH DBF BY EM) 5508 WILLOW BEND TR. KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.8 | UG/L | 60.4999 | 2015-08-27 | L1 |  |  |  | 1.2 | 4738 ASHURST STREET KISSIMMEE (9/15 DBF WITH RSLTS ALL LRAA/T>40 H LOW) SYS. DOES NOT QUALIFY FOR R.M. NO MCL VIOLS NO OE EXCEEDANCES
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-09-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-09-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-09-16 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2015-09-16 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-09-21 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-09-21 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-09-24 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 2.4 | MG/L |  | 2015-09-24 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2015-10-06 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-06 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-10-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-10-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.7 | MG/L |  | 2015-10-21 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-10-21 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-21 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-21 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-11-04 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2015-11-04 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-11-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-11-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-11-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-11-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2015-11-25 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.5 | UG/L | 60.4999 | 2015-11-25 | L1 |  |  |  | 1.4 | 4738 ASHURST STREET KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-11-25 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 49.5 | UG/L | 80.4999 | 2015-11-25 | L2 |  |  |  | 1.2 | 3543 BEAU CHENE DR. KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27 | UG/L | 60.4999 | 2015-11-25 | L2 |  |  |  | 1.2 | 3543 BEAU CHENE DR. KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 48.7 | UG/L | 80.4999 | 2015-11-25 | L4 |  |  |  | 1.5 | 5508 WILLOW BEND TR. KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 50.8 | UG/L | 80.4999 | 2015-11-25 | L1 |  |  |  | 1.4 | 4738 ASHURST STREET KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.5 | UG/L | 60.4999 | 2015-11-25 | L3 |  |  |  | 1.6 | 2942 EVANS DR. KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 32.6 | UG/L | 80.4999 | 2015-11-25 | L3 |  |  |  | 1.6 | 2942 EVANS DR. KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.9 | UG/L | 60.4999 | 2015-11-25 | L4 |  |  |  | 1.5 | 5508 WILLOW BEND TR. KISSIMMEE (DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-12-03 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-12-03 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-12-09 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-12-09 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-12-23 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2015-12-23 | WTP1 |  |  |  |  | P04
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-12-28 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2015-12-28 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-01-05 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-01-05 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-01-07 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.7 | MG/L |  | 2016-01-07 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2016-01-18 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-01-18 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-01-26 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-01-26 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-02-02 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2016-02-02 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-02-04 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-02-13 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2016-02-18 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-02-18 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 1.7 | MG/L | 10.4999 | 2016-02-23 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-23 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-23 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-02-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 54 | UG/L | 80.4999 | 2016-02-26 | L4 |  |  |  | 1.3 | 5508 WILLOW BEND TR. KISSIMMEE (8/17 EW HAS 2ND QTR DBPS W/DB REPORT FOR ENTRY BY EM ALREADY IN OCULUS-BB)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.8 | UG/L | 60.4999 | 2016-02-26 | L4 |  |  |  | 1.3 | 5508 WILLOW BEND TR. KISSIMMEE (8/17 EW HAS 2ND QTR DBPS W/DB REPORT FOR ENTRY BY EM ALREADY IN OCULUS-BB)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 34.3 | UG/L | 80.4999 | 2016-02-26 | L3 |  |  |  | 1.4 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.1 | UG/L | 60.4999 | 2016-02-26 | L3 |  |  |  | 1.4 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 54.6 | UG/L | 80.4999 | 2016-02-26 | L1 |  |  |  | 1.4 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.1 | UG/L | 60.4999 | 2016-02-26 | L1 |  |  |  | 1.4 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 56.4 | UG/L | 80.4999 | 2016-02-26 | L2 |  |  |  | 1.4 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28 | UG/L | 60.4999 | 2016-02-26 | L2 |  |  |  | 1.4 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-02-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2016-03-01 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-03-01 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-03-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-03-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2016-03-16 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-03-16 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-03-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-03-25 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2016-04-01 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-04-01 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-04-05 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-04-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-04-15 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2016-04-15 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-04-25 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-04-25 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-05-03 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2016-05-03 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-05-06 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-05-06 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-05-19 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.8 | MG/L |  | 2016-05-19 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.3 | UG/L | 60.4999 | 2016-05-23 | L3 |  |  |  | 1.4 | 2942 EVANS DR. KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 48.1 | UG/L | 80.4999 | 2016-05-23 | L2 |  |  |  | 1 | 3543 BEAU CHENE DR. KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.4 | UG/L | 60.4999 | 2016-05-23 | L4 |  |  |  | 1.2 | 5508 WILLOW BEND TR. KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 51.1 | UG/L | 80.4999 | 2016-05-23 | L4 |  |  |  | 1.2 | 5508 WILLOW BEND TR. KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.8 | UG/L | 60.4999 | 2016-05-23 | L2 |  |  |  | 1 | 3543 BEAU CHENE DR. KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 27.7 | UG/L | 80.4999 | 2016-05-23 | L3 |  |  |  | 1.4 | 2942 EVANS DR. KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.6 | UG/L | 60.4999 | 2016-05-23 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 41.4 | UG/L | 80.4999 | 2016-05-23 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE (NO LRAA OR OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-05-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-05-25 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2016-06-01 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-06-01 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-06-04 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-06-04 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-06-13 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2016-06-13 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-06-23 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-06-23 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-07-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2016-07-08 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-07-08 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-07-08 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.7 | MG/L |  | 2016-07-15 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-07-15 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-07-25 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-07-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-09 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-08-09 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-09 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-08-10 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-25 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2016-08-25 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-08-28 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.7 | UG/L | 60.4999 | 2016-08-29 | L2 |  |  |  | 0.9 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 57.5 | UG/L | 80.4999 | 2016-08-29 | L2 |  |  |  | 0.9 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.7 | UG/L | 60.4999 | 2016-08-29 | L1 |  |  |  | 1.2 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 45.7 | UG/L | 80.4999 | 2016-08-29 | L4 |  |  |  | 1 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.5 | UG/L | 60.4999 | 2016-08-29 | L4 |  |  |  | 1 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 34.2 | UG/L | 80.4999 | 2016-08-29 | L3 |  |  |  | 1.8 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.2 | UG/L | 60.4999 | 2016-08-29 | L3 |  |  |  | 1.8 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 50.7 | UG/L | 80.4999 | 2016-08-29 | L1 |  |  |  | 1.2 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-09-08 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-09-12 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2016-09-12 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-09-13 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2016-09-23 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2016-09-26 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-09-26 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-09-29 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-10-03 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-10-03 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-10-05 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-10-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-10-19 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-10-19 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2016-10-24 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-10-28 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2016-11-03 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2016-11-03 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.4 | LN(10) |  | 2016-11-08 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-11-14 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-11-17 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2016-11-17 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 53.7 | UG/L | 80.4999 | 2016-11-22 | L4 |  |  |  | 1.3 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.6 | UG/L | 60.4999 | 2016-11-22 | L4 |  |  |  | 1.3 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 37.8 | UG/L | 80.4999 | 2016-11-22 | L3 |  |  |  | 1.5 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.8 | UG/L | 60.4999 | 2016-11-22 | L3 |  |  |  | 1.5 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 50.8 | UG/L | 80.4999 | 2016-11-22 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.9 | UG/L | 60.4999 | 2016-11-22 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 54.8 | UG/L | 80.4999 | 2016-11-22 | L2 |  |  |  | 1.3 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.9 | UG/L | 60.4999 | 2016-11-22 | L2 |  |  |  | 1.3 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.3 | LN(10) |  | 2016-11-23 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-11-25 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-12-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-12-08 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2016-12-08 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.2 | LN(10) |  | 2016-12-12 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2016-12-21 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 1.1 | LN(10) |  | 2016-12-21 | WTP1 |  |  |  |  | PO4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.3 | LN(10) |  | 2016-12-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-12-28 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.6 | UG/L | 60.4999 | 2017-02-23 | L2 |  |  |  | 1.2 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 52 | UG/L | 80.4999 | 2017-02-23 | L2 |  |  |  | 1.2 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.3 | UG/L | 60.4999 | 2017-02-23 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 41.8 | UG/L | 80.4999 | 2017-02-23 | L4 |  |  |  | 1.4 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.7 | UG/L | 60.4999 | 2017-02-23 | L3 |  |  |  | 1.8 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 32.7 | UG/L | 80.4999 | 2017-02-23 | L3 |  |  |  | 1.8 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.1 | UG/L | 60.4999 | 2017-02-23 | L4 |  |  |  | 1.4 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 51.7 | UG/L | 80.4999 | 2017-02-23 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0.03 | MG/L | 10.4999 | 2017-02-27 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-27 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 1.7 | MG/L | 10.4999 | 2017-02-27 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-27 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP3 |  | 0.5499 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP6 |  | 0.5499 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP1 |  | 0.5499 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 1.7 | MG/L | 10.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1005 | ARSENIC | N | 0.0019 | MG/L | 0.0104 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1010 | BARIUM | N | 0.0013 | MG/L | 2.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1010 | BARIUM | N | 0.016 | MG/L | 2.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1025 | FLUORIDE | N | 0.1 | MG/L | 4.0499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1045 | SELENIUM | N | 0.0009 | MG/L | 0.0549 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1052 | SODIUM | N | 96.9 | MG/L | 160.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1074 | ANTIMONY | N | 0.0007 | MG/L | 0.0065 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1017 | CHLORIDE | N | 11.7 | MG/L | 250.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1022 | COPPER | N | 0.0018 | MG/L | 1.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1025 | FLUORIDE | N | 0.1 | MG/L | 2.0499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1055 | SULFATE | N | 31.6 | MG/L | 250.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.1 | LN(10) |  | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 157 | MG/L | 500.4999 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1017 | CHLORIDE | N | 12.9 | MG/L | 250.4999 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1022 | COPPER | N | 0.002 | MG/L | 1.4999 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1025 | FLUORIDE | N | 0.083 | MG/L | 2.0499 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1920 | ODOR THRESHOLD | N | 2 |  | 3.4999 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 137 | MG/L | 500.4999 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1025 | FLUORIDE | N | 0.11 | MG/L | 4.0499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1052 | SODIUM | N | 11 | MG/L | 160.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1017 | CHLORIDE | N | 13.1 | MG/L | 250.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1025 | FLUORIDE | N | 0.11 | MG/L | 2.0499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1055 | SULFATE | N | 2.6 | MG/L | 250.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1920 | ODOR THRESHOLD | N | 4 |  | 3.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.1 | LN(10) |  | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 139 | MG/L | 500.4999 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) ODOR RESULT 4.0 MCL 3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1025 | FLUORIDE | N | 0.083 | MG/L | 4.0499 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1052 | SODIUM | N | 10.4 | MG/L | 160.4999 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1010 | BARIUM | N | 0.011 | MG/L | 2.4999 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-29 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 49.4 | UG/L | 80.4999 | 2017-05-31 | L3 |  |  |  | 2 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 44.4 | UG/L | 80.4999 | 2017-05-31 | L2 |  |  |  | 1.6 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 47.1 | UG/L | 80.4999 | 2017-05-31 | L4 |  |  |  | 1.6 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.4 | UG/L | 60.4999 | 2017-05-31 | L4 |  |  |  | 1.6 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.4 | UG/L | 60.4999 | 2017-05-31 | L2 |  |  |  | 1.6 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.8 | UG/L | 60.4999 | 2017-05-31 | L3 |  |  |  | 2 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 29.7 | UG/L | 80.4999 | 2017-05-31 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15 | UG/L | 60.4999 | 2017-05-31 | L1 |  |  |  | 1.3 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-06-02 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | WTP1 |  | 1.4999 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | WTP3 |  | 1.4999 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 4.75 | PCI/L | 15.4999 | 2017-06-02 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-06-02 | WTP6 |  | 1.4999 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 5.4 | PCI/L | 15.4999 | 2017-06-02 | WTP6 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | D | 7.9 | LN(10) |  | 2017-06-27 | 2940 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | D | 7.8 | LN(10) |  | 2017-06-27 | HURON BAY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | D | 8 | LN(10) |  | 2017-06-27 | 806 HALIFAX DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | D | 7.8 | LN(10) |  | 2017-06-27 | 861 TOLEDO CT
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | D | 7.8 | LN(10) |  | 2017-06-27 | 401 SCORE LANE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | D | 7.9 | LN(10) |  | 2017-06-27 | 601 COUNTRY CLUB RD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | D | 8.1 | LN(10) |  | 2017-06-27 | 406 NAPLE CT
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23 | UG/L | 60.4999 | 2017-08-25 | L2 | 0.48 |  | 1 | 1.4 | 3543 BEAU CHENE DR. (THESE DBPS OK)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 25.4 | UG/L | 60.4999 | 2017-08-25 | L4 | 0.48 |  | 4 | 1.6 | 5508 WILLOW BEND TR. (THESE HAA5S ALL HAVE Q QUALIFIERS - OVER HOLDING TIME - DBPS UNAC FOR 3Q 2017 THIS SITE)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | S | 29.9 | UG/L | 80.4999 | 2017-08-25 | L3 | 0.32 |  | 3 | 1.8 | 2942 EVANS DR. (THESE HAA5S ALL HAVE Q QUALIFIERS - OVER HOLDING TIME - DBPS UNAC FOR 3Q 2017 THIS SITE)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 15.3 | UG/L | 60.4999 | 2017-08-25 | L3 | 0.48 |  | 3 | 1.8 | 2942 EVANS DR. (THESE HAA5S ALL HAVE Q QUALIFIERS - OVER HOLDING TIME - DBPS UNAC FOR 3Q 2017 THIS SITE)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 46.5 | UG/L | 80.4999 | 2017-08-25 | L1 | 0.32 |  | 2 | 1.8 | 4738 ASHURST ST. (THESE DBPS OK)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | S | 53.9 | UG/L | 80.4999 | 2017-08-25 | L4 | 0.32 |  | 4 | 1.6 | 5508 WILLOW BEND TR. (THESE HAA5S ALL HAVE Q QUALIFIERS - OVER HOLDING TIME - DBPS UNAC FOR 3Q 2017 THIS SITE)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 52.2 | UG/L | 80.4999 | 2017-08-25 | L2 | 0.32 |  | 1 | 1.4 | 3543 BEAU CHENE DR. (THESE DBPS OK)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.1 | UG/L | 60.4999 | 2017-08-25 | L1 | 0.48 |  | 2 | 1.8 | 4738 ASHURST ST. (THESE DBPS OK)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP3 |  | 0.0149
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP3 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP3 |  | 1.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP3 |  | 1.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-29 | WTP3 |  | 0.4499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-29 | WTP3 |  | 9.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-29 | WTP3 |  | 6.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-29 | WTP3 |  | 0.6499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP3 |  | 2.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-29 | WTP3 |  | 0.0749
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-29 | WTP3 |  | 0.6499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-29 | WTP3 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-29 | WTP3 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP3 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP3 |  | 0.9499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP3 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP3 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-29 | WTP3 |  | 0.0449
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-29 | WTP3 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP3 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP3 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP3 |  | 0.0449
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-29 | WTP3 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP3 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-29 | WTP3 |  | 0.0149
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP3 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP6 |  | 0.0149
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP6 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP6 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP6 |  | 1.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP6 |  | 1.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-29 | WTP6 |  | 0.4499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-29 | WTP6 |  | 9.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-29 | WTP6 |  | 6.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-29 | WTP6 |  | 0.6499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP6 |  | 2.4999
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-29 | WTP6 |  | 0.0749
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-29 | WTP6 |  | 0.6499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-29 | WTP6 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-29 | WTP6 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP6 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP6 |  | 0.9499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP6 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP6 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-29 | WTP6 |  | 0.0449
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP6 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-29 | WTP6 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP6 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP6 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP6 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP6 |  | 0.0449
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-29 | WTP6 |  | 0.1499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP6 |  | 0.0249
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-29 | WTP6 |  | 0.0149
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP6 |  | 0.2499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP1 |  | 0.0149 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP1 |  | 0.1499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP1 |  | 1.4999 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | N | 0.89 | UG/L | 249.9999 | 2017-08-29 | WTP1 | 0.89 | 1.4999 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-29 | WTP1 |  | 0.4499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-29 | WTP1 |  | 9.4999 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-29 | WTP1 |  | 6.4999 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-29 | WTP1 |  | 0.6499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-29 | WTP1 |  | 2.4999 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-29 | WTP1 |  | 0.0749 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-29 | WTP1 |  | 0.6499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | N | 0.094 | UG/L | 549.9999 | 2017-08-29 | WTP1 |  | 0.1499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | N | 0.16 | UG/L | 7.4999 | 2017-08-29 | WTP1 |  | 0.2499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-29 | WTP1 |  | 0.1499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-29 | WTP1 |  | 0.9499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-29 | WTP1 |  | 0.1499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP1 |  | 0.2499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-29 | WTP1 |  | 0.0449 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2 4-D | N | 0.081 | UG/L | 74.9999 | 2017-08-29 | WTP1 |  | 0.1499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0.16 | UG/L | 54.9999 | 2017-08-29 | WTP1 |  | 0.2499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-29 | WTP1 |  | 0.1499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | N | 0.03 | UG/L | 1.4999 | 2017-08-29 | WTP1 |  | 0.0449 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-29 | WTP1 |  | 0.1499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-29 | WTP1 |  | 0.0249 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-29 | WTP1 |  | 0.0149 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-29 | WTP1 |  | 0.2499 |  |  | DALAPON PICLORAM DINOSEB (2 4-D) (2 4 5-TP) PENTACHLOROPHENOL ALL Q QUALIFERS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 52.2 | UG/L | 80.4999 | 2017-11-27 | L1 |  |  |  | 1.5 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.1 | UG/L | 60.4999 | 2017-11-27 | L3 |  |  |  | 1.3 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 41.4 | UG/L | 80.4999 | 2017-11-27 | L3 |  |  |  | 1.3 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.3 | UG/L | 60.4999 | 2017-11-27 | L1 |  |  |  | 1.5 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 56.6 | UG/L | 80.4999 | 2017-11-27 | L2 |  |  |  | 1.5 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.5 | UG/L | 60.4999 | 2017-11-27 | L4 |  |  |  | 1.4 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 55.6 | UG/L | 80.4999 | 2017-11-27 | L4 |  |  |  | 1.4 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.5 | UG/L | 60.4999 | 2017-11-27 | L2 |  |  |  | 1.5 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-04 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-04 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2018-01-04 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-05 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-17 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2018-01-17 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-19 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-01-22 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-05 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-05 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-08 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-02-08 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-19 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-19 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-02-21 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2018-02-21 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 47.7 | UG/L | 80.4999 | 2018-02-22 | L4 |  |  |  | 1.9 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.8 | UG/L | 60.4999 | 2018-02-22 | L4 |  |  |  | 1.9 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 28.7 | UG/L | 80.4999 | 2018-02-22 | L3 |  |  |  | 1.9 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.4 | UG/L | 60.4999 | 2018-02-22 | L3 |  |  |  | 1.9 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 59 | UG/L | 80.4999 | 2018-02-22 | L1 |  |  |  | 1.6 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 32.6 | UG/L | 80.4999 | 2018-02-22 | L2 |  |  |  | 1.9 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.8 | UG/L | 60.4999 | 2018-02-22 | L2 |  |  |  | 1.9 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.5 | UG/L | 60.4999 | 2018-02-22 | L1 |  |  |  | 1.6 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 1.5 | MG/L | 10.4999 | 2018-02-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-28 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-03-05 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-03-07 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-03-12 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2018-03-12 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-03-22 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-03-23 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2018-03-26 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-03-26 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2018-04-03 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-03 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-05 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-06 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2018-04-17 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-17 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-19 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-04-24 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2018-05-03 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-03 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-07 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-07 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-05-17 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-17 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-18 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-05-25 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-05 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-07 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.7 | UG/L | 60.4999 | 2018-06-08 | L2 | 0.48 |  | 1 | 1.3 | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 45.2 | UG/L | 80.4999 | 2018-06-08 | L2 | 0.32 |  | 1 | 1.3 | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-08 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2018-06-08 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 40.5 | UG/L | 80.4999 | 2018-06-08 | L4 | 0.32 |  | 4 | 1.3 | 5508 WILLOW BEND TR. (6/18 DISINF BYP REPORT RCVD) HLK'D TO SB 7/17/18 - BB
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.1 | UG/L | 60.4999 | 2018-06-08 | L4 | 0.48 |  | 4 | 1.3 | 5508 WILLOW BEND TR. (6/18 DISINF BYP REPORT RCVD) HLK'D TO SB 7/17/18 - BB
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 29 | UG/L | 80.4999 | 2018-06-08 | L3 | 0.32 |  | 3 | 1.3 | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.9 | UG/L | 60.4999 | 2018-06-08 | L3 | 0.48 |  | 3 | 1.3 | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.2 | UG/L | 60.4999 | 2018-06-08 | L1 | 0.48 |  | 2 | 1.2 | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 45.1 | UG/L | 80.4999 | 2018-06-08 | L1 | 0.32 |  | 2 | 1.2 | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-06-18 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-18 | WTP1 |  |  |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-22 | WTP6 |  |  |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-06-22 | WTP3 |  |  |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2018-07-03 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-03 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-03 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-03 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-07-03 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-11 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2018-07-13 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-13 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-24 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-07-30 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-08-03 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-08-08 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-08-20 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2018-08-20 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-08-22 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 36.4 | UG/L | 80.4999 | 2018-08-24 | L4 | 0.32 |  | 4 | 0.4 | 5508 WILLOW BEND TR. (HLKD TO SB) 9/18 QTR DISINF BYP REPORT WAS NOT WITH THESE DBPS - MAY COME IN SEPARATELY (?)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.8 | UG/L | 60.4999 | 2018-08-24 | L4 | 0.48 |  | 4 | 0.4 | 5508 WILLOW BEND TR. (HLKD TO SB) 9/18 QTR DISINF BYP REPORT WAS NOT WITH THESE DBPS - MAY COME IN SEPARATELY (?)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.1 | UG/L | 60.4999 | 2018-08-24 | L2 | 0.48 |  | 1 | 0.8 | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16 | UG/L | 60.4999 | 2018-08-24 | L3 | 0.48 |  | 3 | 1 | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 38.2 | UG/L | 80.4999 | 2018-08-24 | L1 | 0.32 |  | 2 | 0.5 | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.8 | UG/L | 60.4999 | 2018-08-24 | L1 | 0.48 |  | 2 | 0.5 | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 39.5 | UG/L | 80.4999 | 2018-08-24 | L2 | 0.32 |  | 1 | 0.8 | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-08-24 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 29.8 | UG/L | 80.4999 | 2018-08-24 | L3 | 0.32 |  | 3 | 1 | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-09-04 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-09-04 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-09-04 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2018-09-04 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-09-17 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-09-20 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2018-09-20 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-09-21 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2018-10-02 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-10-05 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-10-05 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-10-07 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2018-10-21 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.14 | LN(10) |  | 2018-10-21 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-10-23 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-10-31 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-02 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2018-11-02 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-05 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-05 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-12 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-11-16 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2018-11-16 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-11-22 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 46.8 | UG/L | 80.4999 | 2018-11-28 | L1 |  |  | 2 | 1.5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.6 | UG/L | 60.4999 | 2018-11-28 | L3 |  |  | 3 | 1.8
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 28.7 | UG/L | 80.4999 | 2018-11-28 | L3 |  |  | 3 | 1.8
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.2 | UG/L | 60.4999 | 2018-11-28 | L4 |  |  | 4 | 1.5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 43.6 | UG/L | 80.4999 | 2018-11-28 | L4 |  |  | 4 | 1.5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 45.4 | UG/L | 80.4999 | 2018-11-28 | L2
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.9 | UG/L | 60.4999 | 2018-11-28 | L2
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.7 | UG/L | 60.4999 | 2018-11-28 | L1 |  |  | 2 | 1.5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-01 | WTP1 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-12-03 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-03 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-04 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-06 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-12-06 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2018-12-10 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2018-12-10 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2018-12-14 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2018-12-14 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-17 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2018-12-17 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-24 | WTP3 |  |  |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-24 | WTP6 |  |  |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-12-28 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2018-12-28 | WTP1 |  |  |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2019-01-02 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-02 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-03 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-04 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-01-21 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-01-22 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-24 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2019-01-24 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-05 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-02-05 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-02-05 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-05 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-19 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-19 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-02-25 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-25 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.6 | UG/L | 60.4999 | 2019-02-27 | L4 | 0.48 |  | 4 | 1.5 | 5508 WILLOW BEND TR. KISSIMMEE (3/19 DISINF BYP RPRT RCVD SEP IN "WORD") RSLTS & DB REPORT HLKD TOGETHER
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 37.7 | UG/L | 80.4999 | 2019-02-27 | L4 | 0.32 |  | 4 | 1.5 | 5508 WILLOW BEND TR. KISSIMMEE (3/19 DISINF BYP RPRT RCVD SEP IN "WORD") RSLTS & DB REPORT HLKD TOGETHER
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 30.8 | UG/L | 80.4999 | 2019-02-27 | L3 | 0.32 |  | 3 | 1.7 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.1 | UG/L | 60.4999 | 2019-02-27 | L3 | 0.48 |  | 3 | 1.7 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 46.3 | UG/L | 80.4999 | 2019-02-27 | L1 | 0.32 |  | 2 | 1.2 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.9 | UG/L | 60.4999 | 2019-02-27 | L1 | 0.48 |  | 2 | 1.2 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 41.4 | UG/L | 80.4999 | 2019-02-27 | L2 | 0.32 |  | 1 | 0.9 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.1 | UG/L | 60.4999 | 2019-02-27 | L2 | 0.48 |  | 1 | 0.9 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP3 |  |  |  |  | 2019 NN PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 1.3 | MG/L | 10.4999 | 2019-02-28 | WTP6 |  |  |  |  | 2019 NN HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP6 |  |  |  |  | 2019 NN HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | WTP1 |  |  |  |  | 2019 NNBELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-28 | WTP1 |  |  |  |  | 2019 NNBELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-28 | WTP3 |  |  |  |  | 2019 NN PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-03-05 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-07 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-11 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2019-03-11 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-20 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2019-03-20 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-22 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-22 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2019-04-04 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-04 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-05 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-05 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-19 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2019-04-23 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-23 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-24 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-07 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-07 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2019-05-10 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-10 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-17 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 42.1 | UG/L | 80.4999 | 2019-05-24 | L2 | 0.32 |  | 1 | 1.3 | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16 | UG/L | 60.4999 | 2019-05-24 | L4 | 0.48 |  | 4 | 1.4 | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 44.3 | UG/L | 80.4999 | 2019-05-24 | L3 | 0.32 |  | 3 | 1.3 | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.3 | UG/L | 60.4999 | 2019-05-24 | L3 | 0.48 |  | 3 | 1.3 | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 56.7 | UG/L | 80.4999 | 2019-05-24 | L1 | 0.32 |  | 2 | 1.2 | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.4 | UG/L | 60.4999 | 2019-05-24 | L2 | 0.48 |  | 1 | 1.3 | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 34.2 | UG/L | 80.4999 | 2019-05-24 | L4 | 0.32 |  | 4 | 1.4 | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.8 | UG/L | 60.4999 | 2019-05-24 | L1 | 0.48 |  | 2 | 1.2 | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-25 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-30 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-05-30 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-06-07 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-06-07 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2019-06-12 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-06-12 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-21 | WTP6 |  |  |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-22 | WTP3 |  |  |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2019-06-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-28 | WTP1 |  |  |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 30.7 | UG/L | 80.4999 | 2019-08-26 | L2 |  |  | 1 | 0.6 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.4 | UG/L | 60.4999 | 2019-08-26 | L2 |  |  | 1 | 0.6 | 3543 BEAU CHENE DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 56.5 | UG/L | 80.4999 | 2019-08-26 | L4 |  |  | 4 | 1.4 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.3 | UG/L | 60.4999 | 2019-08-26 | L4 |  |  | 4 | 1.4 | 5508 WILLOW BEND TR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 33.8 | UG/L | 80.4999 | 2019-08-26 | L3 |  |  | 3 | 1.2 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.9 | UG/L | 60.4999 | 2019-08-26 | L3 |  |  | 3 | 1.2 | 2942 EVANS DR. KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 51 | UG/L | 80.4999 | 2019-08-26 | L1 |  |  | 2 | 1 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.8 | UG/L | 60.4999 | 2019-08-26 | L1 |  |  | 2 | 1 | 4738 ASHURST STREET KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 51.4 | UG/L | 80.4999 | 2019-11-26 | L2 | 0.32 |  | 2 | 1.6 | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.3 | UG/L | 60.4999 | 2019-11-26 | L1 | 0.9 |  | 1 | 1.4 | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 47.4 | UG/L | 80.4999 | 2019-11-26 | L1 | 0.32 |  | 1 | 1.4 | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.7 | UG/L | 60.4999 | 2019-11-26 | L2 | 0.9 |  | 2 | 1.6 | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 51.7 | UG/L | 80.4999 | 2019-11-26 | L4 | 0.32 |  | 4 | 1.2 | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.8 | UG/L | 60.4999 | 2019-11-26 | L3 | 0.9 |  | 3 | 0.3 | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | D | 9.6 | UG/L | 80.4999 | 2019-11-26 | L3 | 0.32 |  | 3 | 0.3 | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.8 | UG/L | 60.4999 | 2019-11-26 | L4 | 0.9 |  | 4 | 1.2 | 5508 WILLOW BEND TR
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.6 | UG/L | 60.4999 | 2019-09-05 | L1 | 0.9 |  | 1 | 1.1 | 2722 MATERA DR. (HLKD) TTHMS HIGH
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2950 | TOTAL THMS | D | 113 | UG/L | 80.4999 | 2019-09-05 | L1 | 0.32 |  | 1 | 1.1 | 2722 MATERA DR. (HLKD) TTHMS HIGH
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.9 | UG/L | 60.4999 | 2019-09-05 | L2 | 0.9 |  | 2 | 0.8 | 5690 BARLETTA DR. (HLKD) TTHMS HIGH
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2950 | TOTAL THMS | D | 123 | UG/L | 80.4999 | 2019-09-05 | L2 | 0.32 |  | 2 | 0.8 | 5690 BARLETTA DR. (HLKD) TTHMS HIGH
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2950 | TOTAL THMS | D | 117 | UG/L | 80.4999 | 2019-12-23 | L2 | 0.32 |  | 2 | 0.6 | 5690 BARLETTA DR. (HLKD)
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.6 | UG/L | 60.4999 | 2019-12-23 | L2 | 0.9 |  | 2 | 0.6 | 5690 BARLETTA DR. (HLKD)
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.7 | UG/L | 60.4999 | 2019-12-23 | L1 | 0.9 |  | 1 | 0.5 | 2722 MATERA DR. (HLKD)
3494438 | TWA-NORTHEAST WATER SYSTEM (CONSEC) | DBP | 2950 | TOTAL THMS | D | 112 | UG/L | 80.4999 | 2019-12-23 | L1 | 0.32 |  | 1 | 0.5 | 2722 MATERA DR. (HLKD)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.14 | UG/L | 60.4999 | 2015-01-21 | L2 |  |  |  | 1.2 | 342 BRANTLEY CLUB PLACE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES (1/15 DBPS & DBF IN OC)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.32 | UG/L | 80.4999 | 2015-01-21 | L2 |  |  |  | 1.2 | 342 BRANTLEY CLUB PLACE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES (1/15 DBPS & DBF IN OC)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.63 | UG/L | 60.4999 | 2015-01-21 | L3 |  |  |  | 1.2 | 1021 ARDEN ST. (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 27.07 | UG/L | 80.4999 | 2015-01-21 | L3 |  |  |  | 1.2 | 1021 ARDEN ST. (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.75 | UG/L | 60.4999 | 2015-01-21 | L4 |  |  |  | 1.3 | 496 CENTRAL PARKWAY (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 29.3 | UG/L | 80.4999 | 2015-01-21 | L4 |  |  |  | 1.3 | 496 CENTRAL PARKWAY (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.67 | UG/L | 60.4999 | 2015-01-21 | L1 |  |  |  | 0.9 | 235 S. WYMORE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.49 | UG/L | 80.4999 | 2015-01-21 | L1 |  |  |  | 0.9 | 235 S. WYMORE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-04-22 | WTP2 | 1.5 | 0.6499 |  |  | 3AM/2039-WP2 (MAY STOP AM/2039-WP2 SINCE 2014 2039 0.44 < RDL OF 0.6 UG/L) EM 4/9/15 REMINDER TO TEZEKIDER
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 52.59 | UG/L | 80.4999 | 2015-04-22 | L2 |  |  |  | 1.3 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.38 | UG/L | 60.4999 | 2015-04-22 | L3 |  |  |  | 1.3 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 34.68 | UG/L | 80.4999 | 2015-04-22 | L3 |  |  |  | 1.3 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.09 | UG/L | 60.4999 | 2015-04-22 | L2 |  |  |  | 1.3 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 46.97 | UG/L | 80.4999 | 2015-04-22 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES AT ANY SITE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.8 | UG/L | 60.4999 | 2015-04-22 | L1 |  |  |  | 1.2 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 41.93 | UG/L | 80.4999 | 2015-04-22 | L1 |  |  |  | 1.2 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.64 | UG/L | 60.4999 | 2015-04-22 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES AT ANY SITE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-05-20 | WTP2 |  |  |  |  | WTP#2 (SPRING LAKE/SOUTHWEST) 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0.006 | MG/L | 10.4999 | 2015-05-20 | WTP5 |  |  |  |  | WTP#5 (PEARL LK.CSWY) 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-20 | WTP5 |  |  |  |  | WTP#5 (PEARL LK.CSWY) 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-20 | WTP2 |  |  |  |  | WTP#2 (SPRING LAKE/SOUTHWEST) 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 59.22 | UG/L | 80.4999 | 2015-07-30 | L2 |  |  |  | 0.9 | (1/22/16 EW HAS 10/15 DBPS & 12/15 QTR DBF) 342 BRANTLEY CLUB PLACE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 50.24 | UG/L | 80.4999 | 2015-07-30 | L1 |  |  |  | 0.9 | 235 S. WYMORE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.66 | UG/L | 60.4999 | 2015-07-30 | L1 |  |  |  | 0.9 | 235 S. WYMORE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 53.43 | UG/L | 80.4999 | 2015-07-30 | L4 |  |  |  | 1 | 496 CENTRAL PARKWAY (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.05 | UG/L | 60.4999 | 2015-07-30 | L4 |  |  |  | 1 | 496 CENTRAL PARKWAY (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.45 | UG/L | 80.4999 | 2015-07-30 | L3 |  |  |  | 1.3 | 1021 ARDEN ST. (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.94 | UG/L | 60.4999 | 2015-07-30 | L2 |  |  |  | 0.9 | (1/22/16 EW HAS 10/15 DBPS & 12/15 QTR DBF) 342 BRANTLEY CLUB PLACE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.9 | UG/L | 60.4999 | 2015-07-30 | L3 |  |  |  | 1.3 | 1021 ARDEN ST. (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 34.79 | UG/L | 80.4999 | 2015-10-21 | L3 |  |  |  | 1.4 | 1021 ARDEN ST. (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 65.24 | UG/L | 80.4999 | 2015-10-21 | L2 |  |  |  | 1.3 | 342 BRANTLEY CLUB PLACE (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M. (3/3 EW HAS 1/16 DBPS & DBF)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.51 | UG/L | 60.4999 | 2015-10-21 | L2 |  |  |  | 1.3 | 342 BRANTLEY CLUB PLACE (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M. (3/3 EW HAS 1/16 DBPS & DBF)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 63.8 | UG/L | 80.4999 | 2015-10-21 | L1 |  |  |  | 1.1 | 235 S. WYMORE (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.33 | UG/L | 60.4999 | 2015-10-21 | L3 |  |  |  | 1.4 | 1021 ARDEN ST. (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.95 | UG/L | 60.4999 | 2015-10-21 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 35.01 | UG/L | 80.4999 | 2015-10-21 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.19 | UG/L | 60.4999 | 2015-10-21 | L1 |  |  |  | 1.1 | 235 S. WYMORE (RCVD WITH 12/15 DBF TOGETHER IN OC) DOES NOT QUALIFY FOR R.M.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 51.21 | UG/L | 80.4999 | 2016-01-20 | L4 |  |  |  | 0.9 | 496 CENTRAL PARKWAY (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.25 | UG/L | 60.4999 | 2016-01-20 | L4 |  |  |  | 0.9 | 496 CENTRAL PARKWAY (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 55.84 | UG/L | 80.4999 | 2016-01-20 | L2 |  |  |  | 0.8 | 342 BRANTLEY CLUB PLACE (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.57 | UG/L | 60.4999 | 2016-01-20 | L2 |  |  |  | 0.8 | 342 BRANTLEY CLUB PLACE (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 21.16 | UG/L | 80.4999 | 2016-01-20 | L1 |  |  |  | 0.9 | 235 S. WYMORE (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.51 | UG/L | 60.4999 | 2016-01-20 | L1 |  |  |  | 0.9 | 235 S. WYMORE (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.65 | UG/L | 60.4999 | 2016-01-20 | L3 |  |  |  | 1.3 | 1021 ARDEN ST. (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 29.26 | UG/L | 80.4999 | 2016-01-20 | L3 |  |  |  | 1.3 | 1021 ARDEN ST. (RCVD WITH 3/16 DBF TOGETHER IN OC DOES NOT QUALIFY FOR R.M.)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 62 | UG/L | 80.4999 | 2016-04-20 | L2 |  |  |  | 0.9 | 342 BRANTLEY CLUB PLACE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.25 | UG/L | 60.4999 | 2016-04-20 | L4 |  |  |  | 1.5 | 496 CENTRAL PARKWAY (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES (REVISED 4/16 DISINF BYP REPORT IN OC - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.53 | UG/L | 80.4999 | 2016-04-20 | L4 |  |  |  | 1.5 | 496 CENTRAL PARKWAY (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES (REVISED 4/16 DISINF BYP REPORT IN OC - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.78 | UG/L | 60.4999 | 2016-04-20 | L1 |  |  |  | 0.9 | 235 S. WYMORE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.79 | UG/L | 60.4999 | 2016-04-20 | L3 |  |  |  | 1.2 | 1021 ARDEN ST. (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.52 | UG/L | 60.4999 | 2016-04-20 | L2 |  |  |  | 0.9 | 342 BRANTLEY CLUB PLACE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 51.23 | UG/L | 80.4999 | 2016-04-20 | L1 |  |  |  | 0.9 | 235 S. WYMORE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.44 | UG/L | 80.4999 | 2016-04-20 | L3 |  |  |  | 1.2 | 1021 ARDEN ST. (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0.007 | MG/L | 10.4999 | 2016-06-15 | WTP5 |  |  |  |  | WTP#5 (PEARL LK.CSWY) NITRATE (NITRITE IS OVER HOLDING TIME>EM 8/18/16 TO THOMAS ZEDIKER FOR NO2 RETEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-06-15 | WTP2 |  |  |  |  | WTP#2 (SPRING LAKE/SOUTHWEST) NITRATE (NITRITE IS OVER HOLDING TIME>EM 8/18/16 TO THOMAS ZEDIKER FOR NO2 RETEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-07-13 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-07-13 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-07-13 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-07-13 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.57 | UG/L | 60.4999 | 2016-07-20 | L3 |  |  |  | 0.9 | 1021 ARDEN ST. (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 22.96 | UG/L | 80.4999 | 2016-07-20 | L3 |  |  |  | 0.9 | 1021 ARDEN ST. (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.65 | UG/L | 60.4999 | 2016-07-20 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES (REVISED 9/16 DISINF BYP REPORT IN OC - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 39.78 | UG/L | 80.4999 | 2016-07-20 | L2 |  |  |  | 1.2 | 342 BRANTLEY CLUB PLACE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.78 | UG/L | 60.4999 | 2016-07-20 | L1 |  |  |  | 0.6 | 235 S. WYMORE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.47 | UG/L | 80.4999 | 2016-07-20 | L1 |  |  |  | 0.6 | 235 S. WYMORE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.22 | UG/L | 60.4999 | 2016-07-20 | L2 |  |  |  | 1.2 | 342 BRANTLEY CLUB PLACE (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 13.45 | UG/L | 80.4999 | 2016-07-20 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (DOES NOT QUALIFY FOR R.M.) NO LRAA MCLS OR OE EXCEEDANCES (REVISED 9/16 DISINF BYP REPORT IN OC - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-07-27 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-07-27 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-07-27 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-07-27 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-08-10 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-08-10 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-08-10 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-08-10 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-08-19 | WTP2 | 0.003 |  |  |  | NITRITE RETEST - WP2 (OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-08-19 | WTP5 | 0.003 |  |  |  | NITRITE RETEST - WP5 (OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-08-24 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-08-24 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-08-24 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-08-24 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-09-07 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-09-07 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-09-07 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-09-07 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-09-21 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-09-21 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-09-21 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-09-21 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-10-05 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-10-05 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-10-05 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-10-05 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 40.11 | UG/L | 80.4999 | 2016-10-19 | L1 |  |  |  | 1.1 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.26 | UG/L | 60.4999 | 2016-10-19 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (REVISED 12/16 DISINF BYP REPORT IN OC - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.89 | UG/L | 80.4999 | 2016-10-19 | L4 |  |  |  | 1.2 | 496 CENTRAL PARKWAY (REVISED 12/16 DISINF BYP REPORT IN OC - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.32 | UG/L | 60.4999 | 2016-10-19 | L2 |  |  |  | 0.9 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.11 | UG/L | 80.4999 | 2016-10-19 | L2 |  |  |  | 0.9 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-10-19 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-10-19 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-10-19 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 29.41 | UG/L | 80.4999 | 2016-10-19 | L3 |  |  |  | 1.3 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.35 | UG/L | 60.4999 | 2016-10-19 | L3 |  |  |  | 1.3 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-10-19 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.49 | UG/L | 60.4999 | 2016-10-19 | L1 |  |  |  | 1.1 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-11-02 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-11-02 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-11-02 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-11-02 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-11-16 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-11-16 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-11-16 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-11-16 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-11-30 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-11-30 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-11-30 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-11-30 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-12-14 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-12-14 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-12-14 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-12-14 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-12-28 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-12-28 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-12-28 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2016-12-28 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.73 | UG/L | 60.4999 | 2017-01-25 | L3 | 0.2 |  | 1 | 1.3 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.85 | UG/L | 80.4999 | 2017-01-25 | L3 | 0.14 |  | 1 | 1.3 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.42 | UG/L | 60.4999 | 2017-01-25 | L1 | 0.2 |  | 2 | 1.1 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 39.13 | UG/L | 80.4999 | 2017-01-25 | L1 | 0.14 |  | 2 | 1.1 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.97 | UG/L | 60.4999 | 2017-01-25 | L4 | 0.2 |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 24.52 | UG/L | 80.4999 | 2017-01-25 | L4 | 0.14 |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.91 | UG/L | 60.4999 | 2017-01-25 | L2 | 0.2 |  | 4 | 1.1 | 342 BRANTLEY CLUB PLACE (3/17 DISINF BYP REPORT RCVD-ALL REVISED WITH CORRECT 4/16 FIGURES - IN OC - BB) SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 44.95 | UG/L | 80.4999 | 2017-01-25 | L2 | 0.14 |  | 4 | 1.1 | 342 BRANTLEY CLUB PLACE (3/17 DISINF BYP REPORT RCVD-ALL REVISED WITH CORRECT 4/16 FIGURES - IN OC - BB) SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-23 | WTP2 | 0.0067 | 0.0149 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-23 | WTP2 | 0.0029 | 0.0249 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-23 | WTP2 | 0.049 | 0.1499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP2 | 0.58 | 1.4999 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-23 | WTP2 | 0.89 | 1.4999 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-23 | WTP2 | 0.3 | 0.4499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP2 | 4.3 | 9.4999 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-23 | WTP2 | 4.2 | 6.4999 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-23 | WTP2 | 0.37 | 0.6499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-23 | WTP2 | 0.55 | 2.4999 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-23 | WTP2 | 0.54 | 0.6499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-23 | WTP2 | 0.094 | 0.1499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-23 | WTP2 | 0.16 | 0.2499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-23 | WTP2 | 0.031 | 0.1499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-23 | WTP2 | 0.32 | 0.9499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP2 | 0.061 | 0.1499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-23 | WTP2 | 0.034 | 0.2499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-23 | WTP2 | 0.012 | 0.0449 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-23 | WTP2 | 0.0029 | 0.0249 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-23 | WTP2 | 0.081 | 0.1499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP5 | 0.39 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-23 | WTP5 | 0.0067 | 0.0149 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-23 | WTP5 | 0.0029 | 0.0249 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-23 | WTP5 | 0.049 | 0.1499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP5 | 0.58 | 1.4999 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-23 | WTP5 | 0.89 | 1.4999 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-23 | WTP5 | 0.3 | 0.4499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP5 | 4.3 | 9.4999 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-23 | WTP5 | 4.2 | 6.4999 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-23 | WTP5 | 0.37 | 0.6499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-23 | WTP5 | 0.55 | 2.4999 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-03-23 | WTP5 | 0.066 | 0.0749 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-23 | WTP2 | 0.025 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-03-23 | WTP2 | 0.0005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1010 | BARIUM | N | 0.009 | MG/L | 2.4999 | 2017-03-23 | WTP2 | 0.005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-03-23 | WTP2 | 0.0005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-03-23 | WTP2 | 0.0025 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-03-23 | WTP2 | 0.005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-03-23 | WTP2 | 0.0005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-03-23 | WTP2 | 0.0001 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-03-23 | WTP2 | 0.0025 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-03-23 | WTP2 | 0.0005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1052 | SODIUM | N | 10.3 | MG/L | 160.4999 | 2017-03-23 | WTP2 | 0.5 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-03-23 | WTP2 | 0.0005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-03-23 | WTP2 | 0.0005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-03-23 | WTP2 | 0.0005 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1002 | ALUMINUM | N | 0.0066 | MG/L | 0.2499 | 2017-03-23 | WTP2 | 0.0062 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1022 | COPPER | N | 0.0016 | MG/L | 1.4999 | 2017-03-23 | WTP2 | 0.00093 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-03-23 | WTP2 | 0.02 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-03-23 | WTP2 | 0.0025 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-03-23 | WTP2 | 0.0025 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-03-23 | WTP2 | 0.01 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-03-23 | WTP2 | 5 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 137 | MG/L | 500.4999 | 2017-03-23 | WTP2 | 5 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-03-23 | WTP2 | 0.099 |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.7 | LN(10) |  | 2017-03-23 | WTP2 |  |  |  |  | WP2 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | WTP2 | 0.44 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP2 | 0.39 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-23 | WTP5 | 0.54 | 0.6499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-23 | WTP5 | 0.094 | 0.1499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-23 | WTP5 | 0.16 | 0.2499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-23 | WTP5 | 0.031 | 0.1499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-03-23 | WTP2 | 0.025 |  |  |  | WP2 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP2 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP2 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-23 | WTP5 | 0.32 | 0.9499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP5 | 0.061 | 0.1499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-23 | WTP5 | 0.034 | 0.2499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-23 | WTP5 | 0.012 | 0.0449 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-23 | WTP5 | 0.0029 | 0.0249 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-23 | WTP5 | 0.081 | 0.1499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-23 | WTP5 | 0.16 | 0.2499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP5 | 0.018 | 0.1499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-03-23 | WTP5 | 0.012 | 0.0249 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP5 | 0.03 | 0.0449 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-23 | WTP5 | 0.077 | 0.1499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-23 | WTP5 | 0.0065 | 0.0249 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-23 | WTP5 | 0.0076 | 0.0149 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-23 | WTP5 | 0.045 | 0.2499 |  |  | 1Q SOC/WP5 (GLY J QUAL LCS 122% BIASED HIGH-OK BENZO J QUAL LCS 131% BIASED HIGH-OK BENZO -0-) SIMAZINE IS OK FOR WP5 - NO QUALIFIERS ON IT.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-03-23 | WTP2 | 1 |  |  |  | WP2 ODOR
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-03-23 | WTP2 | 1.84 |  |  |  | WP2 RADS (RESET RADS WVRS BASED ON THESE RESULTS)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2017-03-23 | WTP2 | 1.26 | 1.4999 |  |  | WP2 RADS (RESET RADS WVRS BASED ON THESE RESULTS)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-03-23 | WTP2 | 0.688 | 1.4999 |  |  | WP2 RADS (RESET RADS WVRS BASED ON THESE RESULTS)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-03-23 | WTP5 | 1 |  |  |  | WP5 ODOR
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-03-23 | WTP5 | 2.25 |  |  |  | WP5 RADS (RESET RADS WVRS BASED ON THESE RESULTS)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2017-03-23 | WTP5 | 0.878 | 1.4999 |  |  | WP5 RADS (RESET RADS WVRS BASED ON THESE RESULTS)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-03-23 | WTP5 | 0.764 | 1.4999 |  |  | WP5 RADS (RESET RADS WVRS BASED ON THESE RESULTS)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-23 | WTP2 | 0.16 | 0.2499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP2 | 0.018 | 0.1499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0.02 | UG/L | 0.2499 | 2017-03-23 | WTP2 | 0.012 | 0.0249 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-23 | WTP2 | 0.03 | 0.0449 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-23 | WTP2 | 0.077 | 0.1499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-23 | WTP2 | 0.0064 | 0.0249 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-23 | WTP2 | 0.0075 | 0.0149 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-23 | WTP2 | 0.045 | 0.2499 |  |  | 1Q 28 OF 29 SOCS/WP2-MUST TEST SIM 9/17>6/29/17EM(GLY J QUAL LCS 122% BIASED HIGH-OK BENZO 0.02 J QUAL LCS 131% BIASED HIGH-OK & NOT ABOVE RDL OF 0.02 NO QM RQRD) SIMAZINE MS 0%/MSD 0% RECOV UNACCEP)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-03-23 | WTP5 | 0.025 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-23 | WTP5 | 0.025 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-03-23 | WTP5 | 0.0025 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1010 | BARIUM | N | 0.0062 | MG/L | 2.4999 | 2017-03-23 | WTP5 | 0.005 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-03-23 | WTP5 | 0.0005 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-03-23 | WTP5 | 0.0025 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-03-23 | WTP5 | 0.005 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-03-23 | WTP5 | 0.0005 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-03-23 | WTP5 | 0.0001 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-03-23 | WTP5 | 0.0025 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-03-23 | WTP5 | 0.0025 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1052 | SODIUM | N | 15 | MG/L | 160.4999 | 2017-03-23 | WTP5 | 0.5 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-03-23 | WTP5 | 0.0025 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-03-23 | WTP5 | 0.0005 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-03-23 | WTP5 | 0.0005 |  |  |  | WP5 (NO FL REPORTED)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-03-23 | WTP5 | 0.031 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1022 | COPPER | N | 0.0056 | MG/L | 1.4999 | 2017-03-23 | WTP5 | 0.0046 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-03-23 | WTP5 | 0.02 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-03-23 | WTP5 | 0.0025 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-03-23 | WTP5 | 0.0025 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1095 | ZINC | N | 0.0205 | MG/L | 5.4999 | 2017-03-23 | WTP5 | 0.01 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-03-23 | WTP5 | 5 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.7 | LN(10) |  | 2017-03-23 | WTP5 |  |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 171 | MG/L | 500.4999 | 2017-03-23 | WTP5 | 5 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-03-23 | WTP5 | 0.099 |  |  |  | WP5 (NO CHL NO FL NO SULF NO ODOR) PH ADDED AS RQRD BY PACE LAB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | WTP5 | 0.44 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-23 | WTP5 | 0.25 | 0.5499 |  |  | 3YR 20 OF 21 VOC/WP5 (2378 1 2 4-TRICHLOROBENZENE MISSING) TETRA J QUALIFIER: LCS 134% BIASED SLIGHTLY HIGH (70-130%) - ACCEPTABLE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-26 | WTP5 | 0.41 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-26 | WTP5 | 0.44 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-26 | WTP5 | 0.39 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.78 | UG/L | 60.4999 | 2017-04-26 | L3 | 0.5 |  | 1 | 1.5 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 26.37 | UG/L | 80.4999 | 2017-04-26 | L3 | 0.14 |  | 1 | 1.5 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 21.3 | UG/L | 80.4999 | 2017-04-26 | L4 | 0.14 |  | 2 | 1.6 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.6 | UG/L | 60.4999 | 2017-04-26 | L4 | 0.5 |  | 2 | 1.6 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.91 | UG/L | 60.4999 | 2017-04-26 | L1 | 0.5 |  | 3 | 1.4 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 35.63 | UG/L | 80.4999 | 2017-04-26 | L1 | 0.14 |  | 3 | 1.4 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.47 | UG/L | 60.4999 | 2017-04-26 | L2 | 0.5 |  | 4 | 0.9 | 342 BRANTLEY CLUB PL. (6/17 QTR LRAA/T=41.1175) LRAA > 40 UG/L. SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 46.63 | UG/L | 80.4999 | 2017-04-26 | L2 | 0.14 |  | 4 | 0.9 | 342 BRANTLEY CLUB PL. (6/17 QTR LRAA/T=41.1175) LRAA > 40 UG/L. SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-26 | WTP5 | 0.25 | 0.5499 |  |  | 3YR VOC/WP5 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1017 | CHLORIDE | N | 12.4 | MG/L | 250.4999 | 2017-04-26 | WTP2 | 2.5 |  |  |  | WP2 CHL 12.4 FL 0.58 SULF 5.5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.58 | MG/L | 2.0499 | 2017-04-26 | WTP2 | 0.034 |  |  |  | WP2 CHL 12.4 FL 0.58 SULF 5.5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1055 | SULFATE | N | 5.5 | MG/L | 250.4999 | 2017-04-26 | WTP2 | 2.5 |  |  |  | WP2 CHL 12.4 FL 0.58 SULF 5.5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.58 | MG/L | 4.0499 | 2017-04-26 | WTP2 | 0.034 |  |  |  | WP2 FL 0.58
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.66 | MG/L | 4.0499 | 2017-04-26 | WTP5 | 0.034 |  |  |  | WP5 FL 0.66
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1017 | CHLORIDE | N | 14.8 | MG/L | 250.4999 | 2017-04-26 | WTP5 | 2.5 |  |  |  | WP5 CHL 14.8 FL 0.66 SULF 4.5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.66 | MG/L | 2.0499 | 2017-04-26 | WTP5 | 0.034 |  |  |  | WP5 CHL 14.8 FL 0.66 SULF 4.5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SEC | 1055 | SULFATE | N | 4.5 | MG/L | 250.4999 | 2017-04-26 | WTP5 | 2.5 |  |  |  | WP5 CHL 14.8 FL 0.66 SULF 4.5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-26 | WTP2 | 0.41 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-26 | WTP2 | 0.44 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-26 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-26 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/WP2 (2378 1 2 4-TRI TESTED THIS TIME) VINYL CHLORIDE J QUAL 141% LCSD BIASED HIGH - OK (LCS OK)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-30 | WTP5 | 0.066 | 0.0749 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-30 | WTP2 | 0.07 | 0.0749 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-30 | WTP2 | 0.55 | 2.4999 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-30 | WTP2 | 0.094 | 0.1499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-30 | WTP2 | 0.16 | 0.2499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-30 | WTP2 | 0.032 | 0.1499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-30 | WTP2 | 0.32 | 0.9499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-30 | WTP2 | 0.064 | 0.1499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-30 | WTP2 | 0.035 | 0.2499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-30 | WTP2 | 0.012 | 0.0449 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP2 | 0.003 | 0.0249 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-30 | WTP2 | 0.081 | 0.1499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-30 | WTP2 | 0.16 | 0.2499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-30 | WTP2 | 0.019 | 0.1499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP2 | 0.013 | 0.0249 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-30 | WTP2 | 0.03 | 0.0449 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-30 | WTP2 | 0.081 | 0.1499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP2 | 0.0062 | 0.0249 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-30 | WTP2 | 0.0072 | 0.0149 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-30 | WTP2 | 0.048 | 0.2499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-30 | WTP5 | 0.0067 | 0.0149 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP5 | 0.0029 | 0.0249 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-30 | WTP5 | 0.049 | 0.1499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-30 | WTP5 | 0.58 | 1.4999 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2031 | DALAPON | N | 1.1 | UG/L | 249.9999 | 2017-05-30 | WTP5 | 0.89 | 1.4999 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-30 | WTP5 | 0.3 | 0.4499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-30 | WTP5 | 4.3 | 9.4999 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-30 | WTP5 | 4.2 | 6.4999 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-30 | WTP5 | 0.37 | 0.6499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-30 | WTP5 | 0.55 | 2.4999 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-30 | WTP2 | 0.51 | 0.6499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-30 | WTP5 | 0.48 | 0.6499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-30 | WTP5 | 0.094 | 0.1499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-30 | WTP5 | 0.16 | 0.2499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-30 | WTP5 | 0.031 | 0.1499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-30 | WTP5 | 0.32 | 0.9499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-30 | WTP5 | 0.061 | 0.1499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-30 | WTP5 | 0.034 | 0.2499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-30 | WTP5 | 0.012 | 0.0449 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP5 | 0.0029 | 0.0249 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-30 | WTP5 | 0.081 | 0.1499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-30 | WTP5 | 0.16 | 0.2499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-30 | WTP5 | 0.018 | 0.1499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP5 | 0.012 | 0.0249 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-30 | WTP5 | 0.03 | 0.0449 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-30 | WTP5 | 0.077 | 0.1499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP5 | 0.0062 | 0.0249 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-30 | WTP5 | 0.0072 | 0.0149 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-30 | WTP5 | 0.045 | 0.2499 |  |  | 2Q SOC/WP5(BENZO 0.012 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.022 U <RDL OF 0.024999.BENZ MS/MSD 62%/58%-SUFFICIENT REC RCMMND ACCPTNCE)DAL 1.1-DOES NOT EXCEED RDL OF 1.4999-NO QM RQRD FOR DAL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-30 | WTP2 | 0.0071 | 0.0149 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-30 | WTP2 | 0.003 | 0.0249 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-30 | WTP2 | 0.052 | 0.1499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-30 | WTP2 | 0.62 | 1.4999 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-30 | WTP2 | 0.89 | 1.4999 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-30 | WTP2 | 0.3 | 0.4499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-30 | WTP2 | 4.3 | 9.4999 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-30 | WTP2 | 4.2 | 6.4999 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-30 | WTP2 | 0.39 | 0.6499 |  |  | 2Q SOC/WP2(DIQ 0.30 U J QUAL MS 69%RECOV-AT 100% RSLT CLOSE TO 0.44 U <RDL OF 0.4999&MSD 79% PASSED.BENZO 0.013 U J QUAL LCS 54%RECOV AT 100% RSLT CLOSE TO 0.024 U <RDL OF 0.0249.RCMMND BOTH BE ACCPTD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-07-27 | WTP2 | 0.068 | 0.0749 |  |  | 2Q 1 OF 29 SOC SIM-WP2 7/17 (1Q SIM-WP2 WAS TKN IN 5/17) 3/17 SIM-WP2 HAD MS/MSD 0/0% RECOV & WAS UNACCEP - THIS IS THE RETEST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.01 | UG/L | 80.4999 | 2017-07-27 | L3 | 0.14 |  | 1 | 0.8 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.25 | UG/L | 60.4999 | 2017-07-27 | L2 | 0.5 |  | 4 | 0.6 | 342 BRANTLEY CLUB PL.(9/17 DB RPRT RCVD 9/17 LRAAS/T 4 SITES=RANGE FROM 27-49 LRAAS/H RANGE FROM 13-23)LRAA>40 UG/L.SYS. DOES NOT QUALIFY FOR R.M.NO LRAA MCLS OR OE EXCEEDANCES.HYPRLNKD 8/18/17.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 31.8 | UG/L | 80.4999 | 2017-07-27 | L4 | 0.14 |  | 3 | 0.6 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.55 | UG/L | 60.4999 | 2017-07-27 | L3 | 0.5 |  | 1 | 0.8 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 72.31 | UG/L | 80.4999 | 2017-07-27 | L2 | 0.14 |  | 4 | 0.6 | 342 BRANTLEY CLUB PL.(9/17 DB RPRT RCVD 9/17 LRAAS/T 4 SITES=RANGE FROM 27-49 LRAAS/H RANGE FROM 13-23)LRAA>40 UG/L.SYS. DOES NOT QUALIFY FOR R.M.NO LRAA MCLS OR OE EXCEEDANCES.HYPRLNKD 8/18/17.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.67 | UG/L | 60.4999 | 2017-07-27 | L1 | 0.5 |  | 2 | 1 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 55.2 | UG/L | 80.4999 | 2017-07-27 | L1 | 0.14 |  | 2 | 1 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.41 | UG/L | 60.4999 | 2017-07-27 | L4 | 0.5 |  | 3 | 0.6 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 30.25 | UG/L | 80.4999 | 2017-11-01 | L4 | 0.14 |  | 3 | 0.86 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 24.09 | UG/L | 80.4999 | 2017-11-01 | L3 | 0.14 |  | 1 | 1.18 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 47.01 | UG/L | 80.4999 | 2017-11-01 | L2 | 0.14 |  | 4 | 0.92 | 342 BRANTLEY CLUB PL. (12/17 DB REPORT RCVD W/RSLTS) NO LRAA MCLS OR OE EXCEEDANCES - DOES NOT QUALIFY FOR R.M. (HYPERLINKED TO BW 12-11-17 - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.12 | UG/L | 60.4999 | 2017-11-01 | L2 | 0.5 |  | 4 | 0.92 | 342 BRANTLEY CLUB PL. (12/17 DB REPORT RCVD W/RSLTS) NO LRAA MCLS OR OE EXCEEDANCES - DOES NOT QUALIFY FOR R.M. (HYPERLINKED TO BW 12-11-17 - BB)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14 | UG/L | 60.4999 | 2017-11-01 | L3 | 0.5 |  | 1 | 1.18 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.03 | UG/L | 60.4999 | 2017-11-01 | L4 | 0.5 |  | 3 | 0.86 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 42.45 | UG/L | 80.4999 | 2017-11-01 | L1 | 0.14 |  | 2 | 0.7 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.49 | UG/L | 60.4999 | 2017-11-01 | L1 | 0.5 |  | 2 | 0.7 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.29 | UG/L | 60.4999 | 2018-01-30 | L2 | 0.5 |  | 4 | 1.1 | 342 BRANTLEY CLUB PL. (2/22/18 HPRLNKD TO BW - BB) NO 3/18 DISINF BYP REPORT RCVD W/RSLTS YET (DUE BY 4/10/18)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 31.88 | UG/L | 80.4999 | 2018-01-30 | L4 | 0.14 |  | 3 | 0.6 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.52 | UG/L | 60.4999 | 2018-01-30 | L4 | 0.5 |  | 3 | 0.6 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 42.06 | UG/L | 80.4999 | 2018-01-30 | L1 | 0.14 |  | 2 | 0.5 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.33 | UG/L | 60.4999 | 2018-01-30 | L1 | 0.5 |  | 2 | 0.5 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 34.27 | UG/L | 80.4999 | 2018-01-30 | L3 | 0.14 |  | 1 | 1.1 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.38 | UG/L | 60.4999 | 2018-01-30 | L3 | 0.5 |  | 1 | 1.1 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 44.56 | UG/L | 80.4999 | 2018-01-30 | L2 | 0.14 |  | 4 | 1.1 | 342 BRANTLEY CLUB PL. (2/22/18 HPRLNKD TO BW - BB) NO 3/18 DISINF BYP REPORT RCVD W/RSLTS YET (DUE BY 4/10/18)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.58 | UG/L | 60.4999 | 2018-05-02 | L1 |  |  |  | 1.4 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.56 | UG/L | 60.4999 | 2018-05-02 | L3 |  |  |  | 1.5 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.56 | UG/L | 80.4999 | 2018-05-02 | L4 |  |  |  | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.39 | UG/L | 60.4999 | 2018-05-02 | L4 |  |  |  | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.15 | UG/L | 80.4999 | 2018-05-02 | L1 |  |  |  | 1.4 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.67 | UG/L | 80.4999 | 2018-05-02 | L3 |  |  |  | 1.5 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 70.67 | UG/L | 80.4999 | 2018-05-02 | L2 |  |  |  | 1.1 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.16 | UG/L | 60.4999 | 2018-05-02 | L2 |  |  |  | 1.1 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-06-20 | WTP2 |  |  |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-06-20 | WTP5 |  |  |  |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-06-20 | WTP5 |  |  |  |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-06-20 | WTP2 |  |  |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.89 | UG/L | 60.4999 | 2018-07-25 | L3 | 0.91 |  | 1 | 1.2 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 13.33 | UG/L | 80.4999 | 2018-07-25 | L3 | 0.14 |  | 1 | 1.2 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.59 | UG/L | 60.4999 | 2018-07-25 | L1 | 0.91 |  | 2 | 0.9 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 25.25 | UG/L | 80.4999 | 2018-07-25 | L1 | 0.14 |  | 2 | 0.9 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.41 | UG/L | 60.4999 | 2018-07-25 | L4 | 0.91 |  | 3 | 1 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 26.62 | UG/L | 80.4999 | 2018-07-25 | L4 | 0.14 |  | 3 | 1 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.23 | UG/L | 60.4999 | 2018-07-25 | L2 | 0.91 |  | 4 | 1.3 | 342 BRANTLEY CLUB PLACE (HLKD 8-16-18 - BB) 9/18 QTR DISINF BYP RPRT RCVD WITH LAB RSLTS
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.09 | UG/L | 80.4999 | 2018-07-25 | L2 | 0.39 |  | 4 | 1.3 | 342 BRANTLEY CLUB PLACE (HLKD 8-16-18 - BB) 9/18 QTR DISINF BYP RPRT RCVD WITH LAB RSLTS
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 35.08 | UG/L | 80.4999 | 2018-10-24 | L3 |  |  |  | 1.4 | 2950-1021 ARDEN ST. / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.21 | UG/L | 60.4999 | 2018-10-24 | L1 |  |  |  | 0.8 | 2950-235 S. WYMORE / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 76.47 | UG/L | 80.4999 | 2018-10-24 | L1 |  |  |  | 0.8 | 2950-235 S. WYMORE / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.52 | UG/L | 60.4999 | 2018-10-24 | L4 |  |  |  | 1.5 | 2950-496 CENTRAL PARKWAY / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2450 | MONOCHLORACETIC ACID | D | 0.74 | UG/L |  | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | D | 0 | UG/L |  | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | D | 0.77 | UG/L |  | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | D | 0 | UG/L | 100 | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | D | 0 | UG/L |  | 2018-10-24 | L1 |  |  | 2 | 0.8 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | D | 0.87 | UG/L |  | 2018-10-24 | L1 |  |  | 2 | 0.8 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | D | 0 | UG/L | 100 | 2018-10-24 | L1 |  |  | 2 | 0.8 | 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | D | 0 | UG/L |  | 2018-10-24 | L4 |  |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | D | 0 | UG/L |  | 2018-10-24 | L4 |  |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | D | 0 | UG/L | 100 | 2018-10-24 | L4 |  |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | D | 0.83 | UG/L |  | 2018-10-24 | L2 |  |  | 4 | 0.93 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | D | 0.83 | UG/L |  | 2018-10-24 | L2 |  |  | 4 | 0.93 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | D | 0 | UG/L | 100 | 2018-10-24 | L2 |  |  | 4 | 0.93 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2450 | MONOCHLORACETIC ACID | N | 0.74 | UG/L |  | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | N | 0 | UG/L |  | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | N | 0.77 | UG/L |  | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | N | 0 | UG/L | 100 | 2018-10-24 | L3 |  |  | 1 | 1.4 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | N | 0 | UG/L |  | 2018-10-24 | L1 |  |  | 2 | 0.8 | 235 S. WYMORE **DEP APPROVED TO REPLACE THE 235 S WYMORE LOCATION (DEMOLISHED) WITH 235 W SR 436 (ACROSS THE STREET) AND KEPT THE LOCATION LABELED AS L1 BEGINNING JAN 2019**JMF
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | N | 0.87 | UG/L |  | 2018-10-24 | L1 |  |  | 2 | 0.8 | 235 S. WYMORE **DEP APPROVED TO REPLACE THE 235 S WYMORE LOCATION (DEMOLISHED) WITH 235 W SR 436 (ACROSS THE STREET) AND KEPT THE LOCATION LABELED AS L1 BEGINNING JAN 2019**JMF
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | N | 0 | UG/L | 100 | 2018-10-24 | L1 |  |  | 2 | 0.8 | 235 S. WYMORE **DEP APPROVED TO REPLACE THE 235 S WYMORE LOCATION (DEMOLISHED) WITH 235 W SR 436 (ACROSS THE STREET) AND KEPT THE LOCATION LABELED AS L1 BEGINNING JAN 2019**JMF
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | N | 0 | UG/L |  | 2018-10-24 | L4 |  |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | N | 0 | UG/L |  | 2018-10-24 | L4 |  |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | N | 0 | UG/L | 100 | 2018-10-24 | L4 |  |  | 3 | 1.5 | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2453 | MONOBROMACETIC ACID | D | 0.83 | UG/L |  | 2018-10-24 | L3 |  |  | 4 | 0.93 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2454 | DIBROMOACETIC ACID | D | 0.83 | UG/L |  | 2018-10-24 | L3 |  |  | 4 | 0.93 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2942 | BROMOFORM | D | 0 | UG/L | 100 | 2018-10-24 | L3 |  |  | 4 | 0.93 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.37 | UG/L | 60.4999 | 2018-10-24 | L3 |  |  |  | 1.4 | 2950-1021 ARDEN ST. / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 77.75 | UG/L | 80.4999 | 2018-10-24 | L2 |  |  |  | 0.9 | 2950-342 BRANTLEY CLUB PLACE / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2450 | MONOCHLORACETIC ACID | D | 0.74 | UG/L |  | 2018-10-24 | L3 |  |  | 4 | 0.93 | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 48.62 | UG/L | 80.4999 | 2018-10-24 | L4 |  |  |  | 1.5 | 2950-496 CENTRAL PARKWAY / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.31 | UG/L | 60.4999 | 2018-10-24 | L2 |  |  |  | 0.9 | 2950-342 BRANTLEY CLUB PLACE / SUBCONTRACT LAB E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2019-01-09 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-01-09 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.43 | UG/L | 80.4999 | 2019-01-23 | L3 | 0.39 |  | 3 | 1.1 | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.18 | UG/L | 60.4999 | 2019-01-23 | L3 | 0.91 |  | 3 | 1.1 | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.02 | UG/L | 80.4999 | 2019-01-23 | L4 | 0.39 |  | 2 | 0.8 | 496 CENTRAL PKWY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.34 | UG/L | 60.4999 | 2019-01-23 | L4 | 0.91 |  | 2 | 0.8 | 496 CENTRAL PKWY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.88 | UG/L | 60.4999 | 2019-01-23 | L1 | 0.91 |  | 1 | 0.8 | 230 (235?) W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.9 | UG/L | 80.4999 | 2019-01-23 | L1 | 0.39 |  | 1 | 0.8 | 230 (235?) W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 29.3 | UG/L | 80.4999 | 2019-01-23 | L2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.59 | UG/L | 60.4999 | 2019-01-23 | L2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.43 | UG/L | 80.4999 | 2019-01-23 | L3
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.18 | UG/L | 60.4999 | 2019-01-23 | L3
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.02 | UG/L | 80.4999 | 2019-01-23 | L4
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.34 | UG/L | 60.4999 | 2019-01-23 | L4
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.9 | UG/L | 80.4999 | 2019-01-23 | L1
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 29.3 | UG/L | 80.4999 | 2019-01-23 | L2 | 0.39 |  | 4 | 0.9 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.59 | UG/L | 60.4999 | 2019-01-23 | L2 | 0.91 |  | 4 | 0.9 | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-01-23 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-01-23 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.88 | UG/L | 60.4999 | 2019-01-23 | L1
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-02-06 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-02-06 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2019-02-20 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2019-02-20 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2019-03-06 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-03-06 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0.014 | MG/L | 10.4999 | 2019-03-11 | WTP5 |  |  |  |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-03-11 | WTP2 |  |  |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1040 | NITRATE | N | 0.006 | MG/L | 10.4999 | 2019-03-11 | WTP2 |  |  |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-03-11 | WTP5 |  |  |  |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-03-20 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-03-20 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2019-04-03 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-04-03 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-04-17 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-04-17 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.34 | UG/L | 80.4999 | 2019-04-24 | L3
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.78 | UG/L | 60.4999 | 2019-04-24 | L3
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 46.06 | UG/L | 80.4999 | 2019-04-24 | L4
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.21 | UG/L | 60.4999 | 2019-04-24 | L4
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.04 | UG/L | 80.4999 | 2019-04-24 | L1
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.02 | UG/L | 60.4999 | 2019-04-24 | L1
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 46.06 | UG/L | 80.4999 | 2019-04-24 | L4 |  |  | 3 | 0.9 | 496 CENTRAL PARKWAY / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.34 | UG/L | 80.4999 | 2019-04-24 | L3 |  |  | 4 | 0.8 | 1021 ARDEN ST. / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.78 | UG/L | 60.4999 | 2019-04-24 | L3 |  |  | 4 | 0.8 | 1021 ARDEN ST. / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.21 | UG/L | 60.4999 | 2019-04-24 | L4 |  |  | 3 | 0.9 | 496 CENTRAL PARKWAY / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.04 | UG/L | 80.4999 | 2019-04-24 | L1 |  |  | 2 | 0.9 | 235 W SR 436 REPLACED 235 S. WYMORE / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.02 | UG/L | 60.4999 | 2019-04-24 | L1 |  |  | 2 | 0.9 | 235 W SR 436 REPLACED 235 S. WYMORE / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.67 | UG/L | 60.4999 | 2019-04-24 | L2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 57.08 | UG/L | 80.4999 | 2019-04-24 | L2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.67 | UG/L | 60.4999 | 2019-04-24 | L2 |  |  | 1 | 0.6 | 342 BRANTLEY CLUB PLACE / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 57.08 | UG/L | 80.4999 | 2019-04-24 | L2 |  |  | 1 | 0.6 | 342 BRANTLEY CLUB PLACE / SUBCONTRACT LABS E82535 AND E84589
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2019-05-01 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-05-01 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-05-15 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-05-15 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2019-05-29 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2019-05-29 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2019-06-12 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-06-12 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2019-06-26 | WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-06-26 | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.24 | UG/L | 60.4999 | 2019-07-24 | L3 |  |  | 4 | 1 | 1021 ARDEN ST. / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 31.21 | UG/L | 80.4999 | 2019-07-24 | L3 |  |  | 4 | 1 | 1021 ARDEN ST. / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 50.57 | UG/L | 80.4999 | 2019-07-24 | L4 |  |  | 3 | 1 | 496 CENTRAL PARKWAY / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.75 | UG/L | 60.4999 | 2019-07-24 | L4 |  |  | 3 | 1 | 496 CENTRAL PARKWAY / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 47.13 | UG/L | 80.4999 | 2019-07-24 | L1 |  |  | 2 | 0.4 | 235 W SR 436 REPLACED 235 S. WYMORE / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.17 | UG/L | 60.4999 | 2019-07-24 | L1 |  |  | 2 | 0.4 | 235 W SR 436 REPLACED 235 S. WYMORE / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 49.87 | UG/L | 80.4999 | 2019-07-24 | L2 |  |  | 1 | 0.8 | 342 BRANTLEY CLUB PLACE / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.33 | UG/L | 60.4999 | 2019-07-24 | L2 |  |  | 1 | 0.8 | 342 BRANTLEY CLUB PLACE / SUBCONTRACT LABS E84589 82535
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.3 | UG/L | 60.4999 | 2019-10-23 | L3 | 0.9 |  | 4 | 1.1 | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 31.8 | UG/L | 80.4999 | 2019-10-23 | L3 | 0.32 |  | 4 | 1.1 | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 44.4 | UG/L | 80.4999 | 2019-10-23 | L1 | 0.32 |  | 2 | 0.7 | 235 (230 ON REPORT) W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.8 | UG/L | 60.4999 | 2019-10-23 | L4 | 0.9 |  | 3 | 0.8 | 496 CENTRAL PKWY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 42.6 | UG/L | 80.4999 | 2019-10-23 | L4 | 0.32 |  | 3 | 0.8 | 496 CENTRAL PKWY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.1 | UG/L | 60.4999 | 2019-10-23 | L1 | 0.9 |  | 2 | 0.7 | 235 (230 ON REPORT) W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.3 | UG/L | 60.4999 | 2019-10-23 | L2 | 0.9 |  | 1 | 1 | 842 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | DBP | 2950 | TOTAL THMS | D | 46 | UG/L | 80.4999 | 2019-10-23 | L2 | 0.32 |  | 1 | 1 | 842 BRANTLEY CLUB PLACE
3590039 | APPLE VALLEY (CONSEC) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | AAA |  |  |  |  | (6/18/15 PER MFC 2 VISITS PER WEEK - MINIMUM RQRMNT - NOW THAT IT'S CONSEC) DAV SENT EM 6/18/15 AT 12:37 PM EDT THAT "APPLE VALLEY HAS NOW BEEN CONVERTED IN DEP'S DATABASE TO A CONSECUTIVE SYS."
3590039 | APPLE VALLEY (CONSEC) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-11 | AAA |  |  |  |  | (6/18/15 PER MFC 2 VISITS PER WEEK - MINIMUM RQRMNT - NOW THAT IT'S CONSEC) DAV SENT EM 6/18/15 AT 12:37 PM EDT THAT "APPLE VALLEY HAS NOW BEEN CONVERTED IN DEP'S DATABASE TO A CONSECUTIVE SYS."
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.94 | UG/L | 60.4999 | 2015-07-15 | L1 |  |  |  | 0.52 | AV-12 350 VIRGINIA AVE. (HI T LRAA) (NEXT ROUTINE TEST DUE @ 2ND WEEK 7/16 @ THE SAME 2 SITES) NO MCLS OR OE EXCEEDANCES
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 24.88 | UG/L | 80.4999 | 2015-07-15 | L2 |  |  |  | 0.64 | AV-6 561 E. OAKHURST ST. (HI H LRAA) (NEXT ROUTINE TEST DUE @ 2ND WEEK 7/16 @ THE SAME 2 SITES) NO MCLS OR OE EXCEEDANCES
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.12 | UG/L | 60.4999 | 2015-07-15 | L2 |  |  |  | 0.64 | AV-6 561 E. OAKHURST ST. (HI H LRAA) (NEXT ROUTINE TEST DUE @ 2ND WEEK 7/16 @ THE SAME 2 SITES) NO MCLS OR OE EXCEEDANCES
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 58.58 | UG/L | 80.4999 | 2015-07-15 | L1 |  |  |  | 0.52 | AV-12 350 VIRGINIA AVE. (HI T LRAA) (NEXT ROUTINE TEST DUE @ 2ND WEEK 7/16 @ THE SAME 2 SITES) NO MCLS OR OE EXCEEDANCES
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 54.73 | UG/L | 80.4999 | 2016-07-14 | L1 | 0.14 |  | 2 | 0.6 | AV-12 350 VIRGINIA AVE. (REMAIN ON ROUTINE ANNUAL TESTING 2 SITES DUAL SAMPLES) POP. 3 232 (T ALWAYS > 40) CANNOT GO TO REDUCED NO MCL OR OE EXCEEDANCES
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.17 | UG/L | 60.4999 | 2016-07-14 | L1 | 0.2 |  | 2 | 0.6 | AV-12 350 VIRGINIA AVE. (REMAIN ON ROUTINE ANNUAL TESTING 2 SITES DUAL SAMPLES) POP. 3 232 (T ALWAYS > 40) CANNOT GO TO REDUCED NO MCL OR OE EXCEEDANCES
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 46.07 | UG/L | 80.4999 | 2016-07-14 | L2 | 0.14 |  | 1 | 0.84 | AV-6 561 E. OAKHURST ST.
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.78 | UG/L | 60.4999 | 2016-07-14 | L2 | 0.2 |  | 1 | 0.84 | AV-6 561 E. OAKHURST ST.
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 40.75 | UG/L | 80.4999 | 2017-07-13 | L2 | 0.14 |  | 1 | 0.99 | 561 E. OAKHURST ST. (HYPERLINKED 8/9/17 TO BW-BB) 8/9/17 E. WMS. SCES ADVISED BY BW 8/9/17 TO REMAIN ON ROUTINE ANNUAL MONITORING-BB.
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 62.18 | UG/L | 80.4999 | 2017-07-13 | L1 | 0.14 |  | 2 | 0.38 | 350 VIRGINIA AVE.(J QUAL 2453 BROM.ACID MS 137%-OK)REMAIN ON ROUTINE ANNUAL TESTING 2 SITES DUAL SMPLS IN 2018)POP.3 232(T>40 SINCE STG2 STARTED ON ROUTINE-CANNOT GO TO REDUCED)NO MCL OR OE EXCDNCS
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.61 | UG/L | 60.4999 | 2017-07-13 | L2 | 0.5 |  | 1 | 0.99 | 561 E. OAKHURST ST. (HYPERLINKED 8/9/17 TO BW-BB) 8/9/17 E. WMS. SCES ADVISED BY BW 8/9/17 TO REMAIN ON ROUTINE ANNUAL MONITORING-BB.
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.55 | UG/L | 60.4999 | 2017-07-13 | L1 | 0.5 |  | 2 | 0.38 | 350 VIRGINIA AVE.(J QUAL 2453 BROM.ACID MS 137%-OK)REMAIN ON ROUTINE ANNUAL TESTING 2 SITES DUAL SMPLS IN 2018)POP.3 232(T>40 SINCE STG2 STARTED ON ROUTINE-CANNOT GO TO REDUCED)NO MCL OR OE EXCDNCS
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.26 | UG/L | 60.4999 | 2018-07-12 | L2 | 0.91 |  | 1 | 0.66 | 561 E. OAKHURST ST.
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 34.52 | UG/L | 80.4999 | 2018-07-12 | L2 | 0.14 |  | 1 | 0.66 | 561 E. OAKHURST ST.
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 38.66 | UG/L | 80.4999 | 2018-07-12 | L1 | 0.14 |  | 2 | 0.43 | 350 VIRGINIA AVE. (HLKD 8-22-18 QUALIFIES FOR R.M. ANNUALLY)
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.73 | UG/L | 60.4999 | 2018-07-12 | L1 | 0.91 |  | 2 | 0.43 | 350 VIRGINIA AVE. (HLKD 8-22-18 QUALIFIES FOR R.M. ANNUALLY)
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 47.15 | UG/L | 80.4999 | 2019-07-11 | L1 | 0.39 |  | 1 | 0.75 | 350 VIRGINIA AVE. (HLKD)
3590039 | APPLE VALLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 38.46 | UG/L | 80.4999 | 2019-07-11 | L2 | 0.39 |  | 2 | 0.97 | 561 E. OAKHURST ST. (HLKD)
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.38 | UG/L | 60.4999 | 2019-07-11 | L1 | 0.91 |  | 1 | 0.75 | 350 VIRGINIA AVE. (HLKD)
3590039 | APPLE VALLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.32 | UG/L | 60.4999 | 2019-07-11 | L2 | 0.91 |  | 2 | 0.97 | 561 E. OAKHURST ST. (HLKD)
3590069 | BEAR LAKE MANOR | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-02-17 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590069 | BEAR LAKE MANOR | RAD | 4020 | RADIUM-226 | N | 0.8 | PCI/L | 3.4999 | 2015-02-17 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590069 | BEAR LAKE MANOR | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1010 | BARIUM | N | 0.0075 | MG/L | 2.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1025 | FLUORIDE | N | 0.202 | MG/L | 4.0499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1036 | NICKEL | N | 0.0011 | MG/L | 0.1499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1052 | SODIUM | N | 18.7 | MG/L | 160.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1017 | CHLORIDE | N | 30 | MG/L | 250.4999 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1025 | FLUORIDE | N | 0.202 | MG/L | 2.0499 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1028 | IRON | N | 0.0403 | MG/L | 0.3499 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1055 | SULFATE | N | 8.92 | MG/L | 250.4999 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1095 | ZINC | N | 0.0145 | MG/L | 5.4999 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.11 | LN(10) |  | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 204 | MG/L | 500.4999 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-02-17 | AAA
3590069 | BEAR LAKE MANOR | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-17 | AAA |  | 0.0149
3590069 | BEAR LAKE MANOR | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249
3590069 | BEAR LAKE MANOR | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-17 | AAA |  | 0.1499
3590069 | BEAR LAKE MANOR | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 1.4999
3590069 | BEAR LAKE MANOR | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-02-17 | AAA |  | 1.4999
3590069 | BEAR LAKE MANOR | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-17 | AAA |  | 0.4499
3590069 | BEAR LAKE MANOR | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-17 | AAA |  | 9.4999
3590069 | BEAR LAKE MANOR | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-17 | AAA |  | 6.4999
3590069 | BEAR LAKE MANOR | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-02-17 | AAA |  | 0.6499
3590069 | BEAR LAKE MANOR | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-17 | AAA |  | 2.4999
3590069 | BEAR LAKE MANOR | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-17 | AAA |  | 0.0749
3590069 | BEAR LAKE MANOR | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-02-17 | AAA |  | 0.6499
3590069 | BEAR LAKE MANOR | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-17 | AAA |  | 0.1499
3590069 | BEAR LAKE MANOR | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-17 | AAA |  | 0.2499
3590069 | BEAR LAKE MANOR | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-17 | AAA |  | 0.1499
3590069 | BEAR LAKE MANOR | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-17 | AAA |  | 0.9499
3590069 | BEAR LAKE MANOR | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 0.1499
3590069 | BEAR LAKE MANOR | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-17 | AAA |  | 0.2499
3590069 | BEAR LAKE MANOR | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-17 | AAA |  | 0.0449
3590069 | BEAR LAKE MANOR | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249
3590069 | BEAR LAKE MANOR | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-17 | AAA |  | 0.1499
3590069 | BEAR LAKE MANOR | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-17 | AAA |  | 0.2499
3590069 | BEAR LAKE MANOR | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-17 | AAA |  | 0.1499
3590069 | BEAR LAKE MANOR | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249
3590069 | BEAR LAKE MANOR | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-17 | AAA |  | 0.0449
3590069 | BEAR LAKE MANOR | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-17 | AAA |  | 0.1499
3590069 | BEAR LAKE MANOR | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249
3590069 | BEAR LAKE MANOR | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-17 | AAA |  | 0.0149
3590069 | BEAR LAKE MANOR | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-17 | AAA |  | 0.2499
3590069 | BEAR LAKE MANOR | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.2 | PCI/L | 15.4999 | 2015-02-17 | AAA |  |  |  |  | RADS DUE 2021
3590069 | BEAR LAKE MANOR | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H-2 SITES-DUE 2ND WEEK 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590069 | BEAR LAKE MANOR | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-23 | AAA |  | 0.5499
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 124 | UG/L | 60.4999 | 2015-08-12 | L1 |  |  |  | 2.8 | 3701 ANNA DRIVE (QM/T+H>9/18/15EM>GONGRE) **SEE GONGRE'S 9/3/15 EM: H 124 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 52 | UG/L | 80.4999 | 2015-08-12 | L1 |  |  |  | 2.8 | 3701 ANNA DRIVE (QM/T+H>9/18/15EM>GONGRE) **SEE GONGRE'S 9/3/15 EM: H 124 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 112 | UG/L | 60.4999 | 2015-08-12 | L2 |  |  |  | 2.8 | 1207 ALTON DRIVE (QM/T+H>9/18/15EM>GONGRE) **SEE GONGRE'S 9/3/15 EM: H 124 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 71.7 | UG/L | 80.4999 | 2015-08-12 | L2 |  |  |  | 2.8 | 1207 ALTON DRIVE (QM/T+H>9/18/15EM>GONGRE) **SEE GONGRE'S 9/3/15 EM: H 124 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 41 | UG/L | 80.4999 | 2015-11-11 | L1 |  |  |  | 1.9 | 3701 ANNA DR. (12/15 LRAA/T=23.25 LRAA/H=35.425)
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.7 | UG/L | 60.4999 | 2015-11-11 | L1 |  |  |  | 1.9 | 3701 ANNA DR. (12/15 LRAA/T=23.25 LRAA/H=35.425)
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 45.8 | UG/L | 80.4999 | 2015-11-11 | L2 |  |  |  | 2.2 | 1207 ALTON DR. (12/15 LRAA/T=29.375 LRAA/H=31.675) 3/21 EW HAS 2/16 DBPS (FROM LISA AUGUST SCES)
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.7 | UG/L | 60.4999 | 2015-11-11 | L2 |  |  |  | 2.2 | 1207 ALTON DR. (12/15 LRAA/T=29.375 LRAA/H=31.675) 3/21 EW HAS 2/16 DBPS (FROM LISA AUGUST SCES)
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 43.9 | UG/L | 80.4999 | 2016-02-09 | L2 |  |  |  | 3 | 1207 ALTON DRIVE (3/16 LRAA/T=40.35 LRAA/H=37.55) NO MCLS OR OE EXCEEDANCES ***8/18 EW HAS 5/16 T/H FOR ENTRY-ALREADY IN OC
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.5 | UG/L | 60.4999 | 2016-02-09 | L2 |  |  |  | 3 | 1207 ALTON DRIVE (3/16 LRAA/T=40.35 LRAA/H=37.55) NO MCLS OR OE EXCEEDANCES ***8/18 EW HAS 5/16 T/H FOR ENTRY-ALREADY IN OC
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28 | UG/L | 60.4999 | 2016-02-09 | L1 |  |  |  | 2.6 | 3701 ANNA DRIVE (3/16 LRAA/T=33.125 LRAA/H=42.425) NO MCLS OR OE EXCEEDANCES
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 39.5 | UG/L | 80.4999 | 2016-02-09 | L1 |  |  |  | 2.6 | 3701 ANNA DRIVE (3/16 LRAA/T=33.125 LRAA/H=42.425) NO MCLS OR OE EXCEEDANCES
3590069 | BEAR LAKE MANOR | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-25 | AAA |  |  |  |  | 16 DONE
3590069 | BEAR LAKE MANOR | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-25 | AAA |  |  |  |  | 16 DONE
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 66 | UG/L | 80.4999 | 2016-05-10 | L2 |  |  |  | 1.8 | 1207 ALTON DRIVE (6/16 LRAA/T= 56.85 LRAA/H=47.75) 8/18/16 EM>CONT. QM/T+H DURING 9/16 QTR - NOT ON ANNUAL
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.8 | UG/L | 60.4999 | 2016-05-10 | L2 |  |  |  | 1.8 | 1207 ALTON DRIVE (6/16 LRAA/T= 56.85 LRAA/H=47.75) 8/18/16 EM>CONT. QM/T+H DURING 9/16 QTR - NOT ON ANNUAL
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 57.1 | UG/L | 80.4999 | 2016-05-10 | L1 |  |  |  | 1.6 | 3701 ANNA DRIVE (6/16 LRAA/T=47.4 LRAA/H=48.35) 8/18/16 EM>CONT. QM/T+H DURING 9/16 QTR - NOT ON ANNUAL
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.7 | UG/L | 60.4999 | 2016-05-10 | L1 |  |  |  | 1.6 | 3701 ANNA DRIVE (6/16 LRAA/T=47.4 LRAA/H=48.35) 8/18/16 EM>CONT. QM/T+H DURING 9/16 QTR - NOT ON ANNUAL
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 46.3 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 2 | 3701 ANNA DRIVE (CONTINUE) QUARTERLY MONITORING 4Q 2016)
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 81.3 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 2 | 3701 ANNA DRIVE (CONTINUE) QUARTERLY MONITORING 4Q 2016)
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 46.9 | UG/L | 60.4999 | 2016-08-10 | L2 |  |  |  | 1.8 | ON ROUTINE MONITORING. SAMPLE 3Q 2017
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 73.5 | UG/L | 80.4999 | 2016-08-10 | L2 |  |  |  | 1.8 | ON ROUTINE MONITORING. SAMPLE 3Q 2017
3590069 | BEAR LAKE MANOR | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590069 | BEAR LAKE MANOR | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 63.4 | UG/L | 80.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 3.1 | 1207 ALTON (HYPERLINKED 9/29/17 TO BW - BB)
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 66.8 | UG/L | 80.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.7 | 3701 ANNA
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44.6 | UG/L | 60.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 3.1 | 1207 ALTON (HYPERLINKED 9/29/17 TO BW - BB)
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.8 | UG/L | 60.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.7 | 3701 ANNA
3590069 | BEAR LAKE MANOR | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-02-19 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-02-19 | AAA | 0.05 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 1.4999 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-02-19 | AAA | 0.1 | 1.4999 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-02-19 | AAA | 0.4 | 0.4499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 9 | 9.4999 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-02-19 | AAA | 6 | 6.4999 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-02-19 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-02-19 | AAA | 2 | 2.4999 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-02-19 | AAA | 0.07 | 0.0749 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-02-19 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-02-19 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-02-19 | AAA | 0.9 | 0.9499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-02-19 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-02-19 | AAA | 0.01 | 0.0449 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-02-19 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.04 | 0.0449 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-02-19 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-02-19 | AAA | 0.01 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590069 | BEAR LAKE MANOR | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-19 | AAA | 0.2 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-19 | AAA | 0.2 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1010 | BARIUM | N | 0.0073 | MG/L | 2.4999 | 2018-02-19 | AAA | 0.002 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-19 | AAA | 0.005 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-02-19 | AAA | 0.2 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1030 | LEAD | N | 0.0052 | MG/L | 0.0154 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-19 | AAA | 2e-05 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-19 | AAA | 0.002 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1052 | SODIUM | N | 17.4 | MG/L | 160.4999 | 2018-02-19 | AAA | 0.5 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-19 | AAA | 0.0005 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC.
3590069 | BEAR LAKE MANOR | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-19 | AAA | 0.02
3590069 | BEAR LAKE MANOR | SEC | 1017 | CHLORIDE | N | 27.2 | MG/L | 250.4999 | 2018-02-19 | AAA | 0.4
3590069 | BEAR LAKE MANOR | SEC | 1022 | COPPER | N | 0.0025 | MG/L | 1.4999 | 2018-02-19 | AAA | 0.001
3590069 | BEAR LAKE MANOR | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-02-19 | AAA | 0.4
3590069 | BEAR LAKE MANOR | SEC | 1028 | IRON | N | 0.0469 | MG/L | 0.3499 | 2018-02-19 | AAA | 0.01
3590069 | BEAR LAKE MANOR | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-02-19 | AAA | 0.01
3590069 | BEAR LAKE MANOR | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-19 | AAA | 0.0005
3590069 | BEAR LAKE MANOR | SEC | 1055 | SULFATE | N | 11.4 | MG/L | 250.4999 | 2018-02-19 | AAA | 1
3590069 | BEAR LAKE MANOR | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-02-19 | AAA | 0.01
3590069 | BEAR LAKE MANOR | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-19 | AAA | 5
3590069 | BEAR LAKE MANOR | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-19 | AAA | 1
3590069 | BEAR LAKE MANOR | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.84 | LN(10) |  | 2018-02-19 | AAA | 0.01
3590069 | BEAR LAKE MANOR | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 303 | MG/L | 500.4999 | 2018-02-19 | AAA | 2.5
3590069 | BEAR LAKE MANOR | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-19 | AAA | 0.2
3590069 | BEAR LAKE MANOR | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-19 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 48.3 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.8
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41.2 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.8
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.4 | UG/L | 60.4999 | 2018-08-07 | L2 | 0.5 |  | 1 | 3
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 41.2 | UG/L | 80.4999 | 2018-08-07 | L2 | 0.5 |  | 1 | 3
3590069 | BEAR LAKE MANOR | INOR | 1040 | NITRATE | N | 0.0207 | MG/L | 10.4999 | 2019-02-26 | AAA
3590069 | BEAR LAKE MANOR | INOR | 1041 | NITRITE | N | 0.0205 | MG/L | 1.4999 | 2019-02-26 | AAA
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.6 | UG/L | 60.4999 | 2019-08-12 | L1 | 1 |  | 1 | 3.4 | 3701 ANNA DR.
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 55.7 | UG/L | 80.4999 | 2019-08-12 | L1 | 0.5 |  | 1 | 3.4 | 3701 ANNA DR.
3590069 | BEAR LAKE MANOR | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49.5 | UG/L | 60.4999 | 2019-08-12 | L2 | 1 |  | 2 | 3.4 | 1207 ALTON DR. (**2461 DIC ACID HAS J QUALIFIER** - NO EXPLANATION PROVIDED ON INITIAL LAB REPORT) EXP. GIVEN. ACCEPTED
3590069 | BEAR LAKE MANOR | DBP | 2950 | TOTAL THMS | D | 51.9 | UG/L | 80.4999 | 2019-08-12 | L2 | 0.5 |  | 2 | 3.4 | 1207 ALTON DR. (**2461 DIC ACID HAS J QUALIFIER** - NO EXPLANATION PROVIDED ON INITIAL LAB REPORT) EXP. GIVEN. ACCEPTED
3590111 | DRUID HILLS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-11 | AAA
3590111 | DRUID HILLS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | AAA
3590111 | DRUID HILLS | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.1499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-07-08 | AAA |  | 0.0249 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.0449 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-07-08 | AAA |  | 0.1499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-07-08 | AAA |  | 0.0249 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-07-08 | AAA |  | 0.0149 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-07-08 | AAA |  | 0.4499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1010 | BARIUM | N | 0.0048 | MG/L | 2.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-07-08 | AAA |  | 0.2499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-07-08 | AAA |  | 6.4999 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-07-08 | AAA |  |  |  |  | RADS DUE 2021
3590111 | DRUID HILLS | RAD | 4020 | RADIUM-226 | N | 0.9 | PCI/L | 3.4999 | 2015-07-08 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590111 | DRUID HILLS | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-07-08 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590111 | DRUID HILLS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-07-08 | AAA |  | 0.0149 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-07-08 | AAA |  | 0.0249 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-07-08 | AAA |  | 0.1499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 1.4999 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-07-08 | AAA |  | 1.4999 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | INOR | 1025 | FLUORIDE | N | 0.24 | MG/L | 4.0499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1036 | NICKEL | N | 0.0029 | MG/L | 0.1499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1052 | SODIUM | N | 15 | MG/L | 160.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1074 | ANTIMONY | N | 0.0002 | MG/L | 0.0065 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1017 | CHLORIDE | N | 24 | MG/L | 250.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1025 | FLUORIDE | N | 0.24 | MG/L | 2.0499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1032 | MANGANESE | N | 0.001 | MG/L | 0.0549 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1055 | SULFATE | N | 11 | MG/L | 250.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1095 | ZINC | N | 0.005 | MG/L | 5.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.876 | LN(10) |  | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 220 | MG/L | 500.4999 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-08 | AAA |  |  |  |  | NO MCLS
3590111 | DRUID HILLS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 9.4999 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-07-08 | AAA |  | 0.6499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-07-08 | AAA |  | 2.4999 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-07-08 | AAA |  | 0.0749 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-07-08 | AAA |  | 0.6499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-07-08 | AAA |  | 0.1499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-07-08 | AAA |  | 0.2499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-07-08 | AAA |  | 0.1499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-07-08 | AAA |  | 0.9499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.1499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-07-08 | AAA |  | 0.2499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-07-08 | AAA |  | 0.0449 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-07-08 | AAA |  | 0.0249 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.1499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-07-08 | AAA |  | 0.2499 |  |  | 3YR SOC (ALL OK)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.96 | UG/L | 60.4999 | 2015-07-15 | L1 |  |  |  | 1.19 | (11/20/15 EW HAS 10/15 T/H @ 2 SITES) DH9 YORK WAY@WOOD LAKE DR.(DUALSMP)(8/3/15&9/9/15 EM TO E.WMS S.MCFARLAND>TEST QTRLY FOR T/H BOTH SITES 12/15 QTR & UFN E.WMS.ACKNOWLEDGED QM/T+H BY EM 9/10/15)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 47.18 | UG/L | 80.4999 | 2015-07-15 | L2 |  |  |  | 0.83 | DH4 1215 TRINITY WAY (DUAL SMP) (8/3/15 & 9/9/15 EM TO E.WMS S.MCFARLAND>TEST QTRLY FOR T/H BOTH SITES 12/15 QTR & UFN)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.94 | UG/L | 60.4999 | 2015-07-15 | L2 |  |  |  | 0.83 | DH4 1215 TRINITY WAY (DUAL SMP) (8/3/15 & 9/9/15 EM TO E.WMS S.MCFARLAND>TEST QTRLY FOR T/H BOTH SITES 12/15 QTR & UFN)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 81.32 | UG/L | 80.4999 | 2015-07-15 | L1 |  |  |  | 1.19 | (11/20/15 EW HAS 10/15 T/H @ 2 SITES) DH9 YORK WAY@WOOD LAKE DR.(DUALSMP)(8/3/15&9/9/15 EM TO E.WMS S.MCFARLAND>TEST QTRLY FOR T/H BOTH SITES 12/15 QTR & UFN E.WMS.ACKNOWLEDGED QM/T+H BY EM 9/10/15)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 50.76 | UG/L | 80.4999 | 2015-10-15 | L1 |  |  |  | 1.5 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) (CONT. TO TEST QUARTERLY @ 2 SITES DUE TO TTHMS L1 SINGLE EXCEEDANCE 7/15)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.33 | UG/L | 60.4999 | 2015-10-15 | L1 |  |  |  | 1.5 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) (CONT. TO TEST QUARTERLY @ 2 SITES DUE TO TTHMS L1 SINGLE EXCEEDANCE 7/15)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 48.92 | UG/L | 80.4999 | 2015-10-15 | L2 |  |  |  | 1.63 | DH4 1215 TRINITY WAY (DUAL SMP) (CONT. TO TEST QUARTERLY @ 2 SITES DUE TO TTHMS L1 SINGLE EXCEEDANCE 7/15)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.6 | UG/L | 60.4999 | 2015-10-15 | L2 |  |  |  | 1.63 | DH4 1215 TRINITY WAY (DUAL SMP) (CONT. TO TEST QUARTERLY @ 2 SITES DUE TO TTHMS L1 SINGLE EXCEEDANCE 7/15)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.65 | UG/L | 60.4999 | 2016-01-14 | L1 |  |  |  | 1.27 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) (NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 51.76 | UG/L | 80.4999 | 2016-01-14 | L2 |  |  |  | 1.34 | DH4 1215 TRINITY WAY (DUAL SMP) NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.6 | UG/L | 60.4999 | 2016-01-14 | L2 |  |  |  | 1.34 | DH4 1215 TRINITY WAY (DUAL SMP) NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 51.57 | UG/L | 80.4999 | 2016-01-14 | L1 |  |  |  | 1.27 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) (NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE)
3590111 | DRUID HILLS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-19 | AAA
3590111 | DRUID HILLS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-01-19 | AAA
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.41 | UG/L | 60.4999 | 2016-04-13 | L2 |  |  |  | 1.04 | DH4 1215 TRINITY WAY (DUAL SMP) (6/16 LRAA/T=50.245 LRAA/H=27.1375) NO LRAA MCLS 6/16 QTR (T<60 H<45) QTRLY MONITORING ENDS - ANNUAL T/H DUE 7-9/16
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 52.35 | UG/L | 80.4999 | 2016-04-13 | L1 |  |  |  | 0.95 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) (6/16 LRAA/T=59 LRAA/H=28.1825) NO LRAA MCLS 6/16 QTR (T<60 H<45) QTRLY MONITORING ENDS - ANNUAL T/H DUE 7-9/16
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.79 | UG/L | 60.4999 | 2016-04-13 | L1 |  |  |  | 0.95 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) (6/16 LRAA/T=59 LRAA/H=28.1825) NO LRAA MCLS 6/16 QTR (T<60 H<45) QTRLY MONITORING ENDS - ANNUAL T/H DUE 7-9/16
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 53.12 | UG/L | 80.4999 | 2016-04-13 | L2 |  |  |  | 1.04 | DH4 1215 TRINITY WAY (DUAL SMP) (6/16 LRAA/T=50.245 LRAA/H=27.1375) NO LRAA MCLS 6/16 QTR (T<60 H<45) QTRLY MONITORING ENDS - ANNUAL T/H DUE 7-9/16
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 63.79 | UG/L | 80.4999 | 2016-07-14 | L1 | 0.14 |  | 1 | 1.02 | ON ANN. T/H - DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) 9/16/16 EM TO ELSA WMS ANN. T/H DUE JULY 2017 - 2 SITES. (QTRLY MONITORING ENDED 6/16 QTR) BB
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.97 | UG/L | 60.4999 | 2016-07-14 | L1 | 0.2 |  | 1 | 1.02 | ON ANN. T/H - DH9 YORK WAY @ WOOD LAKE DR. (DUAL SMP) 9/16/16 EM TO ELSA WMS ANN. T/H DUE JULY 2017 - 2 SITES. (QTRLY MONITORING ENDED 6/16 QTR) BB
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 56.74 | UG/L | 80.4999 | 2016-07-14 | L2 | 0.14 |  | 2 | 1.01 | ON ANN. T/H - DH4 1215 TRINITY WAY (DUAL SMP) 9/16/16 EM TO ELSA WMS ANN. T/H DUE JULY 2017 - 2 SITES. (QTRLY MONITORING ENDED 6/16 QTR) BB
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.35 | UG/L | 60.4999 | 2016-07-14 | L2 | 0.2 |  | 2 | 1.01 | ON ANN. T/H - DH4 1215 TRINITY WAY (DUAL SMP) 9/16/16 EM TO ELSA WMS ANN. T/H DUE JULY 2017 - 2 SITES. (QTRLY MONITORING ENDED 6/16 QTR) BB
3590111 | DRUID HILLS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-08 | AAA | 0.051 |  |  |  | NN (HYPERLINKED 3/8/17 TO BW-BB)
3590111 | DRUID HILLS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-08 | AAA | 0.053 |  |  |  | NN (HYPERLINKED 3/8/17 TO BW-BB)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 101.12 | UG/L | 80.4999 | 2017-07-13 | L2 | 0.14 |  | 1 | 0.93 | 1215 TRINITY WAY (TTHMS 101.12 - TRIGGERS QUARTERLY TESTING) HYPERLINKED 8/10/17 TO BW - BB
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.16 | UG/L | 60.4999 | 2017-07-13 | L2 | 0.5 |  | 1 | 0.93 | 1215 TRINITY WAY (TTHMS 101.12 - TRIGGERS QUARTERLY TESTING) HYPERLINKED 8/10/17 TO BW - BB
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 60.11 | UG/L | 80.4999 | 2017-07-13 | L1 | 0.14 |  | 2 | 1.18 | YORK WAY @ WOOD LAKE DR. (START QM/DBPS DUE TO TRINITY TTHMS 101.12 UG/L)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.91 | UG/L | 60.4999 | 2017-07-13 | L1 | 0.5 |  | 2 | 1.18 | YORK WAY @ WOOD LAKE DR. (START QM/DBPS DUE TO TRINITY TTHMS 101.12 UG/L)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.01 | UG/L | 60.4999 | 2017-10-12 | L2 | 0.5 |  | 2 | 1.39 | 2QM-1215 TRINITY WAY (CONTINUE QM/DBPS) HYPERLINKED TO BW 1-2-18 - BB
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 46.65 | UG/L | 80.4999 | 2017-10-12 | L2 | 0.31 |  | 2 | 1.39 | 2QM-1215 TRINITY WAY (CONTINUE QM/DBPS) HYPERLINKED TO BW 1-2-18 - BB
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 47.76 | UG/L | 80.4999 | 2017-10-12 | L1 | 0.31 |  | 1 | 1.54 | 2QM-YORK WAY @ WOOD LAKE DR. (CONTINUE QM/DBPS) HYPERLINKED TO BW 1-2-18 - BB
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.69 | UG/L | 60.4999 | 2017-10-12 | L1 | 0.5 |  | 1 | 1.54 | 2QM-YORK WAY @ WOOD LAKE DR. (CONTINUE QM/DBPS) HYPERLINKED TO BW 1-2-18 - BB
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.99 | UG/L | 60.4999 | 2018-01-11 | L1 | 0.5 |  | 2 | 1.84 | YORK WAY @ WOOD LAKE DR. (AFTER ONLY 3 QTRS 3/18 LRAA/T = 40.1775 HAA5S LOW)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 53.15 | UG/L | 80.4999 | 2018-01-11 | L2 | 0.14 |  | 1 | 1.76 | 1215 TRINITY WAY (AFTER ONLY 3 QTRS 3/18 LRAA/T=50.23 HAA5S LOW)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.87 | UG/L | 60.4999 | 2018-01-11 | L2 | 0.5 |  | 1 | 1.76 | 1215 TRINITY WAY (AFTER ONLY 3 QTRS 3/18 LRAA/T=50.23 HAA5S LOW)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 52.84 | UG/L | 80.4999 | 2018-01-11 | L1 | 0.14 |  | 2 | 1.84 | YORK WAY @ WOOD LAKE DR. (AFTER ONLY 3 QTRS 3/18 LRAA/T = 40.1775 HAA5S LOW)
3590111 | DRUID HILLS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-15 | AAA | 0.053 |  |  |  | NN
3590111 | DRUID HILLS | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2018-02-15 | AAA | 0.051 |  |  |  | NN
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 49.31 | UG/L | 80.4999 | 2018-04-12 | L2 |  |  |  | 1.67 | DH4 1215 TRINITY WAY (DUAL SMP) LRAA/T AFTER 4 QTRS=62.5575
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.84 | UG/L | 60.4999 | 2018-04-12 | L2 |  |  |  | 1.67 | DH4 1215 TRINITY WAY (DUAL SMP) LRAA/T AFTER 4 QTRS=62.5575
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.65 | UG/L | 60.4999 | 2018-04-12 | L1 |  |  |  | 1.57 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SM
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 51.58 | UG/L | 80.4999 | 2018-04-12 | L1 |  |  |  | 1.57 | DH9 YORK WAY @ WOOD LAKE DR. (DUAL SM
3590111 | DRUID HILLS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-05-10 | AAA | 1.5 | 0.6499
3590111 | DRUID HILLS | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-05-10 | AAA | 0.23 | 0.1499
3590111 | DRUID HILLS | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-05-10 | AAA | 0.86 | 0.2499
3590111 | DRUID HILLS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-05-10 | AAA | 0.012 | 0.1499
3590111 | DRUID HILLS | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-05-10 | AAA | 0.28 | 0.9499
3590111 | DRUID HILLS | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-05-10 | AAA | 0.16 | 0.1499
3590111 | DRUID HILLS | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-05-10 | AAA | 0.26 | 0.2499
3590111 | DRUID HILLS | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-05-10 | AAA | 0.006 | 0.0449
3590111 | DRUID HILLS | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-05-10 | AAA | 0.0052 | 0.0249
3590111 | DRUID HILLS | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-05-10 | AAA | 1.5 | 0.1499
3590111 | DRUID HILLS | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-05-10 | AAA | 0.32 | 0.2499
3590111 | DRUID HILLS | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-05-10 | AAA | 0.0063 | 0.1499
3590111 | DRUID HILLS | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-05-10 | AAA | 0.096 | 0.0249
3590111 | DRUID HILLS | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-05-10 | AAA | 0.069 | 0.0449
3590111 | DRUID HILLS | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-05-10 | AAA | 0.11 | 0.1499
3590111 | DRUID HILLS | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-05-10 | AAA | 0.006 | 0.0249
3590111 | DRUID HILLS | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-05-10 | AAA | 0.0062 | 0.0149
3590111 | DRUID HILLS | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-05-10 | AAA | 0.053 | 0.2499
3590111 | DRUID HILLS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-10 | AAA | 0.28 | 0.5499
3590111 | DRUID HILLS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-10 | AAA | 0.32 | 0.5499
3590111 | DRUID HILLS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-10 | AAA | 0.28 | 0.5499
3590111 | DRUID HILLS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-10 | AAA | 0.44 | 0.5499
3590111 | DRUID HILLS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-10 | AAA | 0.46 | 0.5499
3590111 | DRUID HILLS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-10 | AAA | 0.26 | 0.5499
3590111 | DRUID HILLS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-10 | AAA | 0.2 | 0.5499
3590111 | DRUID HILLS | SEC | 1055 | SULFATE | N | 11 | MG/L | 250.4999 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1095 | ZINC | N | 0.033 | MG/L | 5.4999 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.31 | LN(10) |  | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 230 | MG/L | 500.4999 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 2905 | FOAMING AGENTS | N | 0.04 |  | 0.5499 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | INOR | 1040 | NITRATE | N | 0.17 | MG/L | 10.4999 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1041 | NITRITE | N | 0.053 | MG/L | 1.4999 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1005 | ARSENIC | N | 0.0001 | MG/L | 0.0104 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1010 | BARIUM | N | 0.0051 | MG/L | 2.4999 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1015 | CADMIUM | N | 0.0005 | MG/L | 0.0055 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1020 | CHROMIUM | N | 0.0016 | MG/L | 0.1499 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1024 | CYANIDE | N | 0.0048 | MG/L | 0.2499 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1025 | FLUORIDE | N | 0.26 | MG/L | 4.0499 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1030 | LEAD | N | 0.0002 | MG/L | 0.0154 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1036 | NICKEL | N | 0.006 | MG/L | 0.1499 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1045 | SELENIUM | N | 0.0006 | MG/L | 0.0549 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1052 | SODIUM | N | 16 | MG/L | 160.4999 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1074 | ANTIMONY | N | 0.0001 | MG/L | 0.0065 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1075 | BERYLLIUM | N | 0.0004 | MG/L | 0.0045 | 2018-05-10 | AAA
3590111 | DRUID HILLS | INOR | 1085 | THALLIUM | N | 0.0001 | MG/L | 0.0025 | 2018-05-10 | AAA
3590111 | DRUID HILLS | SEC | 1002 | ALUMINUM | N | 0.028 | MG/L | 0.2499 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1017 | CHLORIDE | N | 25 | MG/L | 250.4999 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1022 | COPPER | N | 0.0035 | MG/L | 1.4999 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1025 | FLUORIDE | N | 0.26 | MG/L | 2.0499 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1028 | IRON | N | 0.1 | MG/L | 0.3499 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1032 | MANGANESE | N | 0.0019 | MG/L | 0.0549 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | SEC | 1050 | SILVER | N | 0.0001 | MG/L | 0.1499 | 2018-05-10 | AAA |  |  |  |  | SULFATE WITH J4 QUALIFIER - ACCEPTABLE; PH WITH Q QUALIFIER - ACCEPTABLE_RLB
3590111 | DRUID HILLS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-10 | AAA | 0.18 | 0.5499
3590111 | DRUID HILLS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-10 | AAA | 0.28 | 0.5499
3590111 | DRUID HILLS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-10 | AAA | 0.36 | 0.5499
3590111 | DRUID HILLS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-10 | AAA | 0.39 | 0.5499
3590111 | DRUID HILLS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-10 | AAA | 0.23 | 0.5499
3590111 | DRUID HILLS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-10 | AAA | 0.26 | 0.5499
3590111 | DRUID HILLS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-10 | AAA | 0.28 | 0.5499
3590111 | DRUID HILLS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-10 | AAA | 0.12 | 0.5499
3590111 | DRUID HILLS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-10 | AAA | 0.24 | 0.5499
3590111 | DRUID HILLS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-10 | AAA | 0.12 | 0.5499
3590111 | DRUID HILLS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-10 | AAA | 0.17 | 0.5499
3590111 | DRUID HILLS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-10 | AAA | 0.22 | 0.5499
3590111 | DRUID HILLS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-10 | AAA | 0.17 | 0.5499
3590111 | DRUID HILLS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-10 | AAA | 0.39 | 0.5499
3590111 | DRUID HILLS | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-05-10 | AAA | 0.0069 | 0.0149
3590111 | DRUID HILLS | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-05-10 | AAA | 0.0071 | 0.0249
3590111 | DRUID HILLS | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-05-10 | AAA | 0.0068 | 0.1499
3590111 | DRUID HILLS | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-05-10 | AAA | 0.12 | 1.4999
3590111 | DRUID HILLS | SOC | 2031 | DALAPON | N | 2.3 | UG/L | 249.9999 | 2018-05-10 | AAA | 1 | 1.4999
3590111 | DRUID HILLS | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-05-10 | AAA | 7.6 | 0.4499
3590111 | DRUID HILLS | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-05-10 | AAA | 1.8 | 9.4999
3590111 | DRUID HILLS | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-05-10 | AAA | 6.5 | 6.4999
3590111 | DRUID HILLS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-05-10 | AAA | 0.95 | 0.6499
3590111 | DRUID HILLS | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-05-10 | AAA | 0.57 | 2.4999
3590111 | DRUID HILLS | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-05-10 | AAA | 0.19 | 0.0749
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 54.26 | UG/L | 80.4999 | 2018-07-12 | L1 | 0.14 |  | 2 | 0.75 | QM-YORK WAY & WOOD LAKE DR. (DUAL SMP) HLKD 8/22/18 QUALIFIES TO RETURN TO ROUTINE TESTING ANNUAL (>500)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.31 | UG/L | 60.4999 | 2018-07-12 | L2 | 0.91 |  | 1 | 0.83 | QM-1215 TRINITY WAY (DUAL SMP)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.58 | UG/L | 60.4999 | 2018-07-12 | L1 | 0.91 |  | 2 | 0.75 | QM-YORK WAY & WOOD LAKE DR. (DUAL SMP) HLKD 8/22/18 QUALIFIES TO RETURN TO ROUTINE TESTING ANNUAL (>500)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 49.09 | UG/L | 80.4999 | 2018-07-12 | L2 | 0.14 |  | 1 | 0.83 | QM-1215 TRINITY WAY (DUAL SMP)
3590111 | DRUID HILLS | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-01-31 | AAA |  | 1.4999 |  |  | 1QM - START OF DALAPON QUARTERLY SAMPLES DUE TO DETECT 5/18_RLB (MISSED 2 QUARTERS IN 2018)
3590111 | DRUID HILLS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-14 | AAA
3590111 | DRUID HILLS | INOR | 1040 | NITRATE | N | 0.46 | MG/L | 10.4999 | 2019-02-14 | AAA
3590111 | DRUID HILLS | SOC | 2031 | DALAPON | N | 1.1 | UG/L | 249.9999 | 2019-04-15 | AAA |  | 1.4999 |  |  | 2QM DALAPON (3QM NEXT DUE 7-9/19)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.59 | UG/L | 60.4999 | 2019-07-11 | L1 | 0.91 |  | 2 | 1.09 | YORK WAY @ WOOD LAKE DR. (HLKD)
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 35.83 | UG/L | 80.4999 | 2019-07-11 | L1 | 0.39 |  | 2 | 1.09 | YORK WAY @ WOOD LAKE DR. (HLKD)
3590111 | DRUID HILLS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.71 | UG/L | 60.4999 | 2019-07-11 | L2 | 0.91 |  | 1 | 0.81 | 1215 TRINITY WAY
3590111 | DRUID HILLS | DBP | 2950 | TOTAL THMS | D | 49.82 | UG/L | 80.4999 | 2019-07-11 | L2 | 0.39 |  | 1 | 0.81 | 1215 TRINITY WAY
3590111 | DRUID HILLS | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-07-31 | AAA |  | 1.4999 |  |  | 3QM DALAPON (4QM NEXT DUE 10-12/19)
3590111 | DRUID HILLS | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-10-09 | AAA |  | 1.4999
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.059 | MG/L | 10.4999 | 2015-01-07 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-07 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.094 | MG/L | 10.4999 | 2015-01-07 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-07 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.061 | MG/L | 10.4999 | 2015-01-07 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-07 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-01-07 | WTP2 |  | 0.5499 |  |  | SPECIAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.61 | UG/L | 60.4999 | 2015-02-16 | L3 |  |  |  | 2.6 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.58 | UG/L | 60.4999 | 2015-02-16 | L1 |  |  |  | 1.8 | CWP4 1811 DOVER RD. (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 59.16 | UG/L | 80.4999 | 2015-02-16 | L2 |  |  |  | 1 | 261 LYMAN (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD (***INFORMATIONAL PURPOSES TTHM TKN AT 7603 CITRUS ON 4/16/15 ONLY-NOTIFICATION BY EM 4/16/15 FROM FERNGREN JENNIFER. BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 4.06 | UG/L | 80.4999 | 2015-02-16 | L3 |  |  |  | 2.6 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.06 | UG/L | 60.4999 | 2015-02-16 | L2 |  |  |  | 1 | 261 LYMAN (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD (***INFORMATIONAL PURPOSES TTHM TKN AT 7603 CITRUS ON 4/16/15 ONLY-NOTIFICATION BY EM 4/16/15 FROM FERNGREN JENNIFER. BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 49.14 | UG/L | 80.4999 | 2015-02-16 | L4 |  |  |  | 2.1 | 5401 LAKE HOWELL (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.75 | UG/L | 60.4999 | 2015-02-16 | L4 |  |  |  | 2.1 | 5401 LAKE HOWELL (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 45.77 | UG/L | 80.4999 | 2015-02-16 | L1 |  |  |  | 1.8 | CWP4 1811 DOVER RD. (NO LRAA OR OE EXCEEDANCES) 3/15 DBF RCVD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 34.87 | UG/L | 80.4999 | 2015-05-12 | L1 |  |  |  | 1.8 | CWP4 1811 DOVER RD. (NO LRAA OR OE EXCEEDANCES 6/15 QTR)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.45 | UG/L | 60.4999 | 2015-05-12 | L2 |  |  |  | 0.9 | CWP5 261 LYMAN RD. (NOT DR.) (NO LRAA OR OE EXCEEDANCES 6/15 QTR)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.84 | UG/L | 60.4999 | 2015-05-12 | L1 |  |  |  | 1.8 | CWP4 1811 DOVER RD. (NO LRAA OR OE EXCEEDANCES 6/15 QTR)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 31.82 | UG/L | 80.4999 | 2015-05-12 | L4 |  |  |  | 2.1 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (NO LRAA OR OE EXCEEDANCES 6/15 QTR) >>>>>9/28 EW HAS 8/15 DBPS & DBF (ALL OK)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 56.33 | UG/L | 80.4999 | 2015-05-12 | L2 |  |  |  | 0.9 | CWP5 261 LYMAN RD. (NOT DR.) (NO LRAA OR OE EXCEEDANCES 6/15 QTR)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.64 | UG/L | 60.4999 | 2015-05-12 | L3 |  |  |  | 2.1 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (NO LRAA OR OE EXCEEDANCES 6/15 QTR)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.19 | UG/L | 60.4999 | 2015-05-12 | L4 |  |  |  | 2.1 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (NO LRAA OR OE EXCEEDANCES 6/15 QTR) >>>>>9/28 EW HAS 8/15 DBPS & DBF (ALL OK)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 38.2 | UG/L | 80.4999 | 2015-05-12 | L3 |  |  |  | 2.1 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (NO LRAA OR OE EXCEEDANCES 6/15 QTR)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 49.33 | UG/L | 80.4999 | 2015-08-19 | L4 |  |  |  | 1.3 | (1/25/16 EW HAS 11/15 DBPS&4TH QTR 2015 DBF-ASKD J.FERNGREN FOR MS/MSD FOR 2 HAA CITRUS AVE. 1/25/16EM) CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.42 | UG/L | 60.4999 | 2015-08-19 | L2 |  |  |  | 1.2 | CWP5 261 LYMAN RD. (NOT DR.) (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.28 | UG/L | 80.4999 | 2015-08-19 | L3 |  |  |  | 1.1 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.43 | UG/L | 60.4999 | 2015-08-19 | L3 |  |  |  | 1.1 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 68.52 | UG/L | 80.4999 | 2015-08-19 | L2 |  |  |  | 1.2 | CWP5 261 LYMAN RD. (NOT DR.) (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 39.03 | UG/L | 80.4999 | 2015-08-19 | L1 |  |  |  | 1.2 | CWP4 1811 DOVER RD. (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.29 | UG/L | 60.4999 | 2015-08-19 | L4 |  |  |  | 1.3 | (1/25/16 EW HAS 11/15 DBPS&4TH QTR 2015 DBF-ASKD J.FERNGREN FOR MS/MSD FOR 2 HAA CITRUS AVE. 1/25/16EM) CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.06 | UG/L | 60.4999 | 2015-08-19 | L1 |  |  |  | 1.2 | CWP4 1811 DOVER RD. (DOES NOT QUALIFY FOR R.M. NO LRAA OR OE EXCEEDANCES)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.16 | UG/L | 60.4999 | 2015-11-10 | L3 |  |  |  | 1.2 | CWP2STG1 7603 CITRUS AVE. W.P.(DOES NOT QUALIFY FOR R.M.)J QUAL:2450 MONOCHLOR.ACID & 2454 DIBROM.ACID. LCS OK MS RECOV.LOW FOR 2450(MS 50/MSD 40)BUT OK SINCE RSLT IS SO LOW. 2454 ACCEPTABLE(MS 132%)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 70 | UG/L | 80.4999 | 2015-11-10 | L2 |  |  |  | 0.4 | CWP5 261 LYMAN RD. (NOT DR.) (DOES NOT QUALITY FOR REDUCED MONITORING)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.69 | UG/L | 80.4999 | 2015-11-10 | L4 |  |  |  | 1.1 | (4/27 EW HAS 3/16 DBPS & DB REPORT) CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (DOES NOT QUALIFY FOR REDUCED MONITORING)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 49.79 | UG/L | 80.4999 | 2015-11-10 | L1 |  |  |  | 1.1 | CWP4 1811 DOVER RD. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.38 | UG/L | 60.4999 | 2015-11-10 | L1 |  |  |  | 1.1 | CWP4 1811 DOVER RD. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 55.31 | UG/L | 80.4999 | 2015-11-10 | L3 |  |  |  | 1.2 | CWP2STG1 7603 CITRUS AVE. W.P.(DOES NOT QUALIFY FOR R.M.)J QUAL:2450 MONOCHLOR.ACID & 2454 DIBROM.ACID. LCS OK MS RECOV.LOW FOR 2450(MS 50/MSD 40)BUT OK SINCE RSLT IS SO LOW. 2454 ACCEPTABLE(MS 132%)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.68 | UG/L | 60.4999 | 2015-11-10 | L4 |  |  |  | 1.1 | (4/27 EW HAS 3/16 DBPS & DB REPORT) CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (DOES NOT QUALIFY FOR REDUCED MONITORING)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.72 | UG/L | 60.4999 | 2015-11-10 | L2 |  |  |  | 0.4 | CWP5 261 LYMAN RD. (NOT DR.) (DOES NOT QUALITY FOR REDUCED MONITORING)
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-12 | WTP1 |  |  |  |  | HOWELL PARK WP NN
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-01-12 | WTP1 |  |  |  |  | HOWELL PARK WP NN
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-12 | WTP3 |  |  |  |  | SOUTH WP NN (J QUAL NO2: 79%/81% MS/MSD - SUFFICIENT RECOVERY FOR ACCEPTANCE)
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.33 | MG/L | 10.4999 | 2016-01-12 | WTP3 |  |  |  |  | SOUTH WP NN (J QUAL NO2: 79%/81% MS/MSD - SUFFICIENT RECOVERY FOR ACCEPTANCE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-01-12 | WTP2 |  |  |  |  | NORTH WP NN
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-12 | WTP2 |  |  |  |  | NORTH WP NN
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-01-12 | WTP2 |  | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.87 | UG/L | 80.4999 | 2016-02-09 | L1 |  |  |  | 1.6 | CWP4 1811 DOVER RD. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES (6/16 LRAA/T=46.48 ROUNDED & CK'D LRAA/H=22.03 ROUNDED & CK'D)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 40.1 | UG/L | 80.4999 | 2016-02-09 | L3 |  |  |  | 1.9 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.3 | UG/L | 60.4999 | 2016-02-09 | L3 |  |  |  | 1.9 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48.43 | UG/L | 80.4999 | 2016-02-09 | L2 |  |  |  | 1.5 | CWP5 261 LYMAN RD. (NOT DR.) (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.47 | UG/L | 60.4999 | 2016-02-09 | L4 |  |  |  | 1.2 | (5/20 EWHAS 5/16 DBPS W/ERRANT DB REPORT) CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES (J.FERNGREN LEFT 5/1/16-ADDRESS ALL TO STEVE BAGGS SHE SAID)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.7 | UG/L | 60.4999 | 2016-02-09 | L1 |  |  |  | 1.6 | CWP4 1811 DOVER RD. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES (6/16 LRAA/T=46.48 ROUNDED & CK'D LRAA/H=22.03 ROUNDED & CK'D)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 47.16 | UG/L | 80.4999 | 2016-02-09 | L4 |  |  |  | 1.2 | (5/20 EWHAS 5/16 DBPS W/ERRANT DB REPORT) CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES (J.FERNGREN LEFT 5/1/16-ADDRESS ALL TO STEVE BAGGS SHE SAID)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.13 | UG/L | 60.4999 | 2016-02-09 | L2 |  |  |  | 1.5 | CWP5 261 LYMAN RD. (NOT DR.) (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 53.21 | UG/L | 80.4999 | 2016-05-04 | L1 |  |  |  | 0.9 | CWP4 1811 DOVER RD. (6/16 LRAA/T=46.48 ROUNDED & CK'D LRAA/H=22.03 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.28 | UG/L | 60.4999 | 2016-05-04 | L2 |  |  |  | 1 | CWP5 261 LYMAN RD. (6/16 LRAA/T=61.81 ROUNDED & CK'D LRAA/H=31.39 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.98 | UG/L | 60.4999 | 2016-05-04 | L1 |  |  |  | 0.9 | CWP4 1811 DOVER RD. (6/16 LRAA/T=46.48 ROUNDED & CK'D LRAA/H=22.03 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 44.72 | UG/L | 80.4999 | 2016-05-04 | L4 |  |  |  | 1.6 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (6/16 LRAA/T=47.98 ROUNDED & CK'D (47.99 ON DBF) LRAA/H=26.20 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.34 | UG/L | 60.4999 | 2016-05-04 | L4 |  |  |  | 1.6 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (6/16 LRAA/T=47.98 ROUNDED & CK'D (47.99 ON DBF) LRAA/H=26.20 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 56.38 | UG/L | 80.4999 | 2016-05-04 | L3 |  |  |  | 1.6 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (6/16 LRAA/T=50.52 ROUNDED & CK'D LRAA/H=27.74 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.06 | UG/L | 60.4999 | 2016-05-04 | L3 |  |  |  | 1.6 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (6/16 LRAA/T=50.52 ROUNDED & CK'D LRAA/H=27.74 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 60.29 | UG/L | 80.4999 | 2016-05-04 | L2 |  |  |  | 1 | CWP5 261 LYMAN RD. (6/16 LRAA/T=61.81 ROUNDED & CK'D LRAA/H=31.39 ROUNDED & CK'D) DOES NOT QUALIFY FOR R.M. - LYMAN LRAA/T=61.81.
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.7 |  |  | 2016-07-12 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 112 | MG/L |  | 2016-07-12 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.07 | LN(10) |  | 2016-07-12 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-07-12 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.7 |  |  | 2016-07-12 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 117 | MG/L |  | 2016-07-12 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.87 | LN(10) |  | 2016-07-12 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.5 | MG/L |  | 2016-07-12 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.9 |  |  | 2016-07-12 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 103 | MG/L |  | 2016-07-12 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-07-12 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.79 | LN(10) |  | 2016-07-12 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.6 | MG/L |  | 2016-07-28 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.8 |  |  | 2016-07-28 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 8.09 | LN(10) |  | 2016-07-28 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 99 | MG/L |  | 2016-07-28 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.7 |  |  | 2016-07-28 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 97 | MG/L |  | 2016-07-28 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.82 | LN(10) |  | 2016-07-28 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.8 | MG/L |  | 2016-07-28 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 26.2 |  |  | 2016-07-28 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 1 | MG/L |  | 2016-07-28 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.75 | LN(10) |  | 2016-07-28 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 101 | MG/L |  | 2016-07-28 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-08-08 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 110 | MG/L |  | 2016-08-08 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-08-08 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.03 | LN(10) |  | 2016-08-08 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.7 |  |  | 2016-08-08 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-08-08 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.3 |  |  | 2016-08-08 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 99 | MG/L |  | 2016-08-08 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-08-08 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-08-08 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 122 | MG/L |  | 2016-08-08 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.6 |  |  | 2016-08-08 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.06 | UG/L | 60.4999 | 2016-08-10 | L3 |  |  |  | 1.2 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (3RD QTR 2016 LRAA/T=50.245 LRAA/H=26.237) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.63 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 1.4 | CWP4 1811 DOVER RD. (3RD QTR 2016 LRAA/T=45.875 LRAA/H=25.9725) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 51.42 | UG/L | 80.4999 | 2016-08-10 | L4 |  |  |  | 1.1 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (3RD QTR 2016 LRAA/T=48.4975 LRAA/H=31.43) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.39 | UG/L | 60.4999 | 2016-08-10 | L4 |  |  |  | 1.1 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. (3RD QTR 2016 LRAA/T=48.4975 LRAA/H=31.43) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 60.57 | UG/L | 80.4999 | 2016-08-10 | L2 |  |  |  | 0.6 | CWP5 261 LYMAN RD. (NOT DR.) (3RD QTR 2016 LRAA/T=59.82 LRAA/H=31.43) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 49.19 | UG/L | 80.4999 | 2016-08-10 | L3 |  |  |  | 1.2 | CWP2STG1 7603 CITRUS AVE. WINTER PARK (3RD QTR 2016 LRAA/T=50.245 LRAA/H=26.237) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.19 | UG/L | 60.4999 | 2016-08-10 | L2 |  |  |  | 0.6 | CWP5 261 LYMAN RD. (NOT DR.) (3RD QTR 2016 LRAA/T=59.82 LRAA/H=31.43) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.75 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 1.4 | CWP4 1811 DOVER RD. (3RD QTR 2016 LRAA/T=45.875 LRAA/H=25.9725) DOES NOT QUALIFY FOR RM.
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.9 | MG/L |  | 2016-08-23 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.7 | LN(10) |  | 2016-08-23 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 102 | MG/L |  | 2016-08-23 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.9 |  |  | 2016-08-23 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.7 | MG/L |  | 2016-08-23 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.8 |  |  | 2016-08-23 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 120 | MG/L |  | 2016-08-23 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.9 |  |  | 2016-08-23 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.6 | MG/L |  | 2016-08-23 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 8.07 | LN(10) |  | 2016-08-23 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 112 | MG/L |  | 2016-08-23 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.74 | LN(10) |  | 2016-08-23 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-09-13 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.7 |  |  | 2016-09-13 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 114 | MG/L |  | 2016-09-13 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.11 | LN(10) |  | 2016-09-13 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-09-13 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-09-13 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 102 | MG/L |  | 2016-09-13 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.2 |  |  | 2016-09-13 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-09-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.73 | LN(10) |  | 2016-09-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 122 | MG/L |  | 2016-09-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.6 |  |  | 2016-09-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.5 |  |  | 2016-09-29 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.7 | MG/L |  | 2016-09-29 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.72 | LN(10) |  | 2016-09-29 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 126 | MG/L |  | 2016-09-29 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 120 | MG/L |  | 2016-09-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.7 | MG/L |  | 2016-09-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 8.11 | LN(10) |  | 2016-09-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 122 | MG/L |  | 2016-09-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.5 |  |  | 2016-09-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.8 | MG/L |  | 2016-09-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 24.6 |  |  | 2016-09-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.81 | LN(10) |  | 2016-09-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.11 | LN(10) |  | 2016-10-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 101 | MG/L |  | 2016-10-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.3 |  |  | 2016-10-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.71 | LN(10) |  | 2016-10-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23.2 |  |  | 2016-10-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-10-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-10-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 118 | MG/L |  | 2016-10-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.2 |  |  | 2016-10-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-10-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-10-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 99 | MG/L |  | 2016-10-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 24.3 |  |  | 2016-10-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.7 | MG/L |  | 2016-10-30 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 8.15 | LN(10) |  | 2016-10-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.6 | MG/L |  | 2016-10-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 102 | MG/L |  | 2016-10-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.84 | LN(10) |  | 2016-10-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.8 | MG/L |  | 2016-10-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25 |  |  | 2016-10-30 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 108 | MG/L |  | 2016-10-30 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.64 | LN(10) |  | 2016-10-30 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 120 | MG/L |  | 2016-10-30 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 23.2 |  |  | 2016-10-30 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23.2 |  |  | 2016-11-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.65 | LN(10) |  | 2016-11-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 117 | MG/L |  | 2016-11-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.8 |  |  | 2016-11-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-11-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2016-11-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 104 | MG/L |  | 2016-11-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23 |  |  | 2016-11-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-11-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-11-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-11-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2016-11-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22 | UG/L | 60.4999 | 2016-11-16 | L3 |  |  |  | 1.37 | CWP2STG1 7603 CITRUS AVE. WINTER PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.8 | UG/L | 80.4999 | 2016-11-16 | L3 |  |  |  | 1.37 | CWP2STG1 7603 CITRUS AVE. WINTER PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.46 | UG/L | 60.4999 | 2016-11-16 | L1 |  |  |  | 1.42 | CWP4 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 70.93 | UG/L | 80.4999 | 2016-11-16 | L1 |  |  |  | 1.42 | CWP4 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.48 | UG/L | 60.4999 | 2016-11-16 | L4 |  |  |  | 1.39 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 49.11 | UG/L | 80.4999 | 2016-11-16 | L4 |  |  |  | 1.39 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.11 | UG/L | 60.4999 | 2016-11-16 | L2 |  |  |  | 1.45 | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 69.93 | UG/L | 80.4999 | 2016-11-16 | L2 |  |  |  | 1.45 | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.6 | MG/L |  | 2016-11-22 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 8 | LN(10) |  | 2016-11-22 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 121 | MG/L |  | 2016-11-22 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 21.4 |  |  | 2016-11-22 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 23.7 |  |  | 2016-11-22 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 112 | MG/L |  | 2016-11-22 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.62 | LN(10) |  | 2016-11-22 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.8 | MG/L |  | 2016-11-22 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 19.5 |  |  | 2016-11-25 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 107 | MG/L |  | 2016-11-25 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.84 | LN(10) |  | 2016-11-25 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.7 | MG/L |  | 2016-11-25 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.5 | MG/L |  | 2016-12-05 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.15 | LN(10) |  | 2016-12-05 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.5 |  |  | 2016-12-05 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2016-12-05 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.85 | LN(10) |  | 2016-12-05 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-12-05 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.9 |  |  | 2016-12-05 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 119 | MG/L |  | 2016-12-05 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.67 | LN(10) |  | 2016-12-05 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-12-05 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23.5 |  |  | 2016-12-05 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 112 | MG/L |  | 2016-12-05 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.66 | LN(10) |  | 2016-12-19 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 8.1 | LN(10) |  | 2016-12-19 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.6 | MG/L |  | 2016-12-19 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 23.2 |  |  | 2016-12-19 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 0.8 | MG/L |  | 2016-12-19 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 110 | MG/L |  | 2016-12-19 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 120 | MG/L |  | 2016-12-19 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 25.2 |  |  | 2016-12-19 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | D | 1.3 | MG/L |  | 2016-12-19 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | D | 7.75 | LN(10) |  | 2016-12-19 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | D | 108 | MG/L |  | 2016-12-19 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 23.6 |  |  | 2016-12-19 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.1 | UG/L | 60.4999 | 2017-02-15 | L2 |  |  |  | 0.92 | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 47.11 | UG/L | 80.4999 | 2017-02-15 | L2 |  |  |  | 0.92 | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 29.37 | UG/L | 80.4999 | 2017-02-15 | L1 |  |  |  | 1.33 | CWP4 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.38 | UG/L | 60.4999 | 2017-02-15 | L1 |  |  |  | 1.33 | CWP4 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 32.14 | UG/L | 80.4999 | 2017-02-15 | L4 |  |  |  | 1.49 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.97 | UG/L | 60.4999 | 2017-02-15 | L4 |  |  |  | 1.49 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 41.85 | UG/L | 80.4999 | 2017-02-15 | L3 |  |  |  | 1.27 | CWP2STG1 7603 CITRUS AVE. WINTER PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.03 | UG/L | 60.4999 | 2017-02-15 | L3 |  |  |  | 1.27 | CWP2STG1 7603 CITRUS AVE. WINTER PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-16 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-16 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-16 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-16 | WTP2 | 0.18 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-16 | WTP2 | 0.44 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-16 | WTP2 | 0.46 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-16 | WTP2 | 0.26 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-16 | WTP2 | 0.2 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-16 | WTP2 | 0.39 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-16 | WTP2 | 0.17 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-16 | WTP2 | 0.22 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-16 | WTP2 | 0.17 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-16 | WTP2 | 0.12 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP2 | 0.24 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-16 | WTP2 | 0.12 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-16 | WTP2 | 0.26 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP2 | 0.23 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-16 | WTP2 | 0.39 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP2 | 0.36 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-16 | WTP2 | 0.32 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (HYPERLINKED 3/7/17 TO BW - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.39 | UG/L | 60.4999 | 2017-05-02 | L4 | 0.5 |  | 2 | 1.01 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.31 | UG/L | 60.4999 | 2017-05-02 | L2 | 0.5 |  | 4 | 1.07 | 261 LYMAN
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 46.94 | UG/L | 80.4999 | 2017-05-02 | L4 | 0.14 |  | 2 | 1.01 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 83.68 | UG/L | 80.4999 | 2017-05-02 | L2 | 0.14 |  | 4 | 1.07 | 261 LYMAN
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.98 | UG/L | 60.4999 | 2017-05-02 | L3 | 0.5 |  | 1 | 0.67 | 7603 CITRUS
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 65.21 | UG/L | 80.4999 | 2017-05-02 | L3 | 0.14 |  | 1 | 0.67 | 7603 CITRUS
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.29 | UG/L | 60.4999 | 2017-05-02 | L1 | 0.5 |  | 3 | 1.23 | 1811 DOVER (J4 QUALIFIER ON BROMOACETIC ACID - MS 166% RECOVERY - BIASED HIGH - RESULT IS ACCEPTABLE)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 45.43 | UG/L | 80.4999 | 2017-05-02 | L1 | 0.14 |  | 3 | 1.23 | 1811 DOVER (J4 QUALIFIER ON BROMOACETIC ACID - MS 166% RECOVERY - BIASED HIGH - RESULT IS ACCEPTABLE)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 66.15 | UG/L | 80.4999 | 2017-05-22 | L2 | 0.14 |  | 4 | 0.78 | 261 LYMAN RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.09 | UG/L | 60.4999 | 2017-05-22 | L3 | 0.5 |  | 5 | 1.21 | 7603 CITRUS AVE.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 45.93 | UG/L | 80.4999 | 2017-05-22 | L3 | 0.14 |  | 5 | 1.21 | 7603 CITRUS AVE.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.03 | UG/L | 60.4999 | 2017-05-22 | L2 | 0.5 |  | 4 | 0.78 | 261 LYMAN RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 38.74 | UG/L | 80.4999 | 2017-05-22 | L4 | 0.14 |  | 2 | 1.53 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.76 | UG/L | 60.4999 | 2017-05-22 | L1 | 0.5 |  | 3 | 1.19 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 44.27 | UG/L | 80.4999 | 2017-05-22 | L1 | 0.14 |  | 3 | 1.19 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.45 | UG/L | 60.4999 | 2017-05-22 | L4 | 0.5 |  | 2 | 1.53 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP1 | 0.007 | 0.0149 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP1 | 0.0072 | 0.0249 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-31 | WTP1 | 0.0069 | 0.1499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP1 | 0.12 | 1.4999 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP1 | 1 | 1.4999 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-31 | WTP1 | 7.6 | 0.4499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP1 | 1.2 | 9.4999 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-31 | WTP1 | 6.5 | 6.4999 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-31 | WTP1 | 0.95 | 0.6499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP1 | 0.57 | 2.4999 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-31 | WTP1 | 0.19 | 0.0749 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-31 | WTP1 | 1.5 | 0.6499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-31 | WTP1 | 0.23 | 0.1499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-31 | WTP1 | 0.86 | 0.2499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-31 | WTP1 | 0.013 | 0.1499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-31 | WTP1 | 0.28 | 0.9499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP1 | 0.16 | 0.1499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP1 | 0.26 | 0.2499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-31 | WTP1 | 0.0061 | 0.0449 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP1 | 0.0053 | 0.0249 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP1 | 1.5 | 0.1499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-31 | WTP1 | 0.32 | 0.2499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP1 | 0.0064 | 0.1499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP1 | 0.096 | 0.0249 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP1 | 0.069 | 0.0449 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-31 | WTP1 | 0.11 | 0.1499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-05-31 | WTP1 | 0.051 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-31 | WTP1 | 0.053 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-05-31 | WTP1 | 8e-05 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.0098 | MG/L | 2.4999 | 2017-05-31 | WTP1 | 0.00028 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-05-31 | WTP1 | 0.00032 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP1 | 0.0005 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-05-31 | WTP1 | 0.0048 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.28 | MG/L | 4.0499 | 2017-05-31 | WTP1 | 0.075 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-05-31 | WTP1 | 0.00024 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-05-31 | WTP1 | 1e-05 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP1 | 0.0011 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-05-31 | WTP1 | 0.00058 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 13 | MG/L | 160.4999 | 2017-05-31 | WTP1 | 0.16 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-05-31 | WTP1 | 5e-05 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-05-31 | WTP1 | 0.00013 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-05-31 | WTP1 | 6e-05 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP1 | 0.006 | 0.0249 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-31 | WTP1 | 0.0062 | 0.0149 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP1 | 0.054 | 0.2499 |  |  | 1Q SOC/HOWELL PARK WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-05-31 | WTP1 | 0.061 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 19 | MG/L | 250.4999 | 2017-05-31 | WTP1 | 0.78 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-05-31 | WTP1 | 0.0025 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.28 | MG/L | 2.0499 | 2017-05-31 | WTP1 | 0.075 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-05-31 | WTP1 | 0.03 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-05-31 | WTP1 | 0.00099 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP1 | 3e-05 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 5.1 | MG/L | 250.4999 | 2017-05-31 | WTP1 | 0.52 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0.0094 | MG/L | 5.4999 | 2017-05-31 | WTP1 | 0.002 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-05-31 | WTP1 | 5 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-05-31 | WTP1 | 1 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.088 | LN(10) |  | 2017-05-31 | WTP1 |  |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 160 | MG/L | 500.4999 | 2017-05-31 | WTP1 | 10 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-05-31 | WTP1 | 0.04 |  |  |  | HOWELL PARK WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP1 | 0.32 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-05-31 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP3 | 0.0064 | 0.1499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP3 | 0.096 | 0.0249 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP3 | 0.069 | 0.0449 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-31 | WTP3 | 0.11 | 0.1499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP3 | 0.006 | 0.0249 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-31 | WTP3 | 0.0061 | 0.0149 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP3 | 0.054 | 0.2499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP3 | 0.32 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-05-31 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP3 | 0.44 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-05-31 | WTP3 | 0.46 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-05-31 | WTP3 | 0.26 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP3 | 0.2 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-05-31 | WTP3 | 0.18 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP3 | 0.36 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP3 | 0.39 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP3 | 0.23 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP3 | 0.26 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP3 | 0.12 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP3 | 0.24 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP3 | 0.12 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP3 | 0.17 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-05-31 | WTP3 | 0.22 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-05-31 | WTP3 | 0.17 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP3 | 0.39 | 0.5499 |  |  | 3YR VOC/SOUTH WP (RCVD 1/23/18) **SPECIAL VOC MONITORING IS RQRD ANNUALLY FOR NORTH WP ONLY** HQS HAS SAID IN THE PAST NOT TO DISCONTINUE IT - BW/BB
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.29 | MG/L | 10.4999 | 2017-05-31 | WTP3 | 0.051 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-31 | WTP3 | 0.053 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-05-31 | WTP3 | 8e-05 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.017 | MG/L | 2.4999 | 2017-05-31 | WTP3 | 0.00028 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-05-31 | WTP3 | 0.00032 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP3 | 0.0005 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-05-31 | WTP3 | 0.0048 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.29 | MG/L | 4.0499 | 2017-05-31 | WTP3 | 0.075 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-05-31 | WTP3 | 0.00024 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-05-31 | WTP3 | 1e-05 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP3 | 0.0011 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-05-31 | WTP3 | 0.00058 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 8.9 | MG/L | 160.4999 | 2017-05-31 | WTP3 | 0.16 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-05-31 | WTP3 | 5e-05 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-05-31 | WTP3 | 0.00013 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-05-31 | WTP3 | 6e-05 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP1 | 0.44 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-05-31 | WTP1 | 0.46 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-05-31 | WTP1 | 0.26 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP1 | 0.2 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-05-31 | WTP1 | 0.18 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP1 | 0.36 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP1 | 0.39 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP1 | 0.23 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP1 | 0.26 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP1 | 0.12 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP1 | 0.24 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP1 | 0.12 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP1 | 0.17 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-05-31 | WTP1 | 0.22 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-05-31 | WTP1 | 0.17 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP1 | 0.39 | 0.5499 |  |  | 3YR VOC/HOWELL PARK WP (RCVD 1/23/18)
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-05-31 | WTP2 | 1e-05 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP2 | 0.0011 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-05-31 | WTP2 | 0.00058 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 12 | MG/L | 160.4999 | 2017-05-31 | WTP2 | 0.16 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-05-31 | WTP2 | 5e-05 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-05-31 | WTP2 | 0.00013 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-05-31 | WTP2 | 6e-05 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-05-31 | WTP2 | 0.061 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 18 | MG/L | 250.4999 | 2017-05-31 | WTP2 | 0.78 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-05-31 | WTP2 | 0.0025 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.27 | MG/L | 2.0499 | 2017-05-31 | WTP2 | 0.075 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-05-31 | WTP2 | 0.03 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-05-31 | WTP2 | 0.00099 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP2 | 3e-05 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 5.6 | MG/L | 250.4999 | 2017-05-31 | WTP2 | 0.52 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0.011 | MG/L | 5.4999 | 2017-05-31 | WTP2 | 0.002 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-05-31 | WTP2 | 5 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-05-31 | WTP2 | 1 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.093 | LN(10) |  | 2017-05-31 | WTP2 |  |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 170 | MG/L | 500.4999 | 2017-05-31 | WTP2 | 10 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-05-31 | WTP2 | 0.04 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP2 | 0.32 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-05-31 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP2 | 0.44 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-05-31 | WTP2 | 0.46 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-05-31 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-05-31 | WTP2 | 0.18 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP2 | 0.36 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP2 | 0.23 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-05-31 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP2 | 0.24 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-05-31 | WTP2 | 0.22 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-05-31 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/NORTH WP (RCVD 1/23/18) & SPECIAL ANNUAL VOC TEST FOR NORTH WP (CONTINUE TO TEST NORTH WP ANNUALLY UNTIL FURTHER NOTICE)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP3 | 0.007 | 0.0149 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP3 | 0.0072 | 0.0249 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 7.9 | MG/L | 250.4999 | 2017-05-31 | WTP3 | 0.52 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0.0098 | MG/L | 5.4999 | 2017-05-31 | WTP3 | 0.002 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-05-31 | WTP3 | 5 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-05-31 | WTP3 | 1 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.819 | LN(10) |  | 2017-05-31 | WTP3 |  |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 150 | MG/L | 500.4999 | 2017-05-31 | WTP3 | 10 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0.05 |  | 0.5499 | 2017-05-31 | WTP3 | 0.04 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP3 | 0.57 | 2.4999 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-31 | WTP3 | 0.19 | 0.0749 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-31 | WTP3 | 1.5 | 0.6499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-31 | WTP3 | 0.23 | 0.1499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-31 | WTP3 | 0.86 | 0.2499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-31 | WTP3 | 0.013 | 0.1499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-31 | WTP3 | 0.28 | 0.9499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP3 | 0.16 | 0.1499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP3 | 0.26 | 0.2499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-31 | WTP3 | 0.0051 | 0.0449 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP3 | 0.0053 | 0.0249 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP3 | 1.5 | 0.1499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-31 | WTP3 | 0.32 | 0.2499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-31 | WTP3 | 0.0069 | 0.1499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP3 | 0.12 | 1.4999 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP3 | 1 | 1.4999 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-31 | WTP3 | 7.6 | 0.4499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP3 | 1.2 | 9.4999 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-31 | WTP3 | 6.5 | 6.4999 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-31 | WTP3 | 0.95 | 0.6499 |  |  | 1Q SOC/SOUTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP2 | 0.007 | 0.0149 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP2 | 0.0072 | 0.0249 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-31 | WTP2 | 0.0059 | 0.1499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP2 | 0.12 | 1.4999 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP2 | 1 | 1.4999 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-31 | WTP2 | 7.6 | 0.4499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-31 | WTP2 | 1.2 | 9.4999 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-31 | WTP2 | 6.5 | 6.4999 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-31 | WTP2 | 0.95 | 0.6499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-31 | WTP2 | 0.57 | 2.4999 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-31 | WTP2 | 0.19 | 0.0749 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-31 | WTP2 | 1.5 | 0.6499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-31 | WTP2 | 0.23 | 0.1499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-31 | WTP2 | 0.86 | 0.2499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-31 | WTP2 | 0.013 | 0.1499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-31 | WTP2 | 0.28 | 0.9499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-31 | WTP2 | 0.16 | 0.1499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP2 | 0.26 | 0.2499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-31 | WTP2 | 0.0061 | 0.0449 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP2 | 0.0053 | 0.0249 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-31 | WTP2 | 1.5 | 0.1499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-31 | WTP2 | 0.32 | 0.2499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP2 | 0.0064 | 0.1499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP2 | 0.096 | 0.0249 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-31 | WTP2 | 0.069 | 0.0449 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-05-31 | WTP3 | 0.061 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 13 | MG/L | 250.4999 | 2017-05-31 | WTP3 | 0.78 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-05-31 | WTP3 | 0.0025 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.29 | MG/L | 2.0499 | 2017-05-31 | WTP3 | 0.075 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-05-31 | WTP3 | 0.03 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-05-31 | WTP3 | 0.00099 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP3 | 3e-05 |  |  |  | SOUTH WP (RCVD 1/23/18) E53076 E82001
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-31 | WTP2 | 0.11 | 0.1499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-31 | WTP2 | 0.006 | 0.0249 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-31 | WTP2 | 0.0062 | 0.0149 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-31 | WTP2 | 0.053 | 0.2499 |  |  | 1Q SOC/NORTH WP (RCVD 1/23/18) DIOXIN REPORTED AS -0- BUT THERE'S NO SMP# ON RESULTS PAGE - UNACCEPTABLE AS REPORTED. SYSTEM IS NOT RQRD TO TEST FOR DIOXIN UNLESS IT'S A SURF WTR SYS OR UDI.
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-05-31 | WTP2 | 0.051 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-31 | WTP2 | 0.053 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-05-31 | WTP2 | 8e-05 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.0092 | MG/L | 2.4999 | 2017-05-31 | WTP2 | 0.00028 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-05-31 | WTP2 | 0.00032 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-05-31 | WTP2 | 0.0005 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-05-31 | WTP2 | 0.0048 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.27 | MG/L | 4.0499 | 2017-05-31 | WTP2 | 0.075 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-05-31 | WTP2 | 0.00024 |  |  |  | NORTH WP (RCVD 1/23/18) E53076 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.18 | UG/L | 60.4999 | 2017-08-16 | L3 | 0.5 |  | 1 | 0.57 | 7603 CITRUS AVE. WINTER PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 57.28 | UG/L | 80.4999 | 2017-08-16 | L3 | 0.14 |  | 1 | 0.57 | 7603 CITRUS AVE. WINTER PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 73.48 | UG/L | 80.4999 | 2017-08-16 | L2 | 0.14 |  | 4 | 0.92 | 261 LYMAN RD. (9/17 DB REPORT W/RSLTS) HYPERLINKED 9/25/17 TO BW PER SOP - BB
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.58 | UG/L | 60.4999 | 2017-08-16 | L2 | 0.5 |  | 4 | 0.92 | 261 LYMAN RD. (9/17 DB REPORT W/RSLTS) HYPERLINKED 9/25/17 TO BW PER SOP - BB
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 53.32 | UG/L | 80.4999 | 2017-08-16 | L1 | 0.14 |  | 3 | 0.97 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.58 | UG/L | 60.4999 | 2017-08-16 | L1 | 0.5 |  | 3 | 0.97 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 51.59 | UG/L | 80.4999 | 2017-08-16 | L4 | 0.14 |  | 2 | 0.63 | 5401 LAKE HOWELL RD. (NOT DR.) W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.72 | UG/L | 60.4999 | 2017-08-16 | L4 | 0.5 |  | 2 | 0.63 | 5401 LAKE HOWELL RD. (NOT DR.) W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP2 | 0.096 | 0.0249 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-09-06 | WTP2 | 0.069 | 0.0449 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-09-06 | WTP2 | 0.11 | 0.1499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP2 | 0.0061 | 0.0249 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-09-06 | WTP2 | 0.0063 | 0.0149 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP2 | 0.053 | 0.2499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP1 | 0.0072 | 0.0249 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-09-06 | WTP1 | 0.0069 | 0.1499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-09-06 | WTP1 | 0.12 | 1.4999 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-09-06 | WTP1 | 1 | 1.4999 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-09-06 | WTP1 | 7.6 | 0.4499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-09-06 | WTP1 | 1.2 | 9.4999 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-09-06 | WTP1 | 6.5 | 6.4999 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-09-06 | WTP1 | 0.95 | 0.6499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-09-06 | WTP1 | 0.57 | 2.4999 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-09-06 | WTP1 | 0.19 | 0.0749 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-09-06 | WTP1 | 1.5 | 0.6499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-09-06 | WTP1 | 0.23 | 0.1499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-09-06 | WTP1 | 0.86 | 0.2499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-09-06 | WTP1 | 0.013 | 0.1499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-09-06 | WTP1 | 0.28 | 0.9499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-09-06 | WTP1 | 0.16 | 0.1499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP1 | 0.26 | 0.2499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-09-06 | WTP1 | 0.0061 | 0.0449 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP1 | 0.0053 | 0.0249 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-09-06 | WTP1 | 1.5 | 0.1499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-09-06 | WTP1 | 0.32 | 0.2499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP2 | 0.0069 | 0.0149 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP2 | 0.0071 | 0.0249 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-09-06 | WTP2 | 0.0068 | 0.1499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-09-06 | WTP2 | 0.12 | 1.4999 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-09-06 | WTP2 | 1 | 1.4999 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-09-06 | WTP2 | 7.6 | 0.4499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-09-06 | WTP2 | 1.2 | 9.4999 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-09-06 | WTP2 | 6.5 | 6.4999 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-09-06 | WTP2 | 0.95 | 0.6499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-09-06 | WTP2 | 0.57 | 2.4999 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-09-06 | WTP2 | 0.19 | 0.0749 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-09-06 | WTP2 | 1.5 | 0.6499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-09-06 | WTP1 | 0.0064 | 0.1499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP1 | 0.096 | 0.0249 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-09-06 | WTP1 | 0.069 | 0.0449 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-09-06 | WTP1 | 0.11 | 0.1499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP1 | 0.0061 | 0.0249 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-09-06 | WTP1 | 0.0063 | 0.0149 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP1 | 0.053 | 0.2499 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP3 | 0.0069 | 0.0149 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP3 | 0.0071 | 0.0249 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-09-06 | WTP3 | 0.0068 | 0.1499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-09-06 | WTP3 | 0.12 | 1.4999 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-09-06 | WTP3 | 1 | 1.4999 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-09-06 | WTP3 | 7.6 | 0.4499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-09-06 | WTP3 | 1.2 | 9.4999 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-09-06 | WTP3 | 6.5 | 6.4999 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-09-06 | WTP3 | 0.95 | 0.6499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-09-06 | WTP3 | 0.57 | 2.4999 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-09-06 | WTP3 | 0.19 | 0.0749 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-09-06 | WTP3 | 1.5 | 0.6499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-09-06 | WTP3 | 0.23 | 0.1499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-09-06 | WTP3 | 0.86 | 0.2499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-09-06 | WTP3 | 0.012 | 0.1499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-09-06 | WTP3 | 0.28 | 0.9499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-09-06 | WTP3 | 0.16 | 0.1499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP3 | 0.26 | 0.2499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-09-06 | WTP3 | 0.006 | 0.0449 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP3 | 0.0052 | 0.0249 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-09-06 | WTP3 | 1.5 | 0.1499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-09-06 | WTP3 | 0.32 | 0.2499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-09-06 | WTP3 | 0.0063 | 0.1499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP3 | 0.096 | 0.0249 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-09-06 | WTP3 | 0.069 | 0.0449 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-09-06 | WTP3 | 0.11 | 0.1499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP3 | 0.0061 | 0.0249 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-09-06 | WTP3 | 0.0063 | 0.0149 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP3 | 0.053 | 0.2499 |  |  | 2Q SOC/SOUTH WP (PLACED IN FINAL CHEM HOLDING FOLDER 9/28/17 - BB)
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP1 | 0.007 | 0.0149 |  |  | 2Q SOC/HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-09-06 | WTP2 | 0.23 | 0.1499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-09-06 | WTP2 | 0.86 | 0.2499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-09-06 | WTP2 | 0.012 | 0.1499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-09-06 | WTP2 | 0.28 | 0.9499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-09-06 | WTP2 | 0.16 | 0.1499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-09-06 | WTP2 | 0.26 | 0.2499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-09-06 | WTP2 | 0.006 | 0.0449 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-09-06 | WTP2 | 0.0052 | 0.0249 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-09-06 | WTP2 | 1.5 | 0.1499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-09-06 | WTP2 | 0.32 | 0.2499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-09-06 | WTP2 | 0.0063 | 0.1499 |  |  | 2Q SOC/NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.55 | UG/L | 80.4999 | 2017-11-09 | L2 | 0.14 |  | 4 | 0.38 | 261 LYMAN RD. (12/17 DISINF BYP REPORT RCVD W/RSLTS) 12/27/17 STEVE BAGGS ADDED SPECIFIC SITE ADDRESSES ON THE FOUR PAGE 1S AS RQRD (NOT JUST CWP2 CWP6 CWP4 CWP5) - BB/BW
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.36 | UG/L | 60.4999 | 2017-11-09 | L2 | 0.5 |  | 4 | 0.38 | 261 LYMAN RD. (12/17 DISINF BYP REPORT RCVD W/RSLTS) 12/27/17 STEVE BAGGS ADDED SPECIFIC SITE ADDRESSES ON THE FOUR PAGE 1S AS RQRD (NOT JUST CWP2 CWP6 CWP4 CWP5) - BB/BW
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.17 | UG/L | 60.4999 | 2017-11-09 | L3 | 0.5 |  | 1 | 1.21 | 7603 CITRUS AVE. W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.45 | UG/L | 60.4999 | 2017-11-09 | L1 | 0.5 |  | 3 | 1.03 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 33.01 | UG/L | 80.4999 | 2017-11-09 | L1 | 0.14 |  | 3 | 1.03 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 39.38 | UG/L | 80.4999 | 2017-11-09 | L3 | 0.14 |  | 1 | 1.21 | 7603 CITRUS AVE. W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.16 | UG/L | 60.4999 | 2017-11-09 | L4 | 0.5 |  | 2 | 1.12 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 33.1 | UG/L | 80.4999 | 2017-11-09 | L4 | 0.14 |  | 2 | 1.12 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.75 | LN(10) |  | 2018-01-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 98 | MG/L |  | 2018-01-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-01-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 112 | MG/L |  | 2018-01-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2018-01-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-01-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 103 | MG/L |  | 2018-01-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.32 | LN(10) |  | 2018-01-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-01-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-01-30 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-01-30 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 118 | MG/L |  | 2018-01-30 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.63 | LN(10) |  | 2018-01-30 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 108 | MG/L |  | 2018-01-30 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-01-30 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.56 | LN(10) |  | 2018-01-30 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-01-30 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.27 | LN(10) |  | 2018-01-30 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-31 | WTP2 | 0.051 |  |  |  | NORTH WP (NITRATE J4 - LCS OK MS BIASED HIGH 111% - ACCEPTABLE)
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-31 | WTP2 | 0.053 |  |  |  | NORTH WP (NITRATE J4 - LCS OK MS BIASED HIGH 111% - ACCEPTABLE)
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-31 | WTP3 | 0.053 |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-31 | WTP1 | 0.053 |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.26 | MG/L | 10.4999 | 2018-01-31 | WTP3 | 0.051 |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-31 | WTP1 | 0.051 |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-06 | WTP2 | 0.22 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-06 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-06 | WTP2 | 0.12 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-06 | WTP2 | 0.24 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-06 | WTP2 | 0.12 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-06 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-06 | WTP2 | 0.26 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-06 | WTP2 | 0.23 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-06 | WTP2 | 0.39 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-06 | WTP2 | 0.36 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-06 | WTP2 | 0.39 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-06 | WTP2 | 0.17 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-06 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-06 | WTP2 | 0.32 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-06 | WTP2 | 0.28 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-06 | WTP2 | 0.44 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-06 | WTP2 | 0.46 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-06 | WTP2 | 0.26 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-06 | WTP2 | 0.2 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-06 | WTP2 | 0.18 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-06 | WTP2 | 0.17 | 0.5499 |  |  | SPECIAL ANNUAL VOC MONITORING/NORTH WP (SPECIAL ANNUAL VOC MONITORING IS FOR NORTH WP ONLY)
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.72 | LN(10) |  | 2018-02-07 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.72 | LN(10) |  | 2018-02-07 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2018-02-07 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-02-07 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-02-07 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-02-07 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2018-02-07 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 121 | MG/L |  | 2018-02-07 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2018-02-07 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-02-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.58 | LN(10) |  | 2018-02-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-02-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 120 | MG/L |  | 2018-02-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 108 | MG/L |  | 2018-02-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.72 | LN(10) |  | 2018-02-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-02-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-02-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2018-02-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.53 | UG/L | 60.4999 | 2018-02-28 | L2 | 0.5 |  | 4 | 1.15 | 261 LYMAN RD. (3/18 DISINF BYP RPRT RCVD W/LAB RSLTS) HYPERLINKED 4/16/18 TO BW - BB
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 54.84 | UG/L | 80.4999 | 2018-02-28 | L2 | 0.14 |  | 4 | 1.15 | 261 LYMAN RD. (3/18 DISINF BYP RPRT RCVD W/LAB RSLTS) HYPERLINKED 4/16/18 TO BW - BB
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 39.62 | UG/L | 80.4999 | 2018-02-28 | L1 | 0.14 |  | 3 | 1.35 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.55 | UG/L | 60.4999 | 2018-02-28 | L1 | 0.5 |  | 3 | 1.35 | 1811 DOVER RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.14 | UG/L | 80.4999 | 2018-02-28 | L4 | 0.14 |  | 2 | 1.62 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.08 | UG/L | 60.4999 | 2018-02-28 | L4 | 0.5 |  | 2 | 1.62 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 47 | UG/L | 80.4999 | 2018-02-28 | L3 | 0.14 |  | 1 | 1.35 | 7603 CITRUS AVE. W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.21 | UG/L | 60.4999 | 2018-02-28 | L3 | 0.5 |  | 1 | 1.35 | 7603 CITRUS AVE. W.P.
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.73 | LN(10) |  | 2018-03-13 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 104 | MG/L |  | 2018-03-13 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-03-13 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2018-03-13 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.75 | LN(10) |  | 2018-03-13 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-03-13 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 118 | MG/L |  | 2018-03-13 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2018-03-13 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-03-13 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-03-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.64 | LN(10) |  | 2018-03-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 117 | MG/L |  | 2018-03-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-03-28 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2018-03-28 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2018-03-28 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-03-28 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-03-28 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.75 | LN(10) |  | 2018-03-28 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-04-04 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-04-04 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.61 | LN(10) |  | 2018-04-04 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 121 | MG/L |  | 2018-04-04 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.71 | LN(10) |  | 2018-04-04 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-04-04 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.5 | MG/L |  | 2018-04-04 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.75 | LN(10) |  | 2018-04-04 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 110 | MG/L |  | 2018-04-04 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.66 | LN(10) |  | 2018-04-26 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 122 | MG/L |  | 2018-04-26 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-04-26 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.76 | LN(10) |  | 2018-04-26 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-04-26 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2018-04-26 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-04-26 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.76 | LN(10) |  | 2018-04-26 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 112 | MG/L |  | 2018-04-26 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-05-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-05-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 121 | MG/L |  | 2018-05-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-05-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 111 | MG/L |  | 2018-05-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2018-05-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-05-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.77 | LN(10) |  | 2018-05-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.69 | LN(10) |  | 2018-05-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.36 | UG/L | 60.4999 | 2018-05-23 | L3 | 0.91 |  | 1 | 1.23 | 7603 CITRUS AVE
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 63.15 | UG/L | 80.4999 | 2018-05-23 | L3 | 0.14 |  | 1 | 1.23 | 7603 CITRUS AVE
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.54 | UG/L | 60.4999 | 2018-05-23 | L4 | 0.91 |  | 2 | 1.14 | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 67.77 | UG/L | 80.4999 | 2018-05-23 | L2 | 0.14 |  | 4 | 0.92 | 261 LYMAN RD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.88 | UG/L | 60.4999 | 2018-05-23 | L1 | 0.91 |  | 3 | 1.54 | 1811 DOVER RD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 52.55 | UG/L | 80.4999 | 2018-05-23 | L1 | 0.14 |  | 3 | 1.54 | 1811 DOVER RD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.37 | UG/L | 60.4999 | 2018-05-23 | L2 | 0.91 |  | 4 | 0.92 | 261 LYMAN RD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 62.8 | UG/L | 80.4999 | 2018-05-23 | L4 | 0.14 |  | 2 | 1.14 | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.72 | LN(10) |  | 2018-05-24 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-05-24 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 121 | MG/L |  | 2018-05-24 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-05-24 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-05-24 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 112 | MG/L |  | 2018-05-24 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.79 | LN(10) |  | 2018-05-24 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2018-05-24 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.5 | MG/L |  | 2018-05-24 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-06-12 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 121 | MG/L |  | 2018-06-12 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-06-12 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-06-12 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2018-06-12 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-06-12 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-06-12 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 108 | MG/L |  | 2018-06-12 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-06-12 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-06-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.73 | LN(10) |  | 2018-06-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 121 | MG/L |  | 2018-06-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-06-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 113 | MG/L |  | 2018-06-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-06-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-06-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-06-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.68 | LN(10) |  | 2018-06-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-07-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-07-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 103 | MG/L |  | 2018-07-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-07-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2018-07-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 116 | MG/L |  | 2018-07-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-07-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-07-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-07-10 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-07-24 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2018-07-24 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-07-24 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-07-24 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 122 | MG/L |  | 2018-07-24 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-07-24 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 113 | MG/L |  | 2018-07-24 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-07-24 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-07-24 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.85 | UG/L | 60.4999 | 2018-08-01 | L1 | 0.91 |  | 3 | 1.72 | 1817 DOVER RD. (>>STG 2 SITE IS 1811 DOVER RD. - ENTD WITH "S" SAMPLE TYPE - CHANGE TO "D" SAMPLE TYPE IF ACCEPTABLE)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 25.12 | UG/L | 80.4999 | 2018-08-01 | L1 | 0.39 |  | 3 | 1.72 | 1817 DOVER RD. (>>STG 2 SITE IS 1811 DOVER RD. - ENTD WITH "S" SAMPLE TYPE - CHANGE TO "D" SAMPLE TYPE IF ACCEPTABLE)
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.62 | UG/L | 60.4999 | 2018-08-01 | L2 | 0.91 |  | 4 | 0.95 | 261 LYMAN RD. (HLKD TO RLB) ****ONE SITE TESTED IS NOT ON STAGE 2 PLAN - SEE 1817 DOVER SCREEN SHD BE 1811 DOVER****
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 34.34 | UG/L | 80.4999 | 2018-08-01 | L3 | 0.39 |  | 1 | 1.53 | 7603 CITRUS AVE.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.82 | UG/L | 60.4999 | 2018-08-01 | L3 | 0.91 |  | 1 | 1.53 | 7603 CITRUS AVE.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 39.51 | UG/L | 80.4999 | 2018-08-01 | L2 | 0.39 |  | 4 | 0.95 | 261 LYMAN RD. (HLKD TO RLB) ****ONE SITE TESTED IS NOT ON STAGE 2 PLAN - SEE 1817 DOVER SCREEN SHD BE 1811 DOVER****
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.94 | UG/L | 60.4999 | 2018-08-01 | L4 | 0.91 |  | 2 | 1.18 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 37.85 | UG/L | 80.4999 | 2018-08-01 | L4 | 0.39 |  | 2 | 1.18 | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 119 | MG/L |  | 2018-08-08 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-08-08 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-08-08 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2018-08-08 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-08-08 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-08-08 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2018-08-08 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-08-08 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-08-08 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 101 | MG/L |  | 2018-08-22 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-08-22 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-08-22 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-08-22 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-08-22 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 116 | MG/L |  | 2018-08-22 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-08-22 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-08-22 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-08-22 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2018-09-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-09-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-09-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2018-09-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-09-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-09-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-09-14 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-09-14 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 113 | MG/L |  | 2018-09-14 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-09-25 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-09-25 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-09-25 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-09-25 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-09-25 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-09-25 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-09-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-09-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 108 | MG/L |  | 2018-09-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-10-09 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-10-09 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-10-09 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 111 | MG/L |  | 2018-10-09 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-10-09 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-10-09 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-10-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-10-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2018-10-10 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-10-25 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-10-25 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 87 | MG/L |  | 2018-10-25 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2018-10-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-10-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-10-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 87 | MG/L |  | 2018-10-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 90 | MG/L |  | 2018-10-27 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-10-27 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.37 | UG/L | 60.4999 | 2018-11-06 | L4 |  |  |  | 1 | 2950-CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 58.06 | UG/L | 80.4999 | 2018-11-06 | L4 |  |  |  | 1 | 2950-CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 46.26 | UG/L | 80.4999 | 2018-11-06 | L1 |  |  |  | 1.33 | 2950-CWP4 1817 DOVER RD. / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.08 | UG/L | 60.4999 | 2018-11-06 | L2 |  |  |  | 1.09 | 2950-CWP5 261 LYMAN RD. (NOT DR.) / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 62.84 | UG/L | 80.4999 | 2018-11-06 | L2 |  |  |  | 1.09 | 2950-CWP5 261 LYMAN RD. (NOT DR.) / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 49.87 | UG/L | 80.4999 | 2018-11-06 | L3 |  |  |  | 1.26 | 2950-CWP2STG1 7603 CITRUS AVE. WINTER PARK / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.86 | UG/L | 60.4999 | 2018-11-06 | L3 |  |  |  | 1.26 | 2950-CWP2STG1 7603 CITRUS AVE. WINTER PARK / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.2 | UG/L | 60.4999 | 2018-11-06 | L1 |  |  |  | 1.33 | 2950-CWP4 1817 DOVER RD. / SUBCONTRACT LAB E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2018-11-09 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-11-09 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2018-11-09 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2018-11-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 115 | MG/L |  | 2018-11-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-11-10 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-11-14 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-11-14 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 113 | MG/L |  | 2018-11-14 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 114 | MG/L |  | 2018-11-25 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-11-25 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-11-25 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 101 | MG/L |  | 2018-11-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-11-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 7 | MG/L |  | 2018-11-27 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-11-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-11-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 108 | MG/L |  | 2018-11-28 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 113 | MG/L |  | 2018-12-12 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-12-12 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-12-12 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2018-12-12 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-12-12 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-12-12 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 113 | MG/L |  | 2018-12-12 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2018-12-12 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2018-12-12 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 125 | MG/L |  | 2018-12-26 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 125 | MG/L |  | 2018-12-26 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-12-26 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 125 | MG/L |  | 2018-12-26 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-12-26 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-12-26 | WTP2 |  |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2018-12-26 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2018-12-26 | WTP3 |  |  |  |  | SOUTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2018-12-26 | WTP1 |  |  |  |  | HOWELL PARK WP
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 116 | MG/L |  | 2019-01-09 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.78 | LN(10) |  | 2019-01-09 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-01-09 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 116 | MG/L |  | 2019-01-09 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.74 | LN(10) |  | 2019-01-09 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-01-09 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2019-01-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.59 | LN(10) |  | 2019-01-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 114 | MG/L |  | 2019-01-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2019-01-23 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-01-23 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 115 | MG/L |  | 2019-01-23 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.74 | LN(10) |  | 2019-01-23 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-01-23 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 119 | MG/L |  | 2019-01-23 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 116 | MG/L |  | 2019-01-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.59 | LN(10) |  | 2019-01-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.74 | MG/L |  | 2019-01-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 17.15 | UG/L | 60.4999 | 2019-02-04 | L3
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | M | 36.77 | UG/L | 80.4999 | 2019-02-04 | L3
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 16.5 | UG/L | 60.4999 | 2019-02-04 | L4
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.15 | UG/L | 60.4999 | 2019-02-04 | L3 | 0.91 |  | 1 | 1.44 | 7603 CITRUS AVE
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.77 | UG/L | 80.4999 | 2019-02-04 | L3 | 0.39 |  | 1 | 1.44 | 7603 CITRUS AVE
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.5 | UG/L | 60.4999 | 2019-02-04 | L4 | 0.91 |  | 2 | 1.46 | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 34.44 | UG/L | 80.4999 | 2019-02-04 | L4 | 0.39 |  | 2 | 1.46 | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.47 | UG/L | 60.4999 | 2019-02-04 | L1 | 0.91 |  | 3 | 1.51 | 1817 DOVER
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 32.3 | UG/L | 80.4999 | 2019-02-04 | L1 | 0.39 |  | 3 | 1.51 | 1817 DOVER
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.79 | UG/L | 60.4999 | 2019-02-04 | L2 | 0.91 |  | 4 | 1.33 | 261 LYMAN
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 46.82 | UG/L | 80.4999 | 2019-02-04 | L2 | 0.39 |  | 4 | 1.33 | 261 LYMAN
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | M | 34.44 | UG/L | 80.4999 | 2019-02-04 | L4
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 15.47 | UG/L | 60.4999 | 2019-02-04 | L1
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | M | 32.3 | UG/L | 80.4999 | 2019-02-04 | L1
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 25.79 | UG/L | 60.4999 | 2019-02-04 | L2
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | M | 46.82 | UG/L | 80.4999 | 2019-02-04 | L2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 114 | MG/L |  | 2019-02-12 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.74 | LN(10) |  | 2019-02-12 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-02-12 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 110 | MG/L |  | 2019-02-13 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2019-02-13 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2019-02-13 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 114 | MG/L |  | 2019-02-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.59 | LN(10) |  | 2019-02-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2019-02-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-02-14 | WTP2 | 0.26 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.23 | MG/L | 10.4999 | 2019-02-14 | WTP2 | 0.051 |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-02-14 | WTP2 | 0.18 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-02-14 | WTP2 | 0.28 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-02-14 | WTP2 | 0.36 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-02-14 | WTP2 | 0.39 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-02-14 | WTP2 | 0.23 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-02-14 | WTP2 | 0.26 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-02-14 | WTP2 | 0.28 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-02-14 | WTP2 | 0.12 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-02-14 | WTP2 | 0.24 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-02-14 | WTP2 | 0.12 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-02-14 | WTP2 | 0.17 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-02-14 | WTP2 | 0.22 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-02-14 | WTP2 | 0.17 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-02-14 | WTP2 | 0.39 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-02-14 | WTP2 | 0.28 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-02-14 | WTP2 | 0.32 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-02-14 | WTP2 | 0.2 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-14 | WTP2 | 0.053 |  |  |  | NORTH WP
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-02-14 | WTP2 | 0.28 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-02-14 | WTP2 | 0.46 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-02-14 | WTP2 | 0.44 | 0.5499
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-14 | WTP3 |  |  |  |  | SOUTH WP - NO3 J4 QUALIFIER ACCETPABLE_RLB
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-14 | WTP3 | 0.053 |  |  |  | SOUTH WP - NO3 J4 QUALIFIER ACCETPABLE_RLB
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-14 | WTP1 | 0.053 |  |  |  | HOWELL PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.23 | MG/L | 10.4999 | 2019-02-14 | WTP1 | 0.051 |  |  |  | HOWELL PARK
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 112 | MG/L |  | 2019-02-27 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-02-27 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.76 | MG/L |  | 2019-02-27 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 114 | MG/L |  | 2019-02-27 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.74 | MG/L |  | 2019-02-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2019-02-27 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 116 | MG/L |  | 2019-02-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.59 | LN(10) |  | 2019-02-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.47 | LN(10) |  | 2019-02-27 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.76 | MG/L |  | 2019-03-12 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.78 | LN(10) |  | 2019-03-12 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 90 | MG/L |  | 2019-03-12 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.71 | LN(10) |  | 2019-03-13 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-03-13 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2019-03-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.69 | LN(10) |  | 2019-03-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.79 | MG/L |  | 2019-03-13 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2019-03-13 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.77 | MG/L |  | 2019-03-24 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.78 | LN(10) |  | 2019-03-24 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 111 | MG/L |  | 2019-03-24 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.68 | LN(10) |  | 2019-03-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 110 | MG/L |  | 2019-03-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.77 | MG/L |  | 2019-03-27 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.68 | LN(10) |  | 2019-03-27 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 110 | MG/L |  | 2019-03-27 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.77 | MG/L |  | 2019-03-27 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 108 | MG/L |  | 2019-04-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.65 | MG/L |  | 2019-04-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.69 | LN(10) |  | 2019-04-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.67 | MG/L |  | 2019-04-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.71 | LN(10) |  | 2019-04-10 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 110 | MG/L |  | 2019-04-10 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.73 | MG/L |  | 2019-04-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2019-04-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 104 | MG/L |  | 2019-04-10 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-04-24 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-04-24 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 99 | MG/L |  | 2019-04-24 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.81 | MG/L |  | 2019-04-24 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 105 | MG/L |  | 2019-04-24 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 102 | MG/L |  | 2019-04-24 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.62 | MG/L |  | 2019-04-24 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.69 | LN(10) |  | 2019-04-24 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.85 | LN(10) |  | 2019-04-24 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 39.6 | UG/L | 80.4999 | 2019-05-07 | L1 |  |  | 3 | 1.25 | CWP4 1817 DOVER RD. / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.31 | UG/L | 60.4999 | 2019-05-07 | L2 |  |  | 4 | 1.09 | CWP5 261 LYMAN RD. (NOT DR.) / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 46.14 | UG/L | 80.4999 | 2019-05-07 | L4 |  |  | 2 | 1.12 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.39 | UG/L | 60.4999 | 2019-05-07 | L4 |  |  | 2 | 1.12 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 41.62 | UG/L | 80.4999 | 2019-05-07 | L3 |  |  | 1 | 1.28 | CWP2STG1 7603 CITRUS AVE. WINTER PARK / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.57 | UG/L | 60.4999 | 2019-05-07 | L3 |  |  | 1 | 1.28 | CWP2STG1 7603 CITRUS AVE. WINTER PARK / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48.71 | UG/L | 80.4999 | 2019-05-07 | L2 |  |  | 4 | 1.09 | CWP5 261 LYMAN RD. (NOT DR.) / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.17 | UG/L | 60.4999 | 2019-05-07 | L1 |  |  | 3 | 1.25 | CWP4 1817 DOVER RD. / SUBCONTRACT LABS E82535 E84589
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-05-08 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.77 | LN(10) |  | 2019-05-08 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 90 | MG/L |  | 2019-05-08 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-05-08 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 90 | MG/L |  | 2019-05-08 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 88 | MG/L |  | 2019-05-08 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2019-05-08 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.86 | LN(10) |  | 2019-05-08 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.77 | LN(10) |  | 2019-05-08 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 89 | MG/L |  | 2019-05-22 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-05-22 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.86 | LN(10) |  | 2019-05-22 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 91 | MG/L |  | 2019-05-22 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2019-05-22 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-05-22 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 82 | MG/L |  | 2019-05-22 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2019-05-22 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2019-05-22 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.85 | LN(10) |  | 2019-06-05 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.62 | MG/L |  | 2019-06-05 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.62 | MG/L |  | 2019-06-05 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2019-06-05 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.71 | MG/L |  | 2019-06-05 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 109 | MG/L |  | 2019-06-05 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.88 | LN(10) |  | 2019-06-05 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 106 | MG/L |  | 2019-06-05 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 104 | MG/L |  | 2019-06-05 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 91 | MG/L |  | 2019-06-19 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | N | 107 | MG/L |  | 2019-06-19 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.85 | LN(10) |  | 2019-06-19 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.63 | MG/L |  | 2019-06-19 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.76 | LN(10) |  | 2019-06-19 | WTP3
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.62 | MG/L |  | 2019-06-19 | WTP2
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.75 | LN(10) |  | 2019-06-19 | WTP2 | 105
3590159 | CASSELBERRY CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.73 | MG/L |  | 2019-06-19 | WTP1
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48.86 | UG/L | 80.4999 | 2019-08-06 | L3 |  |  | 1 | 0.81 | CWP2STG1 7603 CITRUS AVE. WINTER PARK / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.03 | UG/L | 60.4999 | 2019-08-06 | L4 |  |  | 2 | 0.63 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48.45 | UG/L | 80.4999 | 2019-08-06 | L4 |  |  | 2 | 0.63 | CWP6 5401 LAKE HOWELL RD. (NOT DR.) W.P. / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 53.23 | UG/L | 80.4999 | 2019-08-06 | L1 |  |  | 3 | 0.71 | CWP4 1817 DOVER RD. / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.87 | UG/L | 60.4999 | 2019-08-06 | L2 |  |  | 4 | 0.9 | CWP5 261 LYMAN RD. (NOT DR.) / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 51.17 | UG/L | 80.4999 | 2019-08-06 | L2 |  |  | 4 | 0.9 | CWP5 261 LYMAN RD. (NOT DR.) / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.07 | UG/L | 60.4999 | 2019-08-06 | L3 |  |  | 1 | 0.81 | CWP2STG1 7603 CITRUS AVE. WINTER PARK / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.61 | UG/L | 60.4999 | 2019-08-06 | L1 |  |  | 3 | 0.71 | CWP4 1817 DOVER RD. / SUBCONTRACT LABS E84589 E82535
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.35 | UG/L | 60.4999 | 2019-11-05 | L3 |  |  |  | 1.22 | 7603 CITRUS AVE. [LRAA TTHM=43.82 ;HAA5=21.78]
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.24 | UG/L | 60.4999 | 2019-11-05 | L1 |  |  |  | 1.47 | 1817 DOVER RD [LRAA TTHM = 40.30; HAA5=20.12 ]
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 48.04 | UG/L | 80.4999 | 2019-11-05 | L3 |  |  |  | 1.22 | 7603 CITRUS AVE. [LRAA TTHM=43.82 ;HAA5=21.78]
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.08 | UG/L | 60.4999 | 2019-11-05 | L2 |  |  |  | 0.91 | 261 LYMAN RD [LRAA TTHM=53.50; HAA5=26.26]
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.1 | UG/L | 80.4999 | 2019-11-05 | L1 |  |  |  | 1.47 | 1817 DOVER RD [LRAA TTHM = 40.30; HAA5=20.12 ]
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 67.31 | UG/L | 80.4999 | 2019-11-05 | L2 |  |  |  | 0.91 | 261 LYMAN RD [LRAA TTHM=53.50; HAA5=26.26]
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.17 | UG/L | 80.4999 | 2019-11-05 | L4 |  |  |  | 1.11 | 5401 LAKE HOWELL RD. (NOT DR.) W.P. [LRAA TTHM = 43.05; HAA5= 22.38]
3590159 | CASSELBERRY CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.61 | UG/L | 60.4999 | 2019-11-05 | L4 |  |  |  | 1.11 | 5401 LAKE HOWELL RD. (NOT DR.) W.P. [LRAA TTHM = 43.05; HAA5= 22.38]
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.36 | UG/L | 60.4999 | 2015-01-15 | L2 |  |  |  | 0.9 | 390 LAKE LENELLE(3/15 LRAA/T=78.825 LRAA/H=18.5525)NO L2 LRAA MCL VIOLS BUT 3/15 OE VALUE=86.92-RCVD 3/15 OE RPRT L1 & L2-IN OC.(3/15 OE REPORT RQSTD 4/20/15 OF D. KIB. B. TRENDEL & M. ROTTEVEEL-BB)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 96.86 | UG/L | 80.4999 | 2015-01-15 | L2 |  |  |  | 0.9 | 390 LAKE LENELLE(3/15 LRAA/T=78.825 LRAA/H=18.5525)NO L2 LRAA MCL VIOLS BUT 3/15 OE VALUE=86.92-RCVD 3/15 OE RPRT L1 & L2-IN OC.(3/15 OE REPORT RQSTD 4/20/15 OF D. KIB. B. TRENDEL & M. ROTTEVEEL-BB)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.45 | UG/L | 60.4999 | 2015-01-15 | L1 |  |  |  | 0.9 | 803 MAZURKA(3/15 LRAA/T=74.6375 LRAA/H=17.535.)NO L1 LRAA MCLS 3/15 QTR BUT OE VALUE=82.7-RCVD 3/15 OE REPORT L1 & L2-IN OC.(3/15 OE REPORT REQUESTED 4/20/15 OF D. KIB. B. TRENDEL & M.ROTTEVEEL-BB)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 95.96 | UG/L | 80.4999 | 2015-01-15 | L1 |  |  |  | 0.9 | 803 MAZURKA(3/15 LRAA/T=74.6375 LRAA/H=17.535.)NO L1 LRAA MCLS 3/15 QTR BUT OE VALUE=82.7-RCVD 3/15 OE REPORT L1 & L2-IN OC.(3/15 OE REPORT REQUESTED 4/20/15 OF D. KIB. B. TRENDEL & M.ROTTEVEEL-BB)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-29 | WTP2
3590186 | CHULUOTA WATER SYSTEM | INOR | 1040 | NITRATE | N | 0.059 | MG/L | 10.4999 | 2015-01-29 | WTP2
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.17 | UG/L | 60.4999 | 2015-04-13 | L1 | 0.52 |  | 1 | 1.1 | 803 MAZURKA (E82574/H) (6/15 LRAA/T=74.13 LRAA/H=17.37) NO 6/15 MCLS OR OE EXCEEDANCES FOR L1 & L2. L1 OE VALUE 73.4425 T.
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.12 | UG/L | 60.4999 | 2015-04-13 | L2 | 0.52 |  | 2 | 0.85 | 390 LK.LENELLE (E82574/H) (6/15 LRAA/T=79.0175 LRAA/H=18.1925) NO LRAA OR OE MCLS FOR 6/15 QTR (6/15 T OE VALUE=75.4125)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 65.25 | UG/L | 80.4999 | 2015-04-13 | L2 | 0.31 |  | 2 | 0.85 | 390 LK.LENELLE (E82574/H) (6/15 LRAA/T=79.0175 LRAA/H=18.1925) NO LRAA OR OE MCLS FOR 6/15 QTR (6/15 T OE VALUE=75.4125)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 61.68 | UG/L | 80.4999 | 2015-04-13 | L1 | 0.31 |  | 1 | 1.1 | 803 MAZURKA (E82574/H) (6/15 LRAA/T=74.13 LRAA/H=17.37) NO 6/15 MCLS OR OE EXCEEDANCES FOR L1 & L2. L1 OE VALUE 73.4425 T.
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.92 | UG/L | 60.4999 | 2015-07-13 | L1 |  |  |  | 0.7 | 803 MAZURKA (9/15 LRAA/T=74.5475 LRAA/H=16.1075) CONT. QM/T+H U.F.N.
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 66.76 | UG/L | 80.4999 | 2015-07-13 | L2 |  |  |  | 0.5 | 390 LAKE LENELLE (9/15 LRAA/T=75.79 LRAA/H=15.9175) CONT. QM/T+H U.F.N.
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.35 | UG/L | 60.4999 | 2015-07-13 | L2 |  |  |  | 0.5 | 390 LAKE LENELLE (9/15 LRAA/T=75.79 LRAA/H=15.9175) CONT. QM/T+H U.F.N.
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 66.1 | UG/L | 80.4999 | 2015-07-13 | L1 |  |  |  | 0.7 | 803 MAZURKA (9/15 LRAA/T=74.5475 LRAA/H=16.1075) CONT. QM/T+H U.F.N.
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.42 | UG/L | 60.4999 | 2015-10-12 | L2 |  |  |  | 0.6 | 390 LAKE LENELLE (12/15 LRAA/T=79.0625 LRAA/H=LOW) CONT. QM/T+H BOTH SITES
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.03 | UG/L | 60.4999 | 2015-10-12 | L1 |  |  |  | 0.7 | 803 MAZURKA (12/15 LRAA/T=73.475 LRAA/H=14.3925) CONT. QM/T+H BOTH SITES (****2/22 EW HAS 1/16 DBPS-BOTH SITES)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 70.16 | UG/L | 80.4999 | 2015-10-12 | L1 |  |  |  | 0.7 | 803 MAZURKA (12/15 LRAA/T=73.475 LRAA/H=14.3925) CONT. QM/T+H BOTH SITES (****2/22 EW HAS 1/16 DBPS-BOTH SITES)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 87.38 | UG/L | 80.4999 | 2015-10-12 | L2 |  |  |  | 0.6 | 390 LAKE LENELLE (12/15 LRAA/T=79.0625 LRAA/H=LOW) CONT. QM/T+H BOTH SITES
3590186 | CHULUOTA WATER SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-05 | WTP2 |  |  |  |  | NN
3590186 | CHULUOTA WATER SYSTEM | INOR | 1040 | NITRATE | N | 0.19 | MG/L | 10.4999 | 2016-01-05 | WTP2 |  |  |  |  | NN
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.55 | UG/L | 60.4999 | 2016-01-11 | L1 |  |  |  | 0.8 | 803 MAZURKA (3/16 LRAA/T=66.65 LRAA/H=12.4175) NO MCLS OR OE EXCEEDANCES 3/16 QTR
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 74.2 | UG/L | 80.4999 | 2016-01-11 | L2 |  |  |  | 0.81 | 390 LAKE LENELLE (3/16 LRAA/T=73.3975 LRAA/H=11.665) NO MCLS OR OE EXCEEDANCES 3/16 QTR
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 68.66 | UG/L | 80.4999 | 2016-01-11 | L1 |  |  |  | 0.8 | 803 MAZURKA (3/16 LRAA/T=66.65 LRAA/H=12.4175) NO MCLS OR OE EXCEEDANCES 3/16 QTR
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.77 | UG/L | 60.4999 | 2016-01-11 | L2 |  |  |  | 0.81 | 390 LAKE LENELLE (3/16 LRAA/T=73.3975 LRAA/H=11.665) NO MCLS OR OE EXCEEDANCES 3/16 QTR
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.35 | UG/L | 60.4999 | 2016-04-14 | L2 | 0.2 |  | 2 | 0.8 | 390 LAKE LENELLE (6/16 LRAA/T=79.2925 LRAA/H=12.2225) 6/16 T OE VALUE=84.81 H OE VALUE LOW. 6/16 T OE REPORT L2 RCVD & IN OC 6/17/16 FROM D. KIBITLEWSKI. BB
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 88.83 | UG/L | 80.4999 | 2016-04-14 | L2 | 0.14 |  | 2 | 0.8 | 390 LAKE LENELLE (6/16 LRAA/T=79.2925 LRAA/H=12.2225) 6/16 T OE VALUE=84.81 H OE VALUE LOW. 6/16 T OE REPORT L2 RCVD & IN OC 6/17/16 FROM D. KIBITLEWSKI. BB
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 88.28 | UG/L | 80.4999 | 2016-04-14 | L1 | 0.14 |  | 1 | 0.7 | 803 MAZURKA (6/16 LRAA/T=73.3 LRAA/H=12.785) J3 QUAL BROMOFORM-BIASED HIGH-OK (6/16 T OE VALUE=78.845 H OE VALUE LOW)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.64 | UG/L | 60.4999 | 2016-04-14 | L1 | 0.2 |  | 1 | 0.7 | 803 MAZURKA (6/16 LRAA/T=73.3 LRAA/H=12.785) J3 QUAL BROMOFORM-BIASED HIGH-OK (6/16 T OE VALUE=78.845 H OE VALUE LOW)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.96 | UG/L | 60.4999 | 2016-07-11 | L2 |  |  |  | 0.7 | 390 LAKE LENELLE (NO 9/16 QTR MCLS OR OE EXCEEDANCES) CONTINUE QM/T+H (LRAAS/T IN 70S)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 51.67 | UG/L | 80.4999 | 2016-07-11 | L1 |  |  |  | 1 | 803 MAZURKA (NO 9/16 QTR MCLS OR OE EXCEEDANCES)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.59 | UG/L | 60.4999 | 2016-07-11 | L1 |  |  |  | 1 | 803 MAZURKA (NO 9/16 QTR MCLS OR OE EXCEEDANCES)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 49.4 | UG/L | 80.4999 | 2016-07-11 | L2 |  |  |  | 0.7 | 390 LAKE LENELLE (NO 9/16 QTR MCLS OR OE EXCEEDANCES) CONTINUE QM/T+H (LRAAS/T IN 70S)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 57.74 | UG/L | 80.4999 | 2016-10-19 | L1 |  |  |  | 0.5 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.78 | UG/L | 60.4999 | 2016-10-19 | L1 |  |  |  | 0.5 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 58.46 | UG/L | 80.4999 | 2016-10-19 | L2 |  |  |  | 0.4 | 390 LAKE LENELLE
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.33 | UG/L | 60.4999 | 2016-10-19 | L2 |  |  |  | 0.4 | 390 LAKE LENELLE
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 79.41 | UG/L | 80.4999 | 2017-01-12 | L2 | 0.14 |  | 2 | 0.41 | 390 LAKE LENELLE (3/17 L2 LRAA/T=69.025 LRAA/H=11.3425) NO LRAA MCL VIOLS L1 OR L2 NO OE EXCEEDANCES L1 OR L2
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 53.8 | UG/L | 80.4999 | 2017-01-12 | L1 | 0.14 |  | 1 | 0.86 | 803 MAZURKA (3/17 L1 LRAA/T=62.8725 LRAA/H=11.5825)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.73 | UG/L | 60.4999 | 2017-01-12 | L2 | 0.2 |  | 2 | 0.41 | 390 LAKE LENELLE (3/17 L2 LRAA/T=69.025 LRAA/H=11.3425) NO LRAA MCL VIOLS L1 OR L2 NO OE EXCEEDANCES L1 OR L2
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.32 | UG/L | 60.4999 | 2017-01-12 | L1 | 0.2 |  | 1 | 0.86 | 803 MAZURKA (3/17 L1 LRAA/T=62.8725 LRAA/H=11.5825)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-08 | WTP2 | 0.051 |  |  |  | WP2 (WP2=CHULUOTA'S ONLY ACTIVE WP IN SYSTEM) HYPERLINKED 2/28/17 TO BW-BB (POP. 3863 - NDS. TRIENNIAL CHEMS 2017)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-08 | WTP2 | 0.053 |  |  |  | WP2 (WP2=CHULUOTA'S ONLY ACTIVE WP IN SYSTEM) HYPERLINKED 2/28/17 TO BW-BB (POP. 3863 - NDS. TRIENNIAL CHEMS 2017)
3590186 | CHULUOTA WATER SYSTEM | RAD | 4020 | RADIUM-226 | N | 1.5 | PCI/L | 3.4999 | 2017-03-30 | WTP2 | 0.4 | 1.4999 |  |  | GA DUE 6 YRS AT STRICTEST R226+R228 DUE 6 YRS UR DUE 6 YRS (RADS WVRS MUST BE UPDATED BASED ON 2017 DATA)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-30 | WTP2 | 0.053 | 0.2499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1040 | NITRATE | N | 0.24 | MG/L | 10.4999 | 2017-03-30 | WTP2 | 0.051 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1041 | NITRITE | N | 0.19 | MG/L | 1.4999 | 2017-03-30 | WTP2 | 0.053 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-03-30 | WTP2 | 8e-05 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1010 | BARIUM | N | 0.019 | MG/L | 2.4999 | 2017-03-30 | WTP2 | 0.00028 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-03-30 | WTP2 | 0.00032 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-03-30 | WTP2 | 0.0005 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-03-30 | WTP2 | 0.0048 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1025 | FLUORIDE | N | 0.19 | MG/L | 4.0499 | 2017-03-30 | WTP2 | 0.075 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-03-30 | WTP2 | 0.00024 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-03-30 | WTP2 | 1e-05 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-03-30 | WTP2 | 0.0011 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-03-30 | WTP2 | 0.00058 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1052 | SODIUM | N | 65 | MG/L | 160.4999 | 2017-03-30 | WTP2 | 0.16 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-03-30 | WTP2 | 5e-05 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-03-30 | WTP2 | 0.00013 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-03-30 | WTP2 | 6e-05 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: NO2 MS/MSD 85%/88% FL MS/MSD 87%/85% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-03-30 | WTP2 | 0.061 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1017 | CHLORIDE | N | 130 | MG/L | 250.4999 | 2017-03-30 | WTP2 | 0.78 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-03-30 | WTP2 | 0.0025 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1025 | FLUORIDE | N | 0.19 | MG/L | 2.0499 | 2017-03-30 | WTP2 | 0.075 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-03-30 | WTP2 | 0.03 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1032 | MANGANESE | N | 0.0057 | MG/L | 0.0549 | 2017-03-30 | WTP2 | 0.00024 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-03-30 | WTP2 | 3e-05 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1055 | SULFATE | N | 17 | MG/L | 250.4999 | 2017-03-30 | WTP2 | 0.52 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1095 | ZINC | N | 0.0095 | MG/L | 5.4999 | 2017-03-30 | WTP2 | 0.002 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-03-30 | WTP2 | 5 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-03-30 | WTP2 | 1 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.15 | LN(10) |  | 2017-03-30 | WTP2 |  |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 420 | MG/L | 500.4999 | 2017-03-30 | WTP2 | 10 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-03-30 | WTP2 | 0.04 |  |  |  | WP2 IS ONLY ACTIVE WP IN SYSTEM (J QUAL RECOVERIES: CHL MS/MSD 78%/78% FL MS/MSD 87%/85% SULF MS/MSD 86%/86% - SUFFICIENT RECOVERIES FOR ACCEPTANCE)
3590186 | CHULUOTA WATER SYSTEM | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 3.2 | PCI/L | 15.4999 | 2017-03-30 | WTP2 | 2.2 |  |  |  | GA DUE 6 YRS AT STRICTEST R226+R228 DUE 6 YRS UR DUE 6 YRS (RADS WVRS MUST BE UPDATED BASED ON 2017 DATA)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP2 | 0.16 | 0.1499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-30 | WTP2 | 0.0069 | 0.0149 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-30 | WTP2 | 0.0071 | 0.0249 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-30 | WTP2 | 0.0068 | 0.1499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-30 | WTP2 | 0.12 | 1.4999 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP2 | 1 | 1.4999 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-30 | WTP2 | 7.6 | 0.4499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-30 | WTP2 | 1.2 | 9.4999 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-30 | WTP2 | 6.5 | 6.4999 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-30 | WTP2 | 0.95 | 0.6499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-30 | WTP2 | 0.57 | 2.4999 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-03-30 | WTP2 | 0.19 | 0.0749 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-30 | WTP2 | 1.5 | 0.6499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-30 | WTP2 | 0.23 | 0.1499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-30 | WTP2 | 0.86 | 0.2499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-30 | WTP2 | 0.012 | 0.1499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-30 | WTP2 | 0.28 | 0.9499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-30 | WTP2 | 0.26 | 0.2499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-30 | WTP2 | 0.006 | 0.0449 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-30 | WTP2 | 0.0052 | 0.0249 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-30 | WTP2 | 1.5 | 0.1499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-30 | WTP2 | 0.32 | 0.2499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP2 | 0.0063 | 0.1499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-03-30 | WTP2 | 0.096 | 0.0249 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-30 | WTP2 | 0.069 | 0.0449 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-30 | WTP2 | 0.11 | 0.1499 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-30 | WTP2 | 0.006 | 0.0249 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-30 | WTP2 | 0.0062 | 0.0149 |  |  | 1Q SOC (NEED 2ND QTR SOCS IN 2017 AT LEAST 60 DAYS APART FROM THESE RESULTS)
3590186 | CHULUOTA WATER SYSTEM | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-03-30 | WTP2 | 0.8 | 1.4999 |  |  | GA DUE 6 YRS AT STRICTEST R226+R228 DUE 6 YRS UR DUE 6 YRS (RADS WVRS MUST BE UPDATED BASED ON 2017 DATA)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.41 | UG/L | 60.4999 | 2017-04-20 | L1 | 0.5 |  | 2 | 0.31 | 803 MAZURKA (6/17 QTR LRAA/T=60.53 T LRAA/H=11.525) 6/17 LRAA/T IS NOT 60.4999 UG/L OR BELOW. MUST CONTINUE QM/T+H 9/17 QTR AT BOTH SITES. 6/17 OE VALUE/T = 67.34 (NO OE REPORT NEEDED) BB/BW
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 78.91 | UG/L | 80.4999 | 2017-04-20 | L1 | 0.14 |  | 2 | 0.31 | 803 MAZURKA (6/17 QTR LRAA/T=60.53 T LRAA/H=11.525) 6/17 LRAA/T IS NOT 60.4999 UG/L OR BELOW. MUST CONTINUE QM/T+H 9/17 QTR AT BOTH SITES. 6/17 OE VALUE/T = 67.34 (NO OE REPORT NEEDED) BB/BW
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 52.21 | UG/L | 80.4999 | 2017-04-20 | L2 | 0.14 |  | 1 | 1.4 | 390 LAKE LENELLE (6/17 QTR RAA/T=59.87 RAA/H=9.7225) 6/17 OE VALUE/T = 60.5725 (NO OE REPORT NEEDED)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.87 | UG/L | 60.4999 | 2017-04-20 | L2 | 0.5 |  | 1 | 1.4 | 390 LAKE LENELLE (6/17 QTR RAA/T=59.87 RAA/H=9.7225) 6/17 OE VALUE/T = 60.5725 (NO OE REPORT NEEDED)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.52 | UG/L | 60.4999 | 2017-07-17 | L1 | 0.5 |  | 1 | 0.5 | 803 MAZURKA (E82535/TTHMS) 9/17 LRAA/T=65.4 LRAA/H=11.5075) 9/17 OE VAL/T=68.7525 OE VAL/H LOW (MUST CONTINUE QM/T+H BOTH SITES)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 98.35 | UG/L | 80.4999 | 2017-07-17 | L2 | 0.14 |  | 2 | 0.72 | 390 LAKE LENELLE (E82535/TTHMS)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.43 | UG/L | 60.4999 | 2017-07-17 | L2 | 0.5 |  | 2 | 0.72 | 390 LAKE LENELLE (E82535/TTHMS)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 71.15 | UG/L | 80.4999 | 2017-07-17 | L1 | 0.14 |  | 1 | 0.5 | 803 MAZURKA (E82535/TTHMS) 9/17 LRAA/T=65.4 LRAA/H=11.5075) 9/17 OE VAL/T=68.7525 OE VAL/H LOW (MUST CONTINUE QM/T+H BOTH SITES)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 86.13 | UG/L | 80.4999 | 2017-08-21 | L2 | 0.14 |  | 1 | 0.66 | 390 LAKE LENELLE (E82535/TTHMS - SPLIT SAMPLE)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 87.5 | UG/L | 80.4999 | 2017-08-21 | L2 | 0.5 |  | 2 | 0.66 | 390 LAKE LENELLE (E83018/TTHMS - SPLIT SAMPLE) 9/17 QTR LRAA/T=70.185 LRAA/H=12.915 (L2 OE VALUE/T=78.235 OE VAL/H LOW) MUST CONTINUE QM/T+H BOTH SITES
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.55 | UG/L | 60.4999 | 2017-08-21 | L2 | 0.5 |  | 1 | 0.66 | 390 LAKE LENELLE (E82535/TTHMS - SPLIT SAMPLE)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.2 | UG/L | 60.4999 | 2017-08-21 | L2 | 0.5 |  | 2 | 0.66 | 390 LAKE LENELLE (E83018/TTHMS - SPLIT SAMPLE) 9/17 QTR LRAA/T=70.185 LRAA/H=12.915 (L2 OE VALUE/T=78.235 OE VAL/H LOW) MUST CONTINUE QM/T+H BOTH SITES
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 99.27 | UG/L | 80.4999 | 2017-10-11 | L2 | 0.14 |  | 2 | 0.43 | 390 LAKE LENELLE (E84589/E82535) 12/17 LRAA/T=80.3875 FOR L2 SITE (JUST < 80.4999 NOT AN LRAA MCL VIOL) L2 OE VALUE/T=85.3525 (**NEED OE REPORT L2 SITE FOR TTHMS) **HYPERLINKED 12/12/17 TO BW - BB
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.16 | UG/L | 60.4999 | 2017-10-11 | L2 | 0.5 |  | 2 | 0.43 | 390 LAKE LENELLE (E84589/E82535) 12/17 LRAA/T=80.3875 FOR L2 SITE (JUST < 80.4999 NOT AN LRAA MCL VIOL) L2 OE VALUE/T=85.3525 (**NEED OE REPORT L2 SITE FOR TTHMS) **HYPERLINKED 12/12/17 TO BW - BB
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 68.69 | UG/L | 80.4999 | 2017-10-11 | L1 | 0.14 |  | 1 | 0.7 | 803 MAZURKA (E84589/E82535) 10/17 RSLTS HYPERLINKED TO BW 12/12/17 - BB
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.49 | UG/L | 60.4999 | 2017-10-11 | L1 | 0.5 |  | 1 | 0.7 | 803 MAZURKA (E84589/E82535) 10/17 RSLTS HYPERLINKED TO BW 12/12/17 - BB
3590186 | CHULUOTA WATER SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-10-31 | WTP2 | 1.5 | 0.6499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-10-31 | WTP2 | 0.23 | 0.1499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-10-31 | WTP2 | 0.86 | 0.2499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-10-31 | WTP2 | 0.014 | 0.1499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-10-31 | WTP2 | 0.28 | 0.9499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-10-31 | WTP2 | 0.16 | 0.1499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-10-31 | WTP2 | 0.27 | 0.2499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-10-31 | WTP2 | 0.0067 | 0.0449 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-10-31 | WTP2 | 0.0058 | 0.0249 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-10-31 | WTP2 | 1.5 | 0.1499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-10-31 | WTP2 | 0.32 | 0.2499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-10-31 | WTP2 | 0.007 | 0.1499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-10-31 | WTP2 | 0.069 | 0.0449 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-10-31 | WTP2 | 0.12 | 0.1499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-10-31 | WTP2 | 0.0061 | 0.0249 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-10-31 | WTP2 | 0.0063 | 0.0149 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-10-31 | WTP2 | 0.059 | 0.2499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-10-31 | WTP2 | 0.0077 | 0.0149 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-10-31 | WTP2 | 0.0079 | 0.0249 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-10-31 | WTP2 | 0.0076 | 0.1499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-10-31 | WTP2 | 0.13 | 1.4999 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-10-31 | WTP2 | 1 | 1.4999 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-10-31 | WTP2 | 7.6 | 0.4499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-10-31 | WTP2 | 1.8 | 9.4999 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-10-31 | WTP2 | 6.5 | 6.4999 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-10-31 | WTP2 | 0.97 | 0.6499 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-10-31 | WTP2 | 0.57 | 2.4999 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-10-31 | WTP2 | 0.19 | 0.0749 |  |  | 2Q SOC-12/22/17 EM FOR BENZO RETEST TO MELISA CC'D TO BW (BENZO MS 0% RECOV PER SHEILA WILCOX AEL IN 12/22/17 EM)HYPRLNKD 12/21/17 TO BW FOR FOLLOW-UP-BB. BENZO IS REPORTED AS 0.098 U J4 A.D. 11/9/17.
3590186 | CHULUOTA WATER SYSTEM | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-12-26 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-12-26 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-12-26 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-12-26 | WTP2 | 0.22 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-12-26 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-12-26 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-12-26 | WTP2 | 0.24 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-12-26 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-12-26 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-12-26 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-12-26 | WTP2 | 0.23 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-12-26 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-12-26 | WTP2 | 0.36 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-12-26 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-12-26 | WTP2 | 0.18 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-12-26 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-12-26 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-12-26 | WTP2 | 0.46 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-12-26 | WTP2 | 0.44 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-12-26 | WTP2 | 0.32 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-12-26 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER 1/10/18 - BB/BW
3590186 | CHULUOTA WATER SYSTEM | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-12-27 | WTP2 | 0.096 | 0.0249 |  |  | BENZO RETEST (ALL OK - NO QUALIFIERS) 2 QTRS OF SOCS TESTED IN 2017 (RCVD 1-10-18 ENTD 1-10-18 PLACED IN FINAL CHEM HOLDING FOLDER 1-10-18 - BB/BW)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.48 | UG/L | 60.4999 | 2018-02-19 | L1 | 0.5 |  | 1 | 0.6 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 74.53 | UG/L | 80.4999 | 2018-02-19 | L2 | 0.14 |  | 2 | 0.7 | 390 LAKE LENELLE (HYPERLINKED TO BW 4/19/18 - BB) TTHM LRAA L1: 75.24 L2: 79.17 - ON QTRLY TESTING
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.47 | UG/L | 60.4999 | 2018-02-19 | L2 | 0.5 |  | 2 | 0.7 | 390 LAKE LENELLE (HYPERLINKED TO BW 4/19/18 - BB) TTHM LRAA L1: 75.24 L2: 79.17 - ON QTRLY TESTING
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 82.1 | UG/L | 80.4999 | 2018-02-19 | L1 | 0.14 |  | 1 | 0.6 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.29 | UG/L | 60.4999 | 2018-05-08 | L1 | 0.91 |  | 1 | 0.75 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.66 | UG/L | 60.4999 | 2018-05-08 | L2 | 0.91 |  | 2 | 0.68 | 390 LK LENELLE
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 55.26 | UG/L | 80.4999 | 2018-05-08 | L2 | 0.14 |  | 2 | 0.68 | 390 LK LENELLE
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 56.65 | UG/L | 80.4999 | 2018-05-08 | L1 | 0.14 |  | 1 | 0.75 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.9 | UG/L | 60.4999 | 2018-07-13 | L1 | 0.91 |  | 1 | 0.3 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 56.65 | UG/L | 80.4999 | 2018-07-13 | L1 | 0.14 |  | 1 | 0.3 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.74 | UG/L | 60.4999 | 2018-07-13 | L2 | 0.91 |  | 2 | 0.31 | 390 LAKE LENELLE (HLKD 8-22-18)
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 53.61 | UG/L | 80.4999 | 2018-07-13 | L2 | 0.14 |  | 2 | 0.31 | 390 LAKE LENELLE (HLKD 8-22-18)
3590186 | CHULUOTA WATER SYSTEM | INOR | 1040 | NITRATE | N | 0.2 | MG/L | 10.4999 | 2018-07-30 | WTP2 |  |  |  |  | WP2
3590186 | CHULUOTA WATER SYSTEM | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-07-30 | WTP2 |  |  |  |  | WP2
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 44.8 | UG/L | 80.4999 | 2018-10-12 | L2 | 0.56 |  | 1 | 0.7 | 390 LAKE LENELLE
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.12 | UG/L | 60.4999 | 2018-10-12 | L2 | 0.91 |  | 1 | 0.7 | 390 LAKE LENELLE
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.3 | UG/L | 60.4999 | 2018-10-12 | L1 | 0.91 |  | 2 | 0.8 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 42.96 | UG/L | 80.4999 | 2018-10-12 | L1 | 0.56 |  | 2 | 0.8 | 803 MAZURKA
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.99 | UG/L | 60.4999 | 2019-01-11 | L1 | 0.91 |  | 1 | 0.8
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.99 | UG/L | 60.4999 | 2019-01-11 | L1
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 59.09 | UG/L | 80.4999 | 2019-01-11 | L1
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 59.09 | UG/L | 80.4999 | 2019-01-11 | L1 | 0.56 |  | 1 | 0.8
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.58 | UG/L | 60.4999 | 2019-01-14 | L2 | 0.91 |  | 2 | 0.73
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.58 | UG/L | 60.4999 | 2019-01-14 | L2
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 66.23 | UG/L | 80.4999 | 2019-01-14 | L2
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 66.23 | UG/L | 80.4999 | 2019-01-14 | L2 | 0.39 |  | 2 | 0.73
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 89.4 | UG/L | 80.4999 | 2019-07-10 | L1 | 0.39 |  | 1 | 0.61 | 803 MAZURKA T/LRAA = 62.0; OEL = 70.2 NO OE REPORT NEEDED; START Q MNTORING_JB
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.02 | UG/L | 60.4999 | 2019-07-10 | L1 | 0.91 |  | 1 | 0.61 | 803 MAZURKA T/LRAA = 62.0; OEL = 70.2 NO OE REPORT NEEDED; START Q MNTORING_JB
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 69.93 | UG/L | 80.4999 | 2019-07-10 | L2 | 0.39 |  | 1 |  | 390 LAKE LENELLE T/LRAA = 58.6 OEL = 62.7
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.17 | UG/L | 60.4999 | 2019-07-10 | L2 | 0.91 |  | 1 |  | 390 LAKE LENELLE
3590186 | CHULUOTA WATER SYSTEM | INOR | 1041 | NITRITE | D | 0 | MG/L | 1.4999 | 2019-07-24 | WTP2
3590186 | CHULUOTA WATER SYSTEM | INOR | 1040 | NITRATE | D | 0.51 | MG/L | 10.4999 | 2019-07-24 | WTP2
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 104.49 | UG/L | 80.4999 | 2019-10-23 | L2 | 0.39 |  | 2 | 0.77 | 390 LAKE LENELLE TTHM LRAA = 71.36; OEL= 86.29 OE REPORT REQUIRED_VP
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.57 | UG/L | 60.4999 | 2019-10-23 | L1 | 0.91 |  | 1 | 0.59 | 803 MAZURKA TTHM LRAA = 74.525 OEL = 90.45 OE REPORT REQUIRTED_VP
3590186 | CHULUOTA WATER SYSTEM | DBP | 2950 | TOTAL THMS | D | 106.65 | UG/L | 80.4999 | 2019-10-23 | L1 | 0.38 |  | 1 | 0.59 | 803 MAZURKA TTHM LRAA = 74.525 OEL = 90.45 OE REPORT REQUIRTED_VP
3590186 | CHULUOTA WATER SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.03 | UG/L | 60.4999 | 2019-10-23 | L2 | 0.91 |  | 2 | 0.77 | 390 LAKE LENELLE TTHM LRAA = 71.36; OEL= 86.29 OE REPORT REQUIRED_VP
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-01-05 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.87 | UG/L | 60.4999 | 2015-02-03 | L2 |  |  |  | 0.9 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (ND. REVISED 3/15 DBF & POSSIBLY REVISED 12/14 DBF PER WHAT JANET APPEL SAID. SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 52.23 | UG/L | 80.4999 | 2015-02-03 | L2 |  |  |  | 0.9 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (ND. REVISED 3/15 DBF & POSSIBLY REVISED 12/14 DBF PER WHAT JANET APPEL SAID. SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.4 | UG/L | 60.4999 | 2015-02-03 | L4 |  |  |  | 0.7 | LKM-28 419 PALM CREST LN LAKE MARY (NEED REVISED DBF ? ORIG. DBF NOT IN OC ? SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 55.5 | UG/L | 80.4999 | 2015-02-03 | L4 |  |  |  | 0.7 | LKM-28 419 PALM CREST LN LAKE MARY (NEED REVISED DBF ? ORIG. DBF NOT IN OC ? SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.61 | UG/L | 60.4999 | 2015-02-03 | L1 |  |  |  | 0.9 | LKM-33 3580 N. HWY 17-92 LAKE MARY (NEED REVISED DBF ? ORIG. DBF NOT IN OC ? SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 48.31 | UG/L | 80.4999 | 2015-02-03 | L1 |  |  |  | 0.9 | LKM-33 3580 N. HWY 17-92 LAKE MARY (NEED REVISED DBF ? ORIG. DBF NOT IN OC ? SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.58 | UG/L | 60.4999 | 2015-02-03 | L3 |  |  |  | 0.7 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (NEED REVISED DBF ? ORIG. DBF NOT IN OC ? SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 51.9 | UG/L | 80.4999 | 2015-02-03 | L3 |  |  |  | 0.7 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (NEED REVISED DBF ? ORIG. DBF NOT IN OC ? SEE 3/1/15 RCVD EM & 4/2/15 SENT EM) SYS. DOES NOT QUALIFY FOR R.M.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-03-02 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT (IN OC)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-05-04 | AAA |  | 0.5499 |  |  | POE SPECIAL VOC MONIT
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.68 | UG/L | 60.4999 | 2015-05-07 | L4 |  |  |  | 0.8 | LKM-28 419 PALM CREST LN LAKE MARY (SYS. DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-07 | AAA |  |  |  |  | BILLING IS DONE @ 4/25/16 - MAY ND. PN BY THURSDAY AFTERNOON 4/14/16 - BB (JILL ALVAREZ FINANCE MAY HANDLE DISTRIBUTION)
3590201 | LAKE MARY CITY OF | INOR | 1040 | NITRATE | N | 0.12 | MG/L | 10.4999 | 2015-05-07 | AAA |  |  |  |  | BILLING IS DONE @ 4/25/16 - MAY ND. PN BY THURSDAY AFTERNOON 4/14/16 - BB (JILL ALVAREZ FINANCE MAY HANDLE DISTRIBUTION)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 51.79 | UG/L | 80.4999 | 2015-05-07 | L2 |  |  |  | 0.8 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (SYS. DOES NOT QUALIFY FOR R.M.)>>>>>>10/24/15 EW HAS 8/15 DBPS & 9/15 DBF FOR PROCESSING
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 49.72 | UG/L | 80.4999 | 2015-05-07 | L4 |  |  |  | 0.8 | LKM-28 419 PALM CREST LN LAKE MARY (SYS. DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 53.48 | UG/L | 80.4999 | 2015-05-07 | L3 |  |  |  | 0.7 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (SYS. DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.59 | UG/L | 60.4999 | 2015-05-07 | L3 |  |  |  | 0.7 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (SYS. DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 37.1 | UG/L | 80.4999 | 2015-05-07 | L1 |  |  |  | 0.9 | LKM-33 3580 N. HWY 17-92 LAKE MARY (SYS. DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.35 | UG/L | 60.4999 | 2015-05-07 | L1 |  |  |  | 0.9 | LKM-33 3580 N. HWY 17-92 LAKE MARY (SYS. DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.25 | UG/L | 60.4999 | 2015-05-07 | L2 |  |  |  | 0.8 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (SYS. DOES NOT QUALIFY FOR R.M.)>>>>>>10/24/15 EW HAS 8/15 DBPS & 9/15 DBF FOR PROCESSING
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 2.9 | UG/L | 10499.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0.21 | UG/L | 74.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0.67 | UG/L | 749.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-06-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC (XY 2.9 ETH 0.67) 2QM/X+E 9/15
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 54.42 | UG/L | 80.4999 | 2015-08-11 | L4 |  |  |  | 0.6 | LKM-28 419 PALM CREST LN LAKE MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.71 | UG/L | 60.4999 | 2015-08-11 | L1 |  |  |  | 1 | LKM-33 3580 N. HWY 17-92 LAKE MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 47.33 | UG/L | 80.4999 | 2015-08-11 | L1 |  |  |  | 1 | LKM-33 3580 N. HWY 17-92 LAKE MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.87 | UG/L | 60.4999 | 2015-08-11 | L3 |  |  |  | 1 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 51.58 | UG/L | 80.4999 | 2015-08-11 | L3 |  |  |  | 1 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.89 | UG/L | 60.4999 | 2015-08-11 | L4 |  |  |  | 0.6 | LKM-28 419 PALM CREST LN LAKE MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.87 | UG/L | 60.4999 | 2015-08-11 | L2 |  |  |  | 1.2 | (4TH QTR 2015 DBF IN OC ALREADY) LKM-51 930 WILLISTON PARK PT. LAKE MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 45.2 | UG/L | 80.4999 | 2015-08-11 | L2 |  |  |  | 1.2 | (4TH QTR 2015 DBF IN OC ALREADY) LKM-51 930 WILLISTON PARK PT. LAKE MARY (ALL LRAAS/T IN 40S-50S PER 9/15 DBF LRAA/H < 20) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-09-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2QM/X+E 9/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-10-05 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-11-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.09 | UG/L | 60.4999 | 2015-11-03 | L4 |  |  |  | 0.8 | LKM-28 419 PALM CREST LN LAKE MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 48.26 | UG/L | 80.4999 | 2015-11-03 | L4 |  |  |  | 0.8 | LKM-28 419 PALM CREST LN LAKE MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.62 | UG/L | 60.4999 | 2015-11-03 | L1 |  |  |  | 0.8 | LKM-33 3580 N. HWY 17-92 LAKE MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 45.85 | UG/L | 80.4999 | 2015-11-03 | L2 |  |  |  | 0.8 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.68 | UG/L | 60.4999 | 2015-11-03 | L3 |  |  |  | 0.9 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 52.12 | UG/L | 80.4999 | 2015-11-03 | L3 |  |  |  | 0.9 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.29 | UG/L | 60.4999 | 2015-11-03 | L2 |  |  |  | 0.8 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 45.2 | UG/L | 80.4999 | 2015-11-03 | L1 |  |  |  | 0.8 | LKM-33 3580 N. HWY 17-92 LAKE MARY (12/15 DBF IN OC ALL LRAAS/T IN 40S-50S PER 12/15 DBF LRAA/H < 21) DOES NOT QUALIFY FOR R.M. NO OE EXCEEDANCES
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-12-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+3QM/X+E 12/15 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-01-04 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-02-01 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.97 | UG/L | 60.4999 | 2016-02-02 | L1 |  |  |  | 1.1 | LKM-33 3580 N. HWY 17-92 LAKE MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 50.65 | UG/L | 80.4999 | 2016-02-02 | L1 |  |  |  | 1.1 | LKM-33 3580 N. HWY 17-92 LAKE MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.5 | UG/L | 60.4999 | 2016-02-02 | L4 |  |  |  | 1 | LKM-28 419 PALM CREST LN LAKE MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 51.84 | UG/L | 80.4999 | 2016-02-02 | L2 |  |  |  | 1 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.72 | UG/L | 60.4999 | 2016-02-02 | L2 |  |  |  | 1 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 59.82 | UG/L | 80.4999 | 2016-02-02 | L4 |  |  |  | 1 | LKM-28 419 PALM CREST LN LAKE MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.94 | UG/L | 60.4999 | 2016-02-02 | L3 |  |  |  | 1.1 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 53.19 | UG/L | 80.4999 | 2016-02-02 | L3 |  |  |  | 1.1 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-03-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+4QM/X+E 3/16 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-04-13 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.53 | UG/L | 60.4999 | 2016-05-02 | L4 | 0.2 |  | 1 | 1.1 | LKM-28 419 PALM CREST LN LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 53.36 | UG/L | 80.4999 | 2016-05-02 | L4 | 0.14 |  | 1 | 1.1 | LKM-28 419 PALM CREST LN LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.22 | UG/L | 60.4999 | 2016-05-02 | L1 | 0.2 |  | 2 | 1.2 | LKM-33 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 40.33 | UG/L | 80.4999 | 2016-05-02 | L1 | 0.14 |  | 2 | 1.2 | LKM-33 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.07 | UG/L | 60.4999 | 2016-05-02 | L3 | 0.2 |  | 3 | 1.2 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 30.3 | UG/L | 80.4999 | 2016-05-02 | L3 | 0.14 |  | 3 | 1.2 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.08 | UG/L | 60.4999 | 2016-05-02 | L2 | 0.2 |  | 4 | 1.4 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (FINAL REVISED 2ND QTR 2016 DB REPORT IN OCULUS) 9/20/16 EW HAS 3Q DBPS BY EM TO PROCESS. JOE GONZALEZ WILL SEND REVISED 3Q 2016 DISINF BYP REPORT-9/30/16 EM)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 66.23 | UG/L | 80.4999 | 2016-05-02 | L2 | 0.14 |  | 4 | 1.4 | LKM-51 930 WILLISTON PARK PT. LAKE MARY (FINAL REVISED 2ND QTR 2016 DB REPORT IN OCULUS) 9/20/16 EW HAS 3Q DBPS BY EM TO PROCESS. JOE GONZALEZ WILL SEND REVISED 3Q 2016 DISINF BYP REPORT-9/30/16 EM)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-05-03 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | INOR | 1040 | NITRATE | N | 0.27 | MG/L | 10.4999 | 2016-05-03 | AAA | 0.051
3590201 | LAKE MARY CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-03 | AAA | 0.053
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-06-06 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-07-07 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR (JANET APPEL NO LONGER AT LAKE MARY AFTER 3/2/16) ALSO RHONDA GORMAN WP OPR 6/16.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-08-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 48.2 | UG/L | 80.4999 | 2016-08-04 | L2 | 0.14 |  | 4 |  | 930 WILLISTON PARK PT.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 34.36 | UG/L | 80.4999 | 2016-08-04 | L4 | 0.14 |  | 1 | 1.1 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.59 | UG/L | 60.4999 | 2016-08-04 | L4 | 0.2 |  | 1 | 1.1 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.19 | UG/L | 60.4999 | 2016-08-04 | L1 | 0.2 |  | 2 | 1.2 | 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 46.79 | UG/L | 80.4999 | 2016-08-04 | L1 | 0.14 |  | 2 | 1.2 | 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.66 | UG/L | 60.4999 | 2016-08-04 | L3 | 0.2 |  | 3 | 1.2 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 48.19 | UG/L | 80.4999 | 2016-08-04 | L3 | 0.14 |  | 3 | 1.2 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.94 | UG/L | 60.4999 | 2016-08-04 | L2 | 0.2 |  | 4 |  | 930 WILLISTON PARK PT.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 1.6 | UG/L | 7.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 4 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 13 | UG/L | 7.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 5 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL-1 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 6 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0.63 | UG/L | 7.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-14 | WELL 2 |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0.44 | UG/L | 7.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-09-14 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-10-03 | AAA |  | 0.5499 |  |  | LKM-2 255 RINEHART RD WELL #3
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-10-04 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.49 | UG/L | 60.4999 | 2016-11-03 | L4 |  |  |  | 1.3 | LKM-28 419 PALM CREST LN LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 46.36 | UG/L | 80.4999 | 2016-11-03 | L4 |  |  |  | 1.3 | LKM-28 419 PALM CREST LN LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.56 | UG/L | 60.4999 | 2016-11-03 | L1 |  |  |  | 1.5 | LKM-33 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 38.44 | UG/L | 80.4999 | 2016-11-03 | L1 |  |  |  | 1.5 | LKM-33 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.3 | UG/L | 60.4999 | 2016-11-03 | L3 |  |  |  | 1.1 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 66.49 | UG/L | 80.4999 | 2016-11-03 | L3 |  |  |  | 1.1 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.49 | UG/L | 60.4999 | 2016-11-03 | L2 |  |  |  | 0.6 | LKM-51 930 WILLISTON PARK PT. LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 47.93 | UG/L | 80.4999 | 2016-11-03 | L2 |  |  |  | 0.6 | LKM-51 930 WILLISTON PARK PT. LAKE MARY
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-03 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER EFF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 11 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-5 420 RINEHART RD WELL #5
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-6 235 RINEHART RD WELL #6
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | TOWER INF 235 RINEHART RD
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-1 235 RINEHART RD WELL #1
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-2 235 RINEHART RD WELL #2
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-3 235 RINEHART RD WTP POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | S | 2.1 | UG/L | 7.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-12-05 | AAA |  | 0.5499 |  |  | LKM-4 401 RINEHART RD WELL #4
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-01-04 | AAA | 0.18 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-01-04 | AAA | 0.39 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-01-04 | AAA | 0.17 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-01-04 | AAA | 0.22 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-01-04 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-01-04 | AAA | 0.32 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-01-04 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-01-04 | AAA | 0.44 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-01-04 | AAA | 0.46 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-01-04 | AAA | 0.26 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-01-04 | AAA | 0.2 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-01-04 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-01-04 | AAA | 0.36 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-01-04 | AAA | 0.39 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-01-04 | AAA | 0.23 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-01-04 | AAA | 0.26 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-04 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-01-04 | AAA | 0.12 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-04 | AAA | 0.24 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-01-04 | AAA | 0.12 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-01-04 | AAA | 0.17 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.35 | UG/L | 60.4999 | 2017-02-01 | L1 | 0.2 |  | 2 | 1.3 | 3580 N. HWY 17-92
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 42.92 | UG/L | 80.4999 | 2017-02-01 | L1 | 0.14 |  | 2 | 1.3 | 3580 N. HWY 17-92
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.87 | UG/L | 60.4999 | 2017-02-01 | L3 | 0.2 |  | 3 | 1.4 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 58.28 | UG/L | 80.4999 | 2017-02-01 | L3 | 0.14 |  | 3 | 1.4 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.49 | UG/L | 60.4999 | 2017-02-01 | L2 | 0.2 |  | 4 | 1.5 | 930 WILLISTON PARK PT. (3/17 DISINF BYP REPORT RCVD SEPARATELY-NO DBP LRAA MCL VIOLS NO OE EXCEEDANCES) CONT. TO TEST QUARTERLY UFN (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 55.21 | UG/L | 80.4999 | 2017-02-01 | L2 | 0.14 |  | 4 | 1.5 | 930 WILLISTON PARK PT. (3/17 DISINF BYP REPORT RCVD SEPARATELY-NO DBP LRAA MCL VIOLS NO OE EXCEEDANCES) CONT. TO TEST QUARTERLY UFN (DOES NOT QUALIFY FOR R.M.)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-01 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-01 | AAA | 0.32 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-01 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-01 | AAA | 0.44 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-01 | AAA | 0.46 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-01 | AAA | 0.26 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-01 | AAA | 0.2 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-01 | AAA | 0.18 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-01 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-01 | AAA | 0.36 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-01 | AAA | 0.39 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-01 | AAA | 0.23 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-01 | AAA | 0.26 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-01 | AAA | 0.28 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-01 | AAA | 0.12 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-01 | AAA | 0.24 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-01 | AAA | 0.12 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-01 | AAA | 0.17 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-01 | AAA | 0.22 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-01 | AAA | 0.17 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-01 | AAA | 0.39 | 0.5499 |  |  | (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE) POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.28 | UG/L | 60.4999 | 2017-02-01 | L4 | 0.2 |  | 1 | 1.3 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 48.84 | UG/L | 80.4999 | 2017-02-01 | L4 | 0.14 |  | 1 | 1.3 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-01 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-01 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-01 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-01 | AAA | 0.24 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-01 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-01 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-03-01 | AAA | 0.00013 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-03-01 | AAA | 6e-05 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | SEC | 1002 | ALUMINUM | N | 0.28 | MG/L | 0.2499 | 2017-03-01 | AAA | 0.061 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1017 | CHLORIDE | N | 19 | MG/L | 250.4999 | 2017-03-01 | AAA | 0.78 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1022 | COPPER | N | 0.0038 | MG/L | 1.4999 | 2017-03-01 | AAA | 0.00011 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1025 | FLUORIDE | N | 0.62 | MG/L | 2.0499 | 2017-03-01 | AAA | 0.075 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-03-01 | AAA | 0.03 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1032 | MANGANESE | N | 0.0015 | MG/L | 0.0549 | 2017-03-01 | AAA | 6e-05 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-03-01 | AAA | 3e-05 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1055 | SULFATE | N | 7.4 | MG/L | 250.4999 | 2017-03-01 | AAA | 0.52 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1095 | ZINC | N | 0.017 | MG/L | 5.4999 | 2017-03-01 | AAA | 0.002 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-03-01 | AAA | 5 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-03-01 | AAA | 1 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.41 | LN(10) |  | 2017-03-01 | AAA |  |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 190 | MG/L | 500.4999 | 2017-03-01 | AAA | 10 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-03-01 | AAA | 0.04 |  |  |  | ALUMINUM 0.28 (TAKE 1 ALUMINIUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF) 4/3/17 HYPERLINKED. SILVER 0.000040 WITH 0.000027 MDL - OK
3590201 | LAKE MARY CITY OF | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-01 | AAA | 0.0069 | 0.0149 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-01 | AAA | 0.0071 | 0.0249 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-01 | AAA | 0.0068 | 0.1499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-01 | AAA | 0.12 | 1.4999 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-01 | AAA | 1 | 1.4999 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-01 | AAA | 7.6 | 0.4499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-01 | AAA | 1.2 | 9.4999 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-01 | AAA | 6.5 | 6.4999 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-01 | AAA | 0.95 | 0.6499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-01 | AAA | 0.57 | 2.4999 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-03-01 | AAA | 0.19 | 0.0749 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-01 | AAA | 1.5 | 0.6499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-01 | AAA | 0.23 | 0.1499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-01 | AAA | 0.86 | 0.2499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-01 | AAA | 0.012 | 0.1499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-01 | AAA | 0.28 | 0.9499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-01 | AAA | 0.16 | 0.1499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-01 | AAA | 0.26 | 0.2499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-01 | AAA | 0.006 | 0.0449 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-01 | AAA | 0.0052 | 0.0249 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-01 | AAA | 1.5 | 0.1499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-01 | AAA | 0.32 | 0.2499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-01 | AAA | 0.0063 | 0.1499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-03-01 | AAA | 0.096 | 0.0249 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-01 | AAA | 0.069 | 0.0449 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-01 | AAA | 0.11 | 0.1499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-01 | AAA | 0.0059 | 0.0249 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-01 | AAA | 0.0061 | 0.0149 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-01 | AAA | 0.053 | 0.2499 |  |  | 1Q SOC (2 QTRS OF SOCS DUE IN 2017 AT LEAST 60 DAYS APART)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-01 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-01 | AAA | 0.32 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-01 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-01 | AAA | 0.44 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-01 | AAA | 0.46 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-01 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-01 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-01 | AAA | 0.18 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-01 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-01 | AAA | 0.36 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-01 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-01 | AAA | 0.23 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-01 | AAA | 0.22 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-01 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-01 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC & ALSO POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) JOE GONZALEZ WP OPR. CHAIN OF CUSTODY HAS WELL SITES. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | INOR | 1040 | NITRATE | N | 0.28 | MG/L | 10.4999 | 2017-03-01 | AAA | 0.051 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-01 | AAA | 0.053 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1005 | ARSENIC | N | 0.0003 | MG/L | 0.0104 | 2017-03-01 | AAA | 8e-05 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1010 | BARIUM | N | 0.0088 | MG/L | 2.4999 | 2017-03-01 | AAA | 0.00028 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-03-01 | AAA | 3e-05 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-03-01 | AAA | 0.00011 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-03-01 | AAA | 0.0048 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1025 | FLUORIDE | N | 0.62 | MG/L | 4.0499 | 2017-03-01 | AAA | 0.075 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1030 | LEAD | N | 0.0004 | MG/L | 0.0154 | 2017-03-01 | AAA | 0.00024 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-03-01 | AAA | 1e-05 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-03-01 | AAA | 0.00011 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-03-01 | AAA | 0.00058 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1052 | SODIUM | N | 9.9 | MG/L | 160.4999 | 2017-03-01 | AAA | 0.16 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | INOR | 1074 | ANTIMONY | N | 0.0001 | MG/L | 0.0065 | 2017-03-01 | AAA | 5e-05 |  |  |  | 2017: 1 ALUMINUM REC PER HQ'S RECENT GUIDANCE 5/25/17 PER JF - HYPERLINKED 4/3/17 (MERCURY 0.000035 WITH 0.000011 MDL ANTIMONY 0.000058 WITH 0.000046 MDL ALL OK ROUNDED IN PWS)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-04 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-04 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-04 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-04 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-04 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-04 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-04 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-04 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-04 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-04 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-04 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-04 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-04 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-04 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-04 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-04 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-04 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-05-03 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.57 | UG/L | 60.4999 | 2017-05-03 | L2 | 0.5 |  | 4 | 1.7 | LKM-51 930 WILLISTON PARK PT. LK MARY(6/17 DBF RCVD CONT.QM-DOES NOT QUALIFY FOR RED.MONIT.)J4 MS:2453 BROMO ACID 164% RECOV-IT IS A NON-DETECTION BIASED HIGH-ACCEPTABLE FOR COMPLIANCE PURPOSES-BB/BW.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 67.47 | UG/L | 80.4999 | 2017-05-03 | L3 | 0.14 |  | 3 | 1.3 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (LIBERTY PARK)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.41 | UG/L | 60.4999 | 2017-05-03 | L3 | 0.5 |  | 3 | 1.3 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY (LIBERTY PARK)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 42.13 | UG/L | 80.4999 | 2017-05-03 | L1 | 0.14 |  | 2 | 1.6 | LKM-33 3580 N. HWY 17-92 LAKE MARY (VICTORIA SQUARE)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.02 | UG/L | 60.4999 | 2017-05-03 | L1 | 0.5 |  | 2 | 1.6 | LKM-33 3580 N. HWY 17-92 LAKE MARY (VICTORIA SQUARE)
3590201 | LAKE MARY CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-03 | AAA | 0.053 |  |  |  | NN (2017: 1 ALUMINUM RECCHECK PER HQ'S RECENT GUIDANCE 5/25/17 PER JF)
3590201 | LAKE MARY CITY OF | INOR | 1040 | NITRATE | N | 0.32 | MG/L | 10.4999 | 2017-05-03 | AAA | 0.051 |  |  |  | NN (2017: 1 ALUMINUM RECCHECK PER HQ'S RECENT GUIDANCE 5/25/17 PER JF)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 75.8 | UG/L | 80.4999 | 2017-05-03 | L4 | 0.14 |  | 1 | 1.6 | LKM-28 419 PALM CREST LN LAKE MARY (HUNTINGTON POOL)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.09 | UG/L | 60.4999 | 2017-05-03 | L4 | 0.5 |  | 1 | 1.6 | LKM-28 419 PALM CREST LN LAKE MARY (HUNTINGTON POOL)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-05-03 | AAA | 0.14 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-05-03 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-05-03 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-05-03 | AAA | 0.15 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-05-03 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-03 | AAA | 0.3 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-05-03 | AAA | 0.35 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-03 | AAA | 0.31 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-05-03 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-05-03 | AAA | 0.29 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-05-03 | AAA | 0.38 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-05-03 | AAA | 0.25 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-05-03 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 65.04 | UG/L | 80.4999 | 2017-05-03 | L2 | 0.14 |  | 4 | 1.7 | LKM-51 930 WILLISTON PARK PT. LK MARY(6/17 DBF RCVD CONT.QM-DOES NOT QUALIFY FOR RED.MONIT.)J4 MS:2453 BROMO ACID 164% RECOV-IT IS A NON-DETECTION BIASED HIGH-ACCEPTABLE FOR COMPLIANCE PURPOSES-BB/BW.
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-05-03 | AAA | 0.13 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-05-03 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-05-03 | AAA | 0.38 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-05-03 | AAA | 0.27 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-05-03 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-05-03 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-05-03 | AAA | 0.15 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW BRADLEY KOHL WP OPERATOR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-09 | AAA | 0.006 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-09 | AAA | 0.0069 | 0.0149 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-09 | AAA | 0.0071 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-09 | AAA | 0.0068 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-09 | AAA | 0.12 | 1.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-09 | AAA | 0.0063 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-09 | AAA | 0.069 | 0.0449 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-09 | AAA | 0.096 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-09 | AAA | 0.32 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-09 | AAA | 1.5 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-09 | AAA | 0.0052 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-09 | AAA | 0.006 | 0.0449 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-09 | AAA | 0.26 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-09 | AAA | 0.16 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-09 | AAA | 0.28 | 0.9499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-09 | AAA | 0.012 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-09 | AAA | 0.86 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-09 | AAA | 0.23 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-09 | AAA | 1.5 | 0.6499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-09 | AAA | 0.19 | 0.0749 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-09 | AAA | 0.57 | 2.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-09 | AAA | 0.95 | 0.6499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-09 | AAA | 6.5 | 6.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-09 | AAA | 1.2 | 9.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-09 | AAA | 7.6 | 0.4499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-09 | AAA | 1 | 1.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-09 | AAA | 0.0062 | 0.0149 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-09 | AAA | 0.11 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-09 | AAA | 0.053 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS OF SOCS DONE IN 2017
3590201 | LAKE MARY CITY OF | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-05-30 | AAA | 0.061 |  |  |  | ALUMINUM RETEST (HYPERLINKED 6/19/17 TO BW - PG1 COMPLETED)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-06-12 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-06-12 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-06-12 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-06-12 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-06-12 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-06-12 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-06-12 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-06-12 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-06-12 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-06-12 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-06-12 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-06-12 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-06-12 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-06-12 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-06-12 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-06-12 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-06-12 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-06-12 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-06-12 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-06-12 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-06-12 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+1AM/X+E DUE 2Q 2017 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-07-05 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-07-05 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-07-05 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-07-05 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-07-05 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-07-05 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-07-05 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-07-05 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-07-05 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-07-05 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-07-05 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-07-05 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-07-05 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-07-05 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-07-05 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-07-05 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-07-05 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-07-05 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-07-05 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-07-05 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-07-05 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-08-01 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-08-01 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-08-01 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-08-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-08-01 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-08-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-08-01 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-08-01 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-08-01 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-08-01 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-08-01 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-08-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-08-01 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-08-01 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-08-01 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-08-01 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-08-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-08-01 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-08-01 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-08-01 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-08-01 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 56.69 | UG/L | 80.4999 | 2017-08-03 | L2 | 0.14 |  | 4 | 1.6 | LKM-51 930 WILLISTON PARK PT. LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.96 | UG/L | 60.4999 | 2017-08-03 | L4 | 0.5 |  | 1 | 0.6 | LKM-28 419 PALM CREST LN LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 71.98 | UG/L | 80.4999 | 2017-08-03 | L4 | 0.14 |  | 1 | 0.6 | LKM-28 419 PALM CREST LN LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.01 | UG/L | 60.4999 | 2017-08-03 | L1 | 0.5 |  | 2 | 1.35 | LKM-33 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 62.73 | UG/L | 80.4999 | 2017-08-03 | L1 | 0.14 |  | 2 | 1.35 | LKM-33 3580 N. HWY 17-92 LAKE MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.92 | UG/L | 60.4999 | 2017-08-03 | L3 | 0.5 |  | 3 | 0.91 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 76.26 | UG/L | 80.4999 | 2017-08-03 | L3 | 0.14 |  | 3 | 0.91 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.64 | UG/L | 60.4999 | 2017-08-03 | L2 | 0.5 |  | 4 | 1.6 | LKM-51 930 WILLISTON PARK PT. LAKE MARY
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-09-06 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-06 | AAA | 0.25 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-09-06 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-06 | AAA | 0.25 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-09-06 | AAA | 0.35 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-09-06 | AAA | 0.15 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-09-06 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-09-06 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-09-06 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-09-06 | AAA | 0.27 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-09-06 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-09-06 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-09-06 | AAA | 0.34 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-09-06 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-09-06 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-09-06 | AAA | 0.19 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-09-06 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-09-06 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-09-06 | AAA | 0.48 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-09-06 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-09-06 | AAA | 0.45 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-10-11 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-10-11 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-10-11 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-10-11 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-10-11 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-10-11 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-10-11 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-10-11 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-10-11 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-10-11 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-10-11 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-10-11 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-10-11 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-10-11 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-10-11 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-10-11 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-10-11 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-10-11 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-10-11 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-10-11 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-10-11 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-11-01 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-11-01 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-11-01 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-11-01 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-11-01 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-11-01 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-11-01 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-11-01 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-11-01 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-11-01 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-11-01 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-11-01 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-11-01 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-11-01 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.88 | UG/L | 60.4999 | 2017-11-02 | L4 | 0.5 |  | 1 | 0.92 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 33.5 | UG/L | 80.4999 | 2017-11-02 | L2 | 0.14 |  | 4 | 1.11 | 930 WILLISTON PARK PT. (11/17 DBPS RCVD W/ 2017-4Q DISINF BYP REPORT) CONTINUE TO TEST QTRLY NO ISSUES NOTED - BB
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.01 | UG/L | 60.4999 | 2017-11-02 | L2 | 0.5 |  | 4 | 1.11 | 930 WILLISTON PARK PT. (11/17 DBPS RCVD W/ 2017-4Q DISINF BYP REPORT) CONTINUE TO TEST QTRLY NO ISSUES NOTED - BB
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 47.86 | UG/L | 80.4999 | 2017-11-02 | L3 | 0.14 |  | 3 | 0.71 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.84 | UG/L | 60.4999 | 2017-11-02 | L3 | 0.5 |  | 3 | 0.71 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 39.36 | UG/L | 80.4999 | 2017-11-02 | L4 | 0.14 |  | 1 | 0.92 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.44 | UG/L | 60.4999 | 2017-11-02 | L1 | 0.5 |  | 2 | 1 | 3580 N. HWY 17-92
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 29.43 | UG/L | 80.4999 | 2017-11-02 | L1 | 0.14 |  | 2 | 1 | 3580 N. HWY 17-92
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-12-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-12-04 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-12-04 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-12-04 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-12-04 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-12-04 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-12-04 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-12-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-12-04 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-12-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-12-04 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-12-04 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-12-04 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-12-04 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-12-04 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-12-04 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-12-04 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-12-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-12-04 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-12-04 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-12-04 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-01-04 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-01-04 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-01-04 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-01-04 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-01-04 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-01-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-01-04 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-01-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-01-04 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-01-04 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-01-04 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-01-04 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-01-04 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-01-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-01-04 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-01-04 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-01-04 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-01-04 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-01-04 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-01-04 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-01-04 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-01 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 43.82 | UG/L | 80.4999 | 2018-02-01 | L2 | 0.14 |  | 4 | 1.2 | 930 WILLISTON PARK PT.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.36 | UG/L | 60.4999 | 2018-02-01 | L2 | 0.5 |  | 4 | 1.2 | 930 WILLISTON PARK PT.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 54.18 | UG/L | 80.4999 | 2018-02-01 | L3 | 0.14 |  | 3 | 0.9 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.55 | UG/L | 60.4999 | 2018-02-01 | L3 | 0.5 |  | 3 | 0.9 | 455 N. COUNTRY CLUB RD.
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 37.8 | UG/L | 80.4999 | 2018-02-01 | L1 | 0.14 |  | 2 | 1.2 | 3580 N. HWY 17-92
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.94 | UG/L | 60.4999 | 2018-02-01 | L1 | 0.5 |  | 2 | 1.2 | 3580 N. HWY 17-92
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 47.37 | UG/L | 80.4999 | 2018-02-01 | L4 | 0.14 |  | 1 | 0.99 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.15 | UG/L | 60.4999 | 2018-02-01 | L4 | 0.5 |  | 1 | 0.99 | 419 PALM CREST LN.
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-01 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-01 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-01 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-01 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-01 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-01 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-01 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-01 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-01 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-01 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-01 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-01 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-01 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-01 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-01 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-01 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-01 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-03-07 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-03-07 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-03-07 | AAA | 0.053 |  |  |  | NN
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | INOR | 1040 | NITRATE | N | 0.25 | MG/L | 10.4999 | 2018-03-07 | AAA | 0.051 |  |  |  | NN
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-03-07 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-03-07 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-03-07 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-03-07 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-03-07 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-03-07 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-03-07 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-03-07 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-03-07 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-04 | AAA | 0.35 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-04 | AAA | 0.15 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-04 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-04 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-04 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-04 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-04 | AAA | 0.45 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-04 | AAA | 0.25 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-04 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-04 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-04 | AAA | 0.19 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-04 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-04 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-04 | AAA | 0.34 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-04 | AAA | 0.21 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-04 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-04 | AAA | 0.27 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-04 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-04 | AAA | 0.25 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-04 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-04 | AAA | 0.48 | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-02 | AAA |  | 0.5499 |  |  | POE SPEC. VOC+2AM/X+E DUE 2Q 2018 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.19 | UG/L | 60.4999 | 2018-05-03 | L1 | 0.91 |  | 2 | 1.06 | LKM 33
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 36.67 | UG/L | 80.4999 | 2018-05-03 | L1 | 0.14 |  | 2 | 1.06 | LKM 33
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.16 | UG/L | 60.4999 | 2018-05-03 | L3 | 0.91 |  | 3 | 0.92 | LKM 32
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 57.47 | UG/L | 80.4999 | 2018-05-03 | L4 | 0.14 |  | 1 | 0.95 | LKM-28
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.8 | UG/L | 60.4999 | 2018-05-03 | L2 | 0.91 |  | 4 | 0.93 | LKM 52
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 51.85 | UG/L | 80.4999 | 2018-05-03 | L2 | 0.14 |  | 4 | 0.93 | LKM 52
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.56 | UG/L | 60.4999 | 2018-05-03 | L4 | 0.91 |  | 1 | 0.95 | LKM-28
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 65.04 | UG/L | 80.4999 | 2018-05-03 | L3 | 0.14 |  | 3 | 0.92 | LKM 32
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-06-13 | AAA | 0.24 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-06-13 | AAA | 0.12 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-06-13 | AAA | 0.17 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-06-13 | AAA | 0.22 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-06-13 | AAA | 0.17 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-06-13 | AAA | 0.39 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-06-13 | AAA | 0.28 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-06-13 | AAA | 0.32 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-06-13 | AAA | 0.28 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-06-13 | AAA | 0.44 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-06-13 | AAA | 0.46 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-06-13 | AAA | 0.26 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-06-13 | AAA | 0.2 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-06-13 | AAA | 0.18 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-06-13 | AAA | 0.28 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-06-13 | AAA | 0.12 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-06-13 | AAA | 0.28 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-06-13 | AAA | 0.26 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-06-13 | AAA | 0.23 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-06-13 | AAA | 0.36 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-06-13 | AAA | 0.39 | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-07-10 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-07-10 | AAA | 0.22 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-07-10 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-07-10 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-10 | AAA | 0.24 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-07-10 | AAA | 0.12 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-10 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-07-10 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-07-10 | AAA | 0.23 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-07-10 | AAA | 0.17 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-07-10 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-07-10 | AAA | 0.32 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-07-10 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-07-10 | AAA | 0.44 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-07-10 | AAA | 0.46 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-07-10 | AAA | 0.26 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-07-10 | AAA | 0.2 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-07-10 | AAA | 0.18 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-07-10 | AAA | 0.28 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-07-10 | AAA | 0.36 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-07-10 | AAA | 0.39 | 0.5499 |  |  | POE SPEC. VOC+3AM/X+E DUE 2Q 2019 (DETECTS XY & ETH 6/15 IN POE/D SPECIAL VOCS) WAS JOE GONZALEZ WP OPR; NOW SCOTT RANKIN CHIEF OPR & SAMPLER ON REPORT. (ONLY LKM-3 NEEDS PWS ENTRY - POE/D SAMPLE)
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-01 | AAA |  | 0.5499 |  |  | ONLY LKM-3 NEEDS PWS ENTRY (POE)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 34.53 | UG/L | 80.4999 | 2018-08-08 | L2 | 0.39 |  | 4 | 0.5 | 930 WILLISTON PARK PT
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 26.4 | UG/L | 80.4999 | 2018-08-08 | L1 | 0.39 |  | 2 | 0.62 | 3580 N HWY 17 92
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11 | UG/L | 60.4999 | 2018-08-08 | L1 | 0.91 |  | 2 | 0.62 | 3580 N HWY 17 92
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.31 | UG/L | 60.4999 | 2018-08-08 | L3 | 0.91 |  | 3 | 0.53 | 455 N COUNTY CLUB RD
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 33.01 | UG/L | 80.4999 | 2018-08-08 | L3 | 0.39 |  | 3 | 0.53 | 455 N COUNTY CLUB RD
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 34.67 | UG/L | 80.4999 | 2018-08-08 | L4 | 0.39 |  | 1 | 0.53 | 419 PALM CREST
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.32 | UG/L | 60.4999 | 2018-08-08 | L4 | 0.91 |  | 1 | 0.53 | 419 PALM CREST
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.4 | UG/L | 60.4999 | 2018-08-08 | L2 | 0.91 |  | 4 | 0.5 | 930 WILLISTON PARK PT
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-09-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-10-03 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-11-07 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.35 | UG/L | 60.4999 | 2018-11-08 | L1 | 0.91 |  | 2 | 0.97
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 55.05 | UG/L | 80.4999 | 2018-11-08 | L4 | 0.56 |  | 1 | 1.12
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.93 | UG/L | 60.4999 | 2018-11-08 | L4 | 0.91 |  | 1 | 1.12
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.37 | UG/L | 60.4999 | 2018-11-08 | L3 | 0.91 |  | 3 | 0.9
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 79.27 | UG/L | 80.4999 | 2018-11-08 | L3 | 0.56 |  | 3 | 0.9
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.24 | UG/L | 60.4999 | 2018-11-08 | L2 | 0.91 |  | 4 | 1.23
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 54.82 | UG/L | 80.4999 | 2018-11-08 | L2 | 0.56 |  | 4 | 1.23
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 45.6 | UG/L | 80.4999 | 2018-11-08 | L1 | 0.56 |  | 2 | 0.97
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-12-12 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-01-09 | AAA | 0.2 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-01-09 | AAA | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-01-09 | AAA | 0.22 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-01-09 | AAA | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-01-09 | AAA | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-01-09 | AAA | 0.24 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-01-09 | AAA | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-01-09 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-01-09 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-01-09 | AAA | 0.32 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-01-09 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-01-09 | AAA | 0.44 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-01-09 | AAA | 0.46 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-01-09 | AAA | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-01-09 | AAA | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-01-09 | AAA | 0.18 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-01-09 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-01-09 | AAA | 0.36 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-01-09 | AAA | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-01-09 | AAA | 0.23 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-01-09 | AAA | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-02-04 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-02-05 | AAA | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-02-05 | AAA | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-02-05 | AAA | 0.22 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-02-05 | AAA | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-02-05 | AAA | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-02-05 | AAA | 0.24 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-02-05 | AAA | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-02-05 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-02-05 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-02-05 | AAA | 0.32 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-02-05 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-02-05 | AAA | 0.44 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-02-05 | AAA | 0.46 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-02-05 | AAA | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-02-05 | AAA | 0.2 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-02-05 | AAA | 0.18 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-02-05 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-02-05 | AAA | 0.36 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-02-05 | AAA | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-02-05 | AAA | 0.23 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-02-05 | AAA | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 44.7 | UG/L | 80.4999 | 2019-02-14 | L2 | 0.39 |  | 4 | 0.88 | LKM 51
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.9 | UG/L | 60.4999 | 2019-02-14 | L2 | 0.91 |  | 4 | 0.88 | LKM 51
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 54.44 | UG/L | 80.4999 | 2019-02-14 | L3 | 0.39 |  | 3 | 0.66 | LKM 32
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | M | 54.44 | UG/L | 80.4999 | 2019-02-14 | L3
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 21.54 | UG/L | 60.4999 | 2019-02-14 | L3
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | N | 36.01 | UG/L | 80.4999 | 2019-02-14 | L1
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | N | 11.95 | UG/L | 60.4999 | 2019-02-14 | L1
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | N | 16.47 | UG/L | 60.4999 | 2019-02-14 | L4
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | N | 48.72 | UG/L | 80.4999 | 2019-02-14 | L4
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.54 | UG/L | 60.4999 | 2019-02-14 | L3 | 0.91 |  | 3 | 0.66 | LKM 32
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 36.01 | UG/L | 80.4999 | 2019-02-14 | L1 | 0.39 |  | 2 | 1.2 | LKM 33
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.95 | UG/L | 60.4999 | 2019-02-14 | L1 | 0.91 |  | 2 | 1.2 | LKM 33
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 48.72 | UG/L | 80.4999 | 2019-02-14 | L4 | 0.39 |  | 1 | 0.65 | LKM-28
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.47 | UG/L | 60.4999 | 2019-02-14 | L4 | 0.91 |  | 1 | 0.65 | LKM-28
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | INOR | 1040 | NITRATE | N | 0.34 | MG/L | 10.4999 | 2019-03-05 | AAA
3590201 | LAKE MARY CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-03-05 | AAA
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-03-05 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-05-02 | AAA | 0.23 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-05-02 | AAA | 0.32 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-05-02 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-05-02 | AAA | 0.44 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-05-02 | AAA | 0.46 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-05-02 | AAA | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-05-02 | AAA | 0.2 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-05-02 | AAA | 0.18 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-05-02 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-05-02 | AAA | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-05-02 | AAA | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-05-02 | AAA | 0.22 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-05-02 | AAA | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-05-02 | AAA | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-05-02 | AAA | 0.24 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-05-02 | AAA | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-05-02 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-05-02 | AAA | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-05-02 | AAA | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-05-02 | AAA | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-05-02 | AAA | 0.36 | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | SEC | 1032 | MANGANESE | N | 0.0015 | MG/L | 0.0549 | 2019-05-06 | AAA | 0.00055 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2019-05-06 | AAA | 7e-05 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1055 | SULFATE | N | 17 | MG/L | 250.4999 | 2019-05-06 | AAA | 2.6 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2019-05-06 | AAA | 0.05 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1905 | COLOR | N | 10 | COLOR UNITS | 15.4999 | 2019-05-06 | AAA | 5 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2019-05-06 | AAA | 1 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.18 | LN(10) |  | 2019-05-06 | AAA |  |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 190 | MG/L | 500.4999 | 2019-05-06 | AAA | 5 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2019-05-06 | AAA | 0.04 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1005 | ARSENIC | N | 0.0002 | MG/L | 0.0104 | 2019-05-06 | AAA | 8e-05 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1010 | BARIUM | N | 0.0091 | MG/L | 2.4999 | 2019-05-06 | AAA | 0.001 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2019-05-06 | AAA | 6e-05 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2019-05-06 | AAA | 0.00011 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2019-05-06 | AAA | 0.0048 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1025 | FLUORIDE | N | 1.3 | MG/L | 4.0499 | 2019-05-06 | AAA | 0.38 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1030 | LEAD | N | 0.0003 | MG/L | 0.0154 | 2019-05-06 | AAA | 0.00024 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2019-05-06 | AAA | 5e-05 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2019-05-06 | AAA | 0.00098 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2019-05-06 | AAA | 0.00058 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1052 | SODIUM | N | 9.3 | MG/L | 160.4999 | 2019-05-06 | AAA | 0.35 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2019-05-06 | AAA | 0.00011 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2019-05-06 | AAA | 0.0005 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2019-05-06 | AAA | 6e-05 |  |  |  | NN OVER HOLDING TIME - HAVE Q QUALIFIERS (NN RESULTS NOT ENTERED) E53076/FL CY/E84589 (A1903575001) FL IN THIS SAMPLE A1903575001 IS OK-NO J QUAL. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2019-05-06 | AAA | 0.04 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1017 | CHLORIDE | N | 29 | MG/L | 250.4999 | 2019-05-06 | AAA | 1.5 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1022 | COPPER | N | 0.0028 | MG/L | 1.4999 | 2019-05-06 | AAA | 0.00035 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1025 | FLUORIDE | N | 1.3 | MG/L | 2.0499 | 2019-05-06 | AAA | 0.38 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2019-05-06 | AAA | 0.1 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (E82574/METALS) COPPER HARD TO READ - LOOKS LIKE 0.0028. FL IN THIS SAMPLE A1903575001 IS OK-NO J. (J QUAL ON A1903576002 ONLY-NOT LAKE MARY'S SMP) BB
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 36.33 | UG/L | 80.4999 | 2019-05-09 | L2 | 0.39 |  | 4 | 0.6 | 930 WILLISTON PARK PT. (H/E84589) 6/19 DISINF BYP RPRT RCVD W/RSLTS (HLKD)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.85 | UG/L | 60.4999 | 2019-05-09 | L2 | 0.91 |  | 4 | 0.6 | 930 WILLISTON PARK PT. (H/E84589) 6/19 DISINF BYP RPRT RCVD W/RSLTS (HLKD)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 49.41 | UG/L | 80.4999 | 2019-05-09 | L3 | 0.39 |  | 3 | 0.7 | 455 N. COUNTRY CLUB RD. (H/E84589)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.61 | UG/L | 60.4999 | 2019-05-09 | L3 | 0.91 |  | 3 | 0.7 | 455 N. COUNTRY CLUB RD. (H/E84589)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 32.23 | UG/L | 80.4999 | 2019-05-09 | L1 | 0.39 |  | 2 | 0.8 | 3580 N. HWY 17-92 (H/E84589)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.95 | UG/L | 60.4999 | 2019-05-09 | L1 | 0.91 |  | 2 | 0.8 | 3580 N. HWY 17-92 (H/E84589)
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.52 | UG/L | 60.4999 | 2019-05-09 | L4 | 0.91 |  | 1 | 0.7 | 419 PALM CREST LN. (H/E84589)
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 44 | UG/L | 80.4999 | 2019-05-09 | L4 | 0.39 |  | 1 | 0.7 | 419 PALM CREST LN. (H/E84589)
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-06-04 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-07-10 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - LKM-3 POE
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.75 | UG/L | 60.4999 | 2019-08-08 | L4 |  |  | 1 | 0.87 | LKM-28 419 PALM CREST LN LAKE MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 43.47 | UG/L | 80.4999 | 2019-08-08 | L4 |  |  | 1 | 0.87 | LKM-28 419 PALM CREST LN LAKE MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.29 | UG/L | 60.4999 | 2019-08-08 | L1 |  |  | 2 | 0.84 | LKM-33 3580 N. HWY 17-92 LAKE MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 40.18 | UG/L | 80.4999 | 2019-08-08 | L1 |  |  | 2 | 0.84 | LKM-33 3580 N. HWY 17-92 LAKE MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.59 | UG/L | 60.4999 | 2019-08-08 | L3 |  |  | 3 | 0.6 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 54.36 | UG/L | 80.4999 | 2019-08-08 | L3 |  |  | 3 | 0.6 | LKM-32 455 N. COUNTRY CLUB RD. LK MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.73 | UG/L | 60.4999 | 2019-08-08 | L2 |  |  | 4 | 0.8 | LKM-51 930 WILLISTON PARK PT. LAKE MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 44.41 | UG/L | 80.4999 | 2019-08-08 | L2 |  |  | 4 | 0.8 | LKM-51 930 WILLISTON PARK PT. LAKE MARY / SUBCONTRACT LABS E82535 E84589
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-09-11 | AAA |  | 0.5499 |  |  | SPECIAL VOC MONITORING - ENTER LKM-3 POE ONLY
3590201 | LAKE MARY CITY OF | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.1 | UG/L | 60.4999 | 2019-11-13 | L4 | 0.9 |  | 1 | 0.89 | 419 PALM CREST
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 53.7 | UG/L | 80.4999 | 2019-11-13 | L4 | 0.32 |  | 1 | 0.89 | 419 PALM CREST
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.2 | UG/L | 60.4999 | 2019-11-13 | L1 | 0.9 |  | 2 | 1.02 | 3580 N HWY 17-92
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 38.7 | UG/L | 80.4999 | 2019-11-13 | L1 | 0.32 |  | 2 | 1.02 | 3580 N HWY 17-92
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.8 | UG/L | 60.4999 | 2019-11-13 | L3 | 0.9 |  | 3 | 0.71 | 455 N COUNTRY CLUB RD
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 57.9 | UG/L | 80.4999 | 2019-11-13 | L3 | 0.32 |  | 3 | 0.71 | 455 N COUNTRY CLUB RD
3590201 | LAKE MARY CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.2 | UG/L | 60.4999 | 2019-11-13 | L2 | 0.9 |  | 5 | 1.15 | 930 WILLISTON PARK PT
3590201 | LAKE MARY CITY OF | DBP | 2950 | TOTAL THMS | D | 42.2 | UG/L | 80.4999 | 2019-11-13 | L2 | 0.32 |  | 5 | 1.15 | 930 WILLISTON PARK PT
3590201 | LAKE MARY CITY OF | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-11-13 | AAA |  | 0.5499
3590201 | LAKE MARY CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-11-13 | AAA |  | 0.5499
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 53.43 | UG/L | 80.4999 | 2015-02-19 | L2 |  |  |  | 0.7 | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.16 | UG/L | 60.4999 | 2015-02-19 | L2 |  |  |  | 0.7 | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 48.69 | UG/L | 80.4999 | 2015-02-19 | L1 |  |  |  | 1.5 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.45 | UG/L | 60.4999 | 2015-02-19 | L1 |  |  |  | 1.5 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 52.65 | UG/L | 80.4999 | 2015-02-19 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.01 | UG/L | 60.4999 | 2015-02-19 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 44.69 | UG/L | 80.4999 | 2015-02-19 | L3 |  |  |  | 0.5 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.69 | UG/L | 60.4999 | 2015-02-19 | L3 |  |  |  | 0.5 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.06 | UG/L | 60.4999 | 2015-05-18 | L2 |  |  |  | 0.8 | (10/30 EW HAS 8/20/15 DBPS FOR PROCESSING) SM-4 1057 N HWY 17-92 (5/15 DBPS & 6/15 DBF IN OC) SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES FOR ANY SITE-BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 50.41 | UG/L | 80.4999 | 2015-05-18 | L2 |  |  |  | 0.8 | (10/30 EW HAS 8/20/15 DBPS FOR PROCESSING) SM-4 1057 N HWY 17-92 (5/15 DBPS & 6/15 DBF IN OC) SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES FOR ANY SITE-BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | N | 25.54 | UG/L | 60.4999 | 2015-05-18 | L3 |  |  |  | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | N | 46.63 | UG/L | 80.4999 | 2015-05-18 | L3 |  |  |  | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.87 | UG/L | 60.4999 | 2015-05-18 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (5/15 DBPS & 6/15 DBF IN OC) SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES FOR ANY SITE-BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.65 | UG/L | 60.4999 | 2015-05-18 | L1 |  |  |  | 1.6 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 50.21 | UG/L | 80.4999 | 2015-05-18 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (5/15 DBPS & 6/15 DBF IN OC) SYS. DOES NOT QUALIFY FOR R.M. NO LRAA MCLS OR OE EXCEEDANCES FOR ANY SITE-BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.47 | UG/L | 80.4999 | 2015-05-18 | L1 |  |  |  | 1.6 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 53.43 | UG/L | 80.4999 | 2015-08-20 | L2 |  |  |  | 0.8 | SM-4 1057 N HWY 17-92 (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 58.13 | UG/L | 80.4999 | 2015-08-20 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.46 | UG/L | 60.4999 | 2015-08-20 | L1 |  |  |  | 1.6 | SM-2 235 W CHURCH AVE. (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 46.44 | UG/L | 80.4999 | 2015-08-20 | L1 |  |  |  | 1.6 | SM-2 235 W CHURCH AVE. (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.32 | UG/L | 60.4999 | 2015-08-20 | L2 |  |  |  | 0.8 | SM-4 1057 N HWY 17-92 (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 65.81 | UG/L | 80.4999 | 2015-08-20 | L3 |  |  |  | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.91 | UG/L | 60.4999 | 2015-08-20 | L3 |  |  |  | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.25 | UG/L | 60.4999 | 2015-08-20 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (9/15 QTR ALL LRAA/T > 40 H LOW) DOES NOT QUALIFY FOR R.M. NO MCLS NO OE EXCEEDANCES 9/15 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-06 | WTP1 |  |  |  |  | WP1 NN
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-06 | WTP1 |  |  |  |  | WP1 NN
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-10-06 | WTP2 |  |  |  |  | WP2 NN
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-10-06 | WTP2 |  |  |  |  | WP2 NN
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 74.04 | UG/L | 80.4999 | 2015-11-20 | L2 |  |  |  | 0.6 | (4/27 EW HAS 3/16 BAC) SM-4 1057 N HWY 17-92 (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.99 | UG/L | 60.4999 | 2015-11-20 | L3 |  |  |  | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.28 | UG/L | 60.4999 | 2015-11-20 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 58.73 | UG/L | 80.4999 | 2015-11-20 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.3 | UG/L | 60.4999 | 2015-11-20 | L1 |  |  |  | 0.8 | SM-2 235 W CHURCH AVE. (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.84 | UG/L | 60.4999 | 2015-11-20 | L2 |  |  |  | 0.6 | (4/27 EW HAS 3/16 BAC) SM-4 1057 N HWY 17-92 (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 56.98 | UG/L | 80.4999 | 2015-11-20 | L1 |  |  |  | 0.8 | SM-2 235 W CHURCH AVE. (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 68.04 | UG/L | 80.4999 | 2015-11-20 | L3 |  |  |  | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION (DOES NOT QUALIFY FOR R.M. - CONT. TO TEST DBPS QTRLY)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.66 | UG/L | 60.4999 | 2016-02-19 | L1 |  |  |  | 1.4 | SM-2 235 W CHURCH AVE. (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 38.96 | UG/L | 80.4999 | 2016-02-19 | L1 |  |  |  | 1.4 | SM-2 235 W CHURCH AVE. (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 56.35 | UG/L | 80.4999 | 2016-02-19 | L2 |  |  |  | 1.2 | (SEE TONY HOHMANN 7/11/16 EM WITH 6/16 QTR DBPS-MAY BE TESTING 1 SITE TWICE FOR 5/16 QTR DBPS) SM-4 1057 N HWY 17-92 (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 47.38 | UG/L | 80.4999 | 2016-02-19 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.15 | UG/L | 60.4999 | 2016-02-19 | L4 |  |  |  | 1.1 | ST1-2 900 NORTH ST (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 52.74 | UG/L | 80.4999 | 2016-02-19 | L3 |  |  |  | 1.1 | ST1-1 801 RAVEN AVE.=LIFT STATION (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.03 | UG/L | 60.4999 | 2016-02-19 | L3 |  |  |  | 1.1 | ST1-1 801 RAVEN AVE.=LIFT STATION (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.18 | UG/L | 60.4999 | 2016-02-19 | L2 |  |  |  | 1.2 | (SEE TONY HOHMANN 7/11/16 EM WITH 6/16 QTR DBPS-MAY BE TESTING 1 SITE TWICE FOR 5/16 QTR DBPS) SM-4 1057 N HWY 17-92 (DOES NOT QUALIFY FOR R.M.) NO OE OR LRAA EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 68.3 | UG/L | 80.4999 | 2016-05-19 | L4 |  |  |  | 1.6 | ST1-2 900 NORTH ST (DOES NOT QUALIFY FOR R.M.)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.79 | UG/L | 60.4999 | 2016-05-19 | L4 |  |  |  | 1.6 | ST1-2 900 NORTH ST (DOES NOT QUALIFY FOR R.M.)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 92.08 | UG/L | 80.4999 | 2016-05-19 | L3 |  |  |  | 0.6 | ST1-1 801 RAVEN AVE.=LIFT STATION (DOES NOT QUALIFY FOR R.M.) NO TTHM OE EXCEEDANCE 6/16 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.54 | UG/L | 60.4999 | 2016-05-19 | L3 |  |  |  | 0.6 | ST1-1 801 RAVEN AVE.=LIFT STATION (DOES NOT QUALIFY FOR R.M.) NO TTHM OE EXCEEDANCE 6/16 QTR
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 51.6 | UG/L | 80.4999 | 2016-05-19 | L1 |  |  |  | 1.6 | SM-2 235 W CHURCH AVE. (DOES NOT QUALIFY FOR R.M.)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.14 | UG/L | 60.4999 | 2016-05-19 | L1 |  |  |  | 1.6 | SM-2 235 W CHURCH AVE. (DOES NOT QUALIFY FOR R.M.)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.35 | UG/L | 60.4999 | 2016-05-19 | L2 |  |  |  | 1.1 | SM-4 1057 N HWY 17-92 (DOES NOT QUALIFY FOR R.M.)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 64.67 | UG/L | 80.4999 | 2016-05-19 | L2 |  |  |  | 1.1 | SM-4 1057 N HWY 17-92 (DOES NOT QUALIFY FOR R.M.)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.25 | UG/L | 60.4999 | 2016-08-12 | L4 |  |  |  | 1.2 | ST1-2 900 NORTH ST
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 67.32 | UG/L | 80.4999 | 2016-08-12 | L2 |  |  |  | 0.8 | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 58.68 | UG/L | 80.4999 | 2016-08-12 | L4 |  |  |  | 1.2 | ST1-2 900 NORTH ST
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 41.91 | UG/L | 80.4999 | 2016-08-12 | L1 |  |  |  | 1.9 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.2 | UG/L | 60.4999 | 2016-08-12 | L1 |  |  |  | 1.9 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 66.13 | UG/L | 80.4999 | 2016-08-12 | L3 |  |  |  | 0.9 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.65 | UG/L | 60.4999 | 2016-08-12 | L3 |  |  |  | 0.9 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.82 | UG/L | 60.4999 | 2016-08-12 | L2 |  |  |  | 0.8 | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-09-01 | WTP2 |  |  |  |  | WP2 NN
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-09-01 | WTP1 |  |  |  |  | WP1 NN
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-09-01 | WTP1 |  |  |  |  | WP1 NN
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-09-01 | WTP2 |  |  |  |  | WP2 NN
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.83 | UG/L | 60.4999 | 2016-11-23 | L4 | 0.2 |  | 2 | 0.7 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 45.18 | UG/L | 80.4999 | 2016-11-23 | L4 | 0.14 |  | 2 | 0.7 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.59 | UG/L | 60.4999 | 2016-11-23 | L1 | 0.2 |  | 3 | 1.7 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 31.71 | UG/L | 80.4999 | 2016-11-23 | L1 | 0.14 |  | 3 | 1.7 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.81 | UG/L | 60.4999 | 2016-11-23 | L2 | 0.2 |  | 4 | 1.2 | 1057 N.HWY 17-92(12/16 DB RPRT RCVD W/11/16 DBPS)HYPRLNKD TO BW 1/19/17-BB(DOES NOT QUALIFY FOR REDUCD MONIT NO LRAA/T OR LRAA/H EXCEEDANCES NO OE EXCEEDANCES)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 49.46 | UG/L | 80.4999 | 2016-11-23 | L2 | 0.14 |  | 4 | 1.2 | 1057 N.HWY 17-92(12/16 DB RPRT RCVD W/11/16 DBPS)HYPRLNKD TO BW 1/19/17-BB(DOES NOT QUALIFY FOR REDUCD MONIT NO LRAA/T OR LRAA/H EXCEEDANCES NO OE EXCEEDANCES)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.7 | UG/L | 60.4999 | 2016-11-23 | L3 | 0.2 |  | 1 | 1.4 | RAVEN AVE. L/S
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.64 | UG/L | 80.4999 | 2016-11-23 | L3 | 0.14 |  | 1 | 1.4 | RAVEN AVE. L/S
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 61 | UG/L | 80.4999 | 2017-02-27 | L3 | 0.14 |  | 1 | 0.9 | 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.48 | UG/L | 60.4999 | 2017-02-27 | L4 | 0.2 |  | 2 | 1 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 57.62 | UG/L | 80.4999 | 2017-02-27 | L4 | 0.14 |  | 2 | 1 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.92 | UG/L | 60.4999 | 2017-02-27 | L1 | 0.2 |  | 3 | 1.1 | 235. W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.38 | UG/L | 60.4999 | 2017-02-27 | L3 | 0.2 |  | 1 | 0.9 | 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 50.12 | UG/L | 80.4999 | 2017-02-27 | L1 | 0.14 |  | 3 | 1.1 | 235. W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 69.07 | UG/L | 80.4999 | 2017-02-27 | L2 | 0.14 |  | 4 | 0.9 | 1057 N. HWY 17-92 (3/17 DISINF BYP REPORT RCVD W/LAB REPORT) FINAL COMPLETE REVISION HYPERLINKED 4/24/17 TO BW - BB (ORIGINAL WHICH NEEDED REVISION HYPERLINKED EARLIER ON 4/18/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.02 | UG/L | 60.4999 | 2017-02-27 | L2 | 0.2 |  | 4 | 0.9 | 1057 N. HWY 17-92 (3/17 DISINF BYP REPORT RCVD W/LAB REPORT) FINAL COMPLETE REVISION HYPERLINKED 4/24/17 TO BW - BB (ORIGINAL WHICH NEEDED REVISION HYPERLINKED EARLIER ON 4/18/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-07 | WTP2 | 0.12 | 0.1499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP2 | 0.0061 | 0.0249 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-07 | WTP2 | 0.0063 | 0.0149 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-07 | WTP2 | 0.058 | 0.2499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-07 | WTP1 | 1 | 1.4999 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-07 | WTP1 | 7.6 | 0.4499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP1 | 1.2 | 9.4999 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-07 | WTP1 | 6.5 | 6.4999 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-07 | WTP1 | 0.96 | 0.6499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-07 | WTP1 | 0.57 | 2.4999 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-07 | WTP1 | 0.19 | 0.0749 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-07 | WTP1 | 1.5 | 0.6499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-07 | WTP1 | 0.23 | 0.1499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-07 | WTP1 | 0.86 | 0.2499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-07 | WTP1 | 0.013 | 0.1499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-07 | WTP1 | 0.28 | 0.9499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-07 | WTP2 | 0.46 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-07 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-07 | WTP2 | 0.18 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-07 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-07 | WTP2 | 0.32 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-07 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-07 | WTP2 | 0.44 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-07 | WTP1 | 0.051 |  |  |  | WP1 - 4 OF 16 PRIM INORG (E53076-NN FL E84589-CY) NITRITE J QUALIFIER: MS/MSD = 87%/88% - SUFFICIENT FOR ACCEPTANCE. LCS FOR NITRITE OK - BB. ALL HERE < MCLS.
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-07 | WTP1 | 0.053 |  |  |  | WP1 - 4 OF 16 PRIM INORG (E53076-NN FL E84589-CY) NITRITE J QUALIFIER: MS/MSD = 87%/88% - SUFFICIENT FOR ACCEPTANCE. LCS FOR NITRITE OK - BB. ALL HERE < MCLS.
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-07 | WTP1 | 0.0048 |  |  |  | WP1 - 4 OF 16 PRIM INORG (E53076-NN FL E84589-CY) NITRITE J QUALIFIER: MS/MSD = 87%/88% - SUFFICIENT FOR ACCEPTANCE. LCS FOR NITRITE OK - BB. ALL HERE < MCLS.
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.7 | MG/L | 4.0499 | 2017-04-07 | WTP1 | 0.075 |  |  |  | WP1 - 4 OF 16 PRIM INORG (E53076-NN FL E84589-CY) NITRITE J QUALIFIER: MS/MSD = 87%/88% - SUFFICIENT FOR ACCEPTANCE. LCS FOR NITRITE OK - BB. ALL HERE < MCLS.
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1017 | CHLORIDE | N | 22 | MG/L | 250.4999 | 2017-04-07 | WTP1 | 0.78 |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.7 | MG/L | 2.0499 | 2017-04-07 | WTP1 | 0.075 |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-07 | WTP1 | 5 |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-04-07 | WTP1 | 1 |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.99 | LN(10) |  | 2017-04-07 | WTP1 |  |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 170 | MG/L | 500.4999 | 2017-04-07 | WTP1 | 10 |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-04-07 | WTP1 | 0.04 |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1055 | SULFATE | N | 4.8 | MG/L | 250.4999 | 2017-04-07 | WTP1 | 0.52 |  |  |  | WP1 (8 OF 14 SECS) NO MCL VIOLS
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-07 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-07 | WTP1 | 0.32 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-07 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-07 | WTP1 | 0.44 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-07 | WTP1 | 0.46 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-07 | WTP1 | 0.26 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP1 | 0.2 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-07 | WTP1 | 0.18 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP1 | 0.36 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-07 | WTP1 | 0.39 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP2 | 0.36 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-07 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP2 | 0.23 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-07 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-07 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP2 | 0.24 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-07 | WTP2 | 0.22 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-07 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/WP2 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-07 | WTP2 | 0.0076 | 0.0149 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP2 | 0.0078 | 0.0249 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-07 | WTP2 | 0.0075 | 0.1499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP2 | 0.13 | 1.4999 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-07 | WTP2 | 1 | 1.4999 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-07 | WTP2 | 7.6 | 0.4499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP2 | 1.2 | 9.4999 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-07 | WTP2 | 6.5 | 6.4999 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-07 | WTP2 | 0.96 | 0.6499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-07 | WTP2 | 0.57 | 2.4999 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-07 | WTP2 | 0.19 | 0.0749 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-07 | WTP2 | 1.5 | 0.6499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-07 | WTP2 | 0.23 | 0.1499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-07 | WTP2 | 0.86 | 0.2499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-07 | WTP2 | 0.014 | 0.1499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-07 | WTP2 | 0.28 | 0.9499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP2 | 0.16 | 0.1499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-07 | WTP2 | 0.26 | 0.2499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-07 | WTP2 | 0.0066 | 0.0449 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP2 | 0.0057 | 0.0249 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-07 | WTP2 | 1.5 | 0.1499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-07 | WTP2 | 0.32 | 0.2499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP2 | 0.0069 | 0.1499 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP2 | 0.097 | 0.0249 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP2 | 0.069 | 0.0449 |  |  | 1Q SOC/WP2 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP1 | 0.23 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-07 | WTP1 | 0.26 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-07 | WTP1 | 0.12 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP1 | 0.24 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP1 | 0.12 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP1 | 0.17 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-07 | WTP1 | 0.22 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-07 | WTP1 | 0.17 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-07 | WTP1 | 0.39 | 0.5499 |  |  | 3YR VOC/WP1 (NO DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP1 | 0.16 | 0.1499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-07 | WTP1 | 0.26 | 0.2499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-07 | WTP1 | 0.0063 | 0.0449 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP1 | 0.0055 | 0.0249 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-07 | WTP1 | 1.5 | 0.1499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-07 | WTP1 | 0.32 | 0.2499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP1 | 0.0066 | 0.1499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP1 | 0.097 | 0.0249 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-07 | WTP1 | 0.069 | 0.0449 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-07 | WTP1 | 0.12 | 0.1499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP1 | 0.006 | 0.0249 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-07 | WTP1 | 0.0062 | 0.0149 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-07 | WTP1 | 0.056 | 0.2499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-07 | WTP1 | 0.0073 | 0.0149 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-07 | WTP1 | 0.0075 | 0.0249 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-07 | WTP1 | 0.0072 | 0.1499 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-07 | WTP1 | 0.13 | 1.4999 |  |  | 1Q SOC/WP1 (NO DETECTIONS IN THESE SOCS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.19 | MG/L | 10.4999 | 2017-04-07 | WTP2 | 0.051 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-07 | WTP2 | 0.053 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-04-07 | WTP2 | 8e-05 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1010 | BARIUM | N | 0.0077 | MG/L | 2.4999 | 2017-04-07 | WTP2 | 0.00028 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-07 | WTP2 | 0.00032 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-07 | WTP2 | 0.0005 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-07 | WTP2 | 0.0048 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.69 | MG/L | 4.0499 | 2017-04-07 | WTP2 | 0.075 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-07 | WTP2 | 0.00024 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-07 | WTP2 | 1e-05 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-07 | WTP2 | 0.0011 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-07 | WTP2 | 0.00058 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1052 | SODIUM | N | 18 | MG/L | 160.4999 | 2017-04-07 | WTP2 | 0.16 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-07 | WTP2 | 5e-05 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-07 | WTP2 | 0.00013 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-07 | WTP2 | 6e-05 |  |  |  | WP2 (ALL HERE < MCLS)
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-07 | WTP2 | 0.061 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1017 | CHLORIDE | N | 27 | MG/L | 250.4999 | 2017-04-07 | WTP2 | 0.78 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-04-07 | WTP2 | 0.0025 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.69 | MG/L | 2.0499 | 2017-04-07 | WTP2 | 0.075 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-07 | WTP2 | 0.03 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1032 | MANGANESE | N | 0.0018 | MG/L | 0.0549 | 2017-04-07 | WTP2 | 0.00024 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-07 | WTP2 | 3e-05 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1055 | SULFATE | N | 10 | MG/L | 250.4999 | 2017-04-07 | WTP2 | 0.52 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1095 | ZINC | N | 0.0082 | MG/L | 5.4999 | 2017-04-07 | WTP2 | 0.002 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-07 | WTP2 | 5 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-04-07 | WTP2 | 1 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.07 | LN(10) |  | 2017-04-07 | WTP2 |  |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 200 | MG/L | 500.4999 | 2017-04-07 | WTP2 | 10 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0.05 |  | 0.5499 | 2017-04-07 | WTP2 | 0.04 |  |  |  | WP2 (ALL 14 TESTED) NO MCL VIOLS HERE (CHL V QUALIFIER - RESULT ACCEPTABLE) V QUAL = CONTAMINANT WAS FOUND IN ASSOCIATED METHOD BLANK SAMPLE AS WELL
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-12 | WTP1 | 0.00013 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-12 | WTP1 | 6e-05 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1052 | SODIUM | N | 14 | MG/L | 160.4999 | 2017-04-12 | WTP1 | 0.16 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-12 | WTP1 | 0.00058 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-12 | WTP1 | 0.0011 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-12 | WTP1 | 1e-05 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-12 | WTP1 | 0.00024 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-12 | WTP1 | 0.0005 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-12 | WTP1 | 0.00032 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1010 | BARIUM | N | 0.0062 | MG/L | 2.4999 | 2017-04-12 | WTP1 | 0.00028 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-04-12 | WTP1 | 8e-05 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-04-12 | WTP1 | 0.002 |  |  |  | WP1 (6 OF 14 SECS) METALS )NO MCL VIOLS HERE)
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-12 | WTP1 | 3e-05 |  |  |  | WP1 (6 OF 14 SECS) METALS )NO MCL VIOLS HERE)
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-04-12 | WTP1 | 0.00024 |  |  |  | WP1 (6 OF 14 SECS) METALS )NO MCL VIOLS HERE)
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-12 | WTP1 | 0.03 |  |  |  | WP1 (6 OF 14 SECS) METALS )NO MCL VIOLS HERE)
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-04-12 | WTP1 | 0.0025 |  |  |  | WP1 (6 OF 14 SECS) METALS )NO MCL VIOLS HERE)
3590202 | LONGWOOD CITY OF (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-12 | WTP1 | 0.061 |  |  |  | WP1 (6 OF 14 SECS) METALS )NO MCL VIOLS HERE)
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-12 | WTP1 | 5e-05 |  |  |  | WP1 - 12 OF 16 PRIM INORG. (METALS) ALL HERE < MCLS (8/23/17 CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR SOC REQUIREMENTS PER WP PER TONY HOHMANN'S EMAIL - ADVISED BW OF THIS ON 8/23/17 - BB)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.84 | UG/L | 60.4999 | 2017-05-23 | L1 | 0.5 |  | 3 | 1.5 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 53.94 | UG/L | 80.4999 | 2017-05-23 | L1 | 0.14 |  | 3 | 1.5 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.22 | UG/L | 60.4999 | 2017-05-23 | L2 | 0.5 |  | 4 | 1.1 | 1057 N. HWY 17-92 (6/17 DISINF BYP REPORT RCVD 6/17 LRAA/TTHMS 4 SITES = 44 - 59 LRAA/HAA5S 4 SITES = 21 - 26) DOES NOT QUALIFY FOR REDUCED MONITORING NO LRAA MCL VIOLS NO OE EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 53.75 | UG/L | 80.4999 | 2017-05-23 | L2 | 0.14 |  | 4 | 1.1 | 1057 N. HWY 17-92 (6/17 DISINF BYP REPORT RCVD 6/17 LRAA/TTHMS 4 SITES = 44 - 59 LRAA/HAA5S 4 SITES = 21 - 26) DOES NOT QUALIFY FOR REDUCED MONITORING NO LRAA MCL VIOLS NO OE EXCEEDANCES
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.1 | UG/L | 60.4999 | 2017-05-23 | L3 | 0.5 |  | 1 | 0.8 | 801 RAVEN AVE. - RAVEN AVE. L/S (LIFT STATION)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.64 | UG/L | 60.4999 | 2017-05-23 | L4 | 0.5 |  | 2 | 1.4 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 65.7 | UG/L | 80.4999 | 2017-05-23 | L4 | 0.14 |  | 2 | 1.4 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 57.69 | UG/L | 80.4999 | 2017-05-23 | L3 | 0.14 |  | 1 | 0.8 | 801 RAVEN AVE. - RAVEN AVE. L/S (LIFT STATION)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-06-28 | WTP1 | 0.054 | 0.2499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-06-28 | WTP1 | 0.0061 | 0.0449 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP1 | 0.0053 | 0.0249 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-06-28 | WTP1 | 1.5 | 0.1499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-06-28 | WTP1 | 0.32 | 0.2499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-06-28 | WTP1 | 0.0064 | 0.1499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP1 | 0.098 | 0.0249 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-06-28 | WTP1 | 0.069 | 0.0449 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-06-28 | WTP1 | 0.11 | 0.1499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP1 | 0.006 | 0.0249 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-06-28 | WTP1 | 0.0062 | 0.0149 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-06-28 | WTP2 | 0.0073 | 0.0149 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP2 | 0.0076 | 0.0249 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-06-28 | WTP2 | 0.0072 | 0.1499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-06-28 | WTP2 | 0.13 | 1.4999 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-06-28 | WTP2 | 1 | 1.4999 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-06-28 | WTP2 | 7.6 | 0.4499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-06-28 | WTP2 | 1.2 | 9.4999 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-06-28 | WTP2 | 6.5 | 6.4999 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-06-28 | WTP2 | 0.95 | 0.6499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-06-28 | WTP2 | 0.57 | 2.4999 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-06-28 | WTP2 | 0.19 | 0.0749 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-06-28 | WTP2 | 1.5 | 0.6499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-06-28 | WTP2 | 0.23 | 0.1499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-06-28 | WTP2 | 0.86 | 0.2499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-06-28 | WTP2 | 0.013 | 0.1499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-06-28 | WTP2 | 0.28 | 0.9499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-06-28 | WTP2 | 0.16 | 0.1499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-06-28 | WTP2 | 0.26 | 0.2499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-06-28 | WTP2 | 0.0064 | 0.0449 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP2 | 0.0055 | 0.0249 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-06-28 | WTP2 | 1.5 | 0.1499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-06-28 | WTP2 | 0.32 | 0.2499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-06-28 | WTP2 | 0.0067 | 0.1499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP2 | 0.096 | 0.0249 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-06-28 | WTP2 | 0.069 | 0.0449 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-06-28 | WTP2 | 0.12 | 0.1499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP2 | 0.0061 | 0.0249 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-06-28 | WTP2 | 0.0063 | 0.0149 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-06-28 | WTP2 | 0.056 | 0.2499 |  |  | EX. 1Q SOC/WP2 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR IN ERROR) 8/23/17 PER TONY HOHMANN'S EMAIL CITY RETESTED SOCS ON 8/22/17 FOR 2ND QTR REQUIREMENTS PER WP - BB
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-06-28 | WTP1 | 0.007 | 0.0149 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-06-28 | WTP1 | 0.0072 | 0.0249 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-06-28 | WTP1 | 0.0069 | 0.1499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-06-28 | WTP1 | 0.12 | 1.4999 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-06-28 | WTP1 | 1 | 1.4999 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-06-28 | WTP1 | 7.6 | 0.4499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-06-28 | WTP1 | 1.2 | 9.4999 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-06-28 | WTP1 | 6.5 | 6.4999 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-06-28 | WTP1 | 0.97 | 0.6499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-06-28 | WTP1 | 0.57 | 2.4999 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-06-28 | WTP1 | 0.19 | 0.0749 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-06-28 | WTP1 | 1.5 | 0.6499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-06-28 | WTP1 | 0.23 | 0.1499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-06-28 | WTP1 | 0.27 | 0.2499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-06-28 | WTP1 | 0.16 | 0.1499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-06-28 | WTP1 | 0.86 | 0.2499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-06-28 | WTP1 | 0.013 | 0.1499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-06-28 | WTP1 | 0.28 | 0.9499 |  |  | EX. 1Q SOC/WP1 (TESTED 4/17 & 6/17 WITHIN 1 CALENDAR QTR) MUST TEST SOCS DURING 8/17 OR 9/17 TO FINISH RQRMNTS
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.02 | UG/L | 60.4999 | 2017-08-17 | L3 | 0.5 |  | 1 | 0.8 | RAVEN. AVE. LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 63.98 | UG/L | 80.4999 | 2017-08-17 | L3 | 0.14 |  | 1 | 0.8 | RAVEN. AVE. LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.12 | UG/L | 60.4999 | 2017-08-17 | L4 | 0.5 |  | 2 | 0.9 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 65.51 | UG/L | 80.4999 | 2017-08-17 | L4 | 0.14 |  | 2 | 0.9 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.18 | UG/L | 60.4999 | 2017-08-17 | L1 | 0.5 |  | 3 | 1.1 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 60.67 | UG/L | 80.4999 | 2017-08-17 | L1 | 0.14 |  | 3 | 1.1 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 58.35 | UG/L | 80.4999 | 2017-08-17 | L2 | 0.14 |  | 4 | 1 | 1057 N. HWY 17-92 (9/17 DISINF BYP REPORT RCVD W/RSLTS) HYPERLINKED 10/19/17 TO BW - BB (NO MCL VIOLS DOES NOT QUALIFY FOR REDUCED MONITORING)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.23 | UG/L | 60.4999 | 2017-08-17 | L2 | 0.5 |  | 4 | 1 | 1057 N. HWY 17-92 (9/17 DISINF BYP REPORT RCVD W/RSLTS) HYPERLINKED 10/19/17 TO BW - BB (NO MCL VIOLS DOES NOT QUALIFY FOR REDUCED MONITORING)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-22 | WTP2 | 1.5 | 0.6499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-22 | WTP2 | 0.23 | 0.1499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-22 | WTP2 | 0.86 | 0.2499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-22 | WTP2 | 0.013 | 0.1499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-22 | WTP2 | 0.28 | 0.9499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-22 | WTP2 | 0.16 | 0.1499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-22 | WTP2 | 0.27 | 0.2499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-22 | WTP2 | 0.032 | 0.0449 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP2 | 0.0055 | 0.0249 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-22 | WTP2 | 1.5 | 0.1499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-22 | WTP2 | 0.32 | 0.2499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-22 | WTP2 | 0.034 | 0.1499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP2 | 0.098 | 0.0249 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-22 | WTP2 | 0.069 | 0.0449 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP2 | 0.0061 | 0.0249 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-22 | WTP2 | 0.0063 | 0.0149 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-22 | WTP2 | 0.056 | 0.2499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-22 | WTP1 | 0.0073 | 0.0149 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP1 | 0.0075 | 0.0249 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-22 | WTP1 | 0.0072 | 0.1499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-22 | WTP1 | 0.13 | 1.4999 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-22 | WTP1 | 1 | 1.4999 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-22 | WTP1 | 7.6 | 0.4499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-22 | WTP1 | 1.2 | 9.4999 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-22 | WTP1 | 6.5 | 6.4999 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-22 | WTP1 | 0.96 | 0.6499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-22 | WTP1 | 0.57 | 2.4999 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-22 | WTP1 | 0.19 | 0.0749 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-22 | WTP1 | 1.5 | 0.6499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-22 | WTP1 | 0.23 | 0.1499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-22 | WTP1 | 0.86 | 0.2499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-22 | WTP1 | 0.013 | 0.1499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-22 | WTP1 | 0.28 | 0.9499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-22 | WTP1 | 0.16 | 0.1499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-22 | WTP1 | 0.26 | 0.2499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-22 | WTP1 | 0.0063 | 0.0449 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP1 | 0.0055 | 0.0249 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-22 | WTP1 | 1.5 | 0.1499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-22 | WTP1 | 0.32 | 0.2499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-22 | WTP1 | 0.0066 | 0.1499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP1 | 0.097 | 0.0249 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-22 | WTP1 | 0.069 | 0.0449 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-22 | WTP1 | 0.12 | 0.1499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP1 | 0.0061 | 0.0249 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-22 | WTP1 | 0.0063 | 0.0149 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-22 | WTP1 | 0.056 | 0.2499 |  |  | 2Q SOC/WP1 (MDLS OK THESE ALL NON-DETECTIONS)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-22 | WTP2 | 0.0073 | 0.0149 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-22 | WTP2 | 0.038 | 0.0249 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-22 | WTP2 | 0.0072 | 0.1499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-22 | WTP2 | 0.13 | 1.4999 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-22 | WTP2 | 1 | 1.4999 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-22 | WTP2 | 7.6 | 0.4499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-22 | WTP2 | 1.2 | 9.4999 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-22 | WTP2 | 6.5 | 6.4999 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-22 | WTP2 | 0.97 | 0.6499 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-22 | WTP2 | 0.57 | 2.4999 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-22 | WTP2 | 0.19 | 0.0749 |  |  | 2Q 28 OF 29 SOC/WP2(PCBS MDL>MCL-CANNOT ENTER PCBS-MUST RETEST PCBS-WP2;LINDANE MDL>RDL BUT<50% MCL-CAN BE ACCPTD)METH.508 CHEMS HAVE ELEVATED MDLS -002 SMPL-BB(HYPERLINKED TO BW ON 9/25/17-BB)
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.85 | UG/L | 60.4999 | 2017-11-22 | L3 | 0.5 |  | 1 | 1.2 | 801 RAVEN AVE. = LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 61.79 | UG/L | 80.4999 | 2017-11-22 | L3 | 0.14 |  | 1 | 1.2 | 801 RAVEN AVE. = LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.99 | UG/L | 60.4999 | 2017-11-22 | L4 | 0.5 |  | 2 | 1.2 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 64.29 | UG/L | 80.4999 | 2017-11-22 | L4 | 0.14 |  | 2 | 1.2 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.21 | UG/L | 60.4999 | 2017-11-22 | L1 | 0.5 |  | 3 | 1.3 | 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.06 | UG/L | 60.4999 | 2017-11-22 | L2 | 0.5 |  | 4 | 1.3 | 1057 N HWY 17-92 (12/17 DISINF BYP REPORT RCVD) HYPERLINKED TO BW 1/19/18 - BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 55.44 | UG/L | 80.4999 | 2017-11-22 | L1 | 0.14 |  | 3 | 1.3 | 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 52.2 | UG/L | 80.4999 | 2017-11-22 | L2 | 0.14 |  | 4 | 1.3 | 1057 N HWY 17-92 (12/17 DISINF BYP REPORT RCVD) HYPERLINKED TO BW 1/19/18 - BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.23 | UG/L | 60.4999 | 2018-02-23 | L4 | 0.5 |  | 2 | 0.9 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 42.71 | UG/L | 80.4999 | 2018-02-23 | L2 | 0.14 |  | 4 | 0.9 | 1057 N HWY 17-92 (3/18 DISINF BYP REPORT RCVD W/RSLTS) 4/19/18 HYPERLINKED TO BW - BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.29 | UG/L | 60.4999 | 2018-02-23 | L2 | 0.5 |  | 4 | 0.9 | 1057 N HWY 17-92 (3/18 DISINF BYP REPORT RCVD W/RSLTS) 4/19/18 HYPERLINKED TO BW - BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.4 | UG/L | 80.4999 | 2018-02-23 | L1 | 0.14 |  | 3 | 1.4 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.92 | UG/L | 60.4999 | 2018-02-23 | L3 | 0.5 |  | 1 | 0.8 | 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 54.94 | UG/L | 80.4999 | 2018-02-23 | L3 | 0.14 |  | 1 | 0.8 | 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 45.18 | UG/L | 80.4999 | 2018-02-23 | L4 | 0.14 |  | 2 | 0.9 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.5 | UG/L | 60.4999 | 2018-02-23 | L1 | 0.5 |  | 3 | 1.4 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.69 | UG/L | 60.4999 | 2018-05-24 | L4 | 0.91 |  | 2 | 1.2 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 85.32 | UG/L | 80.4999 | 2018-05-24 | L4 | 0.14 |  | 2 | 1.2 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 75.75 | UG/L | 80.4999 | 2018-05-24 | L2 | 0.14 |  | 4 | 1.1 | 1057 N. HWY 17-92 (6/18 DISINF BYP REPORT RCVD W/RSLTS) HLKD TO RLB 7/17/18 - BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 66.48 | UG/L | 80.4999 | 2018-05-24 | L1 | 0.14 |  | 3 | 1.3 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.69 | UG/L | 60.4999 | 2018-05-24 | L2 | 0.91 |  | 4 | 1.1 | 1057 N. HWY 17-92 (6/18 DISINF BYP REPORT RCVD W/RSLTS) HLKD TO RLB 7/17/18 - BB
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 84.57 | UG/L | 80.4999 | 2018-05-24 | L3 | 0.14 |  | 1 | 0.7 | RAVEN AVE. L/S
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.83 | UG/L | 60.4999 | 2018-05-24 | L3 | 0.91 |  | 1 | 0.7 | RAVEN AVE. L/S
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.07 | UG/L | 60.4999 | 2018-05-24 | L1 | 0.91 |  | 3 | 1.3 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-07-23 | WTP1 |  |  |  |  | WTP 1 - BOTH UNDETECTED
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-07-23 | WTP2 |  |  |  |  | WTP 2 - BOTH UNDETECTED
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-07-23 | WTP1 |  |  |  |  | WTP 1 - BOTH UNDETECTED
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-07-23 | WTP2 |  |  |  |  | WTP 2 - BOTH UNDETECTED
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 48.22 | UG/L | 80.4999 | 2018-08-17 | L2 |  |  |  | 0.5 | 2950-SM-4 1057 N HWY 17-92 - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.69 | UG/L | 60.4999 | 2018-08-17 | L2 |  |  |  | 0.5 | 2950-SM-4 1057 N HWY 17-92 - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.34 | UG/L | 80.4999 | 2018-08-17 | L1 |  |  |  | 0.8 | 2950-SM-2 235 W CHURCH AVE. - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.08 | UG/L | 60.4999 | 2018-08-17 | L1 |  |  |  | 0.8 | 2950-SM-2 235 W CHURCH AVE. - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.2 | UG/L | 80.4999 | 2018-08-17 | L4 |  |  |  | 0.8 | 2950-ST1-2 900 NORTH ST - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.73 | UG/L | 60.4999 | 2018-08-17 | L4 |  |  |  | 0.8 | 2950-ST1-2 900 NORTH ST - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 51.58 | UG/L | 80.4999 | 2018-08-17 | L3 |  |  |  | 0.6 | 2950-ST1-1 801 RAVEN AVE.=LIFT STATION - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.92 | UG/L | 60.4999 | 2018-08-17 | L3 |  |  |  | 0.6 | 2950-ST1-1 801 RAVEN AVE.=LIFT STATION - SUBCONTRACT LABS E84589 E82535
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.67 | UG/L | 60.4999 | 2018-11-26 | L3 |  |  |  | 1.2 | RAVEN AVE LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.18 | UG/L | 80.4999 | 2018-11-26 | L3 |  |  |  | 1.2 | RAVEN AVE LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.39 | UG/L | 60.4999 | 2018-11-26 | L4 |  |  |  | 0.6 | 900 NORTH STREET
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 57.66 | UG/L | 80.4999 | 2018-11-26 | L4 |  |  |  | 0.6 | 900 NORTH STREET
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.58 | UG/L | 60.4999 | 2018-11-26 | L1 |  |  |  | 1.2 | 235 W. CHURCH AVE
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 39.68 | UG/L | 80.4999 | 2018-11-26 | L1 |  |  |  | 1.2 | 235 W. CHURCH AVE
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 45.52 | UG/L | 80.4999 | 2018-11-26 | L2 |  |  |  | 1.2 | 1057 N. HIGHWAY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.84 | UG/L | 60.4999 | 2018-11-26 | L2 |  |  |  | 1.2 | 1057 N. HIGHWAY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 45.98 | UG/L | 80.4999 | 2019-02-20 | L2
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.46 | UG/L | 60.4999 | 2019-02-20 | L3 | 0.91 |  | 1 | 1 | RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 46.21 | UG/L | 80.4999 | 2019-02-20 | L1
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 19.74 | UG/L | 60.4999 | 2019-02-20 | L1
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 53.11 | UG/L | 80.4999 | 2019-02-20 | L4
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 26.36 | UG/L | 60.4999 | 2019-02-20 | L4
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 47.49 | UG/L | 80.4999 | 2019-02-20 | L3
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 25.46 | UG/L | 60.4999 | 2019-02-20 | L3
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 20.57 | UG/L | 60.4999 | 2019-02-20 | L2
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 47.49 | UG/L | 80.4999 | 2019-02-20 | L3 | 0.39 |  | 1 | 1 | RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 45.98 | UG/L | 80.4999 | 2019-02-20 | L2 | 0.39 |  | 4 | 1.6 | 1057 N. HWY 17-92 (3/19 DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.57 | UG/L | 60.4999 | 2019-02-20 | L2 | 0.91 |  | 4 | 1.6 | 1057 N. HWY 17-92 (3/19 DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 46.21 | UG/L | 80.4999 | 2019-02-20 | L1 | 0.39 |  | 3 | 1.5 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.74 | UG/L | 60.4999 | 2019-02-20 | L1 | 0.91 |  | 3 | 1.5 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 53.11 | UG/L | 80.4999 | 2019-02-20 | L4 | 0.39 |  | 2 | 1 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.36 | UG/L | 60.4999 | 2019-02-20 | L4 | 0.91 |  | 2 | 1 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.83 | UG/L | 60.4999 | 2019-05-20 | L1 |  |  | 3 | 1.5 | SM-2 235 W CHURCH AVE. / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.09 | UG/L | 60.4999 | 2019-05-20 | L3 |  |  | 1 | 1.6 | ST1-1 801 RAVEN AVE.=LIFT STATION / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 52.92 | UG/L | 80.4999 | 2019-05-20 | L3 |  |  | 1 | 1.6 | ST1-1 801 RAVEN AVE.=LIFT STATION / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.74 | UG/L | 60.4999 | 2019-05-20 | L4 |  |  | 2 | 1.4 | ST1-2 900 NORTH ST / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 45.82 | UG/L | 80.4999 | 2019-05-20 | L1 |  |  | 3 | 1.5 | SM-2 235 W CHURCH AVE. / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.78 | UG/L | 60.4999 | 2019-05-20 | L2 |  |  | 4 | 1.7 | SM-4 1057 N HWY 17-92 / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 39.66 | UG/L | 80.4999 | 2019-05-20 | L2 |  |  | 4 | 1.7 | SM-4 1057 N HWY 17-92 / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 64.01 | UG/L | 80.4999 | 2019-05-20 | L4 |  |  | 2 | 1.4 | ST1-2 900 NORTH ST / SUBCONTRACT LABS E82535 E84589
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 16.02 | UG/L | 80.4999 | 2019-08-21 | L3 |  |  | 1 | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.71 | UG/L | 60.4999 | 2019-08-21 | L4 |  |  | 2 | 0.8 | ST1-2 900 NORTH ST
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 55.55 | UG/L | 80.4999 | 2019-08-21 | L4 |  |  | 2 | 0.8 | ST1-2 900 NORTH ST
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.51 | UG/L | 60.4999 | 2019-08-21 | L1 |  |  | 3 | 3.4 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.85 | UG/L | 60.4999 | 2019-08-21 | L2 |  |  | 4 | 2.4 | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 42.37 | UG/L | 80.4999 | 2019-08-21 | L2 |  |  | 4 | 2.4 | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.99 | UG/L | 60.4999 | 2019-08-21 | L3 |  |  | 1 | 1 | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 34.57 | UG/L | 80.4999 | 2019-08-21 | L1 |  |  | 3 | 3.4 | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.22 | MG/L | 10.4999 | 2019-10-23 | WTP1
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-10-23 | WTP1
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.23 | MG/L | 10.4999 | 2019-10-23 | WTP2
3590202 | LONGWOOD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-10-23 | WTP2
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 47.36 | UG/L | 80.4999 | 2019-11-19 | L2 | 0.39 |  | 4 | 1.7 | 1057 N. HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.54 | UG/L | 60.4999 | 2019-11-19 | L2 | 0.91 |  | 4 | 1.7 | 1057 N. HWY 17-92
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 42.77 | UG/L | 80.4999 | 2019-11-19 | L1 | 0.39 |  | 3 | 1.5 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.49 | UG/L | 60.4999 | 2019-11-19 | L1 | 0.91 |  | 3 | 1.5 | 235 W. CHURCH AVE.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 73.35 | UG/L | 80.4999 | 2019-11-19 | L4 | 0.39 |  | 2 | 1.4 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.28 | UG/L | 60.4999 | 2019-11-19 | L4 | 0.91 |  | 2 | 1.4 | 900 NORTH ST.
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.96 | UG/L | 60.4999 | 2019-11-19 | L3 | 0.91 |  | 1 | 1.6 | RAVEN AVE. L/S
3590202 | LONGWOOD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 44.75 | UG/L | 80.4999 | 2019-11-19 | L3 | 0.39 |  | 1 | 1.6 | RAVEN AVE. L/S
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 18 | UG/L | 10.4999 | 2015-01-06 | POE | 3.3 |  | 1 | 1.79 | 1/15 BROMATE-AUX. WP (C.R. NOT RQRD BUT SUPPLIED)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-02-03 | POE | 1 |  | 2 | 1.59 | 2/15 BROMATE-AUX. WP (C.R. NOT RQRD BUT SUPPLIED) 3/15 BROMATE IN 4/8/15 EM FROM TURNER CHARLIE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.09 | UG/L | 60.4999 | 2015-02-18 | S01_L01 | 0.52 |  | 1 | 1.08 | 531 N. PALMETTO AVE. (E82574/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 56.05 | UG/L | 80.4999 | 2015-02-18 | S01_L01 | 0.31 |  | 1 | 1.08 | 531 N. PALMETTO AVE. (E82574/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.86 | UG/L | 60.4999 | 2015-02-18 | S02_L05 | 0.52 |  | 2 | 1.48 | 3751 E. S.R. 46 (E82574/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 8.08 | UG/L | 80.4999 | 2015-02-18 | S01_L02 | 0.31 |  | 4 | 1.65 | 100 WELDON BLVD. (E82574/HAA5) SYS. DOES NOT QUALIFY FOR R.M. (1 SITE LRAA/T @ 66.76) NO LRAA MCL VIOLS OR OE EXCEEDANCES FOR 3/15 QTR
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.79 | UG/L | 60.4999 | 2015-02-18 | S02_L06 | 0.52 |  | 3 | 1.73 | 2501 LAKE MARY BLVD. (E82574/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 9.68 | UG/L | 80.4999 | 2015-02-18 | S02_L06 | 0.31 |  | 3 | 1.73 | 2501 LAKE MARY BLVD. (E82574/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.25 | UG/L | 60.4999 | 2015-02-18 | S01_L02 | 0.52 |  | 4 | 1.65 | 100 WELDON BLVD. (E82574/HAA5) SYS. DOES NOT QUALIFY FOR R.M. (1 SITE LRAA/T @ 66.76) NO LRAA MCL VIOLS OR OE EXCEEDANCES FOR 3/15 QTR
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 11.86 | UG/L | 80.4999 | 2015-02-18 | S02_L05 | 0.31 |  | 2 | 1.48 | 3751 E. S.R. 46 (E82574/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | D | 0 | UG/L | 10.4999 | 2015-03-02 | POE | 1 |  | 3 | 1.76 | (8/27/15 EW HAS 4-5-6-/15 BROMATE & 6/15 BROMATE RAA-ALL IN OC) 3/15 BROMATE-AUX. WP (1ST QTR 2015 BROMATE & RAA IN OC WITH ALL REVISIONS) (C.R. NOT RQRD BUT GVN)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-03-03 | WTP2 | 0.0005 |  |  |  | AUX. WP ARS(DUE TO ASR WELL)NO RECOV.FR.ASR WELL 1Q 2015 PER 4/8/15 LTR W/RSLTS. CY5 TEST BEGAN 11/18/14 INJECTION 11/18/14-3/22/15 STORAGE 3/23/15-4/21/15 RECOV PLANNED 4/19-8/19/15-WL.TEST MONTHLY
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-03-03 | WTP2 | 0.621 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (GA <.965 +/- .583 R226 <.692 +/- .488 R228 <.621 +/- .293 PCI/L) NO RECOV.FROM ASR WELL 1ST QTR 2015 PER 4/8/15 LTR W/RSLTS. RECOVERY PLANNED 4/22/15-8/19/14-WL.TST MONTHLY
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-03-03 | WTP2 | 0.692 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (GA <.965 +/- .583 R226 <.692 +/- .488 R228 <.621 +/- .293 PCI/L) NO RECOV.FROM ASR WELL 1ST QTR 2015 PER 4/8/15 LTR W/RSLTS. RECOVERY PLANNED 4/22/15-8/19/14-WL.TST MONTHLY
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-03-03 | WTP2 | 0.965 |  |  |  | AUX. WP DUE TO ASR WELL (GA <.965 +/- .583 R226 <.692 +/- .488 R228 <.621 +/- .293 PCI/L) NO RECOV.FROM ASR WELL 1ST QTR 2015 PER 4/8/15 LTR W/RSLTS. RECOVERY PLANNED 4/22/15-8/19/14-WL.TST MONTHLY
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-04-07 | POE |  |  |  |  | 4/15 BROMATE-AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.07 | UG/L | 60.4999 | 2015-04-23 | S01_L01 |  |  |  | 1.18 | 531 N PALMETTO AVE (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 56.92 | UG/L | 80.4999 | 2015-04-23 | S01_L01 |  |  |  | 1.18 | 531 N PALMETTO AVE (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.14 | UG/L | 60.4999 | 2015-04-23 | S02_L05 |  |  |  | 1.49 | 3751 E SR 46 (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 20.3 | UG/L | 80.4999 | 2015-04-23 | S02_L05 |  |  |  | 1.49 | 3751 E SR 46 (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.53 | UG/L | 60.4999 | 2015-04-23 | S02_L06 |  |  |  | 1.57 | 2501 LAKE MARY BLVD (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 15.4 | UG/L | 80.4999 | 2015-04-23 | S02_L06 |  |  |  | 1.57 | 2501 LAKE MARY BLVD (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.02 | UG/L | 60.4999 | 2015-04-23 | S01_L02 |  |  |  | 1.61 | 100 WELDON BLVD (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 12.13 | UG/L | 80.4999 | 2015-04-23 | S01_L02 |  |  |  | 1.61 | 100 WELDON BLVD (6/15 DBF RCVD) NO LRAA MCLS OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-05-04 | POE |  |  |  |  | 5/15 BROMATE-AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2015-05-19 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 5 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2015-05-19 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 1 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2015-05-19 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 6 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2015-05-19 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 6 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2015-05-19 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 1 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2015-05-19 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 5 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2015-05-19 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 2 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2015-05-19 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 2 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2015-05-19 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 4 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2015-05-19 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 4 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-05-19 | WTP1 |  | 0.6499 |  |  | 3AM/2039-MAIN WP1 2Q'15 (STOP AM/2039 - LAST 3 YRS -0-) EM 7/31/15 TO MR. TURNER TO STOP AM
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2015-05-19 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 3 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2015-05-19 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 3 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-19 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.27 | MG/L | 10.4999 | 2015-05-19 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-19 | WTP1 |  |  |  |  | MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.21 | MG/L | 10.4999 | 2015-05-19 | WTP1 |  |  |  |  | MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-06-08 | POE |  |  |  |  | 6/15 BROMATE-AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-06-15 | WTP2 |  |  |  |  | AUX.WP DUE TO ASR WELL(NO RECOV.FR.ASR WELL 2Q 2015 PER 7/6/15 LTR W/RSLTS. CY5 TEST BEGAN 11/18/14 INJECTION 11/18/14-3/22/15 STORAGE 3/23/15 TO PRESENT WL. TST MONTHLY WHEN RECOV.STARTS)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-06-15 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-06-15 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-06-15 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-07-06 | POE |  |  |  |  | 7/15 BROMATE-AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 76.98 | UG/L | 80.4999 | 2015-07-23 | S01_L01 |  |  |  | 0.67 | 531 N PALMETTO AVE (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.05 | UG/L | 60.4999 | 2015-07-23 | S02_L06 |  |  |  | 1.57 | 2501 LAKE MARY BLVD (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 19.63 | UG/L | 80.4999 | 2015-07-23 | S02_L06 |  |  |  | 1.57 | 2501 LAKE MARY BLVD (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.04 | UG/L | 60.4999 | 2015-07-23 | S01_L02 |  |  |  | 1.48 | 100 WELDON BLVD (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 5.92 | UG/L | 80.4999 | 2015-07-23 | S01_L02 |  |  |  | 1.48 | 100 WELDON BLVD (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.17 | UG/L | 60.4999 | 2015-07-23 | S02_L05 |  |  |  | 1.4 | 3751 E SR 46 (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 30.77 | UG/L | 80.4999 | 2015-07-23 | S02_L05 |  |  |  | 1.4 | 3751 E SR 46 (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.33 | UG/L | 60.4999 | 2015-07-23 | S01_L01 |  |  |  | 0.67 | 531 N PALMETTO AVE (9/15 DBF W/RESULTS NO LRAA OR OE EXCEEDANCES)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-08-03 | POE |  |  |  |  | 8/15 BROMATE-AUX WP
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-08-19 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0.809 | PCI/L | 3.4999 | 2015-08-19 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-08-19 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-08-19 | WTP2 |  |  |  |  | AUX.WP DUE TO ASR WELL(CY TEST 5-INJECTION 11/18/14-3/22/15. STORAGE EXTENDED TO 7/20/15. ASR RECOVERY TO LAKE ADA ONLY BEGAN 7/20/15-NOT TO AUX. WP. NO PLANS TO RECOVER TO AUX. WP YET)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-09-02 | POE |  |  |  |  | 9/15 BROMATE-AUX WP (9/15 BROMATE RAA = 1.5 9/15 BROMATE RAA WITH TEST RESULTS IN OC)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0.632 | PCI/L | 2.4999 | 2015-09-16 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (ASR RECOVERY TO LAKE ADA ONLY BEGAN 7/20/15-NOT TO AUX. WP. NO PLANS TO RECOVER TO AUX. WP YET BUT WL TEST MONTHLY UNTIL RECOV TO LAKE ENDS SHD AUX WP NEED WTR)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-09-16 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (ASR RECOVERY TO LAKE ADA ONLY BEGAN 7/20/15-NOT TO AUX. WP. NO PLANS TO RECOVER TO AUX. WP YET BUT WL TEST MONTHLY UNTIL RECOV TO LAKE ENDS SHD AUX WP NEED WTR)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-09-16 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (ASR RECOVERY TO LAKE ADA ONLY BEGAN 7/20/15-NOT TO AUX. WP. NO PLANS TO RECOVER TO AUX. WP YET BUT WL TEST MONTHLY UNTIL RECOV TO LAKE ENDS SHD AUX WP NEED WTR)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-09-16 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (ASR RECOVERY TO LAKE ADA ONLY BEGAN 7/20/15-NOT TO AUX. WP. NO PLANS TO RECOVER TO AUX. WP YET BUT WL TEST MONTHLY UNTIL RECOV TO LAKE ENDS SHD AUX WP NEED WTR)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-10-05 | POE |  |  |  |  | 10/15 BROMATE-AUX WP
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-14 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-10-14 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-10-14 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-10-14 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-11-09 | POE |  |  |  |  | 11/15 BROMATE-AUX WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.07 | UG/L | 60.4999 | 2015-11-24 | S01_L02 |  |  |  | 1.56 | 100 WELDON BLVD (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 70.2 | UG/L | 80.4999 | 2015-11-24 | S01_L01 |  |  |  | 0.86 | 531 N PALMETTO AVE (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.85 | UG/L | 60.4999 | 2015-11-24 | S01_L01 |  |  |  | 0.86 | 531 N PALMETTO AVE (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 26.1 | UG/L | 80.4999 | 2015-11-24 | S02_L06 |  |  |  | 1.56 | 2501 LAKE MARY BLVD (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.06 | UG/L | 60.4999 | 2015-11-24 | S02_L06 |  |  |  | 1.56 | 2501 LAKE MARY BLVD (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 41.7 | UG/L | 80.4999 | 2015-11-24 | S02_L05 |  |  |  | 1.47 | 3751 E SR 46 (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.76 | UG/L | 60.4999 | 2015-11-24 | S02_L05 |  |  |  | 1.47 | 3751 E SR 46 (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 27.4 | UG/L | 80.4999 | 2015-11-24 | S01_L02 |  |  |  | 1.56 | 100 WELDON BLVD (DOES NOT QUALITY FOR R.M.) CONT. TO TEST QTRLY FOR T/H
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 17 | UG/L | 10.4999 | 2015-12-07 | POE |  |  |  |  | 12/15 BROMATE-AUX WP (12/15 BROMATE RAA = 3 12/15 BROMATE RAA WITH TEST RESULTS IN OC)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 1.9 | PCI/L | 2.4999 | 2015-12-15 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY CEASED RECOVERY OF ASR WELL TO LAKE ADA FOR CYCLE TEST 5 ON 10/31/15. THERE WAS NO RECOVERY OF WTR TO AUX. WP. DURING CY TEST 5. ONLY NDD QTRLY TEST 12/15 QTR)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-12-15 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY CEASED RECOVERY OF ASR WELL TO LAKE ADA FOR CYCLE TEST 5 ON 10/31/15. THERE WAS NO RECOVERY OF WTR TO AUX. WP. DURING CY TEST 5. ONLY NDD QTRLY TEST 12/15 QTR)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-12-15 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY CEASED RECOVERY OF ASR WELL TO LAKE ADA FOR CYCLE TEST 5 ON 10/31/15. THERE WAS NO RECOVERY OF WTR TO AUX. WP. DURING CY TEST 5. ONLY NDD QTRLY TEST 12/15 QTR)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-12-15 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY CEASED RECOVERY OF ASR WELL TO LAKE ADA FOR CYCLE TEST 5 ON 10/31/15. THERE WAS NO RECOVERY OF WTR TO AUX. WP. DURING CY TEST 5. ONLY NDD QTRLY TEST 12/15 QTR)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 26 | UG/L | 10.4999 | 2016-01-04 | POE |  |  |  |  | 1/4/16 BROMATE 26 - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 28 | UG/L | 10.4999 | 2016-01-19 | POE |  |  |  |  | 1/19/16 BROMATE 28 - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 39.9 | UG/L | 10.4999 | 2016-01-26 | POE |  |  |  |  | 1/26/16 BROMATE 39.9 - AUX. WP (AVG (3) 1/16 BROMATE = 25.74)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 42 | UG/L | 10.4999 | 2016-02-01 | POE |  |  |  |  | 2/16 BROMATE 42 - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2016-02-15 | WTP2 |  |  |  |  | (7/19 EW HAS 2016 NN-EA. WP BY EM) AUX. WP DUE TO ASR WELL (NO CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2016) ONLY QTRLY ARSENIC & RADS NDD DURING 1Q 2016
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2016-02-15 | WTP2 |  |  |  |  | (8/30 EW HAS 5/16 ARSENIC & RADS FOR PROCESSING BY EM) AUX. WP DUE TO ASR WELL (NO CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2016) ONLY QTRLY ARSENIC & RADS NDD DURING 1Q 2016
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0.969 | PCI/L | 2.4999 | 2016-02-15 | WTP2 |  | 1.4999 |  |  | (8/30 EW HAS 5/16 ARSENIC & RADS FOR PROCESSING BY EM) AUX. WP DUE TO ASR WELL (NO CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2016) ONLY QTRLY ARSENIC & RADS NDD DURING 1Q 2016
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2016-02-15 | WTP2 |  | 1.4999 |  |  | (8/30 EW HAS 5/16 ARSENIC & RADS FOR PROCESSING BY EM) AUX. WP DUE TO ASR WELL (NO CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2016) ONLY QTRLY ARSENIC & RADS NDD DURING 1Q 2016
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.15 | UG/L | 60.4999 | 2016-02-17 | S02_L05 |  |  |  | 1.45 | 3751 E SR 46 (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 26.99 | UG/L | 80.4999 | 2016-02-17 | S02_L05 |  |  |  | 1.45 | 3751 E SR 46 (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.52 | UG/L | 60.4999 | 2016-02-17 | S02_L06 |  |  |  | 1.48 | 2501 LAKE MARY BLVD (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 22.03 | UG/L | 80.4999 | 2016-02-17 | S02_L06 |  |  |  | 1.48 | 2501 LAKE MARY BLVD (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.46 | UG/L | 60.4999 | 2016-02-17 | S01_L02 |  |  |  | 1.47 | 100 WELDON BLVD.(DOES NOT QUALIFY FOR R.M.)NO LRAA OR OE EXCEEDANCES. TRICHLOROACETIC ACID J QUAL:140% MS (BIASED HIGH?OK?ACCEPTABLE)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 20.93 | UG/L | 80.4999 | 2016-02-17 | S01_L02 |  |  |  | 1.47 | 100 WELDON BLVD.(DOES NOT QUALIFY FOR R.M.)NO LRAA OR OE EXCEEDANCES. TRICHLOROACETIC ACID J QUAL:140% MS (BIASED HIGH?OK?ACCEPTABLE)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.14 | UG/L | 60.4999 | 2016-02-17 | S01_L01 |  |  |  | 1.03 | 531 N PALMETTO AVE (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 49.91 | UG/L | 80.4999 | 2016-02-17 | S01_L01 |  |  |  | 1.03 | 531 N PALMETTO AVE (DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 10.6 | UG/L | 10.4999 | 2016-03-01 | POE |  |  |  |  | 3/16 BROMATE 10.6 - AUX. WP (3/16 RAA/BROMATE APPROX. 8 PER REPORT) **4/27/16 EW HAS 2/16 DBPS & DB REPORT
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.17 | MG/L | 10.4999 | 2016-04-14 | WTP1 |  |  |  |  | WP1 NN (J QUAL-NITRITE 76% RECOVERY MS SUFFICIENT FOR ACCEPTANCE. LCS OK)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-04-14 | WTP1 |  |  |  |  | WP1 NN (J QUAL-NITRITE 76% RECOVERY MS SUFFICIENT FOR ACCEPTANCE. LCS OK)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.21 | MG/L | 10.4999 | 2016-04-14 | WTP2 |  |  |  |  | WP2 NN (OK) 8/30 EW HAS 5/16 ARS & RADS BY EM FOR PROCESSING
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-04-14 | WTP2 |  |  |  |  | WP2 NN (OK) 8/30 EW HAS 5/16 ARS & RADS BY EM FOR PROCESSING
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2016-04-14 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 4 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2016-04-14 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 4 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2016-04-14 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 3 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2016-04-14 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 3 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2016-04-14 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 1 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2016-04-14 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 1 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2016-04-14 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 2 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2016-04-14 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 5 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2016-04-14 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 5 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2016-04-14 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 2 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2016-04-14 | WTP1 |  | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 6 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | W | 0 | UG/L | 0.2499 | 2016-04-14 | WTP1 |  | 0.0249 |  |  | SPEC. EDB MON. GOLF COURSE WELL 6 MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.28 | UG/L | 60.4999 | 2016-04-27 | S01_L01 |  |  |  | 1.05 | 531 N PALMETTO AVE (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.55 | UG/L | 60.4999 | 2016-04-27 | S02_L06 |  |  |  | 1.51 | 2501 LAKE MARY BLVD (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 39.44 | UG/L | 80.4999 | 2016-04-27 | S02_L05 |  |  |  | 1.3 | 3751 E SR 46 (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.9 | UG/L | 60.4999 | 2016-04-27 | S02_L05 |  |  |  | 1.3 | 3751 E SR 46 (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.86 | UG/L | 80.4999 | 2016-04-27 | S02_L06 |  |  |  | 1.51 | 2501 LAKE MARY BLVD (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 60.22 | UG/L | 80.4999 | 2016-04-27 | S01_L01 |  |  |  | 1.05 | 531 N PALMETTO AVE (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.48 | UG/L | 60.4999 | 2016-04-27 | S01_L02 |  |  |  | 1.56 | 100 WELDON BLVD (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 27.15 | UG/L | 80.4999 | 2016-04-27 | S01_L02 |  |  |  | 1.56 | 100 WELDON BLVD (DOES NOT QUALIFY FOR R.M. DUE TO ONE SITE LRAA/T>40)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 5.4 | UG/L | 10.4999 | 2016-04-28 | POE |  |  |  |  | 4/16 BROMATE - AUX. WP (IF 6/16 QTRLY AVG STAYS AT 5.4 OR LOWER AND IF 9/16 (3) RESULTS @ -0- BOTH RAAS WL STAY UNDER 10 UG/L)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2016-05-16 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 2Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2016-05-16 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 2Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2016-05-16 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 2Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2016-05-16 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 2Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-05-26 | POE |  |  |  |  | (ROAD WIDENED-ST. RD 46 SITE TO BE MOVED BACK ON PROP-WL USE SAME ADDRESS-SHEILA WL SND EM 6/9/16-BB)5/16 BROMATE - AUX. WP (SO FAR RAA STILL UNDER BROMATE MCL OF 10>NOTIFIED CD NJH JF LB 6/6/16 EM)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-06-22 | POE | 1 |  | 1 | 1.72 | (7/16 BROM -0-)6/16 BROMATE-AUX.WP(6/16 RAA/BROMATE=8.9)NO MCL VIOL 6/16 QTR>EM>CD NJH JF W/UPDATE-MUST REALLY WATCH NXT2QTRS.BB(7/19EW HAS 4/16DBPS&6/16QTR DB RPRT>NO MCLS OR OE EXC.-T VAL OK ON DBF)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-07-18 | POE |  |  |  |  | 7/16 BROMATE-AUX.WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 28.9 | UG/L | 80.4999 | 2016-07-27 | S01_L02 |  |  |  | 1.49 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.36 | UG/L | 60.4999 | 2016-07-27 | S01_L02 |  |  |  | 1.49 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 31.11 | UG/L | 80.4999 | 2016-07-27 | S02_L06 |  |  |  | 1.48 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.8 | UG/L | 60.4999 | 2016-07-27 | S02_L06 |  |  |  | 1.48 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.88 | UG/L | 60.4999 | 2016-07-27 | S02_L05 |  |  |  | 1.16 | 3751 E SR 46 (MOVING THIS SITE @ 20 TO 50 FEET DUE TO ROAD WIDENING-MAY KEEP SAME ADDRESS>FORWARDED EM TO BW 11/28/16)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 56.88 | UG/L | 80.4999 | 2016-07-27 | S01_L01 |  |  |  | 0.86 | 531 N PALMETTO AVE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.13 | UG/L | 60.4999 | 2016-07-27 | S01_L01 |  |  |  | 0.86 | 531 N PALMETTO AVE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 48.43 | UG/L | 80.4999 | 2016-07-27 | S02_L05 |  |  |  | 1.16 | 3751 E SR 46 (MOVING THIS SITE @ 20 TO 50 FEET DUE TO ROAD WIDENING-MAY KEEP SAME ADDRESS>FORWARDED EM TO BW 11/28/16)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 9.2 | UG/L | 10.4999 | 2016-08-10 | POE |  |  |  |  | (8/10/16 BROMATE 9.2) 8/16 BROMATE-AUX.WP (6/16 RAA/BROMATE=8.9) NO MCL VIOL AVG AGAIN 9/19 FOR QTR - SO FAR 9.625 UG/L
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2016-08-22 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 3Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2016-08-22 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 3Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2016-08-22 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 3Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2016-08-22 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY SO FAR IN 3Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 7.3 | UG/L | 10.4999 | 2016-08-31 | POE | 1 |  | 1 | 1.75 | (8/31/16 BROMATE 7.3) MUST AVG 2 BROMATE 8/10 & 8/31 FOR 1 AVG FOR THE MONTH OF AUG 2016
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-09-19 | POE |  |  |  | 1.78 | 3Q RAA BROMATE 9.62 <MCL 10
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-10-18 | POE |  |  |  | 1.93 | POE - AUX PLANT #2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-11-21 | POE |  |  |  | 1.67 | POE - AUX PLANT #2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.73 | UG/L | 60.4999 | 2016-11-23 | S01_L02 |  |  |  | 1.54 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 62.7 | UG/L | 80.4999 | 2016-11-23 | S01_L01 |  |  |  | 1.11 | 531 N PALMETTO AVE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.91 | UG/L | 80.4999 | 2016-11-23 | S01_L02 |  |  |  | 1.54 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.85 | UG/L | 80.4999 | 2016-11-23 | S02_L06 |  |  |  | 1.59 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.43 | UG/L | 60.4999 | 2016-11-23 | S02_L06 |  |  |  | 1.59 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.77 | UG/L | 60.4999 | 2016-11-23 | S01_L01 |  |  |  | 1.11 | 531 N PALMETTO AVE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.04 | UG/L | 60.4999 | 2016-11-28 | S02_L05 |  |  | 4 | 0.96 | SO2_L05 - 3751 E SR46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 61.96 | UG/L | 80.4999 | 2016-11-28 | S02_L05 |  |  | 4 | 0.96 | SO2_L05 - 3751 E SR46
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2016-12-22 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 4Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2016-12-22 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 4Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2016-12-22 | WTP2 |  |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 4Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-12-22 | POE | 1 |  | 1 | 1.77 | 12/16 BROMATE - AUX. WP (12/16 BROMATE RAA RCVD WITH 10-11-12/16 BROMATE RESULTS) 12/16 BROMATE RAA REPORTED AS 8.1 ON FORM. HYPERLINKED TO BW 1/19/17-BB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2016-12-22 | WTP2 |  | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 4Q 2016)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-01-24 | POE | 1 |  | 1 | 1.76 | 1/17 BROMATE - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-15 | WTP2 | 0.0005 |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 1Q 2017)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-15 | WTP2 | 0.71 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 1Q 2017)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-02-15 | POE | 1 |  | 1 | 1.88 | 2/17 BROMATE - AUX. WP (3/21/17 HYPERLINKED TO BW - BB)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.16 | PCI/L | 15.4999 | 2017-02-15 | WTP2 | 1.03 |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 1Q 2017)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 1.03 | PCI/L | 3.4999 | 2017-02-15 | WTP2 | 0.639 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY IN 1Q 2017)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.1 | UG/L | 60.4999 | 2017-02-22 | S01_L01 | 0.2 |  | 1 | 1.1 | 531 N PALMETTO AVE.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 77.76 | UG/L | 80.4999 | 2017-02-22 | S01_L01 | 0.14 |  | 1 | 1.1 | 531 N PALMETTO AVE.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.1 | UG/L | 60.4999 | 2017-02-22 | S02_L05 | 0.2 |  | 2 | 1.31 | 3751 E. SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 43.14 | UG/L | 80.4999 | 2017-02-22 | S02_L05 | 0.14 |  | 2 | 1.31 | 3751 E. SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.67 | UG/L | 60.4999 | 2017-02-22 | S02_L06 | 0.2 |  | 3 | 1.72 | 2501 LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 35.48 | UG/L | 80.4999 | 2017-02-22 | S02_L06 | 0.14 |  | 3 | 1.72 | 2501 LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.61 | UG/L | 60.4999 | 2017-02-22 | S01_L02 | 0.2 |  | 4 | 1.7 | 100 WELDON BLVD (3/17 QTR DB REPORT RCVD WITH RESULTS (HYPERLINKED 4/18/17)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.34 | UG/L | 80.4999 | 2017-02-22 | S01_L02 | 0.14 |  | 4 | 1.7 | 100 WELDON BLVD (3/17 QTR DB REPORT RCVD WITH RESULTS (HYPERLINKED 4/18/17)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-03-28 | POE | 1 |  | 1 | 1.77 | 3/17 BROMATE - AUX. WP (3/17 BROMATE RAA RCVD WITH 1-2-3/17 BROMATE RESULTS) 3/17 BROMATE RAA REPORTED AS 1.1 ON FORM. HYPERLINKED TO BW 4/18/17-BB
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-04-24 | POE | 1 |  | 1 | 1.78 | 4/17 BROMATE - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 1.95 | UG/L | 60.4999 | 2017-04-26 | S01_L02 | 0.5 |  | 4 | 1.57 | 100 WELDON BLVD. (6/17 DB REPORT RCVD WITH RSLTS NO LRAA MCL VIOLS OR OE EXCEEDANCES SYS. DOES NOT QUALIFY TO GO TO REDUCED MONITORING) HYPERLINKED RESULTS 6/6/17 TO BW-BB
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 5.32 | UG/L | 80.4999 | 2017-04-26 | S02_L06 | 0.14 |  | 3 | 1.62 | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2 | UG/L | 60.4999 | 2017-04-26 | S02_L06 | 0.5 |  | 3 | 1.62 | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 13.64 | UG/L | 80.4999 | 2017-04-26 | S02_L05 | 0.14 |  | 2 | 1.49 | 3751 E. S.R. 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.61 | UG/L | 60.4999 | 2017-04-26 | S02_L05 | 0.5 |  | 2 | 1.49 | 3751 E. S.R. 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 82.99 | UG/L | 80.4999 | 2017-04-26 | S01_L01 | 0.14 |  | 1 | 0.97 | 531 N. PALMETTO AVE. (6/17 OE T VALUE=76.61) NO TTHM LRAA MCL VIOL 6/17 QTR.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 4.84 | UG/L | 80.4999 | 2017-04-26 | S01_L02 | 0.14 |  | 4 | 1.57 | 100 WELDON BLVD. (6/17 DB REPORT RCVD WITH RSLTS NO LRAA MCL VIOLS OR OE EXCEEDANCES SYS. DOES NOT QUALIFY TO GO TO REDUCED MONITORING) HYPERLINKED RESULTS 6/6/17 TO BW-BB
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.14 | UG/L | 60.4999 | 2017-04-26 | S01_L01 | 0.5 |  | 1 | 0.97 | 531 N. PALMETTO AVE. (6/17 OE T VALUE=76.61) NO TTHM LRAA MCL VIOL 6/17 QTR.
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 1.23 | PCI/L | 3.4999 | 2017-05-24 | WTP2 | 0.13 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 2Q 2017) GA REVISED FROM 4000 TO 4002 AS RQRD - BB/BW. RESULTS PLACED IN FINAL CHEM HOLD. FOLDER 7/11/17-BB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0.95 | PCI/L | 2.4999 | 2017-05-24 | WTP2 | 0.5 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 2Q 2017) GA REVISED FROM 4000 TO 4002 AS RQRD - BB/BW. RESULTS PLACED IN FINAL CHEM HOLD. FOLDER 7/11/17-BB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-05-24 | WTP2 | 2.5 |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 2Q 2017) GA REVISED FROM 4000 TO 4002 AS RQRD - BB/BW. RESULTS PLACED IN FINAL CHEM HOLD. FOLDER 7/11/17-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-05-24 | WTP2 | 0.0005 |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 2Q 2017)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 4.8 | UG/L | 10.4999 | 2017-05-24 | POE | 1 |  | 1 | 1.83 | 5/17 BROMATE - AUX WP (WP2) SIGNED PG1 RCVD AS RQRD FROM SHELLEY FRIEND&MACK MCKINLEY-BB/BW(RSLTS DELAYED BEC. SANFORD ASKED LAB TO RETEST THE SMPL-RSLTS CONFIRMED AFTER INSTRUMENTATION REPAIR&RETEST)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-06-14 | POE | 1 |  | 1 | 1.8 | 6/17 BROMATE - AUX. WP (6/17 BROMATE RAA RCVD WITH 4-5-6/17 BROMATE RESULTS) 6/17 BROMATE RAA REPORTED AS 1.1 ON FORM. HYPERLINKED TO BW 7/10/17-BB.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2017-06-28 | WTP1 | 0.0073 | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 2 MAIN WP 1 (MAYFAIR G.C.) GC WLS 1 & 6 ARE TEMPORARILY OUT OF SVC & NOT SMPLD DUE TO ELECTRICAL ISSUES. GC#1 HAS BEEN OFFLN SINCE 1/3/17 & GC#6 OFFLN SINCE 4/26/17.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2017-06-28 | WTP1 | 0.0071 | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 5 MAIN WP 1 (MAYFAIR G.C.) GC WLS 1 & 6 ARE TEMPORARILY OUT OF SVC & NOT SMPLD DUE TO ELECTRICAL ISSUES. GC#1 HAS BEEN OFFLN SINCE 1/3/17 & GC#6 OFFLN SINCE 4/26/17.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2017-06-28 | WTP1 | 0.0073 | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 4 MAIN WP 1 (MAYFAIR G.C.) GC WLS 1 & 6 ARE TEMPORARILY OUT OF SVC & NOT SMPLD DUE TO ELECTRICAL ISSUES. GC#1 HAS BEEN OFFLN SINCE 1/3/17 & GC#6 OFFLN SINCE 4/26/17.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | W | 0 | UG/L | 0.0249 | 2017-06-28 | WTP1 | 0.0071 | 0.0149 |  |  | SPEC. EDB MON. GOLF COURSE WELL 3 MAIN WP 1 (MAYFAIR G.C.) GC WLS 1 & 6 ARE TEMPORARILY OUT OF SVC & NOT SMPLD DUE TO ELECTRICAL ISSUES. GC#1 HAS BEEN OFFLN SINCE 1/3/17 & GC#6 OFFLN SINCE 4/26/17.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-07-19 | POE | 1 |  | 1 | 1.62 | 7/17 BROMATE - AUX. WP (HYPERLINKED 8/23/17)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 42.36 | UG/L | 80.4999 | 2017-07-26 | S01_L02 | 0.14 |  | 4 | 1.52 | 100 WELDON BLVD. (7/17 DBPS RCVD WITH 9/17 QTR DB REPORT) HYPERLINKED TO BW 10/23/17 - BB (RCVD 9/17 QTR OE REPORT FOR 531 N. PALMETTO AVE. SITE FOR TTHMS)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.47 | UG/L | 60.4999 | 2017-07-26 | S02_L05 | 0.5 |  | 2 | 1.38 | 3751 E. SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 83.94 | UG/L | 80.4999 | 2017-07-26 | S01_L01 | 0.14 |  | 1 | 0.7 | 531 N. PALMETTO AVE. (RCVD 9/17 QTR OE REPORT FOR 531 N. PALMETTO AVE. SITE FOR TTHMS 82.1575 ~ 82.16)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.89 | UG/L | 60.4999 | 2017-07-26 | S01_L01 | 0.5 |  | 1 | 0.7 | 531 N. PALMETTO AVE. (RCVD 9/17 QTR OE REPORT FOR 531 N. PALMETTO AVE. SITE FOR TTHMS 82.1575 ~ 82.16)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.33 | UG/L | 60.4999 | 2017-07-26 | S01_L02 | 0.5 |  | 4 | 1.52 | 100 WELDON BLVD. (7/17 DBPS RCVD WITH 9/17 QTR DB REPORT) HYPERLINKED TO BW 10/23/17 - BB (RCVD 9/17 QTR OE REPORT FOR 531 N. PALMETTO AVE. SITE FOR TTHMS)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 48.3 | UG/L | 80.4999 | 2017-07-26 | S02_L06 | 0.14 |  | 3 | 1.51 | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.41 | UG/L | 60.4999 | 2017-07-26 | S02_L06 | 0.5 |  | 3 | 1.51 | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 70.14 | UG/L | 80.4999 | 2017-07-26 | S02_L05 | 0.14 |  | 2 | 1.38 | 3751 E. SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-08-23 | POE | 1 |  | 1 | 1.74 | 8/17 BROMATE - AUX. WP (HYPERLINKED 8/23/17)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-08-23 | WTP2 | 0.0005 |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 3Q 2017)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-08-23 | WTP2 | 0.8 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 2Q 2017) PG2 REVISED & R228 LAB MDL REVISED FROM 0.9 TO 0.8 AS RQSTD - RCVD REVISIONS 10-3-17 - MFC/BB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0.61 | PCI/L | 3.4999 | 2017-08-23 | WTP2 | 0.13 | 1.4999 |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 2Q 2017) PG2 REVISED & R228 LAB MDL REVISED FROM 0.9 TO 0.8 AS RQSTD - RCVD REVISIONS 10-3-17 - MFC/BB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-08-23 | WTP2 | 2.5 |  |  |  | AUX. WP DUE TO ASR WELL (CITY HAS NOT CONDUCTED CYCLE TESTS OR HAD ASR WELL RECOVERY DURING 2Q 2017) PG2 REVISED & R228 LAB MDL REVISED FROM 0.9 TO 0.8 AS RQSTD - RCVD REVISIONS 10-3-17 - MFC/BB
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-09-27 | POE | 1 |  | 1 | 1.75 | 9/17 BROMATE - AUX. WP (9/17 BROMATE RAA RCVD WITH 7-8-9/17 BROMATE RESULTS) 9/17 BROMATE RAA REPORTED AS 0.4 ON FORM. HYPERLINKED TO BW 10/19/17-BB.
3590205 | SANFORD CITY OF (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-09-28 | WTP2 | 0.099 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1002 | ALUMINUM | N | 0.013 | MG/L | 0.2499 | 2017-09-28 | WTP2 | 0.0062 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1017 | CHLORIDE | N | 42.2 | MG/L | 250.4999 | 2017-09-28 | WTP2 | 2.5 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-09-28 | WTP2 | 0.00093 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.57 | MG/L | 2.0499 | 2017-09-28 | WTP2 | 0.034 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-09-28 | WTP2 | 0.02 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-09-28 | WTP2 | 0.0025 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-09-28 | WTP2 | 0.0025 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1055 | SULFATE | N | 7.7 | MG/L | 250.4999 | 2017-09-28 | WTP2 | 2.5 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-09-28 | WTP2 | 0.01 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1905 | COLOR | N | 10 | COLOR UNITS | 15.4999 | 2017-09-28 | WTP2 | 5 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.03 | MG/L | 10.4999 | 2017-09-28 | WTP1 | 0.025 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-09-28 | WTP1 | 0.025 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0.0014 | MG/L | 0.0104 | 2017-09-28 | WTP1 | 0.0005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1010 | BARIUM | N | 0.023 | MG/L | 2.4999 | 2017-09-28 | WTP1 | 0.005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-09-28 | WTP1 | 0.0005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-09-28 | WTP1 | 0.0025 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.6 | MG/L | 4.0499 | 2017-09-28 | WTP1 | 0.034 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-09-28 | WTP1 | 0.0005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-09-28 | WTP1 | 0.0001 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-09-28 | WTP1 | 0.0025 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-09-28 | WTP1 | 0.0005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1052 | SODIUM | N | 32.7 | MG/L | 160.4999 | 2017-09-28 | WTP1 | 0.5 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-09-28 | WTP1 | 0.0005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-09-28 | WTP1 | 0.0005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-09-28 | WTP1 | 0.0005 |  |  |  | MAIN WP(RSLTS RCVD 1-23-18)*RETEST CY-CY HAS J QUAL DUE TO MS/MSD 0/1% RECOV.FOR THIS SMP# 35338385002-CY NOT ENTD-SEE 38TH PG DOWN IN SCAN IN QC PAGES)LISA HARVEY PACE LAB. HYPRLNKD TO BW 1-24-18-BB
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-09-28 | WTP1 | 0.0062 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1017 | CHLORIDE | N | 51.6 | MG/L | 250.4999 | 2017-09-28 | WTP1 | 2.5 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-09-28 | WTP1 | 0.00093 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.6 | MG/L | 2.0499 | 2017-09-28 | WTP1 | 0.034 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1028 | IRON | N | 0.062 | MG/L | 0.3499 | 2017-09-28 | WTP1 | 0.02 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1032 | MANGANESE | N | 0.0046 | MG/L | 0.0549 | 2017-09-28 | WTP1 | 0.0025 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-09-28 | WTP1 | 0.0025 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1055 | SULFATE | N | 21.4 | MG/L | 250.4999 | 2017-09-28 | WTP1 | 2.5 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-09-28 | WTP1 | 0.01 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1905 | COLOR | N | 10 | COLOR UNITS | 15.4999 | 2017-09-28 | WTP1 | 5 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.7 | LN(10) |  | 2017-09-28 | WTP1 | 0.1 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 283 | MG/L | 500.4999 | 2017-09-28 | WTP1 | 5 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-09-28 | WTP1 | 0.099 |  |  |  | MAIN WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-09-28 | WTP1 | 0.025 |  |  |  | MAIN WP NN
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-09-28 | WTP2 | 0.0067 | 0.0149 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP2 | 0.0029 | 0.0249 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-09-28 | WTP2 | 0.049 | 0.1499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP2 | 0.58 | 1.4999 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-09-28 | WTP2 | 0.89 | 1.4999 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-09-28 | WTP2 | 0.3 | 0.4499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP2 | 6.3 | 9.4999 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-09-28 | WTP2 | 4.2 | 6.4999 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-09-28 | WTP2 | 0.37 | 0.6499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-09-28 | WTP2 | 0.55 | 2.4999 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-09-28 | WTP2 | 0.066 | 0.0749 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-09-28 | WTP2 | 0.48 | 0.6499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-09-28 | WTP2 | 0.094 | 0.1499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-09-28 | WTP2 | 0.16 | 0.2499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-09-28 | WTP2 | 0.031 | 0.1499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-09-28 | WTP2 | 0.32 | 0.9499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP2 | 0.06 | 0.1499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-09-28 | WTP2 | 0.033 | 0.2499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-09-28 | WTP2 | 0.011 | 0.0449 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP2 | 0.0029 | 0.0249 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-09-28 | WTP2 | 0.081 | 0.1499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-09-28 | WTP2 | 0.16 | 0.2499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP2 | 0.018 | 0.1499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP2 | 0.012 | 0.0249 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP2 | 0.03 | 0.0449 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-09-28 | WTP2 | 0.076 | 0.1499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP2 | 0.0063 | 0.0249 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-09-28 | WTP2 | 0.0074 | 0.0149 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-09-28 | WTP2 | 0.045 | 0.2499 |  |  | AUX WP (ALL REVISED)CARBO J QUAL LCS 122% RECOV(120% UPPER CONTROL LIMIT)122% IS BIASED SLIGHTLY HIGH).BENZO J QUAL MS/MSD 64/58% RECOV(70% LOWER LIMIT)AT HIGHEST .0206 U OK SINCE RDL=.02).BOTH J'S OK
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-09-28 | WTP1 | 0.0068 | 0.0149 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP1 | 0.0029 | 0.0249 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-09-28 | WTP1 | 0.049 | 0.1499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP1 | 0.59 | 1.4999 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-09-28 | WTP1 | 0.89 | 1.4999 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-09-28 | WTP1 | 0.3 | 0.4499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP1 | 6.3 | 9.4999 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-09-28 | WTP1 | 4.2 | 6.4999 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-09-28 | WTP1 | 0.36 | 0.6499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-09-28 | WTP1 | 0.55 | 2.4999 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-09-28 | WTP1 | 0.067 | 0.0749 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.26 | MG/L | 10.4999 | 2017-09-28 | WTP2 | 0.025 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-09-28 | WTP2 | 0.025 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-09-28 | WTP2 | 0.0005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1010 | BARIUM | N | 0.0097 | MG/L | 2.4999 | 2017-09-28 | WTP2 | 0.005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-09-28 | WTP2 | 0.0005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-09-28 | WTP2 | 0.0025 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-09-28 | WTP2 | 0.005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.57 | MG/L | 4.0499 | 2017-09-28 | WTP2 | 0.034 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-09-28 | WTP2 | 0.0005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-09-28 | WTP2 | 0.0001 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-09-28 | WTP2 | 0.0025 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-09-28 | WTP2 | 0.0005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1052 | SODIUM | N | 27.9 | MG/L | 160.4999 | 2017-09-28 | WTP2 | 0.5 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-09-28 | WTP2 | 0.0005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-09-28 | WTP2 | 0.0005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-09-28 | WTP2 | 0.0005 |  |  |  | AUX. WP (RSLTS RCVD 1-23-18)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.4 | LN(10) |  | 2017-09-28 | WTP2 | 0.1 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 224 | MG/L | 500.4999 | 2017-09-28 | WTP2 | 5 |  |  |  | AUX. WP (ODOR TSTD SEP)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.26 | MG/L | 10.4999 | 2017-09-28 | WTP2 | 0.025 |  |  |  | AUX. WP NN (NN RSLTS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-09-28 | WTP2 | 0.025 |  |  |  | AUX. WP NN (NN RSLTS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-09-28 | WTP1 | 0.41 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-09-28 | WTP1 | 0.44 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP1 | 0.39 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/MAIN WP
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-09-28 | WTP2 | 0.41 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-09-28 | WTP2 | 0.44 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-09-28 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/AUX. WP (VOCS PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-09-28 | WTP1 | 0.48 | 0.6499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-09-28 | WTP1 | 0.094 | 0.1499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-09-28 | WTP1 | 0.16 | 0.2499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-09-28 | WTP1 | 0.031 | 0.1499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-09-28 | WTP1 | 0.32 | 0.9499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-09-28 | WTP1 | 0.061 | 0.1499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-09-28 | WTP1 | 0.034 | 0.2499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-09-28 | WTP1 | 0.012 | 0.0449 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP1 | 0.0029 | 0.0249 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-09-28 | WTP1 | 0.081 | 0.1499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-09-28 | WTP1 | 0.16 | 0.2499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP1 | 0.018 | 0.1499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP1 | 0.012 | 0.0249 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-09-28 | WTP1 | 0.03 | 0.0449 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-09-28 | WTP1 | 0.077 | 0.1499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-09-28 | WTP1 | 0.0064 | 0.0249 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-09-28 | WTP1 | 0.0075 | 0.0149 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-09-28 | WTP1 | 0.045 | 0.2499 |  |  | MAIN WP (ALL REVISED) CARBO J QUAL LCS 122% RECOV. (120% UPPER CONTROL LIMIT) 122% IS BIASED SLIGHTLY HIGH) RESULT IS ACCEPTABLE FOR COMPLIANCE PURPOSES.
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.03 | MG/L | 10.4999 | 2017-09-28 | WTP1 | 0.025 |  |  |  | MAIN WP NN
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-10-02 | WTP1 | 1 |  |  |  | MAIN WP ODOR
3590205 | SANFORD CITY OF (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 1 |  | 3.4999 | 2017-10-02 | WTP2 | 1 |  |  |  | AUX. WP ODOR
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-10-25 | POE | 1 |  | 1 | 1.7 | 10/17 BROMATE - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-11-15 | POE | 1 |  | 1 | 1.89 | 11/17 BROMATE - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.65 | UG/L | 60.4999 | 2017-11-22 | S02_L06 | 0.5 |  | 3 | 1.48 | 2501 (E.) LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 60.17 | UG/L | 80.4999 | 2017-11-22 | S02_L05 | 0.14 |  | 2 | 1.28 | 3751 E. S.R. 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.15 | UG/L | 60.4999 | 2017-11-22 | S02_L05 | 0.5 |  | 2 | 1.28 | 3751 E. S.R. 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 79.04 | UG/L | 80.4999 | 2017-11-22 | S01_L01 | 0.14 |  | 1 | 1.05 | 531 N. PALMETTO AVE.(ACTUAL 12/17 LRAA/T THIS SITE=80.9325)STILL AN MCL LRAA VIOL FOR 12/17 QTR (ACTUAL 12/17 OE/T THIS SITE = 81.2525) STILL AN OE EXCEEDANCE. NOTIFIED BW+JF OF LRAA/T MCL VIO 1-19-18
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.01 | UG/L | 60.4999 | 2017-11-22 | S01_L01 | 0.5 |  | 1 | 1.05 | 531 N. PALMETTO AVE.(ACTUAL 12/17 LRAA/T THIS SITE=80.9325)STILL AN MCL LRAA VIOL FOR 12/17 QTR (ACTUAL 12/17 OE/T THIS SITE = 81.2525) STILL AN OE EXCEEDANCE. NOTIFIED BW+JF OF LRAA/T MCL VIO 1-19-18
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 35.14 | UG/L | 80.4999 | 2017-11-22 | S02_L06 | 0.14 |  | 3 | 1.48 | 2501 (E.) LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 41.14 | UG/L | 80.4999 | 2017-11-22 | S01_L02 | 0.14 |  | 4 | 1.65 | 100 WELDON BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.96 | UG/L | 60.4999 | 2017-11-22 | S01_L02 | 0.5 |  | 4 | 1.65 | 100 WELDON BLVD.
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-12-11 | WTP2 | 2.78 |  |  |  | AUX WP - DUE TO ASR WELL (PER 1/16/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 4Q 2017." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-12-11 | WTP2 | 0.081 | 0.1499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-12-11 | WTP2 | 0.736 | 1.4999 |  |  | AUX WP - DUE TO ASR WELL (PER 1/16/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 4Q 2017." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-12-11 | WTP2 | 0.001 |  |  |  | ARSENIC - AUX. WP DUE TO ASR WELL (PER 1/16/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 4Q 2017." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | S | 87.02 | UG/L | 80.4999 | 2017-12-11 | S01_L01 | 0.14 |  | 1 | 1.09 | XXX ONLY TTHMS TSTD XXX NOT DUAL SMPL - SHD NOT BE AVGD IN WITH 11/17 RSLTS (531 N PALMETTO AVE) CITY INCLUDED THESE RSLTS IN 11&12/17 LRAA/T & GOT 81.93. INCLUDED IN OE/T & GOT 83.2475~83.25 ON RPRT
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-12-11 | WTP2 | 0.0068 | 0.0149 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP2 | 0.0029 | 0.0249 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-12-11 | WTP2 | 0.049 | 0.1499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-12-11 | WTP2 | 0.59 | 1.4999 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-12-11 | WTP2 | 0.89 | 1.4999 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-12-11 | WTP2 | 0.3 | 0.4499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-12-11 | WTP2 | 4.3 | 9.4999 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-12-11 | WTP2 | 4.2 | 6.4999 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-12-11 | WTP2 | 0.37 | 0.6499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-12-11 | WTP2 | 0.55 | 2.4999 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-12-11 | WTP2 | 0.16 | 0.2499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-12-11 | WTP2 | 0.018 | 0.1499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP2 | 0.013 | 0.0249 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-12-11 | WTP2 | 0.03 | 0.0449 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-12-11 | WTP2 | 0.077 | 0.1499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP2 | 0.0064 | 0.0249 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-12-11 | WTP2 | 0.0075 | 0.0149 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-12-11 | WTP2 | 0.045 | 0.2499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-12-11 | WTP2 | 0.031 | 0.1499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-12-11 | WTP1 | 0.0068 | 0.0149 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP1 | 0.0029 | 0.0249 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-12-11 | WTP1 | 0.049 | 0.1499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-12-11 | WTP1 | 0.59 | 1.4999 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-12-11 | WTP1 | 0.89 | 1.4999 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-12-11 | WTP1 | 0.3 | 0.4499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-12-11 | WTP1 | 4.3 | 9.4999 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-12-11 | WTP1 | 4.2 | 6.4999 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-12-11 | WTP1 | 0.37 | 0.6499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-12-11 | WTP1 | 0.55 | 2.4999 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-12-11 | WTP1 | 0.067 | 0.0749 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-12-11 | WTP1 | 0.48 | 0.6499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-12-11 | WTP1 | 0.094 | 0.1499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-12-11 | WTP1 | 0.16 | 0.2499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-12-11 | WTP1 | 0.32 | 0.9499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-12-11 | WTP1 | 0.076 | 0.1499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-12-11 | WTP1 | 0.034 | 0.2499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-12-11 | WTP1 | 0.012 | 0.0449 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP1 | 0.0029 | 0.0249 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-12-11 | WTP1 | 0.081 | 0.1499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-12-11 | WTP1 | 0.16 | 0.2499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-12-11 | WTP1 | 0.018 | 0.1499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP1 | 0.012 | 0.0249 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-12-11 | WTP1 | 0.03 | 0.0449 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-12-11 | WTP1 | 0.077 | 0.1499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP1 | 0.0064 | 0.0249 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-12-11 | WTP1 | 0.0075 | 0.0149 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-12-11 | WTP1 | 0.045 | 0.2499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-12-11 | WTP1 | 0.031 | 0.1499 |  |  | 2Q SOC - MAIN WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-12-11 | WTP2 | 0.067 | 0.0749 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-12-11 | WTP2 | 0.48 | 0.6499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-12-11 | WTP2 | 0.094 | 0.1499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-12-11 | WTP2 | 0.16 | 0.2499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-12-11 | WTP2 | 0.32 | 0.9499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-12-11 | WTP2 | 0.076 | 0.1499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-12-11 | WTP2 | 0.034 | 0.2499 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-12-11 | WTP2 | 0.012 | 0.0449 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-12-11 | WTP2 | 0.0029 | 0.0249 |  |  | 2Q SOC - AUX WP (SIM 184% RECOV LCS - BIASED HIGH - OK 2042 HEX... 67% RECOV LCS - SUFFICIENT FOR ACCEPTABILITY - BB/BW)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2017-12-11 | WTP2 | 0.634 | 1.4999 |  |  | AUX WP - DUE TO ASR WELL (PER 1/16/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 4Q 2017." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | D | 0 | UG/L | 10.4999 | 2017-12-13 | POE | 1 |  | 1 | 1.9 | (NOTIFIED BW+JF OF 12/17 LRAA/T MCL VIO>1-19-18 EM-BB)12/17 BROMATE-AUX. WP(12/17 BROM RAA RCVD WITH 10-11-12/17 RSLTS.RAA=0.4 UG/L 1/17-12/17)HYPRLNKD TO BW 1/10/18 - BB (MACK.MCKINLEY@SANFORDFL.GOV)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-01-24 | POE | 1 |  | 1 | 1.73 | 1/18 BROMATE - AUX WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-02-15 | POE | 1 |  | 1 | 1.59 | 2/18 BROMATE - AUX WP
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-20 | WTP1 | 0.005 |  |  |  | MAIN WP CYANIDE (MAKE-UP TEST FOR 2017)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20 | UG/L | 60.4999 | 2018-02-21 | S01_L01 | 0.5 |  | 1 | 1.2 | 531 N. PALMETTO AVE. (3/18 LRAA/T=76.825)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.25 | UG/L | 60.4999 | 2018-02-21 | S02_L05 | 0.5 |  | 2 | 1.31 | 3751 E. S.R. 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.39 | UG/L | 60.4999 | 2018-02-21 | S01_L02 | 0.5 |  | 4 | 1.57 | 100 WELDON BLVD. (3/18 DISINF BYP REPORT RCVD W/RSLTS) 4/13/18 DBPS HYPRLNKD TO BW-BB
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 61.33 | UG/L | 80.4999 | 2018-02-21 | S01_L01 | 0.14 |  | 1 | 1.2 | 531 N. PALMETTO AVE. (3/18 LRAA/T=76.825)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 38.44 | UG/L | 80.4999 | 2018-02-21 | S01_L02 | 0.14 |  | 4 | 1.57 | 100 WELDON BLVD. (3/18 DISINF BYP REPORT RCVD W/RSLTS) 4/13/18 DBPS HYPRLNKD TO BW-BB
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 45.76 | UG/L | 80.4999 | 2018-02-21 | S02_L05 | 0.14 |  | 2 | 1.31 | 3751 E. S.R. 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.08 | UG/L | 60.4999 | 2018-02-21 | S02_L06 | 0.5 |  | 3 | 1.7 | 2501 LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 34.5 | UG/L | 80.4999 | 2018-02-21 | S02_L06 | 0.14 |  | 3 | 1.7 | 2501 LAKE MARY BLVD.
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 1.02 | PCI/L | 3.4999 | 2018-03-13 | WTP2 | 0.578 | 1.4999 |  |  | AUX WP - DUE TO ASR WELL (PER 4/3/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2018." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-03-13 | WTP2 | 2.89 |  |  |  | AUX WP - DUE TO ASR WELL (PER 4/3/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2018." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-03-13 | WTP2 | 0.0005 |  |  |  | ARSENIC - AUX. WP DUE TO ASR WELL (PER 4/3/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2018." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-03-13 | WTP2 | 0.757 | 1.4999 |  |  | AUX WP - DUE TO ASR WELL (PER 4/3/18 COVER PAGE THE "CITY HAS NOT PERFORMED CYCLE TESTS OR RECOVERY FROM ASR WELL TO AUX. WP DURING 1Q 2018." NEXT CYCLE WILL BEGIN EARLY SUMMER. BW/BB)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-03-21 | POE | 3.34 |  | 1 | 1.98 | 3/18 BROMATE - AUX. WP (3/18 BROMATE RAA RCVD W/RSLTS) 4/23/18 HYPRLNKD TO BW - BB (ANALYSIS DELAYED BY LAB DUE TO HAVING TO ORDER INSTRUMENT PART - SENT EXPLANATION IN NARRATIVE)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-04-18 | POE | 1 |  | 1 | 1.86 | 4/18 BROMATE - AUX. WP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.96 | UG/L | 60.4999 | 2018-04-25 | S01_L01 |  |  |  | 1.03 | 531 N PALMETTO AVE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 74.88 | UG/L | 80.4999 | 2018-04-25 | S01_L01 |  |  |  | 1.03 | 531 N PALMETTO AVE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.24 | UG/L | 60.4999 | 2018-04-25 | S02_L05 |  |  |  | 1.5 | 3751 E SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 50.85 | UG/L | 80.4999 | 2018-04-25 | S01_L02 |  |  |  | 1.73 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.47 | UG/L | 60.4999 | 2018-04-25 | S02_L06 |  |  |  | 1.72 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 52.69 | UG/L | 80.4999 | 2018-04-25 | S02_L06 |  |  |  | 1.72 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.07 | UG/L | 60.4999 | 2018-04-25 | S01_L02 |  |  |  | 1.73 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 65.55 | UG/L | 80.4999 | 2018-04-25 | S02_L05 |  |  |  | 1.5 | 3751 E SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-05-09 | POE | 1 |  | 1 | 1.82
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-05-31 | WTP2 | 0.0005 |  |  |  | AUX WP-DUE TO ASR WELL(CYCLE 7 BEGAN 4/30/18.CITY'S INTENTION IS TO INJECT 120 MILLION GALLONS OF RAW WTR INTO THE ASR WELL AT@1 MGD UNTIL@8/27/18.THERE'LL BE NO RECOV OF ASR WL TO AUX WP 2Q'18-BB/RLB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-05-31 | WTP2 | 2.91 |  |  |  | AUX WP-DUE TO ASR WELL(CYCLE 7 BEGAN 4/30/18.CITY'S INTENTION IS TO INJECT 120 MILLION GALLONS OF RAW WTR INTO THE ASR WELL AT@1 MGD UNTIL@8/27/18.THERE'LL BE NO RECOV OF ASR WL TO AUX WP 2Q'18-BB/RLB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2018-05-31 | WTP2 | 0.749 | 1.4999 |  |  | AUX WP-DUE TO ASR WELL(CYCLE 7 BEGAN 4/30/18.CITY'S INTENTION IS TO INJECT 120 MILLION GALLONS OF RAW WTR INTO THE ASR WELL AT@1 MGD UNTIL@8/27/18.THERE'LL BE NO RECOV OF ASR WL TO AUX WP 2Q'18-BB/RLB
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-05-31 | WTP2 | 0.882 | 1.4999 |  |  | AUX WP-DUE TO ASR WELL(CYCLE 7 BEGAN 4/30/18.CITY'S INTENTION IS TO INJECT 120 MILLION GALLONS OF RAW WTR INTO THE ASR WELL AT@1 MGD UNTIL@8/27/18.THERE'LL BE NO RECOV OF ASR WL TO AUX WP 2Q'18-BB/RLB
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-06-06 | POE | 1 |  | 1 | 1.77 | 6/18 BROMATE - AUX. WP (6/18 BROMATE RAA RCVD W/RSLTS) 7/17/18 HLKD RSLTS & RAA TO RLB 7/17/18 - BB (SEE NOTE REGARDING 6/18 BROMATE ON COVER PAGE.)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.23 | MG/L | 10.4999 | 2018-07-18 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-07-18 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.076 | MG/L | 10.4999 | 2018-07-18 | WTP1 |  |  |  |  | MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-07-18 | WTP1 |  |  |  |  | MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-07-18 | POE |  |  |  | 1.92 | 07/2018 BROMATE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.22 | UG/L | 60.4999 | 2018-07-25 | S01_L01 | 0.91 |  | 1 | 1.02 | 531 PALMETTO
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.29 | UG/L | 80.4999 | 2018-07-25 | S01_L01 | 0.14 |  | 1 | 1.02 | 531 PALMETTO
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.7 | UG/L | 60.4999 | 2018-07-25 | S02_L05 | 0.91 |  | 2 | 1.48 | 3751 E SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 25.08 | UG/L | 80.4999 | 2018-07-25 | S01_L02 | 0.14 |  | 4 | 1.62 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.64 | UG/L | 60.4999 | 2018-07-25 | S02_L06 | 0.91 |  | 3 | 1.71 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 24.35 | UG/L | 80.4999 | 2018-07-25 | S02_L06 | 0.14 |  | 3 | 1.71 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.91 | UG/L | 60.4999 | 2018-07-25 | S01_L02 | 0.91 |  | 4 | 1.62 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.41 | UG/L | 80.4999 | 2018-07-25 | S02_L05 | 0.14 |  | 2 | 1.48 | 3751 E SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-08-22 | POE | 1 |  | 1 | 1.81 | 8 2018 BROMATE
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-09-05 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-09-05 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0.844 | PCI/L | 3.4999 | 2018-09-05 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-09-05 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-09-19 | POE | 1 |  | 1 | 1.83 | 9 2018 BROMATE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 3.9 | UG/L | 10.4999 | 2018-10-17 | POE |  |  | A1808059 | 1.75 | 10/18 BROMATE
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-10-25 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-10-25 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 1.04 | PCI/L | 3.4999 | 2018-10-25 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-10-25 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-11-14 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 1.64 | PCI/L | 3.4999 | 2018-11-14 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-11-14 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-11-14 | POE |  |  |  | 1.73 | 11/18 BROMATE
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-11-14 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 60.08 | UG/L | 80.4999 | 2018-11-26 | S01_L01 |  |  | 1 | 1.12 | 2950-531 N PALMETTO AVE / SUBCONTRACT LAB E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.11 | UG/L | 60.4999 | 2018-11-26 | S02_L05 |  |  | 2 | 1.45 | 2950-3751 E SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 40.55 | UG/L | 80.4999 | 2018-11-26 | S02_L05 |  |  | 2 | 1.45 | 2950-3751 E SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.66 | UG/L | 60.4999 | 2018-11-26 | S02_L06 |  |  | 3 | 1.63 | 2950-2501 LAKE MARY BLVD / SUBCONTRACT LAB 84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 30.84 | UG/L | 80.4999 | 2018-11-26 | S01_L02 |  |  | 4 | 1.71 | 2950-100 WELDON BLVD / SUBCONTRACT LAB 84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 31.12 | UG/L | 80.4999 | 2018-11-26 | S02_L06 |  |  | 3 | 1.63 | 2950-2501 LAKE MARY BLVD / SUBCONTRACT LAB 84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.43 | UG/L | 60.4999 | 2018-11-26 | S01_L02 |  |  | 4 | 1.71 | 2950-100 WELDON BLVD / SUBCONTRACT LAB 84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.71 | UG/L | 60.4999 | 2018-11-26 | S01_L01 |  |  | 1 | 1.12 | 2950-531 N PALMETTO AVE / SUBCONTRACT LAB E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-12-05 | POE |  |  |  | 1.5 | 12/18 BROMATE
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-12-10 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-12-10 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 1.07 | PCI/L | 3.4999 | 2018-12-10 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-12-10 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.37 | LN(10) |  | 2019-01-07 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.35 | MG/L |  | 2019-01-07 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.69 | LN(10) |  | 2019-01-07 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.39 | MG/L |  | 2019-01-07 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.77 | LN(10) |  | 2019-01-14 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.41 | MG/L |  | 2019-01-14 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.35 | LN(10) |  | 2019-01-14 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.33 | MG/L |  | 2019-01-14 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 7 | UG/L | 10.4999 | 2019-01-16 | POE | 1.6 |  | 1 | 1.85 | 1/19 BROMATE - AUX. WP (HLKD)
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2019-01-16 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2019-01-16 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 3.27 | PCI/L | 15.4999 | 2019-01-16 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2019-01-16 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-01-21 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-01-21 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.45 | LN(10) |  | 2019-01-22 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.36 | MG/L |  | 2019-01-22 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.37 | MG/L |  | 2019-01-28 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.49 | LN(10) |  | 2019-01-28 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.91 | LN(10) |  | 2019-01-28 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.42 | MG/L |  | 2019-01-28 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.39 | MG/L |  | 2019-02-04 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.44 | LN(10) |  | 2019-02-04 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.91 | LN(10) |  | 2019-02-04 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.46 | MG/L |  | 2019-02-04 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-02-06 | POE | 1.6 |  | 1 | 1.79 | BROMATE
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.44 | MG/L |  | 2019-02-11 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.88 | LN(10) |  | 2019-02-11 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.38 | MG/L |  | 2019-02-11 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.43 | LN(10) |  | 2019-02-11 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.46 | MG/L |  | 2019-02-18 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.4 | MG/L |  | 2019-02-18 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.41 | LN(10) |  | 2019-02-18 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-02-18 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.52 | LN(10) |  | 2019-02-25 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.4 | MG/L |  | 2019-02-25 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.78 | LN(10) |  | 2019-02-25 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.42 | MG/L |  | 2019-02-25 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 11.99 | UG/L | 60.4999 | 2019-02-27 | S01_L02
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 33.05 | UG/L | 80.4999 | 2019-02-27 | S02_L06
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 7.39 | UG/L | 60.4999 | 2019-02-27 | S02_L06
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.86 | UG/L | 80.4999 | 2019-02-27 | S01_L01 | 0.39 |  | 1 | 1.27 | 531 PALMETTO
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 39.5 | UG/L | 80.4999 | 2019-02-27 | S01_L02
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.7 | UG/L | 60.4999 | 2019-02-27 | S01_L01 | 0.91 |  | 1 | 1.27 | 531 PALMETTO
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 39.5 | UG/L | 80.4999 | 2019-02-27 | S01_L02 | 0.39 |  | 4 | 1.14 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.99 | UG/L | 60.4999 | 2019-02-27 | S01_L02 | 0.91 |  | 4 | 1.14 | 100 WELDON BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 33.05 | UG/L | 80.4999 | 2019-02-27 | S02_L06 | 0.39 |  | 3 | 1.77 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.39 | UG/L | 60.4999 | 2019-02-27 | S02_L06 | 0.91 |  | 3 | 1.77 | 2501 LAKE MARY BLVD
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.01 | UG/L | 60.4999 | 2019-02-27 | S02_L05 | 0.91 |  | 2 | 1.46 | 3751 SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 40.15 | UG/L | 80.4999 | 2019-02-27 | S02_L05 | 40.15 |  | 2 | 1.46 | 3751 SR 46
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 16.77 | UG/L | 60.4999 | 2019-02-27 | S01_L01
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 40.15 | UG/L | 80.4999 | 2019-02-27 | S02_L05
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 9.01 | UG/L | 60.4999 | 2019-02-27 | S02_L05
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | M | 32.86 | UG/L | 80.4999 | 2019-02-27 | S01_L01
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.89 | LN(10) |  | 2019-03-04 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.41 | MG/L |  | 2019-03-04 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.39 | MG/L |  | 2019-03-04 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.47 | LN(10) |  | 2019-03-04 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-03-06 | POE | 1.6 |  | 1 | 1.86 | 3/19 BROMATE - AUX. WP & 3/19 BROMATE RAA RCVD W/RESULTS (PER 3/19 BROMATE RAA REPORT 4/18 - 3/19 RAA = 0.9)
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.42 | MG/L |  | 2019-03-11 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.91 | LN(10) |  | 2019-03-11 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.39 | MG/L |  | 2019-03-11 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.47 | LN(10) |  | 2019-03-11 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.41 | MG/L |  | 2019-03-15 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-03-15 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.55 | LN(10) |  | 2019-03-18 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.38 | MG/L |  | 2019-03-18 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.45 | MG/L |  | 2019-03-18 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.93 | LN(10) |  | 2019-03-18 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.39 | MG/L |  | 2019-03-25 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.55 | LN(10) |  | 2019-03-25 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.89 | LN(10) |  | 2019-04-01 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.5 | LN(10) |  | 2019-04-01 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.37 | MG/L |  | 2019-04-01 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-04-01 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-04-03 | POE |  |  |  |  | J4 QUALIFIED - ACCEPTABLE_RLB
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.76 | LN(10) |  | 2019-04-08 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.54 | LN(10) |  | 2019-04-08 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.38 | MG/L |  | 2019-04-08 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.36 | MG/L |  | 2019-04-08 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.41 | MG/L |  | 2019-04-15 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.46 | LN(10) |  | 2019-04-15 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.94 | LN(10) |  | 2019-04-15 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-04-15 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2019-04-22 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2019-04-22 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0.658 | PCI/L | 3.4999 | 2019-04-22 | WTP2 |  | 1.4999 |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2019-04-22 | WTP2 |  |  |  |  | AUXILIARY WP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.47 | LN(10) |  | 2019-04-22 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.42 | MG/L |  | 2019-04-22 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.93 | LN(10) |  | 2019-04-22 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-04-22 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 55.55 | UG/L | 80.4999 | 2019-04-24 | S01_L01 |  |  | 1 | 1.25 | 531 N PALMETTO AVE / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 36.98 | UG/L | 80.4999 | 2019-04-24 | S02_L06 |  |  | 3 | 1.68 | 2501 LAKE MARY BLVD / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.77 | UG/L | 60.4999 | 2019-04-24 | S02_L05 |  |  | 3 | 1.61 | 3751 E SR 46 / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 50.16 | UG/L | 80.4999 | 2019-04-24 | S02_L05 |  |  | 3 | 1.61 | 3751 E SR 46 / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.24 | UG/L | 60.4999 | 2019-04-24 | S01_L01 |  |  | 1 | 1.25 | 531 N PALMETTO AVE / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.29 | UG/L | 60.4999 | 2019-04-24 | S01_L02 |  |  | 4 | 1.34 | 100 WELDON BLVD / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 44.19 | UG/L | 80.4999 | 2019-04-24 | S01_L02 |  |  | 4 | 1.34 | 100 WELDON BLVD / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.23 | UG/L | 60.4999 | 2019-04-24 | S02_L06 |  |  | 3 | 1.68 | 2501 LAKE MARY BLVD / SUBCONTRACT LABS E82535 E84589
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.4 | MG/L |  | 2019-04-29 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.91 | LN(10) |  | 2019-04-29 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.41 | MG/L |  | 2019-04-29 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.45 | LN(10) |  | 2019-04-29 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-05-01 | POE |  |  |  | 2.01 | 2019-5 BROMATE - AUX PLANT WTP #2 POE -- J4 QUALIFIER: ACCEPTABLE
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.45 | LN(10) |  | 2019-05-06 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.37 | MG/L |  | 2019-05-06 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-05-06 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.38 | MG/L |  | 2019-05-06 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.41 | MG/L |  | 2019-05-13 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.43 | LN(10) |  | 2019-05-13 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2019-05-14 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.46 | MG/L |  | 2019-05-14 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.44 | LN(10) |  | 2019-05-20 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.46 | MG/L |  | 2019-05-20 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.86 | LN(10) |  | 2019-05-20 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-05-20 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.32 | MG/L | 10.4999 | 2019-05-22 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-22 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1040 | NITRATE | N | 0.059 | MG/L | 10.4999 | 2019-05-22 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-22 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.45 | MG/L |  | 2019-05-28 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.51 | LN(10) |  | 2019-05-28 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.39 | MG/L |  | 2019-05-28 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.93 | LN(10) |  | 2019-05-28 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.52 | LN(10) |  | 2019-06-03 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.52 | MG/L |  | 2019-06-03 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-06-03 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.44 | MG/L |  | 2019-06-03 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-06-05 | POE |  |  |  | 1.81 | 2019-6 BROMATE - AUX PLANT WTP #2 POE
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.51 | LN(10) |  | 2019-06-10 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.5 | MG/L |  | 2019-06-10 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.46 | MG/L |  | 2019-06-10 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.89 | LN(10) |  | 2019-06-10 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.87 | LN(10) |  | 2019-06-17 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-06-17 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.87 | LN(10) |  | 2019-06-17 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-06-17 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.38 | LN(10) |  | 2019-06-17 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.46 | MG/L |  | 2019-06-17 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.87 | LN(10) |  | 2019-06-17 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.43 | MG/L |  | 2019-06-17 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.38 | LN(10) |  | 2019-06-24 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.46 | MG/L |  | 2019-06-24 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1924 | pH (FIELD) | N | 7.81 | LN(10) |  | 2019-06-24 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.42 | MG/L |  | 2019-06-24 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 13 | UG/L | 10.4999 | 2019-07-03 | POE |  |  |  | 1.98 | 2019-7 BROMATE - AUX PLANT WTP #2 POE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.49 | UG/L | 60.4999 | 2019-07-24 | S01_L01 | 0.91 |  | 1 | 1.14 | 531 N. PALMETTO AVE. (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 70.07 | UG/L | 80.4999 | 2019-07-24 | S01_L01 | 0.39 |  | 1 | 1.14 | 531 N. PALMETTO AVE. (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.47 | UG/L | 60.4999 | 2019-07-25 | S02_L05 | 0.91 |  | 2 | 0.93 | 3751 E. S.R. 46 (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 61.48 | UG/L | 80.4999 | 2019-07-25 | S01_L02 | 0.39 |  | 4 | 1.28 | 100 WELDON BLVD. (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.38 | UG/L | 60.4999 | 2019-07-25 | S01_L02 | 0.91 |  | 4 | 1.28 | 100 WELDON BLVD. (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 32.96 | UG/L | 80.4999 | 2019-07-25 | S02_L06 | 0.39 |  | 3 | 1.64 | 2501 E. LAKE MARY BLVD. (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.15 | UG/L | 60.4999 | 2019-07-25 | S02_L06 | 0.91 |  | 3 | 1.64 | 2501 E. LAKE MARY BLVD. (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 66.42 | UG/L | 80.4999 | 2019-07-25 | S02_L05 | 0.39 |  | 2 | 0.93 | 3751 E. S.R. 46 (E82535/TTHM E84589/HAA5)
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-08-07 | POE |  |  |  | 1.79 | 2019-8 BROMATE - AUX PLANT WTP #2 POE
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0.71 | PCI/L | 2.4999 | 2019-08-19 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 1.31 | PCI/L | 3.4999 | 2019-08-19 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2019-08-19 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2019-08-19 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 6.8 | UG/L | 10.4999 | 2019-09-10 | POE |  |  | 1 |  | WTP #2 POE AUX PLANT
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-10-02 | POE | 1.6 |  | 1 | 1.7 | BROMATE
3590205 | SANFORD CITY OF (2 WPS) | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-11-11 | POE | 1.6 |  | 1 | 1.83 | BROMATE
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0.408 | PCI/L | 3.4999 | 2019-11-19 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2019-11-19 | WTP2
3590205 | SANFORD CITY OF (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2019-11-19 | WTP1
3590205 | SANFORD CITY OF (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2019-11-19 | WTP2 |  | 1.4999
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.35 | UG/L | 60.4999 | 2019-11-26 | S01_L01 |  |  |  | 1.13 | 531 N PALMETO AVE [LRAA TTHM =58.26; HAA5=19.46]_VP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 74.56 | UG/L | 80.4999 | 2019-11-26 | S01_L01 |  |  |  | 1.13 | 531 N PALMETO AVE [LRAA TTHM =58.26; HAA5=19.46]_VP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.49 | UG/L | 60.4999 | 2019-11-26 | S02_L05 |  |  |  | 0.73 | 3751 E SR 46 [LRAA TTHM =58.12; HAA5=12.19]_VP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2019-11-26 | S01_L02 |  |  |  | 1.56 | 100 WELDON RD [LRAA TTHM =36.29; HAA5=14.12]_VP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.22 | UG/L | 60.4999 | 2019-11-26 | S02_L06 |  |  |  | 1.45 | 2501 LAKE MARY BLVD [LRAA TTHM =37.79; HAA5=8.5]_VP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 48.17 | UG/L | 80.4999 | 2019-11-26 | S02_L06 |  |  |  | 1.45 | 2501 LAKE MARY BLVD [LRAA TTHM =37.79; HAA5=8.5]_VP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.83 | UG/L | 60.4999 | 2019-11-26 | S01_L02 |  |  |  | 1.56 | 100 WELDON RD [LRAA TTHM =36.29; HAA5=14.12]_VP
3590205 | SANFORD CITY OF (2 WPS) | DBP | 2950 | TOTAL THMS | D | 75.73 | UG/L | 80.4999 | 2019-11-26 | S02_L05 |  |  |  | 0.73 | 3751 E SR 46 [LRAA TTHM =58.12; HAA5=12.19]_VP
3590338 | ELDER SPRINGS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 14 | UG/L | 80.4999 | 2015-09-21 | L1 |  |  |  | 0.2 | LOT 3841 (3841 ELDER SPRINGS CIRCLE) ON R.M. - NEXT T/H DUE @ 2ND WEEK JULY 2018 (<500)
3590338 | ELDER SPRINGS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.9 | UG/L | 60.4999 | 2015-09-21 | L1 |  |  |  | 0.2 | LOT 3841 (3841 ELDER SPRINGS CIRCLE) ON R.M. - NEXT T/H DUE @ 2ND WEEK JULY 2018 (<500)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 92 | MG/L | 250.4999 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0.0029 | MG/L | 1.4999 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 5.65 | MG/L | 250.4999 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.31 | LN(10) |  | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-12-22 | AAA |  | 0.1499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-12-22 | AAA |  | 0.2499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-12-22 | AAA |  | 0.0449 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-12-22 | AAA |  | 0.0249 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0.472 | UG/L | 74.9999 | 2015-12-22 | AAA |  | 0.1499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-12-22 | AAA |  | 0.2499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-12-22 | AAA |  | 0.1499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-12-22 | AAA |  | 0.0249 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-12-22 | AAA |  | 0.0449 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-12-22 | AAA |  | 0.1499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-12-22 | AAA |  | 0.0249 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-12-22 | AAA |  | 0.0149 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-12-22 | AAA |  | 0.2499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-12-22 | AAA |  |  |  |  | RADS DUE 2021
3590338 | ELDER SPRINGS MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-12-22 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 570 | MG/L | 500.4999 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0.289 |  | 0.5499 | 2015-12-22 | AAA |  |  |  |  | TDS 570 - TAKE 3 TDS RECS (EM 1/26/16 TO TED BURLESON & OWNER FOR 3 TDS & FOR 2 4-D) 3/25/16 PER PAMALA TKN 3/22 23 24 & TURNED IN TO LAB
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-12-22 | AAA |  | 0.5499 |  |  | 3YR VOC
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-12-22 | AAA |  | 0.0149 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-12-22 | AAA |  | 0.0249 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-12-22 | AAA |  | 0.1499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-12-22 | AAA |  | 1.4999 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-12-22 | AAA |  | 1.4999 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-12-22 | AAA |  | 0.4499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-12-22 | AAA |  | 9.4999 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-12-22 | AAA |  | 6.4999 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-12-22 | AAA |  | 0.6499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-12-22 | AAA |  | 2.4999 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-12-22 | AAA |  | 0.0749 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-12-22 | AAA |  | 0.6499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-12-22 | AAA |  | 0.1499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-12-22 | AAA |  | 0.2499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-12-22 | AAA |  | 0.1499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-12-22 | AAA |  | 0.9499 |  |  | 3YR SOC(2QM/2 4-D 3/16>TKN PER PAMALA 3/25)EM1/26/16+3/25/16>BURLESON&OWNR(PIC RVSD FR. 0.375 TO -0- BY LAB 2 4-D 0.472-ABOVE RDL 0.1)PIC DOES NOT ND TO BE TSTD QTRLY-FLOWERS LAB REVISED PIC TO BDL.
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.0084 | MG/L | 2.4999 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 60.3 | MG/L | 160.4999 | 2015-12-22 | AAA |  |  |  |  | 15DON/16:2QM/2 4-D 3/16>EM 1/26/16 3 TDS>EM 1/26/16 (TED BURLESON)
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 294 | MG/L | 500.4999 | 2016-03-22 | AAA |  |  |  |  | 3/22 TDS 294
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 298 | MG/L | 500.4999 | 2016-03-23 | AAA |  |  |  |  | 3/23 TDS 298
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 302 | MG/L | 500.4999 | 2016-03-24 | AAA |  |  |  |  | TDS 302 (LAST 3 TDS OK NOTHING ELSE RQRD)
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2016-03-24 | AAA |  | 0.1499 |  |  | 2QM/2 4-D (3QM/2 4-D DUE 6/16>2 4-D TKN ON 6/27/16 PER VANDESTREEK IN 6/27/16 EM C OF C 4QM/2 4-D DUE 9/16) ANALYSIS DATE REVISION RCVD & IN OC
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2016-06-27 | AAA | 0.1 | 0.1499 |  |  | 3QM/2 4-D (4QM/2 4-D >> EM 9/19/16 TO PAMALA VANDESTREEK AS REMINDER SHE IS ORDERING TEST KIT PER EM 9/20/16)
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2016-09-26 | AAA |  | 0.1499 |  |  | 4QM RESULTS OK. START ANNUAL MONITOIRNG IN Q4
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-12 | AAA |  |  |  |  | 16 DONE (ON FTP WEBSITE OPERATOR SENT CHAIN OF CUSTODY FOR 12/4/17 NITRATE & NITRITE & 2 4-D IN THE SOCS PENDING SUBMITTAL OF RESULTS - BB
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-12-12 | AAA |  |  |  |  | 16 DONE (ON FTP WEBSITE OPERATOR SENT CHAIN OF CUSTODY FOR 12/4/17 NITRATE & NITRITE & 2 4-D IN THE SOCS PENDING SUBMITTAL OF RESULTS - BB
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-12-04 | AAA | 0.1 | 0.1499 |  |  | 1AM/2 4-D (2AM/2 4-D DUE 4Q 2018 3AM/2 4-D DUE 4Q 2019 ASSUMING NO RESULTS ABOVE THE MCL DURING THAT TIME WHICH WOULD TRIGGER QTRLY TESTING - BB)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-12-04 | AAA | 0.2 |  |  |  | NN (PLACED IN FINAL CHEM HOLDING FOLDER 12-21-17 - BB)
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-12-04 | AAA | 0.2 |  |  |  | NN (PLACED IN FINAL CHEM HOLDING FOLDER 12-21-17 - BB)
3590338 | ELDER SPRINGS MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-07-05 | L1 |  |  |  | 0.2 | RCVD 2/6/19
3590338 | ELDER SPRINGS MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 1.38 | UG/L | 80.4999 | 2018-07-05 | L1 |  |  |  | 0.2 | RCVD 2/6/19
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 33.5 | MG/L | 160.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 246 | MG/L | 500.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.04 | LN(10) |  | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 58.8 | MG/L | 250.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 5.73 | MG/L | 250.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-12-28 | AAA |  | 0.5499
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1038 | TOTAL NITRATE+NITRITE | N | 0 | MG/L | 10.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.0077 | MG/L | 2.4999 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-12-28 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-12-31 | AAA |  | 0.0149
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-12-31 | AAA |  | 0.0249
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-12-31 | AAA |  | 0.2499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-12-31 | AAA |  | 0.0149
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-12-31 | AAA |  | 0.0249
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-12-31 | AAA |  | 0.0449
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-12-31 | AAA |  | 0.0249
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-12-31 | AAA |  | 0.2499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-12-31 | AAA |  | 0.0249
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-12-31 | AAA |  | 0.0449
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-12-31 | AAA |  | 0.2499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-12-31 | AAA |  | 1.4999
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-12-31 | AAA |  | 1.4999
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-12-31 | AAA |  | 0.4499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-12-31 | AAA |  | 9.4999
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-12-31 | AAA |  | 6.4999
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-12-31 | AAA |  | 0.6499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-12-31 | AAA |  | 2.4999
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-12-31 | AAA |  | 0.0749
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-12-31 | AAA |  | 0.6499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-12-31 | AAA |  | 0.2499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-12-31 | AAA |  | 0.9499
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-12-31 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2019-12-31 | AAA |  | 0.1499
3590338 | ELDER SPRINGS MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-12-31 | AAA
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-01-07 | L5 |  |  |  |  | 1/07/15 BROMATE - COUNTRY CLUB WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-01-28 | L5 |  |  |  |  | 1/28/15 BROMATE - COUNTRY CLUB WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-02-10 | L5 |  |  |  |  | 2/15 BROMATE - COUNTRY CLUB WP (IN OC)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | WTP2 |  |  |  |  | COUNTRY CLUB ESTATES WP 2AM/DAL-CC WP 1Q'16
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.095 | MG/L | 10.4999 | 2015-02-11 | WTP2 |  |  |  |  | COUNTRY CLUB ESTATES WP 2AM/DAL-CC WP 1Q'16
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | WTP1 |  |  |  |  | GREENWOOD LAKES WP
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.083 | MG/L | 10.4999 | 2015-02-11 | WTP1 |  |  |  |  | GREENWOOD LAKES WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.81 | UG/L | 60.4999 | 2015-02-11 | L1 |  |  |  | 0.62 | NE 12 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 11.64 | UG/L | 80.4999 | 2015-02-11 | L4 |  |  |  | 1.04 | NE 23 1076 HIGH POINT LOOP (6/15/15 EW HAS 5/15 DBPS & DBF-AVG 3/15 & 6/15 QTR DBF TO SEE IF ANY QTR QUALIFIES FOR R.M.-BB)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.2 | UG/L | 60.4999 | 2015-02-11 | L4 |  |  |  | 1.04 | NE 23 1076 HIGH POINT LOOP (6/15/15 EW HAS 5/15 DBPS & DBF-AVG 3/15 & 6/15 QTR DBF TO SEE IF ANY QTR QUALIFIES FOR R.M.-BB)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 22.41 | UG/L | 80.4999 | 2015-02-11 | L3 |  |  |  | 1.38 | NE 33 580 GREENWAY BLVD.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 32.17 | UG/L | 80.4999 | 2015-02-11 | L1 |  |  |  | 0.62 | NE 12 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.01 | UG/L | 60.4999 | 2015-02-11 | L2 |  |  |  | 0.91 | NE 22 1606 WILLOW OAK LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 29.35 | UG/L | 80.4999 | 2015-02-11 | L2 |  |  |  | 0.91 | NE 22 1606 WILLOW OAK LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.95 | UG/L | 60.4999 | 2015-02-11 | L3 |  |  |  | 1.38 | NE 33 580 GREENWAY BLVD.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | D | 0 | UG/L | 10.4999 | 2015-03-03 | L5 | 1 |  | 1 | 1.91 | 3/15 BROMATE - CC WP (C.R. NOT RQRD BUT GVN) IN OC (REVISED 3/15 BROMATE RAA IN OC - 3/15 BROMATE RAA 4/14-3/15 = -0-)
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-03-13 | WTP2 | 1 | 1.4999 |  |  | 1AM/DAL-CC WP 1Q'15 (2AM/DAL-CC WP 1Q'16) **>>EM 8/4/15 SNT FOR 2AM/DAL-CC WP 1Q'16 (NEW WVR ALREADY SET UP ON THIS) - SNT TO WMS ELISA & SEAN MCFARLAND-BB. (4/26 EW HAS 1/16 DALAPON-CC WP)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-04-07 | L5 |  |  |  |  | 4/15 BROMATE - CC WP (8/4/15 EW HAS 5/15 & 6/15 BROMATE & 6/15 BROMATE RAA-ALL IN OC ALREADY)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 16.18 | UG/L | 80.4999 | 2015-05-13 | L2 |  |  |  | 1.13 | NE 22 1606 WILLOW OAK LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.92 | UG/L | 60.4999 | 2015-05-13 | L3 |  |  |  | 1.63 | NE 33 580 GREENWAY BLVD.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 7.74 | UG/L | 80.4999 | 2015-05-13 | L3 |  |  |  | 1.63 | NE 33 580 GREENWAY BLVD.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 31.24 | UG/L | 80.4999 | 2015-05-13 | L1 |  |  |  | 0.6 | NE 12 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 11.74 | UG/L | 80.4999 | 2015-05-13 | L4 |  |  |  | 1.26 | NE 23 1076 HIGH POINT LOOP (NO LRAA OR OE MCLS CK. AVERAGES ? MAY HV QUALIFIED LAST QTR FOR R.M. QUALIFIES THIS QTR)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.94 | UG/L | 60.4999 | 2015-05-13 | L1 |  |  |  | 0.6 | NE 12 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-05-13 | L5 |  |  |  |  | 5/15 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.34 | UG/L | 60.4999 | 2015-05-13 | L2 |  |  |  | 1.13 | NE 22 1606 WILLOW OAK LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.01 | UG/L | 60.4999 | 2015-05-13 | L4 |  |  |  | 1.26 | NE 23 1076 HIGH POINT LOOP (NO LRAA OR OE MCLS CK. AVERAGES ? MAY HV QUALIFIED LAST QTR FOR R.M. QUALIFIES THIS QTR)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-06-04 | L5 |  |  |  |  | 6/15 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-07-09 | L5 |  |  |  |  | 7/15 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 33.38 | UG/L | 80.4999 | 2015-08-10 | L1 |  |  |  | 1.01 | NE 12 4267 SHADES CREST LN. (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-08-10 | L5 |  |  |  |  | 8/15 BROMATE- CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 10.02 | UG/L | 80.4999 | 2015-08-10 | L3 |  |  |  | 1.46 | NE 33 580 GREENWAY BLVD. (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.49 | UG/L | 60.4999 | 2015-08-10 | L3 |  |  |  | 1.46 | NE 33 580 GREENWAY BLVD. (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.01 | UG/L | 60.4999 | 2015-08-10 | L2 |  |  |  | 1.24 | NE 22 1606 WILLOW OAK LN. (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.82 | UG/L | 60.4999 | 2015-08-10 | L1 |  |  |  | 1.01 | NE 12 4267 SHADES CREST LN. (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.99 | UG/L | 60.4999 | 2015-08-10 | L4 |  |  |  | 1.65 | NE 23 1076 HIGH POINT LOOP (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 27.98 | UG/L | 80.4999 | 2015-08-10 | L2 |  |  |  | 1.24 | NE 22 1606 WILLOW OAK LN. (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 18.96 | UG/L | 80.4999 | 2015-08-10 | L4 |  |  |  | 1.65 | NE 23 1076 HIGH POINT LOOP (QUALIFIES FOR R.M. - ELISA WMS. SCES WANTS R.M. AFTER 12/31/15 IF STILL QUALIFIED>SEE HER 9/10/15 EM) ALL RESULTS LOW
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-09-08 | L5 |  |  |  |  | 9/15 BROMATE- CC WP (9/15 BROMATE RAA IN OC)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-10-13 | L5 |  |  |  |  | 10/15 BROMATE - CC WP (J QUALIFIER: MSD 78 % RECOVERY - SUFFICIENT RECOVERY FOR ACCEPTANCE LCS OK AT 100% RECOVERY RESULT = @ 1.28 U - OK < MRL & MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-11-09 | L5 |  |  |  |  | 11/15 BROMATE - CC WP **12/15 BROMATE RAAS ARE IN OC & 2/24/16 EW HAS 12/15 BROMATE RESULTS FOR PROCESSING. BB
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.71 | UG/L | 60.4999 | 2015-11-09 | L1 |  |  |  | 1.42 | NE 12 4267 SHADES CREST LN. (12/15 LRAA/T=34.025 LRAA/H=21.57) QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 39.31 | UG/L | 80.4999 | 2015-11-09 | L1 |  |  |  | 1.42 | NE 12 4267 SHADES CREST LN. (12/15 LRAA/T=34.025 LRAA/H=21.57) QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.34 | UG/L | 60.4999 | 2015-11-09 | L2 |  |  |  | 1.36 | NE 22 1606 WILLOW OAK LN. (12/15 LRAA/T=27.075 LRAA/H=20.175) QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 34.79 | UG/L | 80.4999 | 2015-11-09 | L2 |  |  |  | 1.36 | NE 22 1606 WILLOW OAK LN. (12/15 LRAA/T=27.075 LRAA/H=20.175) QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.4 | UG/L | 60.4999 | 2015-11-09 | L3 |  |  |  | 1.73 | NE 33 580 GREENWAY BLVD. (12/15 LRAA/T=14.925 LRAA/H=13.94) QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 19.53 | UG/L | 80.4999 | 2015-11-09 | L3 |  |  |  | 1.73 | NE 33 580 GREENWAY BLVD. (12/15 LRAA/T=14.925 LRAA/H=13.94) QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.33 | UG/L | 60.4999 | 2015-11-09 | L4 |  |  |  | 1.64 | NE 23 1076 HIGH POINT LOOP (12/15 LRAA/T=15.48 LRAA/H=14.8825) ELSA KNOWS-QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 19.58 | UG/L | 80.4999 | 2015-11-09 | L4 |  |  |  | 1.64 | NE 23 1076 HIGH POINT LOOP (12/15 LRAA/T=15.48 LRAA/H=14.8825) ELSA KNOWS-QUALIFIES FOR R.M. L1 4267 SHADES CREST HIGHEST T 4Q 2015 & L2 1606 WILLOW OAK HIGHEST H 4Q 2015
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-12-08 | L5 |  |  |  |  | 12/15 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-01-07 | L5 |  |  |  |  | 1/16 BROMATE - CC WP (4/26 EW HAS 3/16 & 2/16 BROMATE)
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2016-01-07 | WTP2 |  | 1.4999 |  |  | 2AM/DAL-CC WP (3AM/DAL-CC WP 1Q'17) IN OC
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-21 | WTP1 |  |  |  |  | SCES NE GWL - GWL WP
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-21 | WTP2 |  |  |  |  | SCES NE CC - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.25 | MG/L | 10.4999 | 2016-01-21 | WTP1 |  |  |  |  | SCES NE GWL - GWL WP
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.28 | MG/L | 10.4999 | 2016-01-21 | WTP2 |  |  |  |  | SCES NE CC - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-02-03 | L5 |  |  |  |  | 2/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-03-14 | L5 |  |  |  |  | 3/16 BROMATE - CC WP (3/16 BROMATE & 3/16 BROMATE RAA IN OC) 3/16 RAA/BROMATE = -0- PER REPORT
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 2.6 | UG/L | 10.4999 | 2016-04-12 | L5 |  |  |  |  | 4/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-05-10 | L5 |  |  |  |  | 5/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-06-07 | L5 | 1 |  | 1 | 1.5 | 6/16 BROMATE - CC WP (6/16 BROMATE & 6/16 BROMATE RAA IN OC) 6/16 RAA/BROMATE = 0.22 PER REPORT
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-07-12 | L5 | 1 |  | 1 | 1.32 | 7/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-08-10 | L5 |  |  |  |  | 8/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-09-12 | L5 |  |  |  | 1.44 | 9/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-10-03 | L5 |  |  |  | 1.62 | 10/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-11-01 | L5 |  |  |  | 1.52 | 11/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.2 | UG/L | 60.4999 | 2016-11-09 | L2 |  |  |  | 1.58 | NE 22 1606 WILLOW OAK LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 27.71 | UG/L | 80.4999 | 2016-11-09 | L2 |  |  |  | 1.58 | NE 22 1606 WILLOW OAK LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 41.04 | UG/L | 80.4999 | 2016-11-09 | L1 |  |  |  | 1.18 | NE 12 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.37 | UG/L | 60.4999 | 2016-11-09 | L1 |  |  |  | 1.18 | NE 12 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-12-05 | L5 | 1 |  | 1 | 1.9 | 12/16 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-01-03 | L5 | 1 |  | 1 | 1.84 | 1/17 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-02 | WTP2 | 1 | 1.4999 |  |  | 3AM/DAL-CC WP 1Q'17 (HYPERLINKED TO BW 3/8/17 IN THE FOR REVIEW FOLDER-BB) STOP AM/DAL. LAST 3 YRS OK.
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-02 | WTP2 | 0.053 |  |  |  | CC WP NN (HYPERLINKED TO BW 3/8/17-BB)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.25 | MG/L | 10.4999 | 2017-02-02 | WTP2 | 0.051 |  |  |  | CC WP NN (HYPERLINKED TO BW 3/8/17-BB)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-02-02 | L5 | 1 |  | 1 | 1.89 | 2/17 BROMATE - CC WP (HYPERLINKED 3/8/17)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-06 | WTP2 | 0.053 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1005 | ARSENIC | N | 0.0001 | MG/L | 0.0104 | 2017-02-06 | WTP2 | 8e-05 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1010 | BARIUM | N | 0.007 | MG/L | 2.4999 | 2017-02-06 | WTP2 | 0.00028 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-06 | WTP2 | 0.00032 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP2 | 0.0005 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-06 | WTP2 | 0.0048 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1025 | FLUORIDE | N | 0.25 | MG/L | 4.0499 | 2017-02-06 | WTP2 | 0.075 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP2 | 0.0061 | 0.0249 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-06 | WTP2 | 0.0063 | 0.0149 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP2 | 0.053 | 0.2499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-06 | WTP2 | 1.2 |  |  |  | COUNTRY CLUB WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023) MUST RESET RADS WVRS BASED ON 2017 DATA - BB
3590473 | SEMINOLE COUNTY NORTHEAST | RAD | 4020 | RADIUM-226 | N | 0.7 | PCI/L | 3.4999 | 2017-02-06 | WTP2 | 0.3 | 1.4999 |  |  | COUNTRY CLUB WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023) MUST RESET RADS WVRS BASED ON 2017 DATA - BB
3590473 | SEMINOLE COUNTY NORTHEAST | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-06 | WTP2 | 0.6 | 1.4999 |  |  | COUNTRY CLUB WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023) MUST RESET RADS WVRS BASED ON 2017 DATA - BB
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-06 | WTP2 | 0.00024 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-06 | WTP2 | 1e-05 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP2 | 0.0011 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-06 | WTP2 | 0.00058 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1052 | SODIUM | N | 7.8 | MG/L | 160.4999 | 2017-02-06 | WTP2 | 0.16 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-06 | WTP2 | 5e-05 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-06 | WTP2 | 0.00013 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-06 | WTP2 | 6e-05 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-06 | WTP2 | 0.061 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1017 | CHLORIDE | N | 13 | MG/L | 250.4999 | 2017-02-06 | WTP2 | 0.78 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-02-06 | WTP2 | 0.0025 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1025 | FLUORIDE | N | 0.25 | MG/L | 2.0499 | 2017-02-06 | WTP2 | 0.075 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-06 | WTP2 | 0.03 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-06 | WTP2 | 0.00024 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP2 | 3e-05 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1055 | SULFATE | N | 5.4 | MG/L | 250.4999 | 2017-02-06 | WTP2 | 0.52 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-06 | WTP2 | 0.002 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-06 | WTP2 | 5 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-06 | WTP2 | 1 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.51 | LN(10) |  | 2017-02-06 | WTP2 |  |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 210 | MG/L | 500.4999 | 2017-02-06 | WTP2 | 10 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-06 | WTP2 | 0.04 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP2 | 0.32 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-06 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP2 | 0.44 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-06 | WTP2 | 0.46 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-06 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-06 | WTP2 | 0.18 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-06 | WTP2 | 0.32 | 0.2499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP2 | 0.0063 | 0.1499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP2 | 0.096 | 0.0249 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP2 | 0.069 | 0.0449 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-06 | WTP2 | 0.11 | 0.1499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP2 | 0.36 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP2 | 0.23 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP2 | 0.24 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-06 | WTP2 | 0.22 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-06 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/COUNTRY CLUB WP (NO DETECTIONS)
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP2 | 0.0069 | 0.0149 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP2 | 0.0071 | 0.0249 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-06 | WTP2 | 0.0068 | 0.1499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP2 | 0.12 | 1.4999 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP2 | 1 | 1.4999 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-06 | WTP2 | 7.6 | 0.4499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP2 | 1.2 | 9.4999 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-06 | WTP2 | 6.5 | 6.4999 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-06 | WTP2 | 0.95 | 0.6499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP2 | 0.57 | 2.4999 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-06 | WTP2 | 0.19 | 0.0749 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-06 | WTP2 | 1.5 | 0.6499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-06 | WTP2 | 0.23 | 0.1499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-06 | WTP2 | 0.86 | 0.2499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-06 | WTP2 | 0.012 | 0.1499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-06 | WTP2 | 0.28 | 0.9499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP2 | 0.16 | 0.1499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP2 | 0.26 | 0.2499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-06 | WTP2 | 0.006 | 0.0449 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP2 | 0.0052 | 0.0249 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP2 | 1.5 | 0.1499 |  |  | 1Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP IF NO DETECT IN 2Q SOCS. LAST 3 YRS SO FAR -0-) 2 QTRS SOCS DUE IN 2017 AT LEAST 60 DAYS APART
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.25 | MG/L | 10.4999 | 2017-02-06 | WTP2 | 0.051 |  |  |  | COUNTRY CLUB WP (NO RESULTS ABOVE THE MCL)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-03-06 | L5 | 1 |  | 1 | 1.61 | 3/17 BROMATE - CC WP (HYPERLINKED 4/4/17 TO BW-BB) 3/17 BROMATE RAA RCVD (HYPERLINKED 4/4/17 - BB)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-04-03 | L5 | 1 |  | 1 | 1.56 | 4/17 BROMATE - CC WP (HYPERLINKED 5/31/17 TO BW-BB)
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-13 | WTP2 | 1.2 | 9.4999 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP2 | 0.054 | 0.2499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-13 | WTP2 | 0.96 | 0.6499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-13 | WTP2 | 0.57 | 2.4999 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-13 | WTP2 | 0.19 | 0.0749 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-13 | WTP2 | 1.5 | 0.6499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-13 | WTP2 | 0.23 | 0.1499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-13 | WTP2 | 0.86 | 0.2499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-13 | WTP2 | 0.013 | 0.1499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-13 | WTP2 | 0.28 | 0.9499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP2 | 0.007 | 0.0149 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP2 | 0.0072 | 0.0249 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-13 | WTP2 | 0.0069 | 0.1499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP2 | 0.12 | 1.4999 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-13 | WTP2 | 1 | 1.4999 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-13 | WTP2 | 7.6 | 0.4499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP2 | 0.16 | 0.1499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP2 | 0.26 | 0.2499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-13 | WTP2 | 0.0061 | 0.0449 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP2 | 0.0053 | 0.0249 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-13 | WTP2 | 1.5 | 0.1499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-13 | WTP2 | 0.32 | 0.2499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP2 | 0.0064 | 0.1499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP2 | 0.097 | 0.0249 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP2 | 0.069 | 0.0449 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-13 | WTP2 | 0.11 | 0.1499 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP2 | 0.006 | 0.0249 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-13 | WTP2 | 0.0062 | 0.0149 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-13 | WTP2 | 6.5 | 6.4999 |  |  | 2Q SOC/COUNTRY CLUB WP (DAL -0- STOP AM/DAL-CC WP. LAST 3 YRS -0-) 2 QTRS SOCS DONE FOR 2017
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-05-01 | L5 | 1 |  | 1 | 1.54 | 5/17 BROMATE - CC WP (RESULTS HYPERLINKED 6/16/17 TO BW - BB)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-06-06 | L5 | 1 |  | 1 |  | 6/17 BROMATE - CC WP (6/17 BROMATE RAA RCVD RAA REPORTED AS -0-)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-07-11 | L5 | 1 |  | 1 | 1.56 | 7/17 BROMATE - CC WP (HYPERLINKED 8/25/17)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-08-07 | L5 | 1 |  | 1 | 1.46 | 8/17 BROMATE - CC WP (HYPERLINKED 9/15/17)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-09-05 | L5 | 1 |  | 1 | 1.64 | 9/17 BROMATE - CC WP (9/17 BROMATE RAA RCVD RAA REPORTED AS -0-) HYPERLINKED 10/19/17
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-10-12 | L5 | 1 |  | 1 | 1.57 | 10/17 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.43 | UG/L | 60.4999 | 2017-11-09 | L2 | 0.5 |  | 2 | 1.2 | 1606 WILLOW OAK LN. (12/17 ANNUAL DISINF BYP REPORT RCVD W/LAB RSLTS) **REMAIN ON ANNUAL TESTING - TEST L1 & L2 SITES DURING 4Q 2018. HYPERLINKED TO BW 12/26/17 - BB.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 33.3 | UG/L | 80.4999 | 2017-11-09 | L2 | 0.14 |  | 2 | 1.2 | 1606 WILLOW OAK LN. (12/17 ANNUAL DISINF BYP REPORT RCVD W/LAB RSLTS) **REMAIN ON ANNUAL TESTING - TEST L1 & L2 SITES DURING 4Q 2018. HYPERLINKED TO BW 12/26/17 - BB.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 35.11 | UG/L | 80.4999 | 2017-11-09 | L1 | 0.14 |  | 1 | 1.29 | 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.38 | UG/L | 60.4999 | 2017-11-09 | L1 | 0.5 |  | 1 | 1.29 | 4267 SHADES CREST LN.
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-11-14 | L5 | 1 |  | 1 | 1.63 | 11/17 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-12-04 | L5 | 1 |  | 1 | 1.36 | 12/17 BROMATE - CC WP (12/17 BROMATE RAA RCVD RAA REPORTED AS -0-) HYPERLINKED 1/22/18
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-01-02 | L5 | 1 |  | 1 | 1.55 | 1/18 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 11 | UG/L | 10.4999 | 2018-02-13 | L5 | 1 |  | 1 | 1.65 | 2/18 BROMATE - CC WP (HYPRLNKD TO BW 4/13/18 - BB) THERE IS NO LRAA BROMATE MCL VIOL 3/18 QTR - ONLY THIS SINGLE SAMPLE EXCEEDANCE - BW/BB
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-13 | WTP2 | 0.053 |  |  |  | CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.21 | MG/L | 10.4999 | 2018-02-13 | WTP2 | 0.051 |  |  |  | CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | D | 0 | UG/L | 10.4999 | 2018-03-07 | L5 | 1 |  | 1 | 2 | 3/18 BROMATE - CC WP (3/18 BROMATE RAA) HYPERLINKED TO BW 4/20/18 - BB
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-04-10 | L5 |  |  |  |  | 4/18 BROMATE - CC WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-05-02 | L5 | 1 |  |  | 1.5
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-06-04 | L5 | 1 |  |  | 1.5 | 6/18 BROMATE (6/18 BROMATE RAA RCVD)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-07-11 | L5 |  |  |  | 1.5 | 07/2018 BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-08-16 | L5 | 1 |  | 1 | 0.9 | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-09-10 | L5 | 1 |  | 1 | 0.9 | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-10-04 | L5 | 1 |  |  | 1.3 | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-11-06 | L5 | 1 |  | 1 | 1.29 | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 25.93 | UG/L | 80.4999 | 2018-11-08 | L2 | 0.56 |  | 2 | 1.07
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.87 | UG/L | 60.4999 | 2018-11-08 | L2 | 0.91 |  | 2 | 1.07
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.56 | UG/L | 60.4999 | 2018-11-08 | L1 | 0.91 |  | 1 | 0.75
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 40.78 | UG/L | 80.4999 | 2018-11-08 | L1 | 0.56 |  | 1 | 0.75
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-12-03 | L5 |  |  |  | 1.51 | 12-2018 BROMATE / SUBCONTRACT LAB E84589
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-01-07 | L5 | 1.6 |  | 1 | 1.3 | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-02-04 | L5 | 1.6 |  | 1 |  | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-19 | WTP2 |  |  |  |  | COUNTRY CLUB ESTATES WP
3590473 | SEMINOLE COUNTY NORTHEAST | INOR | 1040 | NITRATE | N | 0.3 | MG/L | 10.4999 | 2019-02-19 | WTP2 |  |  |  |  | COUNTRY CLUB ESTATES WP
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-03-05 | L5 | 1.6 |  | 1 | 1.3 | 3/19 BROMATE - CC WP (HLKD) 3/19 BROMATE RAA RCVD W/RSLTS
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-04-03 | L5 |  |  |  | 1.5 | 2019-04 BROMATE - CC POE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-05-02 | L5 |  |  |  | 1.5 | 2019-05 BROMATE / CC POE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-06-03 | L5 |  |  |  | 1.4 | 2019-06 BROMATE / CC POE [RAA= 0]
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-07-02 | L5 | 1.6 |  | 1 | 1.4 | 7/19 BROMATE - CC WP (HLKD)
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-08-06 | L5 |  |  |  | 1.5 | 2019 08 - BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-09-17 | L5 |  |  |  | 1.5 | 2019 09 BROMATE - CC POE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-10-01 | L5 | 1.6 |  | 1 | 1.5 | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-11-04 | L5 | 1.6 |  | 1 | 1.5 | BROMATE
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 34.27 | UG/L | 80.4999 | 2019-11-13 | L2 | 0.39 |  | 2 | 1.24 | 1606 WILLOW OAK LN
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.45 | UG/L | 60.4999 | 2019-11-13 | L2 | 0.91 |  | 2 | 1.24 | 1606 WILLOW OAK LN
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2950 | TOTAL THMS | D | 39.74 | UG/L | 80.4999 | 2019-11-13 | L1 | 0.39 |  | 1 | 0.84 | 4267 SHADES CREST LN
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.08 | UG/L | 60.4999 | 2019-11-13 | L1 | 0.91 |  | 1 | 0.84 | 4267 SHADES CREST LN
3590473 | SEMINOLE COUNTY NORTHEAST | DBP | 1011 | BROMATE | D | 1.6 | UG/L | 10.4999 | 2019-12-02 | L5 | 1.6 |  | 1 | 1.5
3590497 | HARMONY HOMES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-04 | AAA |  |  |  |  | 5/11/15 EW HAS TRIENNIALS WHICH INCLUDE 2Q'15 XY & ETH- SOC WVR SUBMITTED 4/28/15 BY DIANE K US WTR-BB
3590497 | HARMONY HOMES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-04 | AAA |  |  |  |  | 5/11/15 EW HAS TRIENNIALS WHICH INCLUDE 2Q'15 XY & ETH- SOC WVR SUBMITTED 4/28/15 BY DIANE K US WTR-BB
3590497 | HARMONY HOMES | SEC | 1017 | CHLORIDE | N | 25 | MG/L | 250.4999 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1022 | COPPER | N | 0.0078 | MG/L | 1.4999 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1025 | FLUORIDE | N | 0.26 | MG/L | 2.0499 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1028 | IRON | N | 0.44 | MG/L | 0.3499 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1032 | MANGANESE | N | 0.0099 | MG/L | 0.0549 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1050 | SILVER | N | 0.0009 | MG/L | 0.1499 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1055 | SULFATE | N | 16 | MG/L | 250.4999 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1095 | ZINC | N | 0.018 | MG/L | 5.4999 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.2 | LN(10) |  | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 300 | MG/L | 500.4999 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 3.2 | UG/L | 5.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-04-06 | AAA |  | 0.5499 |  |  | 3YR VOC+5AM/XY+ETH>EM 10/21/14+3/31/15 (6AM/XY+ETH 2Q'16>9/14/15 8AM/2983 4Q'15>9/14/15) 2983 1 2-DIC 3.2 UG/L OK-ALREADY ON AM
3590497 | HARMONY HOMES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-04-06 | AAA |  |  |  |  | RADS DUE 2021
3590497 | HARMONY HOMES | RAD | 4020 | RADIUM-226 | N | 1.2 | PCI/L | 3.4999 | 2015-04-06 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590497 | HARMONY HOMES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-04-06 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590497 | HARMONY HOMES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1052 | SODIUM | N | 18 | MG/L | 160.4999 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1074 | ANTIMONY | N | 0.0019 | MG/L | 0.0065 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1085 | THALLIUM | N | 0.0009 | MG/L | 0.0025 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1005 | ARSENIC | N | 0.0011 | MG/L | 0.0104 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1010 | BARIUM | N | 0.0048 | MG/L | 2.4999 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1015 | CADMIUM | N | 0.0009 | MG/L | 0.0055 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1020 | CHROMIUM | N | 0.001 | MG/L | 0.1499 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1025 | FLUORIDE | N | 0.26 | MG/L | 4.0499 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-04-06 | AAA |  |  |  |  | 15DON/16:NN T/H 3RD WEEK 8/18 3AM/1 2-DIC 4Q'15 WVR OF SOCS GRANTED 9/14/15 (US WTR) EM 9/14/15 ASKS FOR 2015:8/15 T/H 3AM/1 2-DIC 4Q'15
3590497 | HARMONY HOMES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-04-06 | AAA |  |  |  |  | IRON 0.44 (PER 4/28/15 EM FROM DIANE K US WTR IRON SEQUESTRATION IS ACTIVELY USED. IRON MAY GO UP TO 1.0 MG/L W/O VIOL)
3590497 | HARMONY HOMES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0.78 | UG/L | 60.4999 | 2015-08-20 | L1 |  |  |  | 0.8 | ON R.M.-121 FORD AVE. (NEXT T/H DUE 3RD WEEK OF AUG. 2018>EM 9/16/15>US WTR) <500
3590497 | HARMONY HOMES | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2015-08-20 | L1 |  |  |  | 0.8 | ON R.M.-121 FORD AVE. (NEXT T/H DUE 3RD WEEK OF AUG. 2018>EM 9/16/15>US WTR) <500
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 2.1 | UG/L | 5.4999 | 2015-10-12 | AAA |  | 0.5499 |  |  | 8AM/2983 4Q'15 (6AM/XY+ETH 2Q'16>9/14/15+EM 11/3/15 9AM/2983 4Q'16>EM 11/3/15) 2983 2.1 - CONTINUE ANNUAL MONIT FOR AT LEAST 3 MORE YEARS
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0.22 | UG/L | 749.9999 | 2016-06-08 | AAA |  | 0.5499 |  |  | 6AM/XY+ETH (7AM/XY+ETH 2Q'17> PREV. EM 9/14/15+EM 11/3/15 9AM/2983 4Q'16>EM 11/3/15) 2983 2.1 - CONTINUE ANNUAL MONIT FOR AT LEAST 3 MORE YEARS
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0.94 | UG/L | 10499.9999 | 2016-06-08 | AAA |  | 0.5499 |  |  | 6AM/XY+ETH (7AM/XY+ETH 2Q'17> PREV. EM 9/14/15+EM 11/3/15 9AM/2983 4Q'16>EM 11/3/15) 2983 2.1 - CONTINUE ANNUAL MONIT FOR AT LEAST 3 MORE YEARS
3590497 | HARMONY HOMES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-06-28 | AAA |  |  |  |  | NN (US WTR)
3590497 | HARMONY HOMES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-06-28 | AAA |  |  |  |  | NN (US WTR)
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 2.3 | UG/L | 5.4999 | 2016-08-17 | AAA |  | 0.5499 |  |  | TESTED EARLY EM SENT TO DIANE KIBITLEWSKI 9-19 TO ALSO TEST IN OCT. 9TH ANNUAL MONITORING FOR 1 2-DICHLOROPROPANE (CHEM 2983) DURING THE 4TH QTR OF 2016 (TEST IN OCTOBER 2016).
3590497 | HARMONY HOMES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 2.6 | UG/L | 5.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-12-14 | AAA |  | 0.5499 |  |  | 9AM/2983 4Q'16
3590497 | HARMONY HOMES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-17 | AAA | 0.053 |  |  |  | 2017 NN
3590497 | HARMONY HOMES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-17 | AAA | 0.26 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-17 | AAA | 0.46 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-17 | AAA | 0.44 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-17 | AAA | 0.28 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-17 | AAA | 0.32 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-17 | AAA | 0.28 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-17 | AAA | 0.18 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-17 | AAA | 0.28 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-17 | AAA | 0.36 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-17 | AAA | 0.39 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-17 | AAA | 0.23 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-17 | AAA | 0.26 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-17 | AAA | 0.28 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-17 | AAA | 0.12 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-17 | AAA | 0.2 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-17 | AAA | 0.051 |  |  |  | 2017 NN
3590497 | HARMONY HOMES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-17 | AAA | 0.39 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-17 | AAA | 0.17 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-17 | AAA | 0.22 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-17 | AAA | 0.17 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-17 | AAA | 0.12 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-17 | AAA | 0.24 | 0.5499 |  |  | 7AM/XY+ETH 2Q'17(PREV.EM 9/14/15+EM 11/3/15)10AM/2983 4Q'17(PREV. EM 11/3/15)ALL -0- HERE.8AM/XY 2Q'18 9AM/XY 2Q'19 MIN(CAN STOP AM/ETH-CD HV STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG)
3590497 | HARMONY HOMES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-11-01 | AAA | 0.12 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-11-01 | AAA | 0.17 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-11-01 | AAA | 0.22 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-11-01 | AAA | 0.17 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-11-01 | AAA | 0.39 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.24 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-11-01 | AAA | 0.12 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0.99 | UG/L | 5.4999 | 2017-11-01 | AAA | 0.26 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.23 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-11-01 | AAA | 0.39 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-11-01 | AAA | 0.36 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-11-01 | AAA | 0.18 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-11-01 | AAA | 0.2 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-11-01 | AAA | 0.26 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-11-01 | AAA | 0.46 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-11-01 | AAA | 0.44 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-11-01 | AAA | 0.32 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-11-01 | AAA | 0.28 | 0.5499 |  |  | 10AM/2983 4Q'17 (8AM/XY DUE 2Q'18 9AM/XY DUE 2Q'19 11AM/2983 DUE 4Q'18-2983 DETECTION 2017) **CAN STOP AM/ETH-COULD HAVE STOPPED AM/ETH AFT. 2013 BUT 2014 MONIT. SCHED WAS WRONG.
3590497 | HARMONY HOMES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 2.7 | UG/L | 5.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | INOR | 1040 | NITRATE | N | 0.15 | MG/L | 10.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1005 | ARSENIC | N | 0.0001 | MG/L | 0.0104 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1010 | BARIUM | N | 0.0055 | MG/L | 2.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1025 | FLUORIDE | N | 0.28 | MG/L | 4.0499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1052 | SODIUM | N | 20 | MG/L | 160.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACT LABS E82574 E84589
3590497 | HARMONY HOMES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 300 | MG/L | 500.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1017 | CHLORIDE | N | 30 | MG/L | 250.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1022 | COPPER | N | 0.014 | MG/L | 1.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1025 | FLUORIDE | N | 0.28 | MG/L | 2.0499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1028 | IRON | N | 0.51 | MG/L | 0.3499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1032 | MANGANESE | N | 0.011 | MG/L | 0.0549 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1055 | SULFATE | N | 20 | MG/L | 250.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.32 | LN(10) |  | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-21 | AAA |  |  |  |  | SUBCONTRACTED LAB E82574
3590497 | HARMONY HOMES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-21 | AAA |  | 0.5499 |  |  | SUBCONTRACT LAB E82535
3590497 | HARMONY HOMES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-25 | AAA | 0.28 | 0.5499
3590497 | HARMONY HOMES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-25 | AAA | 0.32 | 0.5499
3590497 | HARMONY HOMES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-25 | AAA | 0.39 | 0.5499
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-25 | AAA | 0.17 | 0.5499
3590497 | HARMONY HOMES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-25 | AAA | 0.22 | 0.5499
3590497 | HARMONY HOMES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-25 | AAA | 0.17 | 0.5499
3590497 | HARMONY HOMES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-25 | AAA | 0.12 | 0.5499
3590497 | HARMONY HOMES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-25 | AAA | 0.24 | 0.5499
3590497 | HARMONY HOMES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-25 | AAA | 0.12 | 0.5499
3590497 | HARMONY HOMES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-25 | AAA | 0.28 | 0.5499
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 2.3 | UG/L | 5.4999 | 2018-05-25 | AAA | 0.26 | 0.5499
3590497 | HARMONY HOMES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-25 | AAA | 0.23 | 0.5499
3590497 | HARMONY HOMES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-25 | AAA | 0.39 | 0.5499
3590497 | HARMONY HOMES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-25 | AAA | 0.36 | 0.5499
3590497 | HARMONY HOMES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-25 | AAA | 0.28 | 0.5499
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-25 | AAA | 0.28 | 0.5499
3590497 | HARMONY HOMES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-25 | AAA | 0.44 | 0.5499
3590497 | HARMONY HOMES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-25 | AAA | 0.46 | 0.5499
3590497 | HARMONY HOMES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-25 | AAA | 0.26 | 0.5499
3590497 | HARMONY HOMES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-25 | AAA | 0.2 | 0.5499
3590497 | HARMONY HOMES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-25 | AAA | 0.18 | 0.5499
3590497 | HARMONY HOMES | DBP | 2950 | TOTAL THMS | D | 50.73 | UG/L | 80.4999 | 2018-08-14 | L1 | 0.39 |  | 1 | 0.3
3590497 | HARMONY HOMES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.51 | UG/L | 60.4999 | 2018-08-14 | L1 | 0.91 |  | 1 | 0.3
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 1.7 | UG/L | 5.4999 | 2018-08-24 | AAA |  | 0.5499 |  |  | ENTERED AS CONTAM ID 2968. REVISED ON 8/15/19 DURING FILE RVIEW_VP
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 1.9 | UG/L | 5.4999 | 2018-10-10 | AAA |  | 0.5499 |  |  | ENTERED AS CONTAM ID 2968. REVISED ON 8/15/19 DURING FILE RVIEW_VP
3590497 | HARMONY HOMES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 320 | MG/L | 500.4999 | 2018-12-19 | AAA
3590497 | HARMONY HOMES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-12-20 | AAA |  | 1.4999
3590497 | HARMONY HOMES | RAD | 4020 | RADIUM-226 | N | 0.5 | PCI/L | 3.4999 | 2018-12-20 | AAA |  | 1.4999
3590497 | HARMONY HOMES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 5.3 | PCI/L | 15.4999 | 2018-12-20 | AAA
3590497 | HARMONY HOMES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-03-21 | AAA |  | 0.5499
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-04-17 | AAA |  | 0.5499
3590497 | HARMONY HOMES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-04-17 | AAA |  | 0.5499
3590497 | HARMONY HOMES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-04-17 | AAA |  | 0.5499
3590497 | HARMONY HOMES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-04-17 | AAA |  | 0.5499
3590497 | HARMONY HOMES | INOR | 1040 | NITRATE | N | 0.23 | MG/L | 10.4999 | 2019-07-24 | AAA |  |  |  |  | NITRITE UJ QUALIFIED. MS/MSD RECOVERIES 78%/79%. SAMPLE ACCEPTED_VP
3590497 | HARMONY HOMES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-07-24 | AAA |  |  |  |  | NITRITE UJ QUALIFIED. MS/MSD RECOVERIES 78%/79%. SAMPLE ACCEPTED_VP
3590497 | HARMONY HOMES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-10-18 | AAA | 0.26 | 0.5499
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 7.9 | UG/L | 10.4999 | 2015-01-06 | L5 |  |  |  |  | 1/06/15 BROMATE - SOUTHEAST WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-01-28 | L5 |  |  |  |  | 1/28/15 BROMATE - SOUTHEAST WP (1/15 MONTHLY BROMATE AVG = 3.95)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-02-10 | L5 |  |  |  |  | 2/15 BROMATE - SOUTHEAST WP (TESTING T/H 3/10 2 SITES AND 3/25 2 SITES DUE TO 3/25/15 EM SENT TO ELISA WILLIAMS)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | WTP2 | 0.053 |  |  |  | INDIAN HILLS WP NN (J4 QUAL: NO3 MS/MSD RECOV 72%/69% NO2 MS/MSD RECOV 61%/62%-RECOVERY SUFFICIENT FOR ACCEPTANCE. LCS PASSED. J4 OK-BB) (** ND.LAKE HAYES WP NN>EM 5/15/15>PER ELISA 5/20/15-WL TEST)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-11 | WTP2 | 0.051 |  |  |  | INDIAN HILLS WP NN (J4 QUAL: NO3 MS/MSD RECOV 72%/69% NO2 MS/MSD RECOV 61%/62%-RECOVERY SUFFICIENT FOR ACCEPTANCE. LCS PASSED. J4 OK-BB) (** ND.LAKE HAYES WP NN>EM 5/15/15>PER ELISA 5/20/15-WL TEST)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | WTP1 | 0.053 |  |  |  | SE REG. WP NN
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0.092 | MG/L | 10.4999 | 2015-02-11 | WTP1 | 0.051 |  |  |  | SE REG. WP NN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-03-03 | L5 | 1 |  | 1 | 2.02 | 3/15 BROMATE - SE WP (C.R. NOT RQRD BUT GVN) IN OC (REVISED 3/15 BROMATE RAA IN OC - 3/15 BROMATE RAA 4/14-3/15 = 0.68)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.46 | UG/L | 60.4999 | 2015-03-10 | L1 |  |  |  | 1.74 | SE 125 5971 BRICK CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 51.44 | UG/L | 80.4999 | 2015-03-10 | L1 |  |  |  | 1.74 | SE 125 5971 BRICK CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44.2 | UG/L | 60.4999 | 2015-03-10 | L3 |  |  |  | 1.44 | SE 39 4909 PETRA CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 51.58 | UG/L | 80.4999 | 2015-03-10 | L3 |  |  |  | 1.44 | SE 39 4909 PETRA CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-03-12 | WTP2 | 1.5 | 0.6499 |  |  | 1AM/2039 1Q'15-IH WP (1AM/DAL-LK. HAYES WP 2Q'15 & 2AM/2039 1Q'16-IH WP>>EM SNT 5/6/15 TO S. MCFARLAND & ELISA WMS SCES ON 2016 SPECIAL RQRMNTS) IN OC (NEW WVR SET UP FOR 1AM/2039 1Q'15-IH WP)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.6 | UG/L | 60.4999 | 2015-03-26 | L2 |  |  |  | 1.22 | SE 127 5701 DOT COM CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 57.46 | UG/L | 80.4999 | 2015-03-26 | L2 |  |  |  | 1.22 | SE 127 5701 DOT COM CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 52.7 | UG/L | 80.4999 | 2015-03-26 | L4 |  |  |  | 1.11 | SE 126 1104 CITRUS OAKS RUN (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.82 | UG/L | 60.4999 | 2015-03-26 | L4 |  |  |  | 1.11 | SE 126 1104 CITRUS OAKS RUN (NO LRAA MCL VIOLS OR OE EXCEEDANCES) SYS. DOES NOT QUALIFY FOR R.M.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-04-07 | L5 |  |  |  |  | (5/15 6/15 BROMATE & 6/15 BROMATE RAA IN OC-8/4/15 EW HAS RSLTS FOR ENTRY) 4/15 BROMATE - SE WP (**8/4/15 EW HAS 6/11/15 T/H FOR ENTRY IN PWS-ALREADY IN OCULUS>NO MCL OR OE EXCDNCS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-04-14 | WTP3 |  | 1.4999 |  |  | WTP3 INACTIVATED. NFA
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-05-13 | L5 |  |  |  |  | 5/15 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0.1 | MG/L | 10.4999 | 2015-05-18 | WTP3 | 0.051 |  |  |  | LAKES HAYES WP (NO3 OK NO2 HAS BOTH J3 & J4 QUALIFIERS. J3 LCS 88% RECOVERY-SUFFICIENT FOR ACCEPTANCE-AT 100% RSLT WD STILL BE ONLY < 0.060. MS/MSD 88%/89% RECOVERY-SUFFICIENT FOR ACCEPTANCE.)IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-18 | WTP3 | 0.053 |  |  |  | LAKES HAYES WP (NO3 OK NO2 HAS BOTH J3 & J4 QUALIFIERS. J3 LCS 88% RECOVERY-SUFFICIENT FOR ACCEPTANCE-AT 100% RSLT WD STILL BE ONLY < 0.060. MS/MSD 88%/89% RECOVERY-SUFFICIENT FOR ACCEPTANCE.)IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-06-03 | L5 |  |  |  |  | 6/15 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.79 | UG/L | 60.4999 | 2015-06-11 | L3 |  |  |  | 1.31 | SE 39 4909 PETRA CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 64.12 | UG/L | 80.4999 | 2015-06-11 | L3 |  |  |  | 1.31 | SE 39 4909 PETRA CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.93 | UG/L | 60.4999 | 2015-06-11 | L1 |  |  |  | 1.93 | SE 125 5971 BRICK CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 63.04 | UG/L | 80.4999 | 2015-06-11 | L1 |  |  |  | 1.93 | SE 125 5971 BRICK CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.5 | UG/L | 60.4999 | 2015-06-11 | L4 |  |  |  | 1.85 | SE 126 1104 CITRUS OAKS RUN (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 56.89 | UG/L | 80.4999 | 2015-06-11 | L4 |  |  |  | 1.85 | SE 126 1104 CITRUS OAKS RUN (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 57.97 | UG/L | 80.4999 | 2015-06-11 | L2 |  |  |  | 2 | SE 127 5701 DOT COM CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.79 | UG/L | 60.4999 | 2015-06-11 | L2 |  |  |  | 2 | SE 127 5701 DOT COM CT. (NO LRAA MCL VIOLS OR OE EXCEEDANCES) IN OC
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-07-03 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-07-03 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-07-07 | L5 |  |  |  |  | 7/15 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-07-17 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-07-17 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-07-31 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-07-31 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-08-05 | L5 |  |  |  |  | 8/15 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-08-14 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-08-14 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-08-28 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-08-28 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-09-03 | L5 |  |  |  |  | 9/15 BROMATE - SE WP (9/15 BROMATE RAA IN OC)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 75.35 | UG/L | 80.4999 | 2015-09-09 | L2 |  |  |  | 1.51 | (SE 127 5701 DOT COM CT.) DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T'S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.14 | UG/L | 60.4999 | 2015-09-09 | L2 |  |  |  | 1.51 | (SE 127 5701 DOT COM CT.) DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T'S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 72.48 | UG/L | 80.4999 | 2015-09-09 | L4 |  |  |  | 1.42 | (SE 126 1104 CITRUS OAKS RUN)DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T?S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.45 | UG/L | 60.4999 | 2015-09-09 | L4 |  |  |  | 1.42 | (SE 126 1104 CITRUS OAKS RUN)DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T?S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 63.34 | UG/L | 80.4999 | 2015-09-09 | L1 |  |  |  | 1.75 | (SE 125 5971 BRICK CT.) DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T?S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.8 | UG/L | 60.4999 | 2015-09-09 | L1 |  |  |  | 1.75 | (SE 125 5971 BRICK CT.) DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T?S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 94.28 | UG/L | 80.4999 | 2015-09-09 | L3 |  |  |  | 1.06 | (SE 39 4909 PETRA CT.) DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T?S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.31 | UG/L | 60.4999 | 2015-09-09 | L3 |  |  |  | 1.06 | (SE 39 4909 PETRA CT.) DOES NOT QUALIFY FOR R.M. NO LRAA MCL VIOLS NO OE EXCEEDANCES (ALL LRAA/T?S IN 50S/60S LRAA/H?S LOW)
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-09-11 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-09-11 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2015-09-25 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-09-25 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-10-09 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-10-09 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-10-12 | L5 |  |  |  |  | 10/15 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-10-23 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-10-23 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 12 | UG/L | 10.4999 | 2015-11-04 | L5 |  |  |  |  | (1/25/16 EW HAS 12/15 DBPS & 12/15 QTR DBF) 11/15 BROMATE - 11/15 BROMATE - SE WP (BROMATE 12 UG/L) **12/15 BROMATE RAAS ARE IN OC & 2/24/16 EW HAS 12/15 BROMATE - BB
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-11-06 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-11-06 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2015-11-20 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-11-20 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-12-02 | L5 |  |  |  |  | 12/15 BROMATE -SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-12-04 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2015-12-04 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.25 | UG/L | 60.4999 | 2015-12-09 | L2 |  |  |  | 2.06 | SE 127 5701 DOT COM CT. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.91 | UG/L | 60.4999 | 2015-12-09 | L4 |  |  |  | 1.52 | SE 126 1104 CITRUS OAKS RUN (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.89 | UG/L | 60.4999 | 2015-12-09 | L3 |  |  |  | 1.72 | SE 39 4909 PETRA CT. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 58.12 | UG/L | 80.4999 | 2015-12-09 | L3 |  |  |  | 1.72 | SE 39 4909 PETRA CT. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 62.46 | UG/L | 80.4999 | 2015-12-09 | L2 |  |  |  | 2.06 | SE 127 5701 DOT COM CT. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 55.85 | UG/L | 80.4999 | 2015-12-09 | L1 |  |  |  | 1.73 | SE 125 5971 BRICK CT. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 69.74 | UG/L | 80.4999 | 2015-12-09 | L4 |  |  |  | 1.52 | SE 126 1104 CITRUS OAKS RUN (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.39 | UG/L | 60.4999 | 2015-12-09 | L1 |  |  |  | 1.73 | SE 125 5971 BRICK CT. (DOES NOT QUALITY FOR REDUCED MONITORING)
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2015-12-18 | WTP1
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.5 | LN(10) |  | 2015-12-18 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2015-12-19 | WTP2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-01-07 | L5 |  |  |  |  | 1/16 BROMATE - SE WP (4/26 EW HAS 3/16 & 2/16 BROMATE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-19 | WTP1 |  |  |  |  | SE REG. WP NN
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-01-19 | WTP2 |  |  |  |  | IH NN
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0.28 | MG/L | 10.4999 | 2016-01-19 | WTP1 |  |  |  |  | SE REG. WP NN
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-19 | WTP2 |  |  |  |  | IH NN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-02-01 | L5 |  |  |  |  | 2/16 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-03-08 | L5 |  |  |  |  | 3/16 BROMATE - SE WP (4/28 EW HAS 3/16 DBPS) 3/16 BROMATE & 3/16 BROMATE RAA IN OC) 3/16 RAA/BROMATE = 1.00 PER REPORT
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2016-03-08 | WTP2 |  | 0.6499 |  |  | 2AM PHTHALATE. 3AM DUE 1ST Q 2017-IH WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.34 | UG/L | 60.4999 | 2016-03-10 | L3 |  |  |  | 1.48 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.1 | UG/L | 60.4999 | 2016-03-10 | L1 |  |  |  | 1.55 | SE 125 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 55.39 | UG/L | 80.4999 | 2016-03-10 | L1 |  |  |  | 1.55 | SE 125 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.64 | UG/L | 60.4999 | 2016-03-10 | L4 |  |  |  | 1.5 | SE 126 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 53.78 | UG/L | 80.4999 | 2016-03-10 | L4 |  |  |  | 1.5 | SE 126 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.09 | UG/L | 60.4999 | 2016-03-10 | L2 |  |  |  | 1.42 | SE 127 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 54.39 | UG/L | 80.4999 | 2016-03-10 | L2 |  |  |  | 1.42 | SE 127 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 55.28 | UG/L | 80.4999 | 2016-03-10 | L3 |  |  |  | 1.48 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-04-06 | L5 |  |  |  |  | 4/16 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-05-03 | L5 |  |  |  |  | 5/16 BROMATE - SE WP **8/18 EW HAS 6/16 DBPS WITH DB REPORT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 4.7 | UG/L | 10.4999 | 2016-06-08 | L5 | 1 |  | 1 | 2.27 | 6/16 BROMATE - SE REG. WP (6/16 BROMATE & 6/16 BROMATE RAA IN OC) 6/16 RAA/BROMATE = 1.39 PER REPORT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 65.97 | UG/L | 80.4999 | 2016-06-16 | L1 |  |  |  | 1.67 | SE 125 5971 BRICK CT. (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.48 | UG/L | 60.4999 | 2016-06-16 | L4 |  |  |  | 1.4 | SE 126 1104 CITRUS OAKS RUN (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.15 | UG/L | 60.4999 | 2016-06-16 | L3 |  |  |  | 1.43 | SE 39 4909 PETRA CT. (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 66.86 | UG/L | 80.4999 | 2016-06-16 | L4 |  |  |  | 1.4 | SE 126 1104 CITRUS OAKS RUN (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 65.39 | UG/L | 80.4999 | 2016-06-16 | L3 |  |  |  | 1.43 | SE 39 4909 PETRA CT. (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.95 | UG/L | 60.4999 | 2016-06-16 | L1 |  |  |  | 1.67 | SE 125 5971 BRICK CT. (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 60.39 | UG/L | 80.4999 | 2016-06-16 | L2 |  |  |  | 1.56 | SE 127 5701 DOT COM CT. (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.51 | UG/L | 60.4999 | 2016-06-16 | L2 |  |  |  | 1.56 | SE 127 5701 DOT COM CT. (PER DB REPORT NO EXCEEDANCES) QM/T+H
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-07-14 | L5 | 1 |  | 1 | 2.35 | 7/16 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-08-03 | L5 |  |  |  |  | 8/16 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-09-07 | L5 |  |  |  | 2.36 | 9/16 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 62.27 | UG/L | 80.4999 | 2016-09-13 | L4 |  |  |  | 1.51 | SE 126 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.34 | UG/L | 60.4999 | 2016-09-13 | L2 |  |  |  | 1.47 | SE 127 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 53.54 | UG/L | 80.4999 | 2016-09-13 | L2 |  |  |  | 1.47 | SE 127 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.64 | UG/L | 60.4999 | 2016-09-13 | L4 |  |  |  | 1.51 | SE 126 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 64.94 | UG/L | 80.4999 | 2016-09-13 | L1 |  |  |  | 1.47 | SE 125 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 68.19 | UG/L | 80.4999 | 2016-09-13 | L3 |  |  |  | 1.34 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.8 | UG/L | 60.4999 | 2016-09-13 | L3 |  |  |  | 1.34 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.61 | UG/L | 60.4999 | 2016-09-13 | L1 |  |  |  | 1.47 | SE 125 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-10-05 | L5 |  |  |  | 1.87 | 10/16 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-11-02 | L5 |  |  |  | 2.06 | 11/16 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-12-07 | L5 | 1 |  | 1 | 2.07 | 12/16 BROMATE - SE WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.62 | UG/L | 60.4999 | 2016-12-15 | L2 | 0.2 |  | 4 | 1.01 | 5701 DOT COM CT. (12/16 DB REPORT RCVD WITH 12/16 DBPS) HYPERLINKED TO BW 1/19/17. NO LRAA MCLS VIOLS NO OE EXCEEDANCES. SYSTEM DOES NOT QUALIFY FOR REDUCED MONITORING.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 53.55 | UG/L | 80.4999 | 2016-12-15 | L4 | 0.14 |  | 3 | 1.17 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 60.56 | UG/L | 80.4999 | 2016-12-15 | L1 | 0.14 |  | 2 | 0.98 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.98 | UG/L | 60.4999 | 2016-12-15 | L3 | 0.2 |  | 1 | 0.97 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 56.81 | UG/L | 80.4999 | 2016-12-15 | L2 | 0.14 |  | 4 | 1.01 | 5701 DOT COM CT. (12/16 DB REPORT RCVD WITH 12/16 DBPS) HYPERLINKED TO BW 1/19/17. NO LRAA MCLS VIOLS NO OE EXCEEDANCES. SYSTEM DOES NOT QUALIFY FOR REDUCED MONITORING.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 48.84 | UG/L | 80.4999 | 2016-12-15 | L3 | 0.14 |  | 1 | 0.97 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.5 | UG/L | 60.4999 | 2016-12-15 | L4 | 0.2 |  | 3 | 1.17 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.09 | UG/L | 60.4999 | 2016-12-15 | L1 | 0.2 |  | 2 | 0.98 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-01-04 | L5 | 1 |  | 1 | 1.83 | 1/17 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-01 | WTP2 | 0.051 |  |  |  | IH WP NN (3/8/17 HYPERLINKED TO BW-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0.25 | MG/L | 10.4999 | 2017-02-01 | WTP1 | 0.051 |  |  |  | SE REG. WP NN (NO2 J4: MS 84%/MSD 85%) HYPERLINKED TO BW 3/8/17-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-01 | WTP1 | 0.053 |  |  |  | SE REG. WP NN (NO2 J4: MS 84%/MSD 85%) HYPERLINKED TO BW 3/8/17-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-02-01 | L5 | 1 |  | 1 | 2.1 | 2/17 BROMATE - SE REG. WP (HYPERLINKED 3/8/17 - BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-01 | WTP2 | 1.5 | 0.6499 |  |  | 3AM/2039 1Q 2017-IH WP (HYPERLINKED TO FOR REVIEW CHEM FOLDER 3/8/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-01 | WTP2 | 0.053 |  |  |  | IH WP NN (3/8/17 HYPERLINKED TO BW-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP1 | 0.12 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP1 | 0.24 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP1 | 0.12 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP1 | 0.17 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-06 | WTP1 | 0.22 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-06 | WTP1 | 0.17 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP1 | 0.39 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP1 | 0.0069 | 0.0149 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP1 | 0.0071 | 0.0249 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-06 | WTP1 | 0.0068 | 0.1499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP1 | 0.12 | 1.4999 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP1 | 1 | 1.4999 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-06 | WTP1 | 7.6 | 0.4499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP1 | 1.2 | 9.4999 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-06 | WTP1 | 6.5 | 6.4999 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-06 | WTP1 | 0.95 | 0.6499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP1 | 0.57 | 2.4999 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-06 | WTP1 | 0.19 | 0.0749 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-06 | WTP1 | 1.5 | 0.6499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-06 | WTP1 | 0.23 | 0.1499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-06 | WTP1 | 0.86 | 0.2499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-06 | WTP1 | 0.012 | 0.1499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-06 | WTP1 | 0.28 | 0.9499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP1 | 0.16 | 0.1499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP1 | 0.26 | 0.2499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-06 | WTP1 | 0.006 | 0.0449 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP1 | 0.0052 | 0.0249 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP1 | 1.5 | 0.1499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-06 | WTP1 | 0.32 | 0.2499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP1 | 0.0063 | 0.1499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP1 | 0.096 | 0.0249 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP1 | 0.069 | 0.0449 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-06 | WTP1 | 0.11 | 0.1499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP1 | 0.0061 | 0.0249 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-06 | WTP1 | 0.0063 | 0.0149 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP1 | 0.053 | 0.2499 |  |  | 1Q SOC/SE REG. WP (HYPERLINKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0.3 | MG/L | 10.4999 | 2017-02-06 | WTP1 | 0.051 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-06 | WTP1 | 0.053 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1005 | ARSENIC | N | 0.0001 | MG/L | 0.0104 | 2017-02-06 | WTP1 | 8e-05 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1010 | BARIUM | N | 0.0072 | MG/L | 2.4999 | 2017-02-06 | WTP1 | 0.00028 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-06 | WTP1 | 0.00032 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP1 | 0.0005 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-06 | WTP1 | 0.0048 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1025 | FLUORIDE | N | 0.55 | MG/L | 4.0499 | 2017-02-06 | WTP1 | 0.075 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-06 | WTP1 | 0.00024 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-06 | WTP1 | 1e-05 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP1 | 0.0011 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-06 | WTP1 | 0.00058 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1052 | SODIUM | N | 15 | MG/L | 160.4999 | 2017-02-06 | WTP1 | 0.16 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-06 | WTP1 | 5e-05 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-06 | WTP1 | 0.00013 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-06 | WTP1 | 6e-05 |  |  |  | SE REG. WP (HYPERLINKED SE REG. WP'S TRIENNIALS 3/10/17-BB) 3/10/17 DID NOT RCV IH WP'S TRIENNIALS W/SE REG. WP'S TRIENNIALS - BB (4/4/17 RCVD IH RAW WELL 2 REACTIVATION CHEMICALS-NOT FOR COMPLIANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-06 | WTP1 | 0.061 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1017 | CHLORIDE | N | 16 | MG/L | 250.4999 | 2017-02-06 | WTP1 | 0.78 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-02-06 | WTP1 | 0.0025 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1025 | FLUORIDE | N | 0.55 | MG/L | 2.0499 | 2017-02-06 | WTP1 | 0.075 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-06 | WTP1 | 0.03 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-06 | WTP1 | 0.00024 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP1 | 3e-05 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1055 | SULFATE | N | 7.7 | MG/L | 250.4999 | 2017-02-06 | WTP1 | 0.52 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-06 | WTP1 | 0.002 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-06 | WTP1 | 5 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-06 | WTP1 | 1 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.18 | LN(10) |  | 2017-02-06 | WTP1 |  |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 210 | MG/L | 500.4999 | 2017-02-06 | WTP1 | 10 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-06 | WTP1 | 0.04 |  |  |  | SE REG. WP (HYPERLINKED 3/10/17-BB) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB.
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP1 | 0.32 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-06 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP1 | 0.44 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-06 | WTP1 | 0.46 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-06 | WTP1 | 0.26 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP1 | 0.2 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-06 | WTP1 | 0.18 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP1 | 0.28 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP1 | 0.36 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP1 | 0.39 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP1 | 0.23 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP1 | 0.26 | 0.5499 |  |  | 3YR VOC/SE REG. WP (HYPERLINIKED 3/10/17-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-03-08 | L5 | 1 |  | 1 | 2.11 | 3/17 BROMATE - SE REG. WP (HYPERLINKED 4/4/17 - BB) 3/17 BROMATE RAA RCVD (HYPERLINKED 4/4/17 - BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 59.36 | UG/L | 80.4999 | 2017-03-09 | L2 | 0.14 |  | 4 | 1.19 | 5701 DOT COM CT. (3/17 DB REPORT RCVD W/RSLTS NO LRAA MCL VIOLS - TTHMS LRAAS IN THE 50-60'S HAA5S LRAAS IN THE 20'S NO OE EXCEEDANCES. BB/BW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.31 | UG/L | 60.4999 | 2017-03-09 | L2 | 0.2 |  | 4 | 1.19 | 5701 DOT COM CT. (3/17 DB REPORT RCVD W/RSLTS NO LRAA MCL VIOLS - TTHMS LRAAS IN THE 50-60'S HAA5S LRAAS IN THE 20'S NO OE EXCEEDANCES. BB/BW)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 48.91 | UG/L | 80.4999 | 2017-03-09 | L4 | 0.14 |  | 3 | 1.41 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 57.28 | UG/L | 80.4999 | 2017-03-09 | L1 | 0.14 |  | 2 | 1.43 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.53 | UG/L | 60.4999 | 2017-03-09 | L1 | 0.2 |  | 2 | 1.43 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 53.14 | UG/L | 80.4999 | 2017-03-09 | L3 | 0.14 |  | 1 | 1.4 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.02 | UG/L | 60.4999 | 2017-03-09 | L3 | 0.2 |  | 1 | 1.4 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.9 | UG/L | 60.4999 | 2017-03-09 | L4 | 0.2 |  | 3 | 1.41 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-05 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-05 | WTP2 | 0.18 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-05 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-05 | WTP2 | 0.36 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-05 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-05 | WTP2 | 0.23 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-05 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-05 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-05 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-05 | WTP2 | 0.24 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-05 | WTP2 | 0.12 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-05 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-05 | WTP2 | 0.22 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-05 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-05 | WTP2 | 0.39 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-05 | WTP2 | 0.0069 | 0.0149 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-05 | WTP2 | 0.0071 | 0.0249 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-05 | WTP2 | 0.0068 | 0.1499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-05 | WTP2 | 0.12 | 1.4999 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-05 | WTP2 | 1 | 1.4999 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-05 | WTP2 | 7.6 | 0.4499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-05 | WTP2 | 1.2 | 9.4999 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-05 | WTP2 | 6.5 | 6.4999 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-05 | WTP2 | 0.96 | 0.6499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-05 | WTP2 | 0.57 | 2.4999 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-05 | WTP2 | 0.19 | 0.0749 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-05 | WTP2 | 1.5 | 0.6499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-05 | WTP2 | 0.23 | 0.1499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-05 | WTP2 | 0.86 | 0.2499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-05 | WTP2 | 0.012 | 0.1499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-05 | WTP2 | 0.28 | 0.9499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-05 | WTP2 | 0.16 | 0.1499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-05 | WTP2 | 0.26 | 0.2499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-05 | WTP2 | 0.11 | 0.1499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-05 | WTP2 | 0.0061 | 0.0249 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-05 | WTP2 | 0.0063 | 0.0149 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-05 | WTP2 | 0.053 | 0.2499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-05 | WTP2 | 0.006 | 0.0449 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-05 | WTP2 | 0.0052 | 0.0249 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-05 | WTP2 | 1.5 | 0.1499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-05 | WTP2 | 0.32 | 0.2499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-05 | WTP2 | 0.063 | 0.1499 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-05 | WTP2 | 0.097 | 0.0249 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-05 | WTP2 | 0.069 | 0.0449 |  |  | 1Q SOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-04-05 | L5 | 1 |  | 1 | 1.8 | 4/17 BROMATE - SE REG. WP (RCVD SMP# REVISION - ALL OK)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-04-05 | WTP2 | 0.051 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-05 | WTP2 | 0.053 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-04-05 | WTP2 | 8e-05 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1010 | BARIUM | N | 0.0097 | MG/L | 2.4999 | 2017-04-05 | WTP2 | 0.00028 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-05 | WTP2 | 0.00032 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-05 | WTP2 | 0.0005 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-05 | WTP2 | 0.0048 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1025 | FLUORIDE | N | 0.59 | MG/L | 4.0499 | 2017-04-05 | WTP2 | 0.075 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-04-05 | WTP2 | 0.00024 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-05 | WTP2 | 1e-05 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-04-05 | WTP2 | 0.0011 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1045 | SELENIUM | N | 0.001 | MG/L | 0.0549 | 2017-04-05 | WTP2 | 0.00058 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1052 | SODIUM | N | 11 | MG/L | 160.4999 | 2017-04-05 | WTP2 | 0.16 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-05 | WTP2 | 5e-05 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-05 | WTP2 | 0.00013 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-05 | WTP2 | 6e-05 |  |  |  | IH WP (4/17 TRIENNIALS PLACED IN FINAL CHEM HOLDING FOLDER PER NEW 4/17 SOP-BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-05 | WTP2 | 0.061 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1017 | CHLORIDE | N | 18 | MG/L | 250.4999 | 2017-04-05 | WTP2 | 0.78 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1022 | COPPER | N | 0.0061 | MG/L | 1.4999 | 2017-04-05 | WTP2 | 0.0025 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1025 | FLUORIDE | N | 0.59 | MG/L | 2.0499 | 2017-04-05 | WTP2 | 0.075 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-05 | WTP2 | 0.03 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1032 | MANGANESE | N | 0.0011 | MG/L | 0.0549 | 2017-04-05 | WTP2 | 0.00024 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-05 | WTP2 | 3e-05 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1055 | SULFATE | N | 6.7 | MG/L | 250.4999 | 2017-04-05 | WTP2 | 0.52 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1095 | ZINC | N | 0.012 | MG/L | 5.4999 | 2017-04-05 | WTP2 | 0.002 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-05 | WTP2 | 5 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-04-05 | WTP2 | 1 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.12 | LN(10) |  | 2017-04-05 | WTP2 |  |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 160 | MG/L | 500.4999 | 2017-04-05 | WTP2 | 10 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | SEC | 2905 | FOAMING AGENTS | N | 0.042 |  | 0.5499 | 2017-04-05 | WTP2 | 0.04 |  |  |  | IH WP (J QUALIFIERS: CHL MS/MSD BOTH 89% RECOV SULF MS/MSD BOTH 87% RECOV SUFFICENT RECOV FOR ACCEPTANCE)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-05 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-05 | WTP2 | 0.32 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-05 | WTP2 | 0.28 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-05 | WTP2 | 0.44 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-05 | WTP2 | 0.46 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-05 | WTP2 | 0.26 | 0.5499 |  |  | 3YR VOC/IH WP (NO DETECTIONS)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP1 | 0.16 | 0.1499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP1 | 0.26 | 0.2499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-13 | WTP1 | 0.006 | 0.0449 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP1 | 0.0052 | 0.0249 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-13 | WTP1 | 1.5 | 0.1499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-13 | WTP1 | 0.32 | 0.2499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP1 | 0.0063 | 0.1499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP1 | 0.097 | 0.0249 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP1 | 0.069 | 0.0449 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-13 | WTP1 | 0.11 | 0.1499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP1 | 0.0061 | 0.0249 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-13 | WTP1 | 0.0063 | 0.0149 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP1 | 0.053 | 0.2499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP1 | 0.0069 | 0.0149 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP1 | 0.0071 | 0.0249 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-13 | WTP1 | 0.0068 | 0.1499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP1 | 0.12 | 1.4999 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-13 | WTP1 | 1 | 1.4999 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-13 | WTP1 | 7.6 | 0.4499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-13 | WTP1 | 1.2 | 9.4999 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-13 | WTP1 | 6.5 | 6.4999 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-13 | WTP1 | 0.96 | 0.6499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-13 | WTP1 | 0.57 | 2.4999 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-13 | WTP1 | 0.19 | 0.0749 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-13 | WTP1 | 1.5 | 0.6499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-13 | WTP1 | 0.23 | 0.1499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-13 | WTP1 | 0.86 | 0.2499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-13 | WTP1 | 0.012 | 0.1499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-13 | WTP1 | 0.28 | 0.9499 |  |  | 2Q SOC/SE REG. WP (NO DETECTIONS) PLACED IN FINAL CHEM HOLDING FOLDER FOR OC INSERTION 6/6/17 - BB FOR BW
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 12 | UG/L | 10.4999 | 2017-05-03 | L5 | 1 |  | 1 | 1.79 | 5/17 BROMATE - SE REG. WP (RESULTS HYPERLINKED 6/16/17 TO BW - BB) RAA SO FAR OK
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-06-07 | L5 | 1 |  | 1 |  | 6/17 BROMATE - SE REG. WP (6/17 BROMATE RAA RCVD BROMATE RAA REPORTED AS 1)
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-06-07 | WTP2 | 0.006 | 0.0449 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-06-07 | WTP2 | 0.0064 | 0.0149 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-06-07 | WTP2 | 0.053 | 0.2499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-06-07 | WTP2 | 0.26 | 0.2499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-06-07 | WTP2 | 0.16 | 0.1499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-06-07 | WTP2 | 0.28 | 0.9499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-06-07 | WTP2 | 0.012 | 0.1499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-06-07 | WTP2 | 0.86 | 0.2499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-06-07 | WTP2 | 0.0062 | 0.0249 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-06-07 | WTP2 | 0.11 | 0.1499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-06-07 | WTP2 | 0.069 | 0.0449 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-06-07 | WTP2 | 0.096 | 0.0249 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-06-07 | WTP2 | 0.0063 | 0.1499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-06-07 | WTP2 | 0.32 | 0.2499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-06-07 | WTP2 | 1.5 | 0.1499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-06-07 | WTP2 | 0.0052 | 0.0249 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-06-07 | WTP2 | 0.0069 | 0.0149 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-06-07 | WTP2 | 0.0071 | 0.0249 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-06-07 | WTP2 | 0.0068 | 0.1499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-06-07 | WTP2 | 0.12 | 1.4999 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-06-07 | WTP2 | 1 | 1.4999 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-06-07 | WTP2 | 7.6 | 0.4499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-06-07 | WTP2 | 1.2 | 9.4999 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-06-07 | WTP2 | 6.5 | 6.4999 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-06-07 | WTP2 | 0.95 | 0.6499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-06-07 | WTP2 | 0.57 | 2.4999 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-06-07 | WTP2 | 0.19 | 0.0749 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-06-07 | WTP2 | 1.5 | 0.6499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-06-07 | WTP2 | 0.23 | 0.1499 |  |  | 2Q SOC/IH WP(TESTED SOCS FOR IH WP TWICE 6/17 QTR-MUST TEST 2 SEP.QTRS OF SOCS MIN.60 DAYS APART-BB)HYPRLNKD 7/21/17 TO BW&ADVISED HIM TO TELL ELSA WMS THAT SOCS FOR IH WP ND TO BE TSTD 9/17 QTR-BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.02 | UG/L | 60.4999 | 2017-06-15 | L2 | 0.5 |  | 4 | 1.71 | 5701 DOT COM CT. (HYPERLINKED) 6/17 LRAAS/T=IN THE 50S ALL 4 SITES LRAAS/H=IN THE 20S ALL 4 SITES (NO OE EXCEEDANCES NO LRAA MCL VIOLS)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.12 | UG/L | 60.4999 | 2017-06-15 | L4 | 0.5 |  | 3 | 1.55 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 55.07 | UG/L | 80.4999 | 2017-06-15 | L1 | 0.14 |  | 2 | 1.5 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.94 | UG/L | 60.4999 | 2017-06-15 | L1 | 0.5 |  | 2 | 1.5 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 58.75 | UG/L | 80.4999 | 2017-06-15 | L3 | 0.14 |  | 1 | 1.3 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.66 | UG/L | 60.4999 | 2017-06-15 | L3 | 0.5 |  | 1 | 1.3 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 54.76 | UG/L | 80.4999 | 2017-06-15 | L2 | 0.14 |  | 4 | 1.71 | 5701 DOT COM CT. (HYPERLINKED) 6/17 LRAAS/T=IN THE 50S ALL 4 SITES LRAAS/H=IN THE 20S ALL 4 SITES (NO OE EXCEEDANCES NO LRAA MCL VIOLS)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 51.63 | UG/L | 80.4999 | 2017-06-15 | L4 | 0.14 |  | 3 | 1.55 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-07-12 | L5 | 1 |  | 1 | 1.98 | 7/17 BROMATE - SE REG. WP (HYPERLINKED 8/25/17)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-08-02 | L5 | 1 |  | 1 | 2.07 | 8/17 BROMATE - SE REG. WP (HYPERLINKED 9/15/17) J4 QUALIFIER: BIASED HIGH MS/MSD 1040/1030% RECOVERY WITH NON-DETECTION LCS OK - THIS MEANS THE RESULT IS ACCEPTABLE. BW/BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-09-06 | L5 | 1 |  | 1 | 1.97 | 9/17 BROMATE - SE REG. WP (9/17 BROMATE RAA RCVD BROMATE RAA REPORTED AS 1) HYPERLINKED 10-19-17 - BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 63.92 | UG/L | 80.4999 | 2017-09-15 | L1 | 0.14 |  | 2 | 1.42 | SE 125 5971 BRICK CT. (J QUAL: CHLOROFORM MS RECOVERY BIASED LOW - 64% RECOVERY TTHMS COULD BE AS HIGH AS 85.02 AT 100% RECOVERY)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.06 | UG/L | 60.4999 | 2017-09-15 | L3 | 0.5 |  | 1 | 1.67 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 76.9 | UG/L | 80.4999 | 2017-09-15 | L3 | 0.14 |  | 1 | 1.67 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.04 | UG/L | 60.4999 | 2017-09-15 | L1 | 0.5 |  | 2 | 1.42 | SE 125 5971 BRICK CT. (J QUAL: CHLOROFORM MS RECOVERY BIASED LOW - 64% RECOVERY TTHMS COULD BE AS HIGH AS 85.02 AT 100% RECOVERY)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 66.4 | UG/L | 80.4999 | 2017-09-15 | L2 | 0.14 |  | 4 | 1.96 | SE 127 5701 DOT COM CT. (9/17 DISINF BYP REPORT SNT W/RSLTS) JOE VONDRICK OF AEL "SIGNED" PAGE 2 OF EACH OF THE 4 REPORTS WITH "TYPEWRITER" CURSIVE SIGNATURE.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.55 | UG/L | 60.4999 | 2017-09-15 | L4 | 0.5 |  | 3 | 1.7 | SE 126 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 67.97 | UG/L | 80.4999 | 2017-09-15 | L4 | 0.14 |  | 3 | 1.7 | SE 126 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.21 | UG/L | 60.4999 | 2017-09-15 | L2 | 0.5 |  | 4 | 1.96 | SE 127 5701 DOT COM CT. (9/17 DISINF BYP REPORT SNT W/RSLTS) JOE VONDRICK OF AEL "SIGNED" PAGE 2 OF EACH OF THE 4 REPORTS WITH "TYPEWRITER" CURSIVE SIGNATURE.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-10-11 | L5 | 1 |  | 1 | 2.06 | 10/17 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-11-01 | L5 | 1 |  | 1 | 2.18 | 11/17 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-12-06 | L5 | 1 |  | 1 | 1.96 | 12/17 BROMATE - SE REG. WP (12/17 BROMATE RAA RCVD BROMATE RAA REPORTED AS 1) HYPERLINKED 1/22/18
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.99 | UG/L | 60.4999 | 2017-12-14 | L2 | 0.5 |  | 3 | 0.34 | 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 60.61 | UG/L | 80.4999 | 2017-12-14 | L4 | 0.14 |  | 4 | 0.95 | 1104 CITRUS OAKS RUN (12/17 DISINF BYP REPORT RCVD W/DBP LAB RESULTS) CONT. QM/DBPS. NO MCL OR OE EXCEEDANCES. HYPERLINIKED TO BW 1/17/18 - BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.24 | UG/L | 60.4999 | 2017-12-14 | L4 | 0.5 |  | 4 | 0.95 | 1104 CITRUS OAKS RUN (12/17 DISINF BYP REPORT RCVD W/DBP LAB RESULTS) CONT. QM/DBPS. NO MCL OR OE EXCEEDANCES. HYPERLINIKED TO BW 1/17/18 - BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 71.11 | UG/L | 80.4999 | 2017-12-14 | L2 | 0.14 |  | 3 | 0.34 | 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.79 | UG/L | 60.4999 | 2017-12-14 | L3 | 0.5 |  | 1 | 0.93 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 57.93 | UG/L | 80.4999 | 2017-12-14 | L1 | 0.14 |  | 2 | 1.27 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.11 | UG/L | 60.4999 | 2017-12-14 | L1 | 0.5 |  | 2 | 1.27 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 61.09 | UG/L | 80.4999 | 2017-12-14 | L3 | 0.14 |  | 1 | 0.93 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 2.5 | UG/L | 10.4999 | 2018-01-09 | L5 | 1 |  | 1 | 1.84 | 1/18 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-07 | WTP2 | 0.053 |  |  |  | NN - IH WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2018-02-07 | WTP2 | 0.051 |  |  |  | NN - IH WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-07 | WTP1 | 0.051 |  |  |  | NN - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-07 | WTP1 | 0.053 |  |  |  | NN - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-02-07 | L5 | 1 |  | 1 | 1.55 | 2/18 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-03-07 | L5 | 1 |  | 1 | 1.73 | 3/18 BROMATE - S. REG. WP (3/18 BROMATE RAA RCVD SEP - RAA HYPERLINKED 4/20/18) LAB RSLTS HYPERLINKED 4/23/18 TO BW - BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.86 | UG/L | 60.4999 | 2018-03-15 | L2 | 0.5 |  | 4 | 1.14 | 5701 DOT COM CT. (3/18 DISINF BYP REPORT RCVD W/RSLTS) 4/19/18 HYPERLINKED TO BW - BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.27 | UG/L | 60.4999 | 2018-03-15 | L1 | 0.5 |  | 2 | 0.51 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 49.69 | UG/L | 80.4999 | 2018-03-15 | L3 | 0.14 |  | 1 | 1.2 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.61 | UG/L | 60.4999 | 2018-03-15 | L3 | 0.5 |  | 1 | 1.2 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.18 | UG/L | 60.4999 | 2018-03-15 | L4 | 0.5 |  | 3 | 1.57 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 43.93 | UG/L | 80.4999 | 2018-03-15 | L4 | 0.14 |  | 3 | 1.57 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 47.49 | UG/L | 80.4999 | 2018-03-15 | L1 | 0.14 |  | 2 | 0.51 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 45.41 | UG/L | 80.4999 | 2018-03-15 | L2 | 0.14 |  | 4 | 1.14 | 5701 DOT COM CT. (3/18 DISINF BYP REPORT RCVD W/RSLTS) 4/19/18 HYPERLINKED TO BW - BB
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 12 | UG/L | 10.4999 | 2018-04-10 | L5 |  |  |  |  | 4/18 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-05-02 | L5 | 1 |  |  | 1.81
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 11 | UG/L | 10.4999 | 2018-06-04 | L5 | 1 |  | 1 | 1.79 | 6/18 BROMATE - SE REG. WP (6/18 RAA/BROMATE SUBMITTED SEPARATELY RAA REPORTED AS 2.13 ON REPORT)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 123.39 | UG/L | 80.4999 | 2018-06-07 | L3 | 0.14 |  | 1 | 1.05 | 4909 PETRA CT. (RCVD OE REPORT FOR THIS SITE FOR 6/18 QTR OE VALUE 89.39)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 77.13 | UG/L | 80.4999 | 2018-06-07 | L2 | 0.14 |  | 4 | 0.57 | 5701 DOT COM CT. (HLKD DBPS 6/18 QTR DISINF BYP REPORT & PETRA SITE 6/18 OE REPORT FOR TTHMS ON 7/16/18 TO RLB - BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 76.73 | UG/L | 80.4999 | 2018-06-07 | L4 | 0.14 |  | 3 | 0.81 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.42 | UG/L | 60.4999 | 2018-06-07 | L2 | 0.91 |  | 4 | 0.57 | 5701 DOT COM CT. (HLKD DBPS 6/18 QTR DISINF BYP REPORT & PETRA SITE 6/18 OE REPORT FOR TTHMS ON 7/16/18 TO RLB - BB)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.84 | UG/L | 60.4999 | 2018-06-07 | L3 | 0.91 |  | 1 | 1.05 | 4909 PETRA CT. (RCVD OE REPORT FOR THIS SITE FOR 6/18 QTR OE VALUE 89.39)
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.89 | UG/L | 60.4999 | 2018-06-07 | L4 | 0.91 |  | 3 | 0.81 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 88.96 | UG/L | 80.4999 | 2018-06-07 | L1 | 0.14 |  | 2 | 1.21 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.69 | UG/L | 60.4999 | 2018-06-07 | L1 | 0.91 |  | 2 | 1.21 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-07-11 | L5 |  |  |  | 1.81 | 07/2018 BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-08-16 | L5 | 1 |  | 1 | 1.82 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-09-10 | L5 | 1 |  | 1 | 1.8 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.94 | UG/L | 60.4999 | 2018-09-13 | L3 | 0.91 |  | 1 | 1.1 | 4909 PETRA CT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.58 | UG/L | 60.4999 | 2018-09-13 | L2 | 0.91 |  | 4 | 0.96 | 5701 DOT COM CT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 36.58 | UG/L | 80.4999 | 2018-09-13 | L4 | 0.39 |  | 3 | 0.83 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.26 | UG/L | 60.4999 | 2018-09-13 | L4 | 0.91 |  | 3 | 0.83 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 32.84 | UG/L | 80.4999 | 2018-09-13 | L1 | 0.39 |  | 2 | 1.19 | 5971 BRICK CT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.71 | UG/L | 60.4999 | 2018-09-13 | L1 | 0.91 |  | 2 | 1.19 | 5971 BRICK CT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 35.11 | UG/L | 80.4999 | 2018-09-13 | L2 | 0.39 |  | 4 | 0.96 | 5701 DOT COM CT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 39.46 | UG/L | 80.4999 | 2018-09-13 | L3 | 0.39 |  | 1 | 1.1 | 4909 PETRA CT
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-10-04 | L5 | 1 |  |  | 1.89 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-11-06 | L5 | 1 |  | 1 | 1.71 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-12-03 | L5 |  |  |  | 1.75 | 12-2018 BROMATE / SUBCONTRACT LAB E84589
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.08 | UG/L | 60.4999 | 2018-12-13 | L1 |  |  | 2 | 1.3 | 2950-SE 125 5971 BRICK CT. / SUBCONTRACT LABS E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.47 | UG/L | 60.4999 | 2018-12-13 | L4 |  |  | 4 | 0.7 | 2950-SE 126 1104 CITRUS OAKS RUN / SUBCONTRACT E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 48.69 | UG/L | 80.4999 | 2018-12-13 | L4 |  |  | 4 | 0.7 | 2950-SE 126 1104 CITRUS OAKS RUN / SUBCONTRACT E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.23 | UG/L | 60.4999 | 2018-12-13 | L3 |  |  | 1 | 0.91 | 2950-SE 39 4909 PETRA CT. / SUBCONTRACT LABS E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 49.24 | UG/L | 80.4999 | 2018-12-13 | L3 |  |  | 1 | 0.91 | 2950-SE 39 4909 PETRA CT. / SUBCONTRACT LABS E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 61.01 | UG/L | 80.4999 | 2018-12-13 | L2 |  |  | 3 | 0.82 | 2950-SE 127 5701 DOT COM CT. / SUBCONTRACT LABS E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.69 | UG/L | 60.4999 | 2018-12-13 | L2 |  |  | 3 | 0.82 | 2950-SE 127 5701 DOT COM CT. / SUBCONTRACT LABS E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 39.85 | UG/L | 80.4999 | 2018-12-13 | L1 |  |  | 2 | 1.3 | 2950-SE 125 5971 BRICK CT. / SUBCONTRACT LABS E82574 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-01-07 | L5 | 1.6 |  | 1 | 1.78 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-02-04 | L5 | 1.6 |  | 1 | 1.91 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0.56 | MG/L | 10.4999 | 2019-02-12 | WTP2 |  |  |  |  | INDIAN HILLS WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-12 | WTP2 |  |  |  |  | INDIAN HILLS WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-12 | WTP1 |  |  |  |  | SOUTHEAST (CONSUMERS) WP
3590571 | SEMINOLE COUNTY SOUTHEAST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-12 | WTP1 |  |  |  |  | SOUTHEAST (CONSUMERS) WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-03-05 | L5 | 1.6 |  | 1 | 1.77 | 3/19 BROMATE - SE REG. WP (HLKD) 3/19 BROMATE RAA RCVD W/RSLTS
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.43 | UG/L | 60.4999 | 2019-03-13 | L1 | 0.91 |  | 2 | 1.39 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 38.13 | UG/L | 80.4999 | 2019-03-13 | L4 | 0.39 |  | 3 | 0.91 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.97 | UG/L | 60.4999 | 2019-03-13 | L3 | 0.91 |  | 1 | 1.19 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 41.2 | UG/L | 80.4999 | 2019-03-13 | L1 | 0.39 |  | 2 | 1.39 | 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.12 | UG/L | 60.4999 | 2019-03-13 | L4 | 0.91 |  | 3 | 0.91 | 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | M | 41.2 | UG/L | 80.4999 | 2019-03-13 | L1
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 20.12 | UG/L | 60.4999 | 2019-03-13 | L4
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | M | 38.13 | UG/L | 80.4999 | 2019-03-13 | L4
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 21.09 | UG/L | 60.4999 | 2019-03-13 | L2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | M | 0 | UG/L | 80.4999 | 2019-03-13 | L2
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 22.97 | UG/L | 60.4999 | 2019-03-13 | L3
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | M | 59.87 | UG/L | 80.4999 | 2019-03-13 | L3
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 17.43 | UG/L | 60.4999 | 2019-03-13 | L1
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 44.35 | UG/L | 80.4999 | 2019-03-13 | L2 | 0.39 |  | 4 | 0.97 | 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.09 | UG/L | 60.4999 | 2019-03-13 | L2 | 0.91 |  | 4 | 0.97 | 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 59.87 | UG/L | 80.4999 | 2019-03-13 | L3 | 0.39 |  | 1 | 1.19 | 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-04-03 | L5 |  |  |  |  | 2019-04 BROMATE - SER POE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-05-02 | L5 |  |  |  | 2.16 | 2019-05 BROMATE / SER POE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-06-03 | L5 |  |  |  | 1.63 | 2019-06 BROMATE / SER POE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.13 | UG/L | 60.4999 | 2019-06-13 | L3 |  |  | 1 | 1.16 | SE 39 4909 PETRA CT. / SUBCONTRACT LABS E84589 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 45.39 | UG/L | 80.4999 | 2019-06-13 | L2 |  |  | 3 | 0.8 | SE 127 5701 DOT COM CT. / SUBCONTRACT LABS E84589 E82535 [HAA5 LRAA = 21.1925 46.4650 FOR THMS]
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.41 | UG/L | 60.4999 | 2019-06-13 | L2 |  |  | 3 | 0.8 | SE 127 5701 DOT COM CT. / SUBCONTRACT LABS E84589 E82535 [HAA5 LRAA = 21.1925 46.4650 FOR THMS]
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 47.05 | UG/L | 80.4999 | 2019-06-13 | L4 |  |  | 4 | 0.99 | SE 126 1104 CITRUS OAKS RUN / SUBCONTRACT LABS E84589 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.77 | UG/L | 60.4999 | 2019-06-13 | L4 |  |  | 4 | 0.99 | SE 126 1104 CITRUS OAKS RUN / SUBCONTRACT LABS E84589 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 50.24 | UG/L | 80.4999 | 2019-06-13 | L1 |  |  | 2 | 1.04 | SE 125 5971 BRICK CT. / SUBCONTRACT LABS E84589 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.18 | UG/L | 60.4999 | 2019-06-13 | L1 |  |  | 2 | 1.04 | SE 125 5971 BRICK CT. / SUBCONTRACT LABS E84589 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 50.02 | UG/L | 80.4999 | 2019-06-13 | L3 |  |  | 1 | 1.16 | SE 39 4909 PETRA CT. / SUBCONTRACT LABS E84589 E82535
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-07-02 | L5 | 1.6 |  | 1 | 1.74 | 7/19 BROMATE - SE REG. WP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-07-06 | L5 |  |  |  | 1.79 | 2019 08 - BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 88.2 | UG/L | 80.4999 | 2019-09-13 | L4 |  |  | 1 |  | EXCEEDANCE 1104 CITRUS OAKS RUN [TTHM LRAA = 55.52]_VP
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 74.88 | UG/L | 80.4999 | 2019-09-13 | L3 |  |  | 4 | 1.15 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.72 | UG/L | 60.4999 | 2019-09-13 | L4 |  |  | 1 | 1.02 | SE 126 1104 CITRUS OAKS RUN
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.27 | UG/L | 60.4999 | 2019-09-13 | L2 |  |  | 2 | 0.81 | SE 127 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 63.58 | UG/L | 80.4999 | 2019-09-13 | L2 |  |  | 2 | 0.81 | SE 127 5701 DOT COM CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.35 | UG/L | 60.4999 | 2019-09-13 | L1 |  |  | 3 | 0.66 | SE 125 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 61.98 | UG/L | 80.4999 | 2019-09-13 | L1 |  |  | 3 | 0.66 | SE 125 5971 BRICK CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.44 | UG/L | 60.4999 | 2019-09-13 | L3 |  |  | 4 | 1.15 | SE 39 4909 PETRA CT.
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-09-17 | L5 |  |  |  | 1.7 | 2019 09 BROMATE - SER POE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-10-01 | L5 | 1.6 |  | 1 | 1.76 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-11-04 | L5 | 1.6 |  | 1 | 1.74 | BROMATE
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 1011 | BROMATE | D | 1.6 | UG/L | 10.4999 | 2019-12-02 | L5 | 1.6 |  | 1 | 1.82
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.44 | UG/L | 60.4999 | 2019-12-12 | L2 | 0.91 |  | 1 | 1.13
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 61.06 | UG/L | 80.4999 | 2019-12-12 | L2 | 0.39 |  | 1 | 1.13
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.23 | UG/L | 60.4999 | 2019-12-12 | L3 | 0.91 |  | 1 | 1.06
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 56.24 | UG/L | 80.4999 | 2019-12-12 | L4 | 0.39 |  | 1 | 0.98
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.43 | UG/L | 60.4999 | 2019-12-12 | L4 | 0.91 |  | 1 | 0.98
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 60.93 | UG/L | 80.4999 | 2019-12-12 | L1 | 0.39 |  | 1 | 1.11
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2950 | TOTAL THMS | D | 63.24 | UG/L | 80.4999 | 2019-12-12 | L3 | 0.39 |  | 1 | 1.06
3590571 | SEMINOLE COUNTY SOUTHEAST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.1 | UG/L | 60.4999 | 2019-12-12 | L1 | 0.91 |  | 1 | 1.11
3590615 | JANSEN S/D | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-17 | AAA |  | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-17 | AAA |  | 0.0449 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-17 | AAA |  | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-17 | AAA |  | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-17 | AAA |  | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-17 | AAA |  | 0.0449 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-17 | AAA |  | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-17 | AAA |  | 0.0149 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-17 | AAA |  | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-02-17 | AAA |  |  |  |  | RADS DUE 2021
3590615 | JANSEN S/D | RAD | 4020 | RADIUM-226 | N | 0.7 | PCI/L | 3.4999 | 2015-02-17 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590615 | JANSEN S/D | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-02-17 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590615 | JANSEN S/D | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-17 | AAA |  | 9.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-17 | AAA |  | 6.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-02-17 | AAA |  | 0.6499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-17 | AAA |  | 2.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1036 | NICKEL | N | 0.0012 | MG/L | 0.1499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1052 | SODIUM | N | 17.7 | MG/L | 160.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1010 | BARIUM | N | 0 | MG/L | 2.4999 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | INOR | 1025 | FLUORIDE | N | 0.282 | MG/L | 4.0499 | 2015-02-17 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:STG2 T/H DUE 8/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590615 | JANSEN S/D | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1017 | CHLORIDE | N | 23.7 | MG/L | 250.4999 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1022 | COPPER | N | 0.0122 | MG/L | 1.4999 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1025 | FLUORIDE | N | 0.282 | MG/L | 2.0499 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1028 | IRON | N | 0.0501 | MG/L | 0.3499 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1055 | SULFATE | N | 5.37 | MG/L | 250.4999 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1095 | ZINC | N | 0.0325 | MG/L | 5.4999 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.14 | LN(10) |  | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 178 | MG/L | 500.4999 | 2015-02-17 | AAA
3590615 | JANSEN S/D | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-02-17 | AAA
3590615 | JANSEN S/D | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-17 | AAA |  | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-17 | AAA |  | 0.0149 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-17 | AAA |  | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-17 | AAA |  | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-17 | AAA |  | 1.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-02-17 | AAA |  | 1.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-17 | AAA |  | 0.4499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-17 | AAA |  | 0.0749 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-02-17 | AAA |  | 0.6499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-17 | AAA |  | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-17 | AAA |  | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-17 | AAA |  | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-17 | AAA |  | 0.9499 |  |  | 3YR SOC
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.7 | UG/L | 60.4999 | 2015-08-12 | L2 |  |  |  | 0.4 | 1924 BEAR VIEW DRIVE (NO LRAA MCLS OR OE EXCEEDANCES) POP. >500
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 11.2 | UG/L | 80.4999 | 2015-08-12 | L2 |  |  |  | 0.4 | 1924 BEAR VIEW DRIVE (NO LRAA MCLS OR OE EXCEEDANCES) POP. >500
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 11.7 | UG/L | 80.4999 | 2015-08-12 | L1 |  |  |  | 0.4 | 6215 COURTNEY COVE (NO LRAA MCLS OR OE EXCEEDANCES)
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.2 | UG/L | 60.4999 | 2015-08-12 | L1 |  |  |  | 0.4 | 6215 COURTNEY COVE (NO LRAA MCLS OR OE EXCEEDANCES)
3590615 | JANSEN S/D | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3590615 | JANSEN S/D | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 59.6 | UG/L | 80.4999 | 2016-08-10 | L2 |  |  |  | 2.2 | 1924 BEAR VIEW DRIVE CONT. ANNUAL MONITORING
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45 | UG/L | 60.4999 | 2016-08-10 | L2 |  |  |  | 2.2 | 1924 BEAR VIEW DRIVE CONT. ANNUAL MONITORING
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 57 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 2.6 | 6215 COURTNEY COVE CONT. ANNUAL MONITORING
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 2.6 | 6215 COURTNEY COVE CONT. ANNUAL MONITORING
3590615 | JANSEN S/D | INOR | 1040 | NITRATE | N | 0.513 | MG/L | 10.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590615 | JANSEN S/D | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 50.3 | UG/L | 60.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.4 | 6215 COURTNEY (HYPERLINKED 9/28/17 TO BW - BB)
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 69.7 | UG/L | 80.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 0.5 | 1924 BEAR VIEW (HYPERLINKED 9/28/17 TO BW - BB)
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 51.8 | UG/L | 60.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 0.5 | 1924 BEAR VIEW (HYPERLINKED 9/28/17 TO BW - BB)
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 60.5 | UG/L | 80.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.4 | 6215 COURTNEY (HYPERLINKED 9/28/17 TO BW - BB)
3590615 | JANSEN S/D | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-02-19 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-02-19 | AAA | 0.05 | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 1.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-02-19 | AAA | 0.1 | 1.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-02-19 | AAA | 0.4 | 0.4499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 9 | 9.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-02-19 | AAA | 6 | 6.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-02-19 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-02-19 | AAA | 2 | 2.4999 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-02-19 | AAA | 0.07 | 0.0749 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-02-19 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-02-19 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-02-19 | AAA | 0.9 | 0.9499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-02-19 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-02-19 | AAA | 0.01 | 0.0449 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-02-19 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.04 | 0.0449 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-02-19 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-02-19 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-02-19 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC
3590615 | JANSEN S/D | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-02-19 | AAA | 0.01 | 0.2499 |  |  | 3YR SOC
3590615 | JANSEN S/D | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-19 | AAA | 0.2 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-19 | AAA | 0.2 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1010 | BARIUM | N | 0.0043 | MG/L | 2.4999 | 2018-02-19 | AAA | 0.002 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-19 | AAA | 0.005 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1025 | FLUORIDE | N | 0.225 | MG/L | 4.0499 | 2018-02-19 | AAA | 0.2 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1030 | LEAD | N | 0.004 | MG/L | 0.0154 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-19 | AAA | 2e-05 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-19 | AAA | 0.002 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1052 | SODIUM | N | 14.3 | MG/L | 160.4999 | 2018-02-19 | AAA | 0.5 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-19 | AAA | 0.0005 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-19 | AAA | 0.001 |  |  |  | UTILS INC. (IRON 0.801 MG/L ON SECONDARIES SCREEN - DOES SYSTEM STILL HAVE IRON SEQUESTRATION TREATMENT? - BB)
3590615 | JANSEN S/D | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-19 | AAA | 0.02 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1017 | CHLORIDE | N | 20.3 | MG/L | 250.4999 | 2018-02-19 | AAA | 0.4 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1022 | COPPER | N | 0.0488 | MG/L | 1.4999 | 2018-02-19 | AAA | 0.001 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-02-19 | AAA | 0.4 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1028 | IRON | N | 0.801 | MG/L | 0.3499 | 2018-02-19 | AAA | 0.01 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-02-19 | AAA | 0.01 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-19 | AAA | 0.0005 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1055 | SULFATE | N | 5.66 | MG/L | 250.4999 | 2018-02-19 | AAA | 1 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1095 | ZINC | N | 0.0395 | MG/L | 5.4999 | 2018-02-19 | AAA | 0.01 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-19 | AAA | 5 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-19 | AAA | 1 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.68 | LN(10) |  | 2018-02-19 | AAA | 0.01 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 188 | MG/L | 500.4999 | 2018-02-19 | AAA | 2.5 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-19 | AAA | 0.2 |  |  |  | IRON .801 HAS IRON RMVL/SEQUESTATION TREATMENT PER SCREEN - IRON MY GO UP TO 1.0 MG -- IRON SEQUESTRATION WAS IN USE DURING THIS TIME_RLB
3590615 | JANSEN S/D | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-19 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-19 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 48.7 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.6 | 6215 COURTNEY COVE
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.3 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.6 | 6215 COURTNEY COVE
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 46.5 | UG/L | 60.4999 | 2018-08-07 | L2 |  |  |  | 2.1 | 1924 BEAR VIEW DRIVE
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 42.6 | UG/L | 80.4999 | 2018-08-07 | L2 |  |  |  | 2.1 | 1924 BEAR VIEW DRIVE
3590615 | JANSEN S/D | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | AAA
3590615 | JANSEN S/D | INOR | 1040 | NITRATE | N | 0.0172 | MG/L | 10.4999 | 2019-02-26 | AAA
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.9 | UG/L | 60.4999 | 2019-08-12 | L2 | 1 |  | 2 | 3.3 | 1924 BEAR VIEW DRIVE
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 37.4 | UG/L | 80.4999 | 2019-08-12 | L2 | 0.5 |  | 2 | 3.3 | 1924 BEAR VIEW DRIVE
3590615 | JANSEN S/D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.3 | UG/L | 60.4999 | 2019-08-12 | L1 | 1 |  | 1 | 3.2 | 6215 COURTNEY COVE
3590615 | JANSEN S/D | DBP | 2950 | TOTAL THMS | D | 51.3 | UG/L | 80.4999 | 2019-08-12 | L1 | 0.5 |  | 1 | 3.2 | 6215 COURTNEY COVE
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.7 | UG/L | 60.4999 | 2015-07-14 | L1 |  |  |  | 1.41 | ON R.M.-LB3 1800 CAMELLIA DR. (T<60 H<45 CONT. R.M. - NEXT T/H DUE FROM SAME SITE @ 2ND WEEK JULY 2018) <500
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 48.13 | UG/L | 80.4999 | 2015-07-14 | L1 |  |  |  | 1.41 | ON R.M.-LB3 1800 CAMELLIA DR. (T<60 H<45 CONT. R.M. - NEXT T/H DUE FROM SAME SITE @ 2ND WEEK JULY 2018) <500
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 23.56 | UG/L | 80.4999 | 2016-07-14 | L1 | 0.14 |  | 1 | 1.79 | LB3 1800 CAMELLIA DR. (STILL QUALIFIES FOR R.M. 2ND WEEK JULY 2018) SYSTEM VOLUNTARILY TESTED ANNUALLY 2016
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.03 | UG/L | 60.4999 | 2016-07-14 | L1 | 0.2 |  | 1 | 1.79 | LB3 1800 CAMELLIA DR. (STILL QUALIFIES FOR R.M. 2ND WEEK JULY 2018) SYSTEM VOLUNTARILY TESTED ANNUALLY 2016
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.95 | UG/L | 60.4999 | 2017-07-13 | L1 | 0.5 |  | 1 | 1 | LB3 1800 CAMELLIA DR. (STILL QUALIFIES FOR R.M. 2ND WEEK JULY 2018) SYSTEM VOLUNTARILY TESTED ANNUALLY 2016 & 2017
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 19.79 | UG/L | 80.4999 | 2017-07-13 | L1 | 0.14 |  | 1 | 1 | LB3 1800 CAMELLIA DR. (STILL QUALIFIES FOR R.M. 2ND WEEK JULY 2018) SYSTEM VOLUNTARILY TESTED ANNUALLY 2016 & 2017
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.83 | UG/L | 60.4999 | 2018-07-12 | L1 | 0.91 |  | 1 | 1.85 | 1800 CAMELLIA DR. (HLKD 8-22-18)
3590685 | LAKE BRANTLEY (CONSEC) | DBP | 2950 | TOTAL THMS | D | 33.53 | UG/L | 80.4999 | 2018-07-12 | L1 | 0.14 |  | 1 | 1.85 | 1800 CAMELLIA DR. (HLKD 8-22-18)
3590698 | LAKE HARNEY WATER ASSOCIATION | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.6 | PCI/L | 15.4999 | 2015-08-14 | AAA |  |  |  |  | DUE 2021
3590698 | LAKE HARNEY WATER ASSOCIATION | RAD | 4020 | RADIUM-226 | N | 0.9 | PCI/L | 3.4999 | 2015-08-14 | AAA |  | 1.4999 |  |  | DUE 2021
3590698 | LAKE HARNEY WATER ASSOCIATION | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-08-14 | AAA |  | 1.4999 |  |  | DUE 2021
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0.201 | MG/L | 10.4999 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1010 | BARIUM | N | 0.0145 | MG/L | 2.4999 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1052 | SODIUM | N | 14.3 | MG/L | 160.4999 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-08-14 | AAA |  |  |  |  | NN ANALYSIS DATES REVISED AS RQRD
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1017 | CHLORIDE | N | 22.6 | MG/L | 250.4999 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1028 | IRON | N | 0.329 | MG/L | 0.3499 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1055 | SULFATE | N | 1.28 | MG/L | 250.4999 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.88 | LN(10) |  | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 236 | MG/L | 500.4999 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-08-14 | AAA |  |  |  |  | CHL SULF ODOR & F. AGENTS ANALYSIS DATES REVISED AS RQRD (PER 11/17/15 EM FROM MELISA US WTR THE OPERATOR CONFIRMED THAT AN IRON REMOVAL/SEQUESTRATION AGENT IS BEING USED AT THE SYSTEM. BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-14 | AAA |  | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-08-14 | AAA |  | 0.0149
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-08-14 | AAA |  | 0.0249
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-08-14 | AAA |  | 0.1499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-08-14 | AAA |  | 1.4999
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-08-14 | AAA |  | 1.4999
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-08-14 | AAA |  | 0.4499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-08-14 | AAA |  | 9.4999
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-08-14 | AAA |  | 6.4999
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-08-14 | AAA |  | 0.6499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-08-14 | AAA |  | 2.4999
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-08-14 | AAA |  | 0.0749
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-08-14 | AAA |  | 0.6499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-08-14 | AAA |  | 0.1499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-08-14 | AAA |  | 0.2499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-08-14 | AAA |  | 0.1499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-08-14 | AAA |  | 0.9499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-08-14 | AAA |  | 0.1499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-08-14 | AAA |  | 0.2499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-08-14 | AAA |  | 0.0449
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-08-14 | AAA |  | 0.0249
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-08-14 | AAA |  | 0.1499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-08-14 | AAA |  | 0.2499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-08-14 | AAA |  | 0.1499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-08-14 | AAA |  | 0.0249
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-08-14 | AAA |  | 0.0449
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-08-14 | AAA |  | 0.1499
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-08-14 | AAA |  | 0.0249
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-08-14 | AAA |  | 0.0149
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-08-14 | AAA |  | 0.2499
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49.21 | UG/L | 60.4999 | 2015-08-21 | L1 |  |  |  | 0.4 | 4342 PREVATT (TTHMS>MCL 2QM/T/H 12/15) EM 9/21/15>US WTR & OWNER FOR QM AT SAME 2 SITES
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 109.33 | UG/L | 80.4999 | 2015-08-21 | L1 |  |  |  | 0.4 | 4342 PREVATT (TTHMS>MCL 2QM/T/H 12/15) EM 9/21/15>US WTR & OWNER FOR QM AT SAME 2 SITES
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 50.09 | UG/L | 60.4999 | 2015-08-21 | L2 |  |  |  | 1.1 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR (TTHMS>MCL 2QM/T/H 12/15) EM 9/21/15>US WTR & OWNER FOR QM AT SAME 2 SITES
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 103.88 | UG/L | 80.4999 | 2015-08-21 | L2 |  |  |  | 1.1 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR (TTHMS>MCL 2QM/T/H 12/15) EM 9/21/15>US WTR & OWNER FOR QM AT SAME 2 SITES
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 59.98 | UG/L | 80.4999 | 2015-11-17 | L2 |  |  |  | 0.5 | 2QM/T+H-4100 LK HARNEY CIR. (WAS 4116 LK HARNEY CIR (NO MCL VIOL) 3/22 EW HAS 3/16 QTR DBPS BY EM
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.81 | UG/L | 60.4999 | 2015-11-17 | L2 |  |  |  | 0.5 | 2QM/T+H-4100 LK HARNEY CIR. (WAS 4116 LK HARNEY CIR (NO MCL VIOL) 3/22 EW HAS 3/16 QTR DBPS BY EM
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 59.25 | UG/L | 80.4999 | 2015-11-17 | L1 |  |  |  | 0.4 | 2QM/T+H-4342 PREVATT(NO MCL VIOL)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.56 | UG/L | 60.4999 | 2015-11-17 | L1 |  |  |  | 0.4 | 2QM/T+H-4342 PREVATT(NO MCL VIOL)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.6 | UG/L | 60.4999 | 2016-02-18 | L2 |  |  |  | 2 | (8/18/16EM TO MELISA FOR 6/16 QTR T/H-SHE SAID THEY SMPL THEIR OWN;STEVEN MAGEE TOOK THE 2/16-8/19EM>OWNER&S.MAGEE) 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR (NO LRAA MCLS OR OE EXCEEDANCES FOR T/H)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 61.5 | UG/L | 80.4999 | 2016-02-18 | L2 |  |  |  | 2 | (8/18/16EM TO MELISA FOR 6/16 QTR T/H-SHE SAID THEY SMPL THEIR OWN;STEVEN MAGEE TOOK THE 2/16-8/19EM>OWNER&S.MAGEE) 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR (NO LRAA MCLS OR OE EXCEEDANCES FOR T/H)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 62.4 | UG/L | 80.4999 | 2016-02-18 | L1 |  |  |  | 1 | 4342 PREVATT (NO LRAA MCLS OR OE EXCEEDANCES FOR T/H)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.08 | UG/L | 60.4999 | 2016-02-18 | L1 |  |  |  | 1 | 4342 PREVATT (NO LRAA MCLS OR OE EXCEEDANCES FOR T/H)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.7 | UG/L | 60.4999 | 2016-05-19 | L1 | 0.5 |  | 1 | 1.2 | 4342 PREVATT RD. (6/16 LRAA/T=60.1325 LRAA/H=24.3875) T=60 H<45 (SYS. TECHNICALLY ON ROUTINE T/H FOR 9/16 QTR)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 9.55 | UG/L | 80.4999 | 2016-05-19 | L1 | 0.5 |  | 1 | 1.2 | 4342 PREVATT RD. (6/16 LRAA/T=60.1325 LRAA/H=24.3875) T=60 H<45 (SYS. TECHNICALLY ON ROUTINE T/H FOR 9/16 QTR)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.7 | UG/L | 60.4999 | 2016-05-19 | L2 | 0.5 |  | 2 | 1.8 | 4100 LK. HARNEY CIR. (6/16 LRAA/T=60.04 LRAA/H=33.3) T=60 H<45 (SYS. TECHNICALLY ON ROUTINE T/H FOR 9/16 QTR) (PER 9/14/16 CALL FROM S. MAGEE 9/16 T/H RSLTS NOT YET SENT TO DEP)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 14.8 | UG/L | 80.4999 | 2016-05-19 | L2 | 0.5 |  | 2 | 1.8 | 4100 LK. HARNEY CIR. (6/16 LRAA/T=60.04 LRAA/H=33.3) T=60 H<45 (SYS. TECHNICALLY ON ROUTINE T/H FOR 9/16 QTR) (PER 9/14/16 CALL FROM S. MAGEE 9/16 T/H RSLTS NOT YET SENT TO DEP)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-08-17 | AAA |  |  |  |  | **8/2/17 MFC ADVISED BIOMETRICS THAT NN HAS NOT BEEN DONE YET FOR 2017 BY EM (BIOMETRICS NEW OPR 8/2/17)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-08-17 | AAA |  |  |  |  | **8/2/17 MFC ADVISED BIOMETRICS THAT NN HAS NOT BEEN DONE YET FOR 2017 BY EM (BIOMETRICS NEW OPR 8/2/17)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 78.4 | UG/L | 80.4999 | 2016-08-21 | L2 | 0.5 |  | 2 | 1.4 | ON ROUTINE T/H (>500) 4100 LAKE HARNEY CIR. (RCVD LATE ON 10/28/16 BY EMAIL FROM STEVEN MAGEE DUE BY 10/10/16)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49.9 | UG/L | 60.4999 | 2016-08-21 | L2 | 0.5 |  | 2 | 1.4 | ON ROUTINE T/H (>500) 4100 LAKE HARNEY CIR. (RCVD LATE ON 10/28/16 BY EMAIL FROM STEVEN MAGEE DUE BY 10/10/16)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 79.5 | UG/L | 80.4999 | 2016-08-21 | L1 | 0.5 |  | 1 | 1 | ON ROUTINE T/H (>500) 4342 PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.38 | UG/L | 60.4999 | 2016-08-21 | L1 | 0.5 |  | 1 | 1 | ON ROUTINE T/H (>500) 4342 PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 58.1 | UG/L | 60.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 1.2 | 4342 PREVATT (PHOTOS OF LAB REPORT RCVD BY BW 11/7/17 FROM OWNER BETTER COPIES RCVD LATER ALL IN OC)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 82.6 | UG/L | 80.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 1 | 4100 LK HARNEY CIR. (11/8/17 PER BW HE WILL CONTACT OWNER/OPR TO TEST QTRLY DUE TO 82.6 TTHMS - BB) THESE RESULTS RCVD 11/7/17 FROM OWNER (LATE) & 11/8/17 FROM S. MAGEE - BB.
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 54.1 | UG/L | 60.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 1 | 4100 LK HARNEY CIR. (11/8/17 PER BW HE WILL CONTACT OWNER/OPR TO TEST QTRLY DUE TO 82.6 TTHMS - BB) THESE RESULTS RCVD 11/7/17 FROM OWNER (LATE) & 11/8/17 FROM S. MAGEE - BB.
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 77.5 | UG/L | 80.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 1.2 | 4342 PREVATT (PHOTOS OF LAB REPORT RCVD BY BW 11/7/17 FROM OWNER BETTER COPIES RCVD LATER ALL IN OC)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-08-25 | AAA | 0.025 |  |  |  | ALL REVISED AS OF 2/2/18 (LAB NUMBERED SMP#S INCORRECTLY AT 1ST BUT SENT REVISED REPORT & C OF C-ALL IN OC - OK NOW 2-2-18 - BW/BB) CARLOS TOLA BIOMETRICS (HYPERLINKED TO BW 1-31-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-08-25 | AAA | 0.025 |  |  |  | ALL REVISED AS OF 2/2/18 (LAB NUMBERED SMP#S INCORRECTLY AT 1ST BUT SENT REVISED REPORT & C OF C-ALL IN OC - OK NOW 2-2-18 - BW/BB) CARLOS TOLA BIOMETRICS (HYPERLINKED TO BW 1-31-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.5 | UG/L | 60.4999 | 2017-11-14 | L1 | 0.5 |  | 2 | 0.4 | 2QM-4342 PREVATT RD. (12/22/17 HYPERLINKED TO BW - BB) CONTINUE QM/DBPS
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2017-11-14 | L2 | 0.5 |  | 1 | 0.5 | 2QM-4100 LAKE HARNEY CIRCLE
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 25.1 | UG/L | 80.4999 | 2017-11-14 | L1 | 0.5 |  | 2 | 0.4 | 2QM-4342 PREVATT RD. (12/22/17 HYPERLINKED TO BW - BB) CONTINUE QM/DBPS
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.01 | UG/L | 60.4999 | 2017-11-14 | L2 | 0.5 |  | 1 | 0.5 | 2QM-4100 LAKE HARNEY CIRCLE
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1028 | IRON | N | 0.33 | MG/L | 0.3499 | 2018-03-08 | AAA | 0.02
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1032 | MANGANESE | N | 0.0048 | MG/L | 0.0549 | 2018-03-08 | AAA | 0.0025
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-03-08 | AAA | 0.0025
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2018-03-08 | AAA | 2.5
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-03-08 | AAA | 0.01
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2018-03-08 | AAA | 5
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-03-08 | AAA | 1
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.7 | LN(10) |  | 2018-03-08 | AAA | 0.1
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 166 | MG/L | 500.4999 | 2018-03-08 | AAA | 5
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-03-08 | AAA | 0.099
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-03-08 | AAA | 0.41 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | AAA | 0.44 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-03-08 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3YR VOC
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-03-08 | AAA | 0.025 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-03-08 | AAA | 0.025 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-03-08 | AAA | 0.001 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1010 | BARIUM | N | 0.014 | MG/L | 2.4999 | 2018-03-08 | AAA | 0.005 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-03-08 | AAA | 0.0005 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-03-08 | AAA | 0.0025 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-03-08 | AAA | 0.005 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1025 | FLUORIDE | N | 0.072 | MG/L | 4.0499 | 2018-03-08 | AAA | 0.034 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-03-08 | AAA | 0.0005 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-03-08 | AAA | 0.0001 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-03-08 | AAA | 0.0025 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-03-08 | AAA | 0.001 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1052 | SODIUM | N | 11.7 | MG/L | 160.4999 | 2018-03-08 | AAA | 0.5 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-03-08 | AAA | 0.001 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-03-08 | AAA | 0.0005 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-03-08 | AAA | 0.0005 |  |  |  | SOCS NOT TESTED WITH THESE 3/8/18 TRIENNIALS - BB (5/4/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-03-08 | AAA | 0.05
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1017 | CHLORIDE | N | 15.1 | MG/L | 250.4999 | 2018-03-08 | AAA | 2.5
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1022 | COPPER | N | 0.0028 | MG/L | 1.4999 | 2018-03-08 | AAA | 0.0025
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1025 | FLUORIDE | N | 0.072 | MG/L | 2.0499 | 2018-03-08 | AAA | 0.034
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29 | UG/L | 60.4999 | 2018-04-24 | L1 |  |  |  | 0.5 | 4342 PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 45.6 | UG/L | 80.4999 | 2018-04-24 | L2 |  |  |  | 0.6 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 49.9 | UG/L | 60.4999 | 2018-04-24 | L2 |  |  |  | 0.6 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 12.9 | UG/L | 80.4999 | 2018-04-24 | L1 |  |  |  | 0.5 | 4342 PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.3 | UG/L | 60.4999 | 2018-06-19 | L1 |  |  |  | 0.5 | 4342 PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 66.4 | UG/L | 80.4999 | 2018-06-19 | L2 |  |  |  | 0.5 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.7 | UG/L | 60.4999 | 2018-06-19 | L2 |  |  |  | 0.5 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 75.3 | UG/L | 80.4999 | 2018-06-19 | L1 |  |  |  | 0.5 | 4342 PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 89.5 | UG/L | 80.4999 | 2018-09-17 | L1 | 0.5 |  | 1 | 1 | 4342 PREVATT (RCVD LATE 10/30/18 HLKD 11/6/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 63.4 | UG/L | 60.4999 | 2018-09-17 | L2 | 0.5 |  | 2 | 1.4 | 4100 LAKE HARNEY CIRCLE (RCVD LATE 10/30/18 HLKD 11/6/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 76.3 | UG/L | 80.4999 | 2018-09-17 | L2 | 0.5 |  | 2 | 1.4 | 4100 LAKE HARNEY CIRCLE (RCVD LATE 10/30/18 HLKD 11/6/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 53.6 | UG/L | 60.4999 | 2018-09-17 | L1 | 0.5 |  | 1 | 1 | 4342 PREVATT (RCVD LATE 10/30/18 HLKD 11/6/18)
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1052 | SODIUM | N | 17.3 | MG/L | 160.4999 | 2018-09-18 | AAA | 0.5 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-09-18 | AAA | 0.001 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-09-18 | AAA | 0.0005 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-09-18 | AAA | 0.001 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-09-18 | AAA | 0.01
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1017 | CHLORIDE | N | 17.2 | MG/L | 250.4999 | 2018-09-18 | AAA | 0.4
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1022 | COPPER | N | 0.0018 | MG/L | 1.4999 | 2018-09-18 | AAA | 0.001
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-09-18 | AAA | 0.2
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1028 | IRON | N | 0.303 | MG/L | 0.3499 | 2018-09-18 | AAA | 0.01
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-09-18 | AAA | 0.01
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-09-18 | AAA | 0.0005
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1055 | SULFATE | N | 1.33 | MG/L | 250.4999 | 2018-09-18 | AAA | 1
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-09-18 | AAA | 0.01
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-09-18 | AAA | 5
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-09-18 | AAA | 1
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.03 | LN(10) |  | 2018-09-18 | AAA | 0.01
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 286 | MG/L | 500.4999 | 2018-09-18 | AAA | 2.5
3590698 | LAKE HARNEY WATER ASSOCIATION | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-09-18 | AAA | 0.2
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-09-18 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | N | 0.59 | UG/L | 5.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-09-18 | AAA | 9 | 9.4999 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-09-18 | AAA | 6 | 6.4999 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-09-18 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-09-18 | AAA | 2 | 2.4999 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-09-18 | AAA | 0.07 | 0.0749 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-09-18 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-09-18 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (1QM DIC 0.59 UG/L) TRIGGERS QM/DIC (HLKD TO RLB 11-27-18 - BB)
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-09-18 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-09-18 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-09-18 | AAA | 0.05 | 0.1499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-09-18 | AAA | 0.5 | 1.4999 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-09-18 | AAA | 0.1 | 1.4999 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-09-18 | AAA | 0.4 | 0.4499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-09-18 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-09-18 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-09-18 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-09-18 | AAA | 0.9 | 0.9499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-09-18 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-09-18 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-09-18 | AAA | 0.01 | 0.0449 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-09-18 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-09-18 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-09-18 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-09-18 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-09-18 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-09-18 | AAA | 0.04 | 0.0449 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-09-18 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-09-18 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-09-18 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-09-18 | AAA | 0.01 | 0.2499 |  |  | 3YR SOC
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-09-18 | AAA | 0.2 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-09-18 | AAA | 0.2 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-09-18 | AAA | 0.001 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1010 | BARIUM | N | 0.0136 | MG/L | 2.4999 | 2018-09-18 | AAA | 0.002 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-09-18 | AAA | 0.001 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1020 | CHROMIUM | N | 0.0016 | MG/L | 0.1499 | 2018-09-18 | AAA | 0.001 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-09-18 | AAA | 0.005 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-09-18 | AAA | 0.2 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-09-18 | AAA | 0.001 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-09-18 | AAA | 2e-05 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-09-18 | AAA | 0.001 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-09-18 | AAA | 0.002 |  |  |  | CHNG "S" TO "N" SMP TYPE ONCE 1038 NN IS RMVD FROM PRIM INORG RSLTS PAGE. IF YOU WANT TO ACCEPT THE PAGE AS IS CHNG SMP TYPE "S" TO "N" & TELL FLOWERS 1038 GOES ON "OTHER CONTAMINANTS" PG IN FUTURE.
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-10-17 | L1 | 0.5 |  | 2 | 0.8 | 4342 PREVATT (HLKD TO RLB)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 22.8 | UG/L | 80.4999 | 2018-10-17 | L2 | 0.5 |  | 1 | 1 | 4100 LK HARNEY CIR (HLKD TO RLB)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.4 | UG/L | 60.4999 | 2018-10-17 | L2 | 0.5 |  | 1 | 1 | 4100 LK HARNEY CIR (HLKD TO RLB)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 3.11 | UG/L | 80.4999 | 2018-10-17 | L1 | 0.5 |  | 2 | 0.8 | 4342 PREVATT (HLKD TO RLB)
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.9 | UG/L | 60.4999 | 2018-12-17 | L1 |  |  |  | 0.5 | 4342 PREVATT RD [RCVD 10/18/19]_VP
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 44.6 | UG/L | 80.4999 | 2018-12-17 | L1 |  |  |  | 0.5 | 4342 PREVATT RD [RCVD 10/18/19]_VP
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.6 | UG/L | 60.4999 | 2018-12-17 | L2 |  |  | 1 | 0.8 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 52.8 | UG/L | 80.4999 | 2018-12-17 | L2 |  |  | 1 | 0.8 | 4100 LK HARNEY CIR(WAS4116 LK HARNEY CIR
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 56 | UG/L | 80.4999 | 2019-03-18 | L1 |  |  |  | 1.2 | 4342 PREVATT: LRAA HAA5=33.55; TTHM=55.98
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44.1 | UG/L | 60.4999 | 2019-03-18 | L2 |  |  |  | 1.1 | 4100 LAKE HARNEY: LRAA HAA5=41.4; TTHM=53.38
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.3 | UG/L | 60.4999 | 2019-03-18 | L1 |  |  |  | 1.2 | 4342 PREVATT: LRAA HAA5=33.55; TTHM=55.98
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 48 | UG/L | 80.4999 | 2019-03-18 | L2 |  |  |  | 1.1 | 4100 LAKE HARNEY: LRAA HAA5=41.4; TTHM=53.38
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-05-28 | AAA |  | 0.5499 |  |  | 1QM (2QM DUE 7-9 2019) 4Q 18 AND 1Q 19 MISSING. RESTART 4 CONSECUTIVE SAMPLING FOR DICHLORMETHANE. OTHER CONTAM. EXTRA SAMPLES.
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 132 | UG/L | 60.4999 | 2019-07-05 | L2 |  |  | 2 | 0.5 | 4100 LK HARNEY CIR(: LRAA- HAA5: 64.5; TTHM: 51.07
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 82.4 | UG/L | 80.4999 | 2019-07-05 | L2 |  |  | 2 | 0.5 | 4100 LK HARNEY CIR(: LRAA- HAA5: 64.5; TTHM: 51.07
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 95.6 | UG/L | 80.4999 | 2019-07-05 | L1 |  |  | 1 | 0.5 | 4342 PREVATT: LRAA HAA5: 46.1; TTHM: 22.90
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 101 | UG/L | 60.4999 | 2019-07-05 | L1 |  |  | 1 | 0.5 | 4342 PREVATT: LRAA HAA5: 46.1; TTHM: 22.90
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-09-27 | AAA | 0.5 | 0.5499 |  |  | 2QM/DIC
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.4 | UG/L | 60.4999 | 2019-10-01 | L1 | 1 |  | 2 | 0.3 | PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.4 | UG/L | 60.4999 | 2019-10-01 | L2 | 1 |  | 1 | 0.5 | LAKE HARNEY CIRCLE
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 21 | UG/L | 80.4999 | 2019-10-01 | L1 | 0.5 |  | 2 | 0.3 | PREVATT
3590698 | LAKE HARNEY WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 20.6 | UG/L | 80.4999 | 2019-10-01 | L2 | 0.5 |  | 1 | 0.5 | LAKE HARNEY CIRCLE
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2985 | 1 1 2-TRICHLOROETHANE | D | 0 | UG/L | 5.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2987 | TETRACHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2984 | TRICHLOROETHYLENE | D | 0 | UG/L | 3.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2983 | 1 2-DICHLOROPROPANE | D | 0 | UG/L | 5.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2982 | CARBON TETRACHLORIDE | D | 0 | UG/L | 3.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2981 | 1 1 1-TRICHLOROETHANE | D | 0 | UG/L | 249.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2980 | 1 2-DICHLOROETHANE | D | 0 | UG/L | 3.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | D | 0 | UG/L | 149.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2977 | 1 1-DICHLOROETHENE | D | 0 | UG/L | 7.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2976 | VINYL CHLORIDE | D | 0 | UG/L | 1.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2969 | P-DICHLOROBENZENE | D | 0 | UG/L | 75.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2968 | 1 2-DICHLOROBENZENE | D | 0 | UG/L | 649.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | D | 0 | UG/L | 5.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | D | 0 | UG/L | 10499.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | D | 0 | UG/L | 74.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | D | 0 | UG/L | 74.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2996 | STYRENE | D | 0 | UG/L | 149.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2992 | ETHYLBENZENE | D | 0 | UG/L | 749.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2991 | TOLUENE | D | 0 | UG/L | 1499.9999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2990 | BENZENE | D | 0 | UG/L | 1.4999 | 2019-11-01 | AAA |  | 0.5499
3590698 | LAKE HARNEY WATER ASSOCIATION | VOC | 2989 | CHLOROBENZENE | D | 0 | UG/L | 149.9999 | 2019-11-01 | AAA |  | 0.5499
3590762 | LITTLE WEKIVA ESTATES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-18 | AAA |  | 0.0449 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.0449 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 3.2 | PCI/L | 15.4999 | 2015-02-18 | AAA |  |  |  |  | RADS DUE 2021
3590762 | LITTLE WEKIVA ESTATES | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-02-18 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590762 | LITTLE WEKIVA ESTATES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-02-18 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590762 | LITTLE WEKIVA ESTATES | INOR | 1052 | SODIUM | N | 11.6 | MG/L | 160.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-18 | AAA |  | 0.0149 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1040 | NITRATE | N | 0.277 | MG/L | 10.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1010 | BARIUM | N | 0.005 | MG/L | 2.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1025 | FLUORIDE | N | 0.209 | MG/L | 4.0499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1036 | NICKEL | N | 0.0011 | MG/L | 0.1499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15:2QM/T+H 12/15 RADS 2021 (SCOTT GOSNELL AREA MGR)
3590762 | LITTLE WEKIVA ESTATES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1017 | CHLORIDE | N | 17.5 | MG/L | 250.4999 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1022 | COPPER | N | 0.0125 | MG/L | 1.4999 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1025 | FLUORIDE | N | 0.209 | MG/L | 2.0499 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1028 | IRON | N | 0.0661 | MG/L | 0.3499 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1055 | SULFATE | N | 7.56 | MG/L | 250.4999 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1095 | ZINC | N | 0.0311 | MG/L | 5.4999 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.83 | LN(10) |  | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 210 | MG/L | 500.4999 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-02-18 | AAA
3590762 | LITTLE WEKIVA ESTATES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590762 | LITTLE WEKIVA ESTATES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.0149 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 1.4999 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 1.4999 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-18 | AAA |  | 0.4499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 9.4999 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-18 | AAA |  | 6.4999 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-02-18 | AAA |  | 0.6499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 2.4999 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-18 | AAA |  | 0.0749 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-02-18 | AAA |  | 0.6499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-18 | AAA |  | 0.9499 |  |  | 3YR SOC (JRC HANDLED SEMINOLE CO. MONITORING IN 2012)
3590762 | LITTLE WEKIVA ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 63.5 | UG/L | 60.4999 | 2015-08-12 | L1 |  |  |  | 2.14 | 789 RICHBEE (START QM/T+H H>60) **GONGRE'S 9/3/15 EM: H 63.5 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590762 | LITTLE WEKIVA ESTATES | DBP | 2950 | TOTAL THMS | D | 35.1 | UG/L | 80.4999 | 2015-08-12 | L1 |  |  |  | 2.14 | 789 RICHBEE (START QM/T+H H>60) **GONGRE'S 9/3/15 EM: H 63.5 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590762 | LITTLE WEKIVA ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.8 | UG/L | 60.4999 | 2015-11-11 | L1 |  |  |  | 2 | 789 RICHBEE (12/15 LRAA/T=14.3 LRAA/H=19.825)
3590762 | LITTLE WEKIVA ESTATES | DBP | 2950 | TOTAL THMS | D | 22.1 | UG/L | 80.4999 | 2015-11-11 | L1 |  |  |  | 2 | 789 RICHBEE (12/15 LRAA/T=14.3 LRAA/H=19.825)
3590762 | LITTLE WEKIVA ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.7 | UG/L | 60.4999 | 2016-02-09 | L1 |  |  |  | 2.5 | (8/18 EW HAS 5/16 T/H FOR ENTRY-ALREADY IN OC) 789 RICHBEE (3/16 LRAA/T=20.85 LRAA/H=24.25) NO MCLS OR OE EXCEEDANCES (LISA AUGUST UTILS INC. SENT RSLTS)
3590762 | LITTLE WEKIVA ESTATES | DBP | 2950 | TOTAL THMS | D | 26.2 | UG/L | 80.4999 | 2016-02-09 | L1 |  |  |  | 2.5 | (8/18 EW HAS 5/16 T/H FOR ENTRY-ALREADY IN OC) 789 RICHBEE (3/16 LRAA/T=20.85 LRAA/H=24.25) NO MCLS OR OE EXCEEDANCES (LISA AUGUST UTILS INC. SENT RSLTS)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-25 | AAA | 0.2 |  |  |  | 4/17/17 PER BW USE RCVD DATE OF 1/23/17-SYS. BEING GVN BENEFIT OF DOUBT AS HAVING SUBMITTED 2016 NN RSLTS WITH THE OTHER UTILS INC SYSTEMS ON 1/23/17. POT.VIOL WAS DELETED 1/25/17.RCVD 4/10/17 & ENTD
3590762 | LITTLE WEKIVA ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-25 | AAA | 0.2 |  |  |  | 4/17/17 PER BW USE RCVD DATE OF 1/23/17-SYS. BEING GVN BENEFIT OF DOUBT AS HAVING SUBMITTED 2016 NN RSLTS WITH THE OTHER UTILS INC SYSTEMS ON 1/23/17. POT.VIOL WAS DELETED 1/25/17.RCVD 4/10/17 & ENTD
3590762 | LITTLE WEKIVA ESTATES | DBP | 2950 | TOTAL THMS | D | 58.2 | UG/L | 80.4999 | 2016-05-10 | L1 |  |  |  | 2.1 | 789 RICHBEE (6/16 LRAA/T=35.4 LRAA/H=30.15) ON ANNUAL 9/16 QTR
3590762 | LITTLE WEKIVA ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.6 | UG/L | 60.4999 | 2016-05-10 | L1 |  |  |  | 2.1 | 789 RICHBEE (6/16 LRAA/T=35.4 LRAA/H=30.15) ON ANNUAL 9/16 QTR
3590762 | LITTLE WEKIVA ESTATES | DBP | 2950 | TOTAL THMS | D | 27.6 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 1.6 | 789 RICHBEE
3590762 | LITTLE WEKIVA ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.3 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 1.6 | 789 RICHBEE
3590762 | LITTLE WEKIVA ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1040 | NITRATE | N | 0.291 | MG/L | 10.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590762 | LITTLE WEKIVA ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.6 | UG/L | 60.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.6 | 789 RICHBEE (HYPERLINKED TO BW 9/29/17 - BB)
3590762 | LITTLE WEKIVA ESTATES | DBP | 2950 | TOTAL THMS | D | 36.1 | UG/L | 80.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.6 | 789 RICHBEE (HYPERLINKED TO BW 9/29/17 - BB)
3590762 | LITTLE WEKIVA ESTATES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-02-14 | AAA | 0.01
3590762 | LITTLE WEKIVA ESTATES | SEC | 1050 | SILVER | N | 0.0159 | MG/L | 0.1499 | 2018-02-14 | AAA | 0.0005
3590762 | LITTLE WEKIVA ESTATES | SEC | 1055 | SULFATE | N | 8.17 | MG/L | 250.4999 | 2018-02-14 | AAA | 1
3590762 | LITTLE WEKIVA ESTATES | SEC | 1095 | ZINC | N | 0.0757 | MG/L | 5.4999 | 2018-02-14 | AAA | 0.01
3590762 | LITTLE WEKIVA ESTATES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-14 | AAA | 5
3590762 | LITTLE WEKIVA ESTATES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-14 | AAA | 1
3590762 | LITTLE WEKIVA ESTATES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.68 | LN(10) |  | 2018-02-14 | AAA | 0.01
3590762 | LITTLE WEKIVA ESTATES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 160 | MG/L | 500.4999 | 2018-02-14 | AAA | 2.5
3590762 | LITTLE WEKIVA ESTATES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-14 | AAA | 0.2
3590762 | LITTLE WEKIVA ESTATES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-14 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-02-14 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-02-14 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-02-14 | AAA | 0.05 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.5 | 1.4999 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-02-14 | AAA | 0.1 | 1.4999 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-02-14 | AAA | 0.4 | 0.4499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-02-14 | AAA | 9 | 9.4999 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-02-14 | AAA | 6 | 6.4999 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-02-14 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-02-14 | AAA | 2 | 2.4999 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-02-14 | AAA | 0.07 | 0.0749 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-02-14 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-02-14 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-02-14 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-02-14 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-02-14 | AAA | 0.9 | 0.9499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-02-14 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-02-14 | AAA | 0.01 | 0.0449 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-02-14 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-02-14 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-02-14 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-02-14 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-02-14 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-02-14 | AAA | 0.04 | 0.0449 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-02-14 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-02-14 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-02-14 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-02-14 | AAA | 0.01 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590762 | LITTLE WEKIVA ESTATES | INOR | 1040 | NITRATE | N | 0.529 | MG/L | 10.4999 | 2018-02-14 | AAA | 0.2 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-14 | AAA | 0.2 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-14 | AAA | 0.001 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1010 | BARIUM | N | 0.005 | MG/L | 2.4999 | 2018-02-14 | AAA | 0.002 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-14 | AAA | 0.001 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1020 | CHROMIUM | N | 0.0011 | MG/L | 0.1499 | 2018-02-14 | AAA | 0.001 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-14 | AAA | 0.005 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1025 | FLUORIDE | N | 0.212 | MG/L | 4.0499 | 2018-02-14 | AAA | 0.2 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-14 | AAA | 0.001 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-14 | AAA | 2e-05 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1036 | NICKEL | N | 0.0019 | MG/L | 0.1499 | 2018-02-14 | AAA | 0.001 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1045 | SELENIUM | N | 0.0099 | MG/L | 0.0549 | 2018-02-14 | AAA | 0.002 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1052 | SODIUM | N | 13.9 | MG/L | 160.4999 | 2018-02-14 | AAA | 0.5 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1074 | ANTIMONY | N | 0.0061 | MG/L | 0.0065 | 2018-02-14 | AAA | 0.001 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-14 | AAA | 0.0005 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-14 | AAA | 0.001 |  |  |  | UTILS INC. (ANTIMONY 0.00610 - NOT ABOVE THE MCL OF 0.006 WHICH IS = 0.00649 WHEN ROUNDED TO THE HIGHEST MCL LIMIT POSSIBLE) 0.00649 IS WHAT USED TO BE CALLED THE CHEMREGS NUMBER FOR THE MCL - BB
3590762 | LITTLE WEKIVA ESTATES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-14 | AAA | 0.02
3590762 | LITTLE WEKIVA ESTATES | SEC | 1017 | CHLORIDE | N | 18.9 | MG/L | 250.4999 | 2018-02-14 | AAA | 0.4
3590762 | LITTLE WEKIVA ESTATES | SEC | 1022 | COPPER | N | 0.0524 | MG/L | 1.4999 | 2018-02-14 | AAA | 0.001
3590762 | LITTLE WEKIVA ESTATES | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-02-14 | AAA | 0.4
3590762 | LITTLE WEKIVA ESTATES | SEC | 1028 | IRON | N | 0.0632 | MG/L | 0.3499 | 2018-02-14 | AAA | 0.01
3590762 | LITTLE WEKIVA ESTATES | DBP | 2950 | TOTAL THMS | D | 35.2 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.5
3590762 | LITTLE WEKIVA ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.4 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.5
3590762 | LITTLE WEKIVA ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | AAA
3590762 | LITTLE WEKIVA ESTATES | INOR | 1040 | NITRATE | N | 0.143 | MG/L | 10.4999 | 2019-02-26 | AAA
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 37.71 | UG/L | 80.4999 | 2015-01-14 | L2 |  |  |  | 1.83 | SW 34 9877 MONTCLAIR CIR. (7/22/15 EW HAS 4/15 DBPS & DB REPORT)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 45.88 | UG/L | 80.4999 | 2015-01-14 | L1 |  |  |  | 0.69 | SW 33 631 W. LAKE BRANTLEY RD.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.1 | UG/L | 60.4999 | 2015-01-14 | L1 |  |  |  | 0.69 | SW 33 631 W. LAKE BRANTLEY RD.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.44 | UG/L | 60.4999 | 2015-01-14 | L4 |  |  |  | 2.13 | SW 25 198 VARSITY CIR.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 34.5 | UG/L | 80.4999 | 2015-01-14 | L3 |  |  |  | 0.68 | SW 20 3035 SUWANEE CT.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.38 | UG/L | 60.4999 | 2015-01-14 | L3 |  |  |  | 0.68 | SW 20 3035 SUWANEE CT.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.09 | UG/L | 60.4999 | 2015-01-14 | L2 |  |  |  | 1.83 | SW 34 9877 MONTCLAIR CIR. (7/22/15 EW HAS 4/15 DBPS & DB REPORT)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 39.54 | UG/L | 80.4999 | 2015-01-14 | L4 |  |  |  | 2.13 | SW 25 198 VARSITY CIR.
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-11 | AAA
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | AAA
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 22.7 | UG/L | 80.4999 | 2015-04-16 | L2 |  |  |  | 1.8 | SW 34 9877 MONTCLAIR CIR. (LRAAS T & H BOTH LOW) IN OC
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.06 | UG/L | 60.4999 | 2015-04-16 | L3 |  |  |  | 1.68 | SW 20 3035 SUWANEE CT. (LRAAS T & H BOTH LOW)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 21.91 | UG/L | 80.4999 | 2015-04-16 | L3 |  |  |  | 1.68 | SW 20 3035 SUWANEE CT. (LRAAS T & H BOTH LOW)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.96 | UG/L | 60.4999 | 2015-04-16 | L4 |  |  |  | 1.88 | SW 25 198 VARSITY CIR. (LRAAS T & H BOTH LOW)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 23.12 | UG/L | 80.4999 | 2015-04-16 | L4 |  |  |  | 1.88 | SW 25 198 VARSITY CIR. (LRAAS T & H BOTH LOW)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 33.98 | UG/L | 80.4999 | 2015-04-16 | L1 |  |  |  | 1.5 | SW 33 631 W. LAKE BRANTLEY RD. (LRAA/T=41.285 NOT < OR = 40 MUST REMAIN ON ROUTINE T/H TESTING CANNOT GO TO REDUCED)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.87 | UG/L | 60.4999 | 2015-04-16 | L1 |  |  |  | 1.5 | SW 33 631 W. LAKE BRANTLEY RD. (LRAA/T=41.285 NOT < OR = 40 MUST REMAIN ON ROUTINE T/H TESTING CANNOT GO TO REDUCED)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.56 | UG/L | 60.4999 | 2015-04-16 | L2 |  |  |  | 1.8 | SW 34 9877 MONTCLAIR CIR. (LRAAS T & H BOTH LOW) IN OC
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 25.34 | UG/L | 80.4999 | 2015-07-14 | L4 |  |  |  | 1.2 | SW 25 198 VARSITY CIR. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.19 | UG/L | 60.4999 | 2015-07-14 | L3 |  |  |  | 1.35 | SW 20 3035 SUWANEE CT. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 24.24 | UG/L | 80.4999 | 2015-07-14 | L3 |  |  |  | 1.35 | SW 20 3035 SUWANEE CT. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.37 | UG/L | 60.4999 | 2015-07-14 | L4 |  |  |  | 1.2 | SW 25 198 VARSITY CIR. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.05 | UG/L | 60.4999 | 2015-07-14 | L1 |  |  |  | 1.06 | SW 33 631 W. LAKE BRANTLEY RD. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 35.67 | UG/L | 80.4999 | 2015-07-14 | L1 |  |  |  | 1.06 | SW 33 631 W. LAKE BRANTLEY RD. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 28.88 | UG/L | 80.4999 | 2015-07-14 | L2 |  |  |  | 1.2 | SW 34 9877 MONTCLAIR CIR. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.93 | UG/L | 60.4999 | 2015-07-14 | L2 |  |  |  | 1.2 | SW 34 9877 MONTCLAIR CIR. (9/15 DBF W/RSLTS DOES NOT QUALIFY FOR R.M. LRAA/T>40 1 SITE) >10 000 4 SITES QTRLY
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 21.12 | UG/L | 80.4999 | 2015-10-15 | L3 |  |  |  | 1.49 | SW 20 3035 SUWANEE CT. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 ? 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.17 | UG/L | 60.4999 | 2015-10-15 | L3 |  |  |  | 1.49 | SW 20 3035 SUWANEE CT. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 ? 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 22.96 | UG/L | 80.4999 | 2015-10-15 | L2 |  |  |  | 1.45 | (4/26/16 REQSTD Q WVR TO END 12/31/15 START A WVR L1+L4 1Q 2016 EFFEC. 1/1/16 OF KS DW VH) SW 34 9877 MONTCLAIR CIR. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 ? 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.09 | UG/L | 60.4999 | 2015-10-15 | L2 |  |  |  | 1.45 | (4/26/16 REQSTD Q WVR TO END 12/31/15 START A WVR L1+L4 1Q 2016 EFFEC. 1/1/16 OF KS DW VH) SW 34 9877 MONTCLAIR CIR. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 ? 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 22.18 | UG/L | 80.4999 | 2015-10-15 | L4 |  |  |  | 1.13 | SW 25 198 VARSITY CIR. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 ? 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.44 | UG/L | 60.4999 | 2015-10-15 | L4 |  |  |  | 1.13 | SW 25 198 VARSITY CIR. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 ? 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 32.7 | UG/L | 80.4999 | 2015-10-15 | L1 |  |  |  | 1.07 | SW 33 631 W. LAKE BRANTLEY RD. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 - 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.89 | UG/L | 60.4999 | 2015-10-15 | L1 |  |  |  | 1.07 | SW 33 631 W. LAKE BRANTLEY RD. (SYS. MAY QUALIFY FOR R.M>CHECK LRAAS 1/15 - 12/15 & NOTIFY E. WMS & S. MCFARLAND)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 23.85 | UG/L | 80.4999 | 2016-01-14 | L4 |  |  |  | 1.36 | SW 25 198 VARSITY CIR. (1/1/16 QUAL. FOR R.M. AT 2 SITES L1 & L4 BRANTLEY & VARSITY BOTH DURING 1Q 2016) NXT T/H DUE 1Q 2017 AT SAME 2 SITES. EM 4/26/16>E.WMS>ANN. DBF
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.95 | UG/L | 60.4999 | 2016-01-14 | L4 |  |  |  | 1.36 | SW 25 198 VARSITY CIR. (1/1/16 QUAL. FOR R.M. AT 2 SITES L1 & L4 BRANTLEY & VARSITY BOTH DURING 1Q 2016) NXT T/H DUE 1Q 2017 AT SAME 2 SITES. EM 4/26/16>E.WMS>ANN. DBF
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 31.13 | UG/L | 80.4999 | 2016-01-14 | L1 |  |  |  | 1.23 | SW 33 631 W. LAKE BRANTLEY RD. (1/1/16 QUAL. FOR R.M. AT 2 SITES L1 & L4 BRANTLEY & VARSITY BOTH DURING 1Q 2016) NXT T/H DUE 1Q 2017 AT SAME 2 SITES. EM 4/26/16>E.WMS>ANN. DBF
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.6 | UG/L | 60.4999 | 2016-01-14 | L1 |  |  |  | 1.23 | SW 33 631 W. LAKE BRANTLEY RD. (1/1/16 QUAL. FOR R.M. AT 2 SITES L1 & L4 BRANTLEY & VARSITY BOTH DURING 1Q 2016) NXT T/H DUE 1Q 2017 AT SAME 2 SITES. EM 4/26/16>E.WMS>ANN. DBF
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-01-19 | AAA
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-19 | AAA
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 32.36 | UG/L | 80.4999 | 2017-01-11 | L1 | 0.14 |  | 2 | 0.38 | 631 W. LAKE BRANTLEY RD. (3/17 DB REPORT RCVD L1 SITE: 32.36 T 11.47 H)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.47 | UG/L | 60.4999 | 2017-01-11 | L1 | 0.2 |  | 2 | 0.38 | 631 W. LAKE BRANTLEY RD. (3/17 DB REPORT RCVD L1 SITE: 32.36 T 11.47 H)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 30.23 | UG/L | 80.4999 | 2017-01-11 | L4 | 0.14 |  | 1 | 1.32 | 198 VARSITY CIR. (3/17 DB REPORT RCVD L4 SITE: 30.23 T 9.50 H)
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.5 | UG/L | 60.4999 | 2017-01-11 | L4 | 0.2 |  | 1 | 1.32 | 198 VARSITY CIR. (3/17 DB REPORT RCVD L4 SITE: 30.23 T 9.50 H)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1025 | FLUORIDE | N | 0.65 | MG/L | 2.0499 | 2017-02-06 | AAA | 0.075 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-06 | AAA | 0.03 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-06 | AAA | 0.00024 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-06 | AAA | 3e-05 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-06 | AAA | 0.36 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-06 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-06 | AAA | 0.23 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | AAA | 0.24 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-06 | AAA | 0.22 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-06 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1055 | SULFATE | N | 4.2 | MG/L | 250.4999 | 2017-02-06 | AAA | 0.52 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-06 | AAA | 0.002 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-06 | AAA | 5 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-06 | AAA | 1 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.18 | LN(10) |  | 2017-02-06 | AAA |  |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 140 | MG/L | 500.4999 | 2017-02-06 | AAA | 10 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-06 | AAA | 0.04 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | AAA | 0.32 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-06 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | AAA | 0.44 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-06 | AAA | 0.46 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-06 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-06 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-06 | AAA | 0.18 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-06 | AAA | 0.0069 | 0.0149 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | AAA | 0.0071 | 0.0249 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-06 | AAA | 0.0068 | 0.1499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | AAA | 0.12 | 1.4999 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-06 | AAA | 1 | 1.4999 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-06 | AAA | 7.6 | 0.4499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-06 | AAA | 1.2 | 9.4999 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-06 | AAA | 6.5 | 6.4999 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-06 | AAA | 0.95 | 0.6499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-06 | AAA | 0.57 | 2.4999 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-06 | AAA | 0.19 | 0.0749 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-06 | AAA | 1.5 | 0.6499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-06 | AAA | 0.23 | 0.1499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-06 | AAA | 0.86 | 0.2499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-06 | AAA | 0.012 | 0.1499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-06 | AAA | 0.28 | 0.9499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-06 | AAA | 0.16 | 0.1499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-06 | AAA | 0.26 | 0.2499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-06 | AAA | 0.006 | 0.0449 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-06 | AAA | 0.0052 | 0.0249 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-06 | AAA | 1.5 | 0.1499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-06 | AAA | 0.32 | 0.2499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | AAA | 0.0063 | 0.1499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-06 | AAA | 0.096 | 0.0249 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-06 | AAA | 0.069 | 0.0449 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-06 | AAA | 0.11 | 0.1499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | AAA | 0.0061 | 0.0249 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-06 | AAA | 0.0063 | 0.0149 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-06 | AAA | 0.053 | 0.2499 |  |  | 1Q SOC/LYNWOOD WP (ONLY WP IN SYSTEM) HYPERLINKED 3/8/17
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-06 | AAA | 0.051 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-06 | AAA | 0.053 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-06 | AAA | 8e-05 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1010 | BARIUM | N | 0.0091 | MG/L | 2.4999 | 2017-02-06 | AAA | 0.00028 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-06 | AAA | 0.00032 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-06 | AAA | 0.0005 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-06 | AAA | 0.0048 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1025 | FLUORIDE | N | 0.65 | MG/L | 4.0499 | 2017-02-06 | AAA | 0.075 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-06 | AAA | 0.00024 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-06 | AAA | 1e-05 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-06 | AAA | 0.0011 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-06 | AAA | 0.00058 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1052 | SODIUM | N | 8.6 | MG/L | 160.4999 | 2017-02-06 | AAA | 0.16 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-06 | AAA | 5e-05 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-06 | AAA | 0.00013 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-06 | AAA | 6e-05 |  |  |  | TRIENNIALS HYPERLINKED 3/8/17 TO BW IN FOR REVIEW FOLDER - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-06 | AAA | 0.061 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1017 | CHLORIDE | N | 13 | MG/L | 250.4999 | 2017-02-06 | AAA | 0.78 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-02-06 | AAA | 0.0025 |  |  |  | HYPERLINKED 3/8/17 (PH HAS Q QUAL. A Q-QUALIFIED PH CAN BE ACCEPTED FOR COMPLIANCE PURPOSES PER HQ'S DECISION YEARS AGO BUT OTHER CHEMICALS WITH Q QUALIFIERS MUST BE RETESTED FOR COMPLIANCE PURPOSES.)
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-08 | AAA | 0.053 |  |  |  | NN (3/8/17 HYPERLINKED TO BW-BB)
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-08 | AAA | 0.051 |  |  |  | NN (3/8/17 HYPERLINKED TO BW-BB)
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-13 | AAA | 0.0069 | 0.0149 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-13 | AAA | 0.0063 | 0.1499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-13 | AAA | 0.0068 | 0.1499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-13 | AAA | 0.12 | 1.4999 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-13 | AAA | 1 | 1.4999 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-13 | AAA | 7.6 | 0.4499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-13 | AAA | 1.2 | 9.4999 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-13 | AAA | 6.5 | 6.4999 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-13 | AAA | 0.96 | 0.6499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-13 | AAA | 0.57 | 2.4999 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-13 | AAA | 0.19 | 0.0749 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-13 | AAA | 1.5 | 0.6499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-13 | AAA | 0.23 | 0.1499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-13 | AAA | 0.097 | 0.0249 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-13 | AAA | 0.069 | 0.0449 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-13 | AAA | 0.11 | 0.1499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | AAA | 0.0061 | 0.0249 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-13 | AAA | 0.0063 | 0.0149 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-13 | AAA | 0.053 | 0.2499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-13 | AAA | 0.86 | 0.2499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-13 | AAA | 0.012 | 0.1499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-13 | AAA | 0.28 | 0.9499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-13 | AAA | 0.16 | 0.1499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-13 | AAA | 0.26 | 0.2499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-13 | AAA | 0.006 | 0.0449 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-13 | AAA | 0.0052 | 0.0249 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-13 | AAA | 1.5 | 0.1499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-13 | AAA | 0.32 | 0.2499 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | AAA | 0.0071 | 0.0249 |  |  | 2Q SOC/LYNWOOD WP(ONLY WP IN SYS)J4 QUAL HEP MS 568% RECOV W/NO DETECT & 2274 HEX...MS 1060% RECOV W/NO DETECT-BIASED HIGH.IF THERE HAD BEEN ANY OF THE TARGET ANALYTE IN THE CLIENT SMP IT WD HV SHOWN.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.89 | UG/L | 60.4999 | 2018-01-11 | L1 | 0.5 |  | 2 | 1.21 | 631 W. LAKE BRANTLEY DR. (ANNUAL 3/18 DISINF BYP REPORT RCVD W/RSLTS) HYPERLINKED TO BW 2/26/18 - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 27.25 | UG/L | 80.4999 | 2018-01-11 | L4 | 0.14 |  | 1 | 1.85 | 198 VARSITY CIR.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.16 | UG/L | 60.4999 | 2018-01-11 | L4 | 0.5 |  | 1 | 1.85 | 198 VARSITY CIR.
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 48.08 | UG/L | 80.4999 | 2018-01-11 | L1 | 0.14 |  | 2 | 1.21 | 631 W. LAKE BRANTLEY DR. (ANNUAL 3/18 DISINF BYP REPORT RCVD W/RSLTS) HYPERLINKED TO BW 2/26/18 - BB
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-14 | AAA | 0.053 |  |  |  | NN (J4 QUAL: NITRATE MS/MSD 111/110% - LCS OK NITRITE MS/MSD 87/87% - LCS OK) RECOVERY FOR NITRITE ACCEPTABLE - BOTH NN OK
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-14 | AAA | 0.051 |  |  |  | NN (J4 QUAL: NITRATE MS/MSD 111/110% - LCS OK NITRITE MS/MSD 87/87% - LCS OK) RECOVERY FOR NITRITE ACCEPTABLE - BOTH NN OK
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.28 | UG/L | 60.4999 | 2019-01-10 | L4 | 0.91 |  | 2 | 1.52 | VARSITY CIR
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 25.23 | UG/L | 80.4999 | 2019-01-10 | L4 | 0.39 |  | 2 | 1.52 | VARSITY CIR
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.57 | UG/L | 60.4999 | 2019-01-10 | L1 | 0.91 |  | 1 | 1.13 | W LAKE BRANTLEY RD
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 13.57 | UG/L | 60.4999 | 2019-01-10 | L1
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | D | 31.8 | UG/L | 80.4999 | 2019-01-10 | L1 | 0.39 |  | 1 | 1.13 | W LAKE BRANTLEY RD
3590785 | SEMINOLE COUNTY SOUTHWEST | DBP | 2950 | TOTAL THMS | M | 31.8 | UG/L | 80.4999 | 2019-01-10 | L1
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1040 | NITRATE | N | 0.46 | MG/L | 10.4999 | 2019-02-14 | AAA
3590785 | SEMINOLE COUNTY SOUTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-14 | AAA
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 24.38 | UG/L | 80.4999 | 2015-07-14 | L2 |  |  |  | 2.28 | MM12 407 WEKIVA SPRINGS RD. (DUAL SMP) (QUALIFIES FOR R.M. AT 1 SITE ANNUALLY 130 GUM ST. TEST @ 2ND WEEK 7/16) >500
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.36 | UG/L | 60.4999 | 2015-07-14 | L2 |  |  |  | 2.28 | MM12 407 WEKIVA SPRINGS RD. (DUAL SMP) (QUALIFIES FOR R.M. AT 1 SITE ANNUALLY 130 GUM ST. TEST @ 2ND WEEK 7/16) >500
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.98 | UG/L | 60.4999 | 2015-07-14 | L1 |  |  |  | 1.27 | MM3 130 GUM ST. (DUAL SMP) (QUALIFIES FOR R.M. AT 1 SITE ANNUALLY 130 GUM ST. TEST @ 2ND WEEK 7/16) >500
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 35.29 | UG/L | 80.4999 | 2015-07-14 | L1 |  |  |  | 1.27 | MM3 130 GUM ST. (DUAL SMP) (QUALIFIES FOR R.M. AT 1 SITE ANNUALLY 130 GUM ST. TEST @ 2ND WEEK 7/16) >500
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 39.53 | UG/L | 80.4999 | 2016-07-14 | L1 | 0.14 |  | 1 | 2.46 | ON R.M. - MM3 130 GUM ST. (T<60 H<45 MAY REMAIN ON REDUCED MONITORING FOR 2ND WEEK JULY 2017 AT 1 SITE 130 GUM ST. DUAL SAMPLE ANNUALLY) POP. 1 656
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.05 | UG/L | 60.4999 | 2016-07-14 | L1 | 0.2 |  | 1 | 2.46 | ON R.M. - MM3 130 GUM ST. (T<60 H<45 MAY REMAIN ON REDUCED MONITORING FOR 2ND WEEK JULY 2017 AT 1 SITE 130 GUM ST. DUAL SAMPLE ANNUALLY) POP. 1 656
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.05 | UG/L | 60.4999 | 2017-07-13 | L1 | 0.5 |  | 1 | 1.77 | ON R.M. - MM3 130 GUM ST. (T<60 H<45 MAY REMAIN ON REDUCED MONITORING FOR 2ND WEEK JULY 2018 AT 1 SITE 130 GUM ST. DUAL SAMPLE ANNUALLY) POP. 1 656
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 28.59 | UG/L | 80.4999 | 2017-07-13 | L1 | 0.14 |  | 1 | 1.77 | ON R.M. - MM3 130 GUM ST. (T<60 H<45 MAY REMAIN ON REDUCED MONITORING FOR 2ND WEEK JULY 2018 AT 1 SITE 130 GUM ST. DUAL SAMPLE ANNUALLY) POP. 1 656
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.75 | UG/L | 60.4999 | 2018-07-12 | L1 | 0.91 |  | 1 | 3.03 | ON R.M. - 130 GUM ST. (HLKD 8-22-18)
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 33.04 | UG/L | 80.4999 | 2018-07-12 | L1 | 0.14 |  | 1 | 3.03 | ON R.M. - 130 GUM ST. (HLKD 8-22-18)
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 32.02 | UG/L | 80.4999 | 2019-07-11 | L1 | 0.39 |  | 1 | 1.73 | ON R.M. - 130 GUM ST. (HLKD)
3590823 | MEREDITH MANOR (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.98 | UG/L | 60.4999 | 2019-07-11 | L1 | 0.91 |  | 1 | 1.73 | ON R.M. - 130 GUM ST. (HLKD)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1005 | ARSENIC | N | 0.0006 | MG/L | 0.0104 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1010 | BARIUM | N | 0.021 | MG/L | 2.4999 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1025 | FLUORIDE | N | 0.073 | MG/L | 4.0499 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1052 | SODIUM | N | 13.1 | MG/L | 160.4999 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-06-08 | AAA |  |  |  |  | 15DON/16:4QM/XY 3/16 (RCVD 6/15 TRIENNIALS 9/30/15-NOTIFIED BIOMETRICS TO TEST ASAP ON 9/30/15 FOR QM/XY DUE TO 6/15 DETECTION) QTRLY DBPS-2 SITES RADS 2021 (BIOMETRICS)
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1017 | CHLORIDE | N | 15.8 | MG/L | 250.4999 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1022 | COPPER | N | 0.0052 | MG/L | 1.4999 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1025 | FLUORIDE | N | 0.073 | MG/L | 2.0499 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1028 | IRON | N | 0.39 | MG/L | 0.3499 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1032 | MANGANESE | N | 0.0047 | MG/L | 0.0549 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.6 | LN(10) |  | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 217 | MG/L | 500.4999 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-06-08 | AAA |  |  |  |  | **CONFIRMED 10/20/15 EM BY JESSICA BIOMETRICS: SYS. USES IRON SEQUESTRATION TREATMENT G18. IRON MAY GO UP TO 1.0 MG/L W/O VIOLATION. FE. 0.39 MG/L IS NOT A VIOL. BB
3590865 | MULLET LAKE WATER ASSOCIATION | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-06-08 | AAA |  |  |  |  | RADS DUE 2021
3590865 | MULLET LAKE WATER ASSOCIATION | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-06-08 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 1.7 | UG/L | 10499.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-06-08 | AAA |  | 0.5499 |  |  | 3YR VOCS+1QM/XY (2QM/XY 9/15>9/30/15 EM RQSTD QTRLY XY - TRIENNIAL CHEMS RCVD 9/30/15 - ALMOST TOO LATE TO ASK FOR QTRLY XY AFTER DETECTION - BIOMETRICS SAMPLED THE SAME DAY - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 104 | UG/L | 80.4999 | 2015-09-04 | L1 |  |  |  | 3.5 | TTHMS-2002 RUSSELL COVE (MISSED HAA5>TESTING 10/19/15 WEEK AS MAKE-UP TESTS) EM 10/16/15>BIOMETRICS FOR QM/BOTH T+H DUE TO TTHMS 104 EXCEEDANCE.
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.5 | UG/L | 60.4999 | 2015-09-04 | L2 |  |  |  | 1.5 | (MAKE-UP DBPS IN 11/10/15 EM FROM BIOMETRICS) HAA5S-1860 MARSH RD. (MISSED TTHMS>TESTING 10/19/15 WEEK AS MAKE-UP TESTS) EM 10/16/15>BIOMETRICS FOR QM/BOTH T+H DUE TO HIGH TTHMS @ RUSSELL COVE SITE
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 3.3 | UG/L | 10499.9999 | 2015-09-30 | AAA |  | 0.5499 |  |  | EM 12/18/15 FOR REMINDER OF OCT-NOV-DEC. 2015 XY DUE TO BIOMETRICS - BB ) **PER 12/18/15 EM BIOMETRICS IS WAITING FOR 12/15 QTR XY RESULTS FROM LAB - BB. 2QM/XY 9/15
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.1 | UG/L | 60.4999 | 2015-10-22 | L1 | 0.37 |  | 1 | 3.5 | 2002 RUSSELL COVE (HAA5 MAKE-UP TESTS FOR 9/15 AS RQRD)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | S | 73.4 | UG/L | 80.4999 | 2015-10-22 | L2 | 0.25 |  | 2 | 3.5 | (**DBPS WERE TAKEN ON 12/2/15 & BIOMETRICS IS WAITING ON RSLTS*** 1860 MARSH RD. (TTHM MAKE-UP TESTS FOR 9/15 AS RQRD)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-12-02 | AAA |  | 0.5499 |  |  | 3QM/XY (4QM/XY DUE 3/16) EM 2/22/16 TO BIOMETRICS FOR 4QM/XY 3/16-BB
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.8 | UG/L | 60.4999 | 2015-12-02 | L1 |  |  |  | 0.3 | 2002 RUSSELL COVE(AFT.2 QTRS 12/15 LRAA/T=35.75 LRAA/H=4.93)THERE IS NO 9/15 H RSLT (MISSED)-12/15 LRAA/H FOR RUSSELL COVE=14.8 DIVIDED BY 3 =4.93 FOR 12/15 QTR)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 39 | UG/L | 80.4999 | 2015-12-02 | L1 |  |  |  | 0.3 | 2002 RUSSELL COVE(AFT.2 QTRS 12/15 LRAA/T=35.75 LRAA/H=4.93)THERE IS NO 9/15 H RSLT (MISSED)-12/15 LRAA/H FOR RUSSELL COVE=14.8 DIVIDED BY 3 =4.93 FOR 12/15 QTR)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.8 | UG/L | 60.4999 | 2015-12-02 | L2 |  |  |  | 1.5 | 1860 MARSH RD.(AFT.2 QTRS 12/15 LRAA/T=13.4667 LRAA/H=13.575)THERE IS NO 9/15 T RSLT (MISSED)-12/15 LRAA/T FOR MARSH RD.=40.4 DIVIDED BY 3=13.4667 FOR 12/15 QTR
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 40.4 | UG/L | 80.4999 | 2015-12-02 | L2 |  |  |  | 1.5 | 1860 MARSH RD.(AFT.2 QTRS 12/15 LRAA/T=13.4667 LRAA/H=13.575)THERE IS NO 9/15 T RSLT (MISSED)-12/15 LRAA/T FOR MARSH RD.=40.4 DIVIDED BY 3=13.4667 FOR 12/15 QTR
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-03-01 | AAA |  | 0.5499 |  |  | 4QM/XYLENES (MAY STOP QM/XY) 1AM/XY 3Q 2017
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 39.2 | UG/L | 80.4999 | 2016-03-01 | L2 |  |  |  | 1.5 | 1860 MARSH RD. (3/16 LRAA/T=26.53 AFTER 2 QTRS LRAA/H=18.8 AFTER 3 QTRS) 7/12 EW HAS 6/14/16 DBPS>LOW RSLTS 7/12/16 EM TO BIOM TO TEST 9/16 QTR AT EA. SITE FOR DBPS. BB
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 39.3 | UG/L | 80.4999 | 2016-03-01 | L1 |  |  |  | 1.2 | 2002 RUSSELL COVE (3/16 LRAA/T=45.575 AFTER 3 QTRS LRAA/H=11.3 AFTER 2 QTRS) T EXCEEDANCE 9/15 L1 SITE
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.9 | UG/L | 60.4999 | 2016-03-01 | L2 |  |  |  | 1.5 | 1860 MARSH RD. (3/16 LRAA/T=26.53 AFTER 2 QTRS LRAA/H=18.8 AFTER 3 QTRS) 7/12 EW HAS 6/14/16 DBPS>LOW RSLTS 7/12/16 EM TO BIOM TO TEST 9/16 QTR AT EA. SITE FOR DBPS. BB
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.1 | UG/L | 60.4999 | 2016-03-01 | L1 |  |  |  | 1.2 | 2002 RUSSELL COVE (3/16 LRAA/T=45.575 AFTER 3 QTRS LRAA/H=11.3 AFTER 2 QTRS) T EXCEEDANCE 9/15 L1 SITE
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-04-05 | AAA
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-04-05 | AAA
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 33.1 | UG/L | 80.4999 | 2016-06-14 | L2 |  |  |  | 0.4 | 1860 MARSH RD. (NO LRAA MCL VIOLS EITHER SITE)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.8 | UG/L | 60.4999 | 2016-06-14 | L1 |  |  |  | 0.2 | 2002 RUSSELL COVE (NO LRAA MCL VIOLS EITHER SITE)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.2 | UG/L | 60.4999 | 2016-06-14 | L2 |  |  |  | 0.4 | 1860 MARSH RD. (NO LRAA MCL VIOLS EITHER SITE)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 12.5 | UG/L | 80.4999 | 2016-06-14 | L1 |  |  |  | 0.2 | 2002 RUSSELL COVE (NO LRAA MCL VIOLS EITHER SITE)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.2 | UG/L | 60.4999 | 2016-09-15 | L1 |  |  |  | 0 | 2002 RUSSELL COVE (9/16 LRAA/T=36.225 LRAA/H=14.975 WITH 4 FULL QTRS OF TEST RESULTS 10/15 - 9/16)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 41.9 | UG/L | 80.4999 | 2016-09-15 | L2 |  |  |  | 1.1 | 1860 MARSH RD. (9/16 LRAA/T=38.65 LRAA/H=17.5 W/4 FULL QTRS OF TEST RESULTS 10/15 - 9/16)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.1 | UG/L | 60.4999 | 2016-09-15 | L2 |  |  |  | 1.1 | 1860 MARSH RD. (9/16 LRAA/T=38.65 LRAA/H=17.5 W/4 FULL QTRS OF TEST RESULTS 10/15 - 9/16)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 54.1 | UG/L | 80.4999 | 2016-09-15 | L1 |  |  |  | 0 | 2002 RUSSELL COVE (9/16 LRAA/T=36.225 LRAA/H=14.975 WITH 4 FULL QTRS OF TEST RESULTS 10/15 - 9/16)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-06-20 | AAA | 0.025 |  |  |  | NN (REPORT PLACED IN FINAL CHEM HOLDING FOLDER 8/18/17 - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-06-20 | AAA | 0.025 |  |  |  | NN (REPORT PLACED IN FINAL CHEM HOLDING FOLDER 8/18/17 - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.8 | UG/L | 60.4999 | 2017-09-07 | L1 | 1 |  | 1 | 1.8 | 2002 RUSSELL COVE
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 9.9 | UG/L | 80.4999 | 2017-09-07 | L1 | 0.32 |  | 1 | 1.8 | 2002 RUSSELL COVE
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.7 | UG/L | 60.4999 | 2017-09-07 | L2 | 1 |  | 2 | 1.8 | 1860 MARSH RD. (HYPERLINKED 10/23/17 TO BW - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 7 | UG/L | 80.4999 | 2017-09-07 | L2 | 0.32 |  | 2 | 1.8 | 1860 MARSH RD. (HYPERLINKED 10/23/17 TO BW - BB)
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-11-16 | AAA | 0.25 | 0.5499 |  |  | 1AM/XY (LATE FOR 3Q) **2AM/XY DUE 3Q 2018**
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-03-08 | AAA | 0.0005 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1010 | BARIUM | N | 0.017 | MG/L | 2.4999 | 2018-03-08 | AAA | 0.005 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-03-08 | AAA | 0.005 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1025 | FLUORIDE | N | 0.093 | MG/L | 4.0499 | 2018-03-08 | AAA | 0.034 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-03-08 | AAA | 0.0005 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-03-08 | AAA | 0.0001 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-03-08 | AAA | 0.0025 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-03-08 | AAA | 0.001 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1052 | SODIUM | N | 0 | MG/L | 160.4999 | 2018-03-08 | AAA | 16.2 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-03-08 | AAA | 0.001 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-03-08 | AAA | 0.0005 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-03-08 | AAA | 0.0005 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-03-08 | AAA | 0.05 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1017 | CHLORIDE | N | 17.5 | MG/L | 250.4999 | 2018-03-08 | AAA | 2.5 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1022 | COPPER | N | 0.0032 | MG/L | 1.4999 | 2018-03-08 | AAA | 0.0025 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1025 | FLUORIDE | N | 0.093 | MG/L | 2.0499 | 2018-03-08 | AAA | 0.034 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1028 | IRON | N | 0.31 | MG/L | 0.3499 | 2018-03-08 | AAA | 0.02 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1032 | MANGANESE | N | 0.0041 | MG/L | 0.0549 | 2018-03-08 | AAA | 0.0025 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-03-08 | AAA | 0.0025 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2018-03-08 | AAA | 2.5 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-03-08 | AAA | 0.01 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2018-03-08 | AAA | 5 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1920 | ODOR THRESHOLD | N | 2 |  | 3.4999 | 2018-03-08 | AAA | 1 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.8 | LN(10) |  | 2018-03-08 | AAA | 0.1 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 189 | MG/L | 500.4999 | 2018-03-08 | AAA | 5 |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | SEC | 2905 | FOAMING AGENTS | N | 0.099 |  | 0.5499 | 2018-03-08 | AAA |  |  |  |  | J QUALIFIER FOAMING AGENTS MS AT 83% RECOVERY_ACCEPTED_JMF
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-03-08 | AAA | 0.41 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | AAA | 0.44 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-03-08 | AAA | 0.39 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | AAA | 0.25 | 0.5499 |  |  | 3 YR VOC
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-03-08 | AAA | 0.025 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-03-08 | AAA | 0.025 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-03-08 | AAA | 0.001 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-03-08 | AAA | 0.0025 |  |  |  | J QUALIFIER NITRITE MS AT 1% RECOVERY. LAB STATES THAT LCS RECOVERY IS ACCEPTABLE AT 102%_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | N | 5.5 | UG/L | 60.4999 | 2018-08-09 | L1 |  |  |  | 0.3 | 2002 RUSSELL COVE -- RESULTS RCVD 4/2/19. LATE REPORTING_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | N | 15.2 | UG/L | 80.4999 | 2018-08-09 | L1 |  |  |  | 0.3 | 2002 RUSSELL COVE -- RESULTS RCVD 4/2/19. LATE REPORTING_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | N | 4.9 | UG/L | 60.4999 | 2018-08-09 | L2 |  |  |  | 0.3 | 1860 MARSH ROAD - RCVD EMAIL WITH RESULTS 4/2/19--LATE REPORTING_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | N | 14 | UG/L | 80.4999 | 2018-08-09 | L2 |  |  |  | 0.3 | 1860 MARSH ROAD - RCVD EMAIL WITH RESULTS 4/2/19--LATE REPORTING_RLB
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-19 | AAA | 0.25 | 0.5499 |  |  | 2AM/XY (3AM/XY DUE 3Q 2019) RCVD 11-13-18 (BIOMETRIC)
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 64.6 | UG/L | 60.4999 | 2019-08-15 | L2 |  |  | 1 | 1.5 | 1860 MARSH RD.
3590865 | MULLET LAKE WATER ASSOCIATION | DBP | 2950 | TOTAL THMS | D | 77 | UG/L | 80.4999 | 2019-08-15 | L2 |  |  | 1 | 1.5 | 1860 MARSH RD.
3590865 | MULLET LAKE WATER ASSOCIATION | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-09-17 | AAA | 0.25 | 0.5499 |  |  | 3AM/XY DUE (HLKD)
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-12-09 | AAA
3590865 | MULLET LAKE WATER ASSOCIATION | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-12-09 | AAA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-01-13 | WTP3 |  | 0.6499 |  |  | 4QM/2039-WP1 TUSKAWILLA WP (STOP QM/2039. 1AM/2039-WP1 TUSKAWILLA 2Q'16>EM 1/26/15+9/25/15 EM>PUT IN 2015 MONIT. SCHED.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-01-14 | WTP2 |  | 0.5499 |  |  | 6AM/CIS-1 2-WP3 BAHAMA(7AM/CIS-1 2-WP3 BAHAMA 1Q 2016-WE ARE CONSIDERING 0.536 UG/L TO BE A DETECTION-CLOSE TO 0.549-IN THIS CASE. CONT.AM/CIS-1 2 UNTIL 3 CONSEC.YRS W/O DETECT MINIMUM-TALLAH.INTEREST
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.62 | UG/L | 60.4999 | 2015-03-06 | L2 |  |  |  | 0.7 | SM-4 606 MORGAN (L2 3/15 LRAA/T=57.6225 (57.62 DBF) LRAA/H=21.2475 (21.24 DBF)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.71 | UG/L | 60.4999 | 2015-03-06 | L4 |  |  |  | 2.1 | STG 1 MRT WP3 410 SANDRINGHAM (L4 3/15 LRAA/T=47.875 (47.87 DBF) LRAA/H=26.305 (26.30 DBF) NOTE: 3/15 OE REPORTS IN OC FOR THE WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.11 | UG/L | 60.4999 | 2015-03-06 | L1 |  |  |  | 0.8 | SM-6 1626 WRENTHAM (L1 3/15 LRAA/T=102.8175 (102.81 DBF) LRAA/H=40.8525 (40.85 DBF) IN OC (3/15 OE REPORTS IN OC FOR THE WRENTHAM & ONEIDA SITES)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 83.27 | UG/L | 80.4999 | 2015-03-06 | L1 |  |  |  | 0.8 | SM-6 1626 WRENTHAM (L1 3/15 LRAA/T=102.8175 (102.81 DBF) LRAA/H=40.8525 (40.85 DBF) IN OC (3/15 OE REPORTS IN OC FOR THE WRENTHAM & ONEIDA SITES)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 51 | UG/L | 80.4999 | 2015-03-06 | L4 |  |  |  | 2.1 | STG 1 MRT WP3 410 SANDRINGHAM (L4 3/15 LRAA/T=47.875 (47.87 DBF) LRAA/H=26.305 (26.30 DBF) NOTE: 3/15 OE REPORTS IN OC FOR THE WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 69.59 | UG/L | 80.4999 | 2015-03-06 | L2 |  |  |  | 0.7 | SM-4 606 MORGAN (L2 3/15 LRAA/T=57.6225 (57.62 DBF) LRAA/H=21.2475 (21.24 DBF)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.43 | UG/L | 60.4999 | 2015-03-06 | L3 |  |  |  | 1 | STG 1 MRT WP1 674 ONEIDA CT. (L3 3/15 LRAA/T=91.6175 (91.61 DBF) LRAA/H=44.3575 (44.35 DBF) 3/15 OE REPORTS IN OC FOR THE WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 83.77 | UG/L | 80.4999 | 2015-03-06 | L3 |  |  |  | 1 | STG 1 MRT WP1 674 ONEIDA CT. (L3 3/15 LRAA/T=91.6175 (91.61 DBF) LRAA/H=44.3575 (44.35 DBF) 3/15 OE REPORTS IN OC FOR THE WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-03-25 | WTP3 |  |  |  |  | WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-03-25 | WTP3 |  |  |  |  | WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-03-25 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-03-25 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-03-25 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.) 4/26 EW HAS 3/16 NN - ASKED WAYLON TO SEND BETTER COPY - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-03-25 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.) 4/26 EW HAS 3/16 NN - ASKED WAYLON TO SEND BETTER COPY - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 100.88 | UG/L | 80.4999 | 2015-06-04 | L1 |  |  |  | 1 | SM-6 1626 WRENTHAM (DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.47 | UG/L | 60.4999 | 2015-06-04 | L4 |  |  |  | 1.9 | STG 1 MRT WP3 410 SANDRINGHAM (DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES (6/9/15 DEP MNGMNT APPROVED W. SPGS. TESTING DBPS THE 1ST MO. OF EA. QTR RATHER THAN LAST MO.-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.42 | UG/L | 60.4999 | 2015-06-04 | L2 |  |  |  | 1.7 | SM-4 606 MORGAN(DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 88.83 | UG/L | 80.4999 | 2015-06-04 | L2 |  |  |  | 1.7 | SM-4 606 MORGAN(DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.69 | UG/L | 60.4999 | 2015-06-04 | L3 |  |  |  | 1.3 | STG 1 MRT WP1 674 ONEIDA CT.(DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 117.42 | UG/L | 80.4999 | 2015-06-04 | L3 |  |  |  | 1.3 | STG 1 MRT WP1 674 ONEIDA CT.(DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 74.55 | UG/L | 80.4999 | 2015-06-04 | L4 |  |  |  | 1.9 | STG 1 MRT WP3 410 SANDRINGHAM (DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES (6/9/15 DEP MNGMNT APPROVED W. SPGS. TESTING DBPS THE 1ST MO. OF EA. QTR RATHER THAN LAST MO.-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.44 | UG/L | 60.4999 | 2015-06-04 | L1 |  |  |  | 1 | SM-6 1626 WRENTHAM (DOES NOT QUALIFY FOR R.M.) PN ISSUED FOR WRENTHAM & ONEIDA SITES
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.08 | UG/L | 60.4999 | 2015-07-14 | L3 |  |  |  | 0.9 | STG 1 MRT WP1 674 ONEIDA CT. (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 93.34 | UG/L | 80.4999 | 2015-07-14 | L3 |  |  |  | 0.9 | STG 1 MRT WP1 674 ONEIDA CT. (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.84 | UG/L | 60.4999 | 2015-07-14 | L4 |  |  |  | 1.8 | (12/4/15 OE REPORT 4TH QTR 2015 MORGAN SITE RCVD & IN OC) STG 1 MRT WP3 410 SANDRINGHAM (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 57.89 | UG/L | 80.4999 | 2015-07-14 | L4 |  |  |  | 1.8 | (12/4/15 OE REPORT 4TH QTR 2015 MORGAN SITE RCVD & IN OC) STG 1 MRT WP3 410 SANDRINGHAM (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.61 | UG/L | 60.4999 | 2015-07-14 | L2 |  |  |  | 1.7 | SM-4 606 MORGAN (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 80.34 | UG/L | 80.4999 | 2015-07-14 | L2 |  |  |  | 1.7 | SM-4 606 MORGAN (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.7 | UG/L | 60.4999 | 2015-07-14 | L1 |  |  |  | 1.3 | SM-6 1626 WRENTHAM (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 103.96 | UG/L | 80.4999 | 2015-07-14 | L1 |  |  |  | 1.3 | SM-6 1626 WRENTHAM (WRENTHAM & ONEIDA SITES HAVE TTHM LRAA MCL VIOLS 9/15 QTR)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 94.2 | UG/L | 80.4999 | 2015-10-20 | L1 |  |  |  | 0.7 | SM-6 1626 WRENTHAM (12/15 LRAA/T=95.5775 LRAA/H=30.1575 ) 12/15 OE VALUE T=98.31 & 12/15 OE REPORT IN OC
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.38 | UG/L | 60.4999 | 2015-10-20 | L1 |  |  |  | 0.7 | SM-6 1626 WRENTHAM (12/15 LRAA/T=95.5775 LRAA/H=30.1575 ) 12/15 OE VALUE T=98.31 & 12/15 OE REPORT IN OC
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.92 | UG/L | 60.4999 | 2015-10-20 | L4 |  |  |  | 0.6 | STG 1 MRT WP3 410 SANDRINGHAM (12/15 LRAA/T=59.465 LRAA/H=33.985) 12/15 OE VALUE T=60.32 (NO OE REPORT NDD)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 98.46 | UG/L | 80.4999 | 2015-10-20 | L3 |  |  |  | 0.5 | STG 1 MRT WP1 674 ONEIDA CT. (12/15 LRAA/T=98.2475 LRAA/H=28.22) 12/15 OE VALUE T=101.92 & 12/15 OE REPORT IN OC
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.68 | UG/L | 60.4999 | 2015-10-20 | L3 |  |  |  | 0.5 | STG 1 MRT WP1 674 ONEIDA CT. (12/15 LRAA/T=98.2475 LRAA/H=28.22) 12/15 OE VALUE T=101.92 & 12/15 OE REPORT IN OC
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 54.42 | UG/L | 80.4999 | 2015-10-20 | L4 |  |  |  | 0.6 | STG 1 MRT WP3 410 SANDRINGHAM (12/15 LRAA/T=59.465 LRAA/H=33.985) 12/15 OE VALUE T=60.32 (NO OE REPORT NDD)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 77.15 | UG/L | 80.4999 | 2015-10-20 | L2 |  |  |  | 1.3 | SM-4 606 MORGAN (12/15 LRAA/T=78.9775 LRAA/H=29.515) 12/15 OE VALUE T=80.8675 ? ND. OE REPORT>EM 12/3/15 TO W.LOCKLEAR
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.41 | UG/L | 60.4999 | 2015-10-20 | L2 |  |  |  | 1.3 | SM-4 606 MORGAN (12/15 LRAA/T=78.9775 LRAA/H=29.515) 12/15 OE VALUE T=80.8675 ? ND. OE REPORT>EM 12/3/15 TO W.LOCKLEAR
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-01-07 | WTP2 |  | 0.5499 |  |  | 7AM/CIS-1 2-WP3 BAHAMA 1Q 2016 (8AM/CIS-1 2-WP3 BAHAMA 1Q 2017)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 80.18 | UG/L | 80.4999 | 2016-01-28 | L3 |  |  |  | 1.1 | STG 1 MRT WP1 674 ONEIDA CT. (3/16 LRAA/T=97.35 LRAA/H=28.29) 3/16 OE T VALUE=88.04(3/16 OE REPORT IN OC)3/2/16 PN & COD IN OC(HAD OE VALUE FOR LRAA-CORRECTING NXT PN)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 55.61 | UG/L | 80.4999 | 2016-01-28 | L4 |  |  |  | 1.7 | STG 1 MRT WP3 410 SANDRINGHAM (3/16 LRAA/T=60.61 LRAA/H=34.99) NO OE EXCEEDANCE FOR SANDRINGHAM SITE
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.45 | UG/L | 60.4999 | 2016-01-28 | L1 |  |  |  | 1 | SM-6 1626 WRENTHAM (3/16 LRAA/T=95.985 LRAA/H=30.49) 3/16 OE T VALUE=91.99(3/16 OE REPORT IN OC)3/2/16 PN & COD IN OC(HAD 98.98 SHD BE 98.99)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 84.9 | UG/L | 80.4999 | 2016-01-28 | L1 |  |  |  | 1 | SM-6 1626 WRENTHAM (3/16 LRAA/T=95.985 LRAA/H=30.49) 3/16 OE T VALUE=91.99(3/16 OE REPORT IN OC)3/2/16 PN & COD IN OC(HAD 98.98 SHD BE 98.99)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.56 | UG/L | 60.4999 | 2016-01-28 | L2 |  |  |  | 1.4 | SM-4 606 MORGAN (3/16 LRAA/T=77.75 LRAA/H=29.75) NO OE EXCEEDANCE FOR MORGAN SITE
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 64.71 | UG/L | 80.4999 | 2016-01-28 | L2 |  |  |  | 1.4 | SM-4 606 MORGAN (3/16 LRAA/T=77.75 LRAA/H=29.75) NO OE EXCEEDANCE FOR MORGAN SITE
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.73 | UG/L | 60.4999 | 2016-01-28 | L3 |  |  |  | 1.1 | STG 1 MRT WP1 674 ONEIDA CT. (3/16 LRAA/T=97.35 LRAA/H=28.29) 3/16 OE T VALUE=88.04(3/16 OE REPORT IN OC)3/2/16 PN & COD IN OC(HAD OE VALUE FOR LRAA-CORRECTING NXT PN)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.76 | UG/L | 60.4999 | 2016-01-28 | L4 |  |  |  | 1.7 | STG 1 MRT WP3 410 SANDRINGHAM (3/16 LRAA/T=60.61 LRAA/H=34.99) NO OE EXCEEDANCE FOR SANDRINGHAM SITE
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-03-09 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.) 17:TRIENNIALS PER WP 9AM/CIS-1 2 BAHAMA WP3 1Q 2018 (DETECTION 2017)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-03-09 | WTP3 |  |  |  |  | WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-03-09 | WTP3 |  |  |  |  | WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-03-09 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-03-09 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-03-09 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.) 17:TRIENNIALS PER WP 9AM/CIS-1 2 BAHAMA WP3 1Q 2018 (DETECTION 2017)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2016-04-04 | WTP3 |  | 0.6499 |  |  | 1AM/2039-WP1 TUSKAWILLA (2AM/2039-WP1 TUSKAWILLA 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.27 | UG/L | 60.4999 | 2016-04-12 | L1 |  |  |  | 0.3 | SM-6 1626 WRENTHAM (6/16 QTR LRAA/TTHMS MCL VIOL=99.0425) 6/16 OF VALUE/T=101.33 (6/16 OE REPORT IN OC)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 113.11 | UG/L | 80.4999 | 2016-04-12 | L1 |  |  |  | 0.3 | SM-6 1626 WRENTHAM (6/16 QTR LRAA/TTHMS MCL VIOL=99.0425) 6/16 OF VALUE/T=101.33 (6/16 OE REPORT IN OC)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.68 | UG/L | 60.4999 | 2016-04-12 | L2 |  |  |  | 1.4 | SM-4 606 MORGAN (**ENTER MCL VIOLS MANUALLY BECAUSE VALUES WHICH GENERATED ARE INCORRECT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 66.19 | UG/L | 80.4999 | 2016-04-12 | L4 |  |  |  | 1.1 | STG 1 MRT WP3 410 SANDRINGHAM (**ENTER MCL VIOLS MANUALLY BECAUSE VALUES WHICH GENERATED ARE INCORRECT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 85.03 | UG/L | 80.4999 | 2016-04-12 | L2 |  |  |  | 1.4 | SM-4 606 MORGAN (**ENTER MCL VIOLS MANUALLY BECAUSE VALUES WHICH GENERATED ARE INCORRECT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.85 | UG/L | 60.4999 | 2016-04-12 | L4 |  |  |  | 1.1 | STG 1 MRT WP3 410 SANDRINGHAM (**ENTER MCL VIOLS MANUALLY BECAUSE VALUES WHICH GENERATED ARE INCORRECT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 100.29 | UG/L | 80.4999 | 2016-04-12 | L3 |  |  |  | 0.6 | STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.) (**ENTER MCL VIOLS MANUALLY BECAUSE VALUES WHICH GENERATED ARE INCORRECT) 4/16 OE VALUE/T = 94.805 (6/16 OE REPORT IN OC)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.67 | UG/L | 60.4999 | 2016-04-12 | L3 |  |  |  | 0.6 | STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.) (**ENTER MCL VIOLS MANUALLY BECAUSE VALUES WHICH GENERATED ARE INCORRECT) 4/16 OE VALUE/T = 94.805 (6/16 OE REPORT IN OC)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-07-11 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-07-11 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-07-12 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.7 | LN(10) |  | 2016-07-12 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-07-12 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-07-12 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.15 | UG/L | 60.4999 | 2016-07-18 | L1 | 0.2 |  | 1 | 0.5 | 1626 WRENTHAM (9/16 LRAA/T=103.3975 LRAA/H=@29.06 PER DBF) W.LKLR HAS APPROVED DRAFT PN FOR ISSUANCE. 9/16 OE VAL/T-WRENTHAM=110.1925-RCVD OE REPORT-IN OC OE VAL/H IS LOW)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 110.85 | UG/L | 80.4999 | 2016-07-18 | L3 | 0.14 |  | 3 | 0.7 | 674 ONEIDA LN. (9/16 LRAA/T=97.445 LRAA/H=@25.81 PER DBF) W. LKLR HAS APPROVED PN FOR ISSUANCE. 9/16 OE VAL/T-ONEIDA=100.5425-RCVD OE REPORT-IN OC OE VAL/H IS LOW)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.15 | UG/L | 60.4999 | 2016-07-18 | L3 | 0.2 |  | 3 | 0.7 | 674 ONEIDA LN. (9/16 LRAA/T=97.445 LRAA/H=@25.81 PER DBF) W. LKLR HAS APPROVED PN FOR ISSUANCE. 9/16 OE VAL/T-ONEIDA=100.5425-RCVD OE REPORT-IN OC OE VAL/H IS LOW)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 82.78 | UG/L | 80.4999 | 2016-07-18 | L2 | 0.14 |  | 2 | 0.9 | 606 MORGAN (9/16 LRAA/T=77.4175 LRAA/H=26.58 PER DBF) 9/16 OE VAL/T=78.825(OK) OE VAL/H IS LOW. NO OE REPORT NEEDED FOR L2 SITE.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 61.69 | UG/L | 80.4999 | 2016-07-18 | L4 | 0.14 |  | 4 | 1 | 410 SANDRINGHAM (9/16 LRAA/T=59.4775 LRAA/H=@34.79 PER DBF) 9/16 OE VAL/T=61.295 OE VAL/H IS LOW.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 121.38 | UG/L | 80.4999 | 2016-07-18 | L1 | 0.14 |  | 1 | 0.5 | 1626 WRENTHAM (9/16 LRAA/T=103.3975 LRAA/H=@29.06 PER DBF) W.LKLR HAS APPROVED DRAFT PN FOR ISSUANCE. 9/16 OE VAL/T-WRENTHAM=110.1925-RCVD OE REPORT-IN OC OE VAL/H IS LOW)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.69 | UG/L | 60.4999 | 2016-07-18 | L2 | 0.2 |  | 2 | 0.9 | 606 MORGAN (9/16 LRAA/T=77.4175 LRAA/H=26.58 PER DBF) 9/16 OE VAL/T=78.825(OK) OE VAL/H IS LOW. NO OE REPORT NEEDED FOR L2 SITE.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.64 | UG/L | 60.4999 | 2016-07-18 | L4 | 0.2 |  | 4 | 1 | 410 SANDRINGHAM (9/16 LRAA/T=59.4775 LRAA/H=@34.79 PER DBF) 9/16 OE VAL/T=61.295 OE VAL/H IS LOW.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-07-22 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-07-22 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.6 | MG/L |  | 2016-07-22 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-07-22 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-07-22 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-07-22 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-08-08 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-08-08 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-08-08 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.5 | MG/L |  | 2016-08-08 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-08 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-08-08 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.65 | MG/L |  | 2016-08-15 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-15 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-08-15 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-08-15 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2016-08-15 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-08-15 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2016-08-31 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-08-31 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-08-31 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-08-31 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.6 | MG/L |  | 2016-08-31 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-08-31 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-09-12 | WTP3 |  |  |  |  | THERE ARE NO 9/12/16 ORTHOPHOSPHATE OR PH RESULTS FOR WPS 2 & 3 IN THIS SUBMITTAL - ONLY FOR WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-09-12 | WTP3 |  |  |  |  | THERE ARE NO 9/12/16 ORTHOPHOSPHATE OR PH RESULTS FOR WPS 2 & 3 IN THIS SUBMITTAL - ONLY FOR WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-09-15 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-09-15 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-09-15 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2016-09-15 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2016-09-15 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2016-09-15 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-09-28 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2016-09-28 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-09-28 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-09-28 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-09-28 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-09-28 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 76.36 | UG/L | 80.4999 | 2016-10-11 | L3 |  |  |  | 0.3 | STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.98 | UG/L | 60.4999 | 2016-10-11 | L3 |  |  |  | 0.3 | STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 69.55 | UG/L | 80.4999 | 2016-10-11 | L2 |  |  |  | 0.9 | SM-4 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.63 | UG/L | 60.4999 | 2016-10-11 | L2 |  |  |  | 0.9 | SM-4 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 69.95 | UG/L | 80.4999 | 2016-10-11 | L1 |  |  |  | 0.6 | SM-6 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.59 | UG/L | 60.4999 | 2016-10-11 | L4 |  |  |  | 0.5 | STG 1 MRT WP3 410 SANDRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.24 | UG/L | 60.4999 | 2016-10-11 | L1 |  |  |  | 0.6 | SM-6 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 57.64 | UG/L | 80.4999 | 2016-10-11 | L4 |  |  |  | 0.5 | STG 1 MRT WP3 410 SANDRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-10-14 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2016-10-14 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-10-14 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-10-14 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-10-14 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-10-14 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.7 | MG/L |  | 2016-10-27 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2016-10-27 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-10-27 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.8 | LN(10) |  | 2016-10-27 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2016-10-27 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2016-10-27 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-11-09 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-11-09 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-11-09 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-11-09 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-11-09 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2016-11-09 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-11-23 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-11-23 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-11-23 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-11-23 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-11-23 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2016-11-23 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-12-09 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.78 | MG/L |  | 2016-12-09 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2016-12-09 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.83 | MG/L |  | 2016-12-09 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-12-09 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.99 | MG/L |  | 2016-12-09 | WTP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.81 | MG/L |  | 2016-12-21 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-12-21 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-12-21 | WTP2 |  |  |  |  | 7-9/16 POE WQPS IN OCULUS - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2016-12-21 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.98 | MG/L |  | 2016-12-21 | WTP2 |  |  |  |  | 7-9/16 POE WQPS IN OCULUS - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.77 | MG/L |  | 2016-12-21 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-01-18 | WTP1 | 0.012 | 0.1499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-01-18 | WTP1 | 0.28 | 0.9499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP1 | 0.16 | 0.1499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-01-18 | WTP2 | 1.9 |  |  |  | BAHAMA WP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | N | 0.8 | PCI/L | 3.4999 | 2017-01-18 | WTP2 | 0.4 | 1.4999 |  |  | BAHAMA WP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | N | 1.1 | PCI/L | 2.4999 | 2017-01-18 | WTP2 | 0.7 | 1.4999 |  |  | BAHAMA WP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0.0048 | MG/L | 0.0549 | 2017-01-18 | WTP2 | 0.00024 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP2 | 3e-05 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 4.4 | MG/L | 250.4999 | 2017-01-18 | WTP2 | 0.52 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0.011 | MG/L | 5.4999 | 2017-01-18 | WTP2 | 0.002 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-01-18 | WTP2 | 5 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-01-18 | WTP2 | 1 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.94 | LN(10) |  | 2017-01-18 | WTP2 |  |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 10 | MG/L | 500.4999 | 2017-01-18 | WTP2 | 10 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-01-18 | WTP2 | 0.04 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-01-18 | WTP2 | 0.38 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 20 | MG/L | 250.4999 | 2017-01-18 | WTP1 | 0.78 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-01-18 | WTP1 | 0.0025 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.24 | MG/L | 2.0499 | 2017-01-18 | WTP1 | 0.075 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP2 | 0.25 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-01-18 | WTP2 | 0.24 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-01-18 | WTP2 | 0.23 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP2 | 0.13 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-01-18 | WTP2 | 0.18 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP2 | 0.38 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP2 | 0.27 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP2 | 0.21 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP2 | 0.24 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP2 | 0.15 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP2 | 0.31 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP2 | 0.35 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP2 | 0.3 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP2 | 0.17 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP2 | 0.15 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-01-18 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-01-18 | WTP2 | 0.21 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP2 | 0.14 | 0.5499 |  |  | 3YR VOC/BAHAMA WP3 (CIS-1 2 IS OVER HOLDING TIME WITH Q QUALIFIER UNACCEPTABLE REVISION IN OC-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP2 | 0.0069 | 0.0149 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP2 | 0.0071 | 0.0249 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-01-18 | WTP2 | 0.0068 | 0.1499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP2 | 0.12 | 1.4999 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP2 | 1 | 1.4999 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-01-18 | WTP2 | 7.6 | 0.4499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP2 | 1.2 | 9.4999 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-01-18 | WTP2 | 6.5 | 6.4999 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-01-18 | WTP2 | 0.95 | 0.6499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP2 | 0.57 | 2.4999 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-01-18 | WTP2 | 0.19 | 0.0749 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-01-18 | WTP2 | 1.5 | 0.6499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-01-18 | WTP2 | 0.23 | 0.1499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-01-18 | WTP2 | 0.86 | 0.2499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-01-18 | WTP2 | 0.012 | 0.1499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-01-18 | WTP2 | 0.28 | 0.9499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP2 | 0.16 | 0.1499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP2 | 0.26 | 0.2499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-01-18 | WTP2 | 0.006 | 0.0449 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP2 | 0.0052 | 0.0249 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP2 | 1.5 | 0.1499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-01-18 | WTP2 | 0.32 | 0.2499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP2 | 0.0063 | 0.1499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP2 | 0.096 | 0.0249 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP2 | 0.069 | 0.0449 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-01-18 | WTP2 | 0.11 | 0.1499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP2 | 0.006 | 0.0249 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-01-18 | WTP2 | 0.0062 | 0.0149 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP2 | 0.053 | 0.2499 |  |  | 1Q SOC/BAHAMA WP3 (2AM/2039-WP1 TUSKAWILLA IS DUE 2Q'17>EM 4/26/16 TO WAYLON)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP1 | 0.0069 | 0.0149 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP1 | 0.0071 | 0.0249 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-01-18 | WTP1 | 0.0068 | 0.1499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP1 | 0.12 | 1.4999 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP1 | 1 | 1.4999 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-01-18 | WTP1 | 7.6 | 0.4499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP1 | 1.2 | 9.4999 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-01-18 | WTP1 | 6.5 | 6.4999 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-01-18 | WTP1 | 0.95 | 0.6499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP1 | 0.57 | 2.4999 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-01-18 | WTP1 | 0.19 | 0.0749 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-01-18 | WTP1 | 1.5 | 0.6499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-01-18 | WTP1 | 0.23 | 0.1499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-01-18 | WTP1 | 0.86 | 0.2499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP3 | 0.24 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP3 | 0.15 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP3 | 0.31 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP1 | 0.26 | 0.2499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-01-18 | WTP1 | 0.006 | 0.0449 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP1 | 0.0052 | 0.0249 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP1 | 1.5 | 0.1499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-01-18 | WTP1 | 0.32 | 0.2499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP1 | 0.0063 | 0.1499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP1 | 0.096 | 0.0249 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP1 | 0.069 | 0.0449 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-01-18 | WTP1 | 0.11 | 0.1499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP1 | 0.006 | 0.0249 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-01-18 | WTP1 | 0.0062 | 0.0149 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP1 | 0.053 | 0.2499 |  |  | 1Q SOC/SHEOAH WP2 (2042 HEX...J4: MS 188% RECOV - BIASED HIGH LCS & LCSD OK. SINCE BIASED HIGH & BDL RESULT IS ACCEPTABLE-BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-01-18 | WTP1 | 2.2 |  |  |  | SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | N | 0.6 | PCI/L | 3.4999 | 2017-01-18 | WTP1 | 0.4 | 1.4999 |  |  | SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | N | 1 | PCI/L | 2.4999 | 2017-01-18 | WTP1 | 0.7 | 1.4999 |  |  | SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-01-18 | WTP2 | 8e-05 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.011 | MG/L | 2.4999 | 2017-01-18 | WTP2 | 0.00028 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-01-18 | WTP2 | 0.00032 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP2 | 0.0005 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-01-18 | WTP2 | 0.0048 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.28 | MG/L | 4.0499 | 2017-01-18 | WTP2 | 0.075 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-01-18 | WTP2 | 0.00024 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-01-18 | WTP2 | 1e-05 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP2 | 0.0011 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-01-18 | WTP2 | 0.00058 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 15 | MG/L | 160.4999 | 2017-01-18 | WTP2 | 0.16 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-01-18 | WTP2 | 5e-05 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-01-18 | WTP2 | 0.00013 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-01-18 | WTP2 | 6e-05 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-01-18 | WTP2 | 0.051 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-01-18 | WTP2 | 0.053 |  |  |  | BAHAMA WP3 (MERCURY 0.000012 PWS ENT'D AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-01-18 | WTP2 | 0.061 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 22 | MG/L | 250.4999 | 2017-01-18 | WTP2 | 0.78 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0.0029 | MG/L | 1.4999 | 2017-01-18 | WTP2 | 0.0025 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.28 | MG/L | 2.0499 | 2017-01-18 | WTP2 | 0.075 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0.033 | MG/L | 0.3499 | 2017-01-18 | WTP2 | 0.03 |  |  |  | BAMAHA WP3 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP3 | 0.069 | 0.0449 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-01-18 | WTP3 | 0.11 | 0.1499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP3 | 0.006 | 0.0249 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-01-18 | WTP3 | 0.0062 | 0.0149 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP3 | 0.053 | 0.2499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.9 | PCI/L | 15.4999 | 2017-01-18 | WTP3 | 1.3 |  |  |  | TUSKAWILLA WP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | N | 1.4 | PCI/L | 3.4999 | 2017-01-18 | WTP3 | 0.4 | 1.4999 |  |  | TUSKAWILLA WP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-01-18 | WTP3 | 0.7 | 1.4999 |  |  | TUSKAWILLA WP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-01-18 | WTP1 | 0.051 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-01-18 | WTP1 | 0.053 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-01-18 | WTP1 | 8e-05 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.0085 | MG/L | 2.4999 | 2017-01-18 | WTP1 | 0.00028 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-01-18 | WTP1 | 0.00032 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP1 | 0.0005 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-01-18 | WTP1 | 0.0048 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.24 | MG/L | 4.0499 | 2017-01-18 | WTP1 | 0.075 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-01-18 | WTP1 | 0.00024 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-01-18 | WTP1 | 1e-05 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP1 | 0.0011 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-01-18 | WTP1 | 0.00058 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 14 | MG/L | 160.4999 | 2017-01-18 | WTP1 | 0.16 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-01-18 | WTP1 | 5e-05 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-01-18 | WTP1 | 0.00013 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-01-18 | WTP1 | 6e-05 |  |  |  | SHEOAH WP2 (MERCURY -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-01-18 | WTP1 | 0.061 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-01-18 | WTP3 | 0.0048 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | N | 0.31 | MG/L | 4.0499 | 2017-01-18 | WTP3 | 0.075 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-01-18 | WTP3 | 0.00024 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-01-18 | WTP1 | 0.03 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0.0021 | MG/L | 0.0549 | 2017-01-18 | WTP1 | 0.00024 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP1 | 3e-05 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 4.6 | MG/L | 250.4999 | 2017-01-18 | WTP1 | 0.52 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0.011 | MG/L | 5.4999 | 2017-01-18 | WTP1 | 0.002 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-01-18 | WTP1 | 5 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-01-18 | WTP1 | 1 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.03 | LN(10) |  | 2017-01-18 | WTP1 |  |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 180 | MG/L | 500.4999 | 2017-01-18 | WTP1 | 10 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-01-18 | WTP1 | 0.04 |  |  |  | SHEOAH WP2 (PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP1 | 0.2 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP1 | 0.29 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-01-18 | WTP1 | 0.38 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP1 | 0.25 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-01-18 | WTP1 | 0.24 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-01-18 | WTP1 | 0.23 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP1 | 0.13 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-01-18 | WTP1 | 0.18 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP1 | 0.38 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP1 | 0.27 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP1 | 0.21 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP1 | 0.24 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP1 | 0.15 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP1 | 0.31 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP1 | 0.35 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP1 | 0.3 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP1 | 0.17 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP1 | 0.15 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-01-18 | WTP1 | 0.2 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-01-18 | WTP1 | 0.21 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP1 | 0.14 | 0.5499 |  |  | 3YR VOC/SHEOAH WP2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-01-18 | WTP3 | 0.00058 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1052 | SODIUM | N | 33 | MG/L | 160.4999 | 2017-01-18 | WTP3 | 0.16 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-01-18 | WTP3 | 5e-05 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-01-18 | WTP3 | 0.00013 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-01-18 | WTP3 | 6e-05 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-01-18 | WTP3 | 0.061 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | N | 57 | MG/L | 250.4999 | 2017-01-18 | WTP3 | 0.78 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1022 | COPPER | N | 0.019 | MG/L | 1.4999 | 2017-01-18 | WTP3 | 0.0025 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | N | 0.31 | MG/L | 2.0499 | 2017-01-18 | WTP3 | 0.075 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-01-18 | WTP3 | 0.03 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-01-18 | WTP3 | 0.00024 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP3 | 3e-05 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1055 | SULFATE | N | 13 | MG/L | 250.4999 | 2017-01-18 | WTP3 | 0.52 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1095 | ZINC | N | 0.019 | MG/L | 5.4999 | 2017-01-18 | WTP3 | 0.002 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-01-18 | WTP3 | 5 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-01-18 | WTP3 | 1 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.98 | LN(10) |  | 2017-01-18 | WTP3 |  |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 250 | MG/L | 500.4999 | 2017-01-18 | WTP3 | 10 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-01-18 | WTP3 | 0.04 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) PH HAS Q QUALIFIER - THE ONLY ACCEPTABLE "CHEMICAL" WITH A Q QUALIFIER IS PH - HQS ALLOWED ACCEPTANCE OF A PH WITH A Q QUALIFIER YEARS AGO - BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP3 | 0.2 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP3 | 0.29 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-01-18 | WTP3 | 0.38 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP3 | 0.25 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-01-18 | WTP3 | 0.24 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-01-18 | WTP3 | 0.23 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP3 | 0.13 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-01-18 | WTP3 | 0.18 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP3 | 0.38 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP3 | 0.27 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP3 | 0.21 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-01-18 | WTP3 | 1e-05 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-01-18 | WTP3 | 0.0011 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.57 | UG/L | 60.4999 | 2017-01-18 | L1 | 0.2 |  | 1 |  | 1626 WRENTHAM CT. (3/17 LRAA/T=100.5775 LRAA/H=24.5575) 3/17 L1 OE VALUE/T REPORTED ON DBF = 96.77 (96.7675).
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 97.87 | UG/L | 80.4999 | 2017-01-18 | L1 | 0.14 |  | 1 |  | 1626 WRENTHAM CT. (3/17 LRAA/T=100.5775 LRAA/H=24.5575) 3/17 L1 OE VALUE/T REPORTED ON DBF = 96.77 (96.7675).
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.7 | UG/L | 60.4999 | 2017-01-18 | L2 | 0.2 |  | 2 | 1.2 | 606 MORGAN (3/17 LRAA/T=78.1225 LRAA/H=20.925)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 75.13 | UG/L | 80.4999 | 2017-01-18 | L2 | 0.14 |  | 2 | 1.2 | 606 MORGAN (3/17 LRAA/T=78.1225 LRAA/H=20.925)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.46 | UG/L | 60.4999 | 2017-01-18 | L3 | 0.2 |  | 3 | 1.4 | 674 ONEIDA LN. (3/17 LRAA/T=92.965 LRAA/H=22.065) 3/17 L3 OE VALUE/T REPORTED ON DBF = 88.98 (88.9825).
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 84.36 | UG/L | 80.4999 | 2017-01-18 | L3 | 0.14 |  | 3 | 1.4 | 674 ONEIDA LN. (3/17 LRAA/T=92.965 LRAA/H=22.065) 3/17 L3 OE VALUE/T REPORTED ON DBF = 88.98 (88.9825).
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.29 | UG/L | 60.4999 | 2017-01-18 | L4 | 0.2 |  | 4 | 1.4 | 410 SANDRINGHAM CT. (3/17 LRAA/T=62.3575 LRAA/H=28.5925)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 63.91 | UG/L | 80.4999 | 2017-01-18 | L4 | 0.14 |  | 4 | 1.4 | 410 SANDRINGHAM CT. (3/17 LRAA/T=62.3575 LRAA/H=28.5925)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-01-18 | WTP3 | 0.35 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP3 | 0.3 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP3 | 0.17 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP3 | 0.15 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-01-18 | WTP3 | 0.2 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-01-18 | WTP3 | 0.21 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP3 | 0.14 | 0.5499 |  |  | 3YR VOC/TUSKAWILLA WP1 (NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP3 | 0.0069 | 0.0149 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP3 | 0.0071 | 0.0249 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-01-18 | WTP3 | 0.0068 | 0.1499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP3 | 0.12 | 1.4999 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP3 | 1 | 1.4999 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-01-18 | WTP3 | 7.6 | 0.4499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-01-18 | WTP3 | 1.2 | 9.4999 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-01-18 | WTP3 | 6.5 | 6.4999 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-01-18 | WTP3 | 0.95 | 0.6499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-01-18 | WTP3 | 0.57 | 2.4999 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-01-18 | WTP3 | 0.19 | 0.0749 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-01-18 | WTP3 | 1.5 | 0.6499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-01-18 | WTP3 | 0.23 | 0.1499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-01-18 | WTP3 | 0.86 | 0.2499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-01-18 | WTP3 | 0.012 | 0.1499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-01-18 | WTP3 | 0.28 | 0.9499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-01-18 | WTP3 | 0.16 | 0.1499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-01-18 | WTP3 | 0.26 | 0.2499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-01-18 | WTP3 | 0.006 | 0.0449 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP3 | 0.0052 | 0.0249 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-01-18 | WTP3 | 1.5 | 0.1499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-01-18 | WTP3 | 0.32 | 0.2499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-01-18 | WTP3 | 0.0063 | 0.1499 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-01-18 | WTP3 | 0.096 | 0.0249 |  |  | 1Q SOC/TUSKAWILLA WP1(NORTHERN WAY)EDB HAS J4:MS 59% RECOV-BIASED LOW(AT 100% RSLT WD STILL BE < MCL & WD NOT EXCEED RDL OF 0.01~0.0149)LCS 89% RECOV LCSD 97% RECOV(LCS & LCSD OK) EDB OK
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-01-18 | WTP3 | 0.051 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-01-18 | WTP3 | 0.053 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-01-18 | WTP3 | 8e-05 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1010 | BARIUM | N | 0.012 | MG/L | 2.4999 | 2017-01-18 | WTP3 | 0.00028 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-01-18 | WTP3 | 0.00032 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | N | 0.0007 | MG/L | 0.1499 | 2017-01-18 | WTP3 | 0.0005 |  |  |  | TUSKAWILLA WP1 (NORTHERN WAY) MERCURY 0.000020 (PWS ENTERS IT AS -0-)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 1.3 | UG/L | 74.9999 | 2017-02-20 | WTP2 | 0.32 | 0.5499 |  |  | 8AM/CIS-1 2-WP3 BAHAMA 1Q 2017 (9AM/CIS-1 2-WP3 BAHAMA 1Q 2018) THIS CIS-1 2 1.3 UG/L >RDL OF 0.5. MUST CONTINUE AM/CIS-1 2 FOR AT LEAST 3 MORE YRS-2018 2019 2020 - BB/BW
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.96 | UG/L | 60.4999 | 2017-04-11 | L1 | 0.5 |  | 1 | 0.4 | 1626 WRENTHAM (6/17 LRAA/T=94.0325 LRAA/H=23.98) 6/17 OE VALUE/T = 85.42 (6/17 QTR OE REPORT RCVD FOR TTHMS FOR WRENTHAM SITE)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 86.93 | UG/L | 80.4999 | 2017-04-11 | L1 | 0.14 |  | 1 | 0.4 | 1626 WRENTHAM (6/17 LRAA/T=94.0325 LRAA/H=23.98) 6/17 OE VALUE/T = 85.42 (6/17 QTR OE REPORT RCVD FOR TTHMS FOR WRENTHAM SITE)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.43 | UG/L | 60.4999 | 2017-04-11 | L2 | 0.5 |  | 2 | 1 | 606 MORGAN (6/17 LRAA/T=76.1175 LRAA/H=21.3625) 6/17 OE VALUE/T = 74.675 (NO 6/17 OE REPORT NDD FOR MORGAN SITE)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 77.01 | UG/L | 80.4999 | 2017-04-11 | L2 | 0.14 |  | 2 | 1 | 606 MORGAN (6/17 LRAA/T=76.1175 LRAA/H=21.3625) 6/17 OE VALUE/T = 74.675 (NO 6/17 OE REPORT NDD FOR MORGAN SITE)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-11 | WTP3 | 1.5 | 0.6499 |  |  | 2AM/2039-WP1 TUSKAWILLA (3AM/2039-WP1 TUSKAWILLA 2Q'18) PER NEW 4/17 SOP THESE RSLTS PLACED IN FINAL CHEM HOLDING FOLDER ON 5/31/17-BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 84.57 | UG/L | 80.4999 | 2017-04-11 | L3 | 0.14 |  | 3 | 0.3 | 674 ONEIDA LN. (6/17 LRAA/T=89.035 LRAA/H=21.37) 6/17 OE VALUE/T = 82.465 (6/17 OE REPORT RCVD FOR TTHMS FOR ONEIDA SITE)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.47 | UG/L | 60.4999 | 2017-04-11 | L4 | 0.5 |  | 4 | 1.2 | 410 SANDRINGHAM(6/17LRAA/T=61.02 LRAA/H=26.7475)6/17 OE VAL/T=60.8075(NO 6/17 OE RPRT NDD FOR SANDRINGHAM SITE)5/4/17 PN(DATED AT BOTTOM)RCVD ON FTP WEBSITE.NO COD YET.HYPRLNKD RSLTS 6/7/17>BW W/PN-BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 60.84 | UG/L | 80.4999 | 2017-04-11 | L4 | 0.14 |  | 4 | 1.2 | 410 SANDRINGHAM(6/17LRAA/T=61.02 LRAA/H=26.7475)6/17 OE VAL/T=60.8075(NO 6/17 OE RPRT NDD FOR SANDRINGHAM SITE)5/4/17 PN(DATED AT BOTTOM)RCVD ON FTP WEBSITE.NO COD YET.HYPRLNKD RSLTS 6/7/17>BW W/PN-BB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.89 | UG/L | 60.4999 | 2017-04-11 | L3 | 0.5 |  | 3 | 0.3 | 674 ONEIDA LN. (6/17 LRAA/T=89.035 LRAA/H=21.37) 6/17 OE VALUE/T = 82.465 (6/17 OE REPORT RCVD FOR TTHMS FOR ONEIDA SITE)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 66.89 | UG/L | 80.4999 | 2017-07-26 | L4 | 0.14 |  | 4 | 0.3 | 410 SANDRINGHAM CT. (9/17 LRAA/T=62.32 LRAA/H=26.7475) 2453 BROM ACID J4 QUAL: MS 141% RECOV. LCS OK BIASED HIGH OK-ACCEPTABLE. NO OE EXCEEDANCES THIS SITE.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.64 | UG/L | 60.4999 | 2017-07-26 | L4 | 0.5 |  | 4 | 0.3 | 410 SANDRINGHAM CT. (9/17 LRAA/T=62.32 LRAA/H=26.7475) 2453 BROM ACID J4 QUAL: MS 141% RECOV. LCS OK BIASED HIGH OK-ACCEPTABLE. NO OE EXCEEDANCES THIS SITE.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 89.2 | UG/L | 80.4999 | 2017-07-26 | L3 | 0.14 |  | 3 | 0.4 | 674 ONEIDA LN. (9/17 LRAA/T=83.6225 LRAA/H=23.5475) 9/17 OE VAL/T=86.8325 OE VAL/H LOW (RCVD 9/17 OE REPORT FOR TTHMS FOR THIS SITE-IN OC)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 46.1 | UG/L | 80.4999 | 2017-07-26 | L2 | 0.14 |  | 2 | 1.2 | 606 MORGAN (9/17 LRAA/T=66.9475 LRAA/H=19.3775) NO OE EXCEEDANCES FOR THIS SITE
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.86 | UG/L | 60.4999 | 2017-07-26 | L3 | 0.5 |  | 3 | 0.4 | 674 ONEIDA LN. (9/17 LRAA/T=83.6225 LRAA/H=23.5475) 9/17 OE VAL/T=86.8325 OE VAL/H LOW (RCVD 9/17 OE REPORT FOR TTHMS FOR THIS SITE-IN OC)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.75 | UG/L | 60.4999 | 2017-07-26 | L2 | 0.5 |  | 2 | 1.2 | 606 MORGAN (9/17 LRAA/T=66.9475 LRAA/H=19.3775) NO OE EXCEEDANCES FOR THIS SITE
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 99.49 | UG/L | 80.4999 | 2017-07-26 | L1 | 0.14 |  | 1 | 0.9 | 1626 WRENTHAM (9/17 LRAA/T=88.56 LRAA/H=22.7075) 9/17 OE VAL/T=95.945 (OE VAL/H LOW) RCVD OE REPORT L1 SITE FOR TTHMS-IN OC.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.06 | UG/L | 60.4999 | 2017-07-26 | L1 | 0.5 |  | 1 | 0.9 | 1626 WRENTHAM (9/17 LRAA/T=88.56 LRAA/H=22.7075) 9/17 OE VAL/T=95.945 (OE VAL/H LOW) RCVD OE REPORT L1 SITE FOR TTHMS-IN OC.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.9 | UG/L | 60.4999 | 2017-09-06 | L3 |  |  | 3 | 0.3 | TTHM LRAA = 74.52 HAA5 LRAA = 20.8 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 18.4 | UG/L | 80.4999 | 2017-09-06 | L2 |  |  | 2 | 1.3 | TTHM LRAA = 63.48 HAA5 LRAA = 18.57 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.35 | UG/L | 60.4999 | 2017-09-06 | L2 |  |  | 2 | 1.3 | TTHM LRAA = 63.48 HAA5 LRAA = 18.57 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 82.12 | UG/L | 80.4999 | 2017-09-06 | L4 |  |  | 4 | 0.9 | TTHM LRAA = 64.22 HAA5 LRAA = 27.39 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.14 | UG/L | 60.4999 | 2017-09-06 | L1 |  |  | 1 | 0.4 | TTHM LRAA = 83.7 HAA5 LRAA = 21.71 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 16.39 | UG/L | 80.4999 | 2017-09-06 | L3 |  |  | 3 | 0.3 | TTHM LRAA = 74.52 HAA5 LRAA = 20.8 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.84 | UG/L | 60.4999 | 2017-09-06 | L4 |  |  | 4 | 0.9 | TTHM LRAA = 64.22 HAA5 LRAA = 27.39 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 60.61 | UG/L | 80.4999 | 2017-09-06 | L1 |  |  | 1 | 0.4 | TTHM LRAA = 83.7 HAA5 LRAA = 21.71 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.95 | UG/L | 60.4999 | 2017-10-17 | L1 |  |  | 1 | 0.6 | LRAA TTHM = 82.31 LRAA HAA5 = 21.39 NO OE EXCEEDANCES_JMF (12/19/17 OE REPORT RCVD FOR TTHMS 73.94 BUT ONE WAS NOT RQRD - IN OC) PN IN OC FOR 82.31 TTHMS - WRENTHAM SITE-NO COD RCVD W/IT
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 64.39 | UG/L | 80.4999 | 2017-10-17 | L1 |  |  | 1 | 0.6 | LRAA TTHM = 82.31 LRAA HAA5 = 21.39 NO OE EXCEEDANCES_JMF (12/19/17 OE REPORT RCVD FOR TTHMS 73.94 BUT ONE WAS NOT RQRD - IN OC) PN IN OC FOR 82.31 TTHMS - WRENTHAM SITE-NO COD RCVD W/IT
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.73 | UG/L | 60.4999 | 2017-10-17 | L2 |  |  | 2 | 1 | TTHM LRAA = 53.52 HAA5 LRAA = 15.85 NO OE EXCEEDANCES_JMF (ON 12/19/17 REVISED TTHMS 29.39 TO 29.69 REVISED TTHMS LRAA 53.44 TO 53.52 - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 29.69 | UG/L | 80.4999 | 2017-10-17 | L2 |  |  | 2 | 1 | TTHM LRAA = 53.52 HAA5 LRAA = 15.85 NO OE EXCEEDANCES_JMF (ON 12/19/17 REVISED TTHMS 29.39 TO 29.69 REVISED TTHMS LRAA 53.44 TO 53.52 - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.91 | UG/L | 60.4999 | 2017-10-17 | L3 |  |  | 3 | 0.4 | TTHM LRAA = 64.95 HAA5 LRAA = 18.28 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 55.94 | UG/L | 80.4999 | 2017-10-17 | L4 |  |  | 4 | 0.4 | TTHM LRAA = 63.79 HAA5 LRAA = 24.48 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.95 | UG/L | 60.4999 | 2017-10-17 | L4 |  |  | 4 | 0.4 | TTHM LRAA = 63.79 HAA5 LRAA = 24.48 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 38.1 | UG/L | 80.4999 | 2017-10-17 | L3 |  |  | 3 | 0.4 | TTHM LRAA = 64.95 HAA5 LRAA = 18.28 NO OE EXCEEDANCES_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 46.59 | UG/L | 80.4999 | 2018-01-08 | L1 | 0.14 |  | 1 | 1 | 1626 WRENTHAM LRAA T=69.49
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 62.61 | UG/L | 80.4999 | 2018-01-08 | L4 | 0.14 |  | 4 | 0.6 | 410 SANDRINGHAM (HYPERLINKED TO BW 2/20/18 - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.17 | UG/L | 60.4999 | 2018-01-08 | L4 | 0.5 |  | 4 | 0.6 | 410 SANDRINGHAM (HYPERLINKED TO BW 2/20/18 - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.01 | UG/L | 80.4999 | 2018-01-08 | L3 | 0.14 |  | 3 | 1.5 | 674 ONEIDA LN.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.09 | UG/L | 60.4999 | 2018-01-08 | L3 | 0.5 |  | 3 | 1.5 | 674 ONEIDA LN.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.91 | UG/L | 80.4999 | 2018-01-08 | L2 | 0.14 |  | 2 | 1.4 | 606 MORGAN ST.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.75 | UG/L | 60.4999 | 2018-01-08 | L2 | 0.5 |  | 2 | 1.4 | 606 MORGAN ST.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.02 | UG/L | 60.4999 | 2018-01-08 | L1 | 0.5 |  | 1 | 1 | 1626 WRENTHAM LRAA T=69.49
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0.86 | UG/L | 74.9999 | 2018-01-24 | WTP2 | 0.32 | 0.5499 |  |  | 9AM/CIS-1 2-WP3 BAHAMA (0.86)**10AM/CIS-1 2-WP3 BAHAMA DUE 1Q 2019**(THERE WAS TALLAHASSEE INTEREST IN VOCS IN 2015 FOR W.S.&CASSELBERRY-CK WITH TALLAH BEFORE ENDING ANY SPECIAL TESTING OR ANN. MONIT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-24 | WTP3 | 0.051 |  |  |  | TUSKAWILLA WP1 NN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-24 | WTP3 | 0.053 |  |  |  | TUSKAWILLA WP1 NN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-24 | WTP1 | 0.051 |  |  |  | SHEOAH WP2 NN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-24 | WTP1 | 0.053 |  |  |  | SHEOAH WP2 NN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2018-01-24 | WTP2 | 0.051 |  |  |  | BAHAMA WP3 NN (NN-3 WPS RCVD 2/20/18 ENTD 3/5/18 - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-24 | WTP2 | 0.053 |  |  |  | BAHAMA WP3 NN (NN-3 WPS RCVD 2/20/18 ENTD 3/5/18 - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-01-24 | WTP3 | 0.28 | 0.9499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-01-24 | WTP3 | 0.16 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP3 | 0.26 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-01-24 | WTP3 | 0.006 | 0.0449 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP3 | 0.0052 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-01-24 | WTP3 | 1.5 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-01-24 | WTP3 | 0.32 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-01-24 | WTP3 | 0.0063 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP3 | 0.096 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-01-24 | WTP3 | 0.069 | 0.0449 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-01-24 | WTP3 | 0.11 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP3 | 0.006 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-01-24 | WTP3 | 0.0062 | 0.0149 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP3 | 0.053 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP3 | 0.0069 | 0.0149 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP3 | 0.0071 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-01-24 | WTP3 | 0.0068 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-01-24 | WTP3 | 0.12 | 1.4999 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-01-24 | WTP3 | 1 | 1.4999 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-01-24 | WTP3 | 7.6 | 0.4499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-01-24 | WTP3 | 1.8 | 9.4999 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-01-24 | WTP3 | 6.5 | 6.4999 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-01-24 | WTP3 | 0.95 | 0.6499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-01-24 | WTP3 | 0.57 | 2.4999 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-01-24 | WTP3 | 0.19 | 0.0749 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-01-24 | WTP3 | 1.5 | 0.6499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-01-24 | WTP3 | 0.23 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-01-24 | WTP3 | 0.86 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-01-24 | WTP3 | 0.012 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-01-24 | WTP1 | 0.0068 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-01-24 | WTP1 | 0.12 | 1.4999 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-01-24 | WTP1 | 1 | 1.4999 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-01-24 | WTP1 | 7.6 | 0.4499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-01-24 | WTP1 | 1.8 | 9.4999 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-01-24 | WTP1 | 6.5 | 6.4999 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-01-24 | WTP1 | 0.95 | 0.6499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-01-24 | WTP1 | 0.57 | 2.4999 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-01-24 | WTP1 | 0.19 | 0.0749 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-01-24 | WTP1 | 1.5 | 0.6499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-01-24 | WTP1 | 0.23 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-01-24 | WTP1 | 0.86 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-01-24 | WTP1 | 0.012 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-01-24 | WTP1 | 0.28 | 0.9499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-01-24 | WTP1 | 0.16 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP1 | 0.26 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-01-24 | WTP1 | 0.006 | 0.0449 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP1 | 0.0052 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-01-24 | WTP1 | 1.5 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-01-24 | WTP1 | 0.32 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-01-24 | WTP1 | 0.0063 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP1 | 0.096 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-01-24 | WTP1 | 0.069 | 0.0449 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-01-24 | WTP1 | 0.11 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP1 | 0.006 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-01-24 | WTP1 | 0.0062 | 0.0149 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP1 | 0.053 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP2 | 0.0069 | 0.0149 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP2 | 0.0071 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-01-24 | WTP2 | 0.0068 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-01-24 | WTP2 | 0.12 | 1.4999 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 1.8 | UG/L | 249.9999 | 2018-01-24 | WTP2 | 1 | 1.4999 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-01-24 | WTP2 | 7.6 | 0.4499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-01-24 | WTP2 | 1.8 | 9.4999 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-01-24 | WTP2 | 6.5 | 6.4999 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-01-24 | WTP2 | 0.95 | 0.6499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-01-24 | WTP2 | 0.57 | 2.4999 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-01-24 | WTP2 | 0.19 | 0.0749 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-01-24 | WTP2 | 1.5 | 0.6499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-01-24 | WTP2 | 0.23 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-01-24 | WTP2 | 0.86 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-01-24 | WTP2 | 0.012 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-01-24 | WTP2 | 0.28 | 0.9499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-01-24 | WTP2 | 0.16 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP2 | 0.26 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-01-24 | WTP2 | 0.006 | 0.0449 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP2 | 0.0052 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-01-24 | WTP2 | 1.5 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-01-24 | WTP2 | 0.32 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-01-24 | WTP2 | 0.0063 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP2 | 0.096 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-01-24 | WTP2 | 0.069 | 0.0449 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-01-24 | WTP2 | 0.11 | 0.1499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP2 | 0.006 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-01-24 | WTP2 | 0.0062 | 0.0149 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP2 | 0.053 | 0.2499 |  |  | LATE 2Q SOCS FOR 2017/WP3 BAHAMA BLVD. (DALAPON 1.8 >RDL OF 1 - 2QM/DAL DUE 6/18 3QM DUE 9/18 4QM DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-01-24 | WTP1 | 0.0069 | 0.0149 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-01-24 | WTP1 | 0.0071 | 0.0249 |  |  | LATE 2Q SOCS FOR 2017/WP2 SHEOAH BLVD.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.3 | UG/L | 60.4999 | 2018-04-03 | L1 | 0.5 |  | 1 | 1.2 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 63.27 | UG/L | 80.4999 | 2018-04-03 | L1 | 0.14 |  | 1 | 1.2 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.49 | UG/L | 60.4999 | 2018-04-03 | L2 | 0.5 |  | 2 | 1.1 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 41.82 | UG/L | 80.4999 | 2018-04-03 | L2 | 0.14 |  | 2 | 1.1 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.77 | UG/L | 60.4999 | 2018-04-03 | L3 | 0.5 |  | 3 | 1.2 | 674 ONEIDA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 41.3 | UG/L | 80.4999 | 2018-04-03 | L3 | 0.14 |  | 3 | 1.2 | 674 ONEIDA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-04-03 | WTP3 | 1.5 | 0.6499 |  |  | 3AM/2039-WP1 TUSKAWILLA 2Q'18 (MAY STOP AM/2039-WP1 TUSKAWILLA) LAST 3 YRS -0- (HLK'D TO RLB 5/14/18 TO NOTIFY SYS. - BB)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.05 | UG/L | 60.4999 | 2018-04-03 | L4 | 0.5 |  | 4 | 1.4 | 410 SANDRINGHAM (6/18 DISINF BYP REPORT W/RSLTS)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.82 | UG/L | 80.4999 | 2018-04-03 | L4 | 0.14 |  | 4 | 1.4 | 410 SANDRINGHAM (6/18 DISINF BYP REPORT W/RSLTS)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-04-03 | WTP2 | 1 | 1.4999 |  |  | 2QM/DAL-WP3 BAHAMA BLVD (3QM/DAL-WP3 BAHAMA BLVD DUE 9/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.17 | UG/L | 60.4999 | 2018-07-02 | L4 |  |  |  | 0.99 | STG 1 MRT WP3 410 SANDRINGHAM (SEE SCREEN 3/3 NOTES ON SAMPLING LOCATION FOR 674 ONEIDA)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 72.88 | UG/L | 80.4999 | 2018-07-02 | L4 |  |  |  | 0.99 | STG 1 MRT WP3 410 SANDRINGHAM (SEE SCREEN 3/3 NOTES ON SAMPLING LOCATION FOR 674 ONEIDA)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 32.67 | UG/L | 80.4999 | 2018-07-02 | L2 |  |  |  | 0.66 | SM-4 606 MORGAN {**SEE SCREEN 3/3 FOR DBP LOCATION MIX-UP**}JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.38 | UG/L | 60.4999 | 2018-07-02 | L2 |  |  |  | 0.66 | SM-4 606 MORGAN {**SEE SCREEN 3/3 FOR DBP LOCATION MIX-UP**}JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.77 | UG/L | 80.4999 | 2018-07-02 | L1 |  |  |  | 0.22 | SM-6 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.05 | UG/L | 60.4999 | 2018-07-02 | L1 |  |  |  | 0.22 | SM-6 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 1.5 | UG/L | 249.9999 | 2018-07-02 | WTP2 | 1 | 1.4999 |  |  | 3QM/DAL-WP3 BAHAMA BLVD. (4QM/DAL-WP3 BAHAMA BLVD. DUE 12/18)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 35.52 | UG/L | 80.4999 | 2018-08-02 | L3 | 0.39 |  | 1 | 1.5 | 674 ONEIDA LN. (SEE SCREEN 3/3 NOTES ON SAMPLING LOCATION FOR 674 ONEIDA) HLKD 8-24-18 - SYSTEM SHOULD TEST 12/18 QTR PER APPROVED 7/17/18 STG2 PLAN IN OCULUS.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.32 | UG/L | 60.4999 | 2018-08-02 | L3 | 0.91 |  | 1 | 1.5 | 674 ONEIDA LN. (SEE SCREEN 3/3 NOTES ON SAMPLING LOCATION FOR 674 ONEIDA) HLKD 8-24-18 - SYSTEM SHOULD TEST 12/18 QTR PER APPROVED 7/17/18 STG2 PLAN IN OCULUS.
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 1.4 | UG/L | 249.9999 | 2018-10-02 | WTP2 |  | 1.4999 |  |  | 4QM- DAL WTP #3 BAHAMA RD. BEGIN AM DURING 1ST QTR 2019 2020 2021_JMF
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.45 | UG/L | 60.4999 | 2018-10-02 | L4 | 0.91 |  | 4 | 1.6 | 410 SANDRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 76.42 | UG/L | 80.4999 | 2018-10-02 | L4 | 1 |  | 4 | 1.6 | 410 SANDRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 62.55 | UG/L | 80.4999 | 2018-10-02 | L3 | 1 |  | 3 | 1.3 | 674 ONIEDA LN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.5 | UG/L | 60.4999 | 2018-10-02 | L3 | 0.91 |  | 3 | 1.3 | 674 ONIEDA LN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 96.8 | UG/L | 80.4999 | 2018-10-02 | L2 | 1 |  | 2 | 1.3 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.3 | UG/L | 60.4999 | 2018-10-02 | L2 | 0.91 |  | 2 | 1.3 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 75.08 | UG/L | 80.4999 | 2018-10-02 | L1 | 1 |  | 1 | 1.3 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.77 | UG/L | 60.4999 | 2018-10-02 | L1 | 0.91 |  | 1 | 1.3 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 31.76 | UG/L | 80.4999 | 2018-12-14 | L3 |  |  | 3 | 1.6 | 2950-STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.) / SUBCONTRACT LAB E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 38.88 | UG/L | 80.4999 | 2018-12-14 | L2 |  |  | 2 | 1.4 | 2950-SM-4 606 MORGAN / SUBCONTRACT LAB E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 31.5 | UG/L | 80.4999 | 2018-12-14 | L1 |  |  | 1 | 1.7 | 2950-SM-6 1626 WRENTHAM / SUBCONTRACT LAB E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 49.14 | UG/L | 80.4999 | 2018-12-14 | L4 |  |  | 4 | 1.2 | 2950-STG 1 MRT WP3 410 SANDRINGHAM / SUBCONTRACT LAB E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2019-01-03 | L4
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2019-01-03 | WTP2 |  |  |  |  | WTP2 - WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-01-03 | WTP2 |  |  |  |  | WTP2 - WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2019-01-03 | WTP3 |  |  |  |  | WTP3 - WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-01-03 | WTP3 |  |  |  |  | WTP3 - WP1 TUSKAWILLA
3590879 | WINTER SPRINGS CITY OF (3 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-01-03 | WTP2 | 0.32 | 0.5499 |  |  | 10 AM CIS-1 2-DICHLOROETHYLENE BAHAMA BLVD [CONTINUE ON AM 2020 2021]_VP
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.91 | UG/L | 60.4999 | 2019-01-03 | L4
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 38.59 | UG/L | 80.4999 | 2019-01-03 | L3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.73 | UG/L | 60.4999 | 2019-01-03 | L3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.4 | UG/L | 80.4999 | 2019-01-03 | L2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.54 | UG/L | 60.4999 | 2019-01-03 | L2
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.84 | UG/L | 60.4999 | 2019-01-03 | L1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 54.13 | UG/L | 80.4999 | 2019-01-03 | L1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 51.9 | UG/L | 80.4999 | 2019-01-03 | L4 | 0.39 |  | 4 | 1.8 | 410 SANRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.91 | UG/L | 60.4999 | 2019-01-03 | L4 | 0.5 |  | 4 | 1.8 | 410 SANRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 38.59 | UG/L | 80.4999 | 2019-01-03 | L3 | 0.39 |  | 3 | 1.1 | 674 ONEIDA LN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.73 | UG/L | 60.4999 | 2019-01-03 | L3 | 0.5 |  | 3 | 1.1 | 674 ONEIDA LN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 36.4 | UG/L | 80.4999 | 2019-01-03 | L2 | 0.39 |  | 2 | 1.8 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.54 | UG/L | 60.4999 | 2019-01-03 | L2 | 0.91 |  | 2 | 1.8 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 54.13 | UG/L | 80.4999 | 2019-01-03 | L1 | 0.39 |  | 1 | 1.7 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.84 | UG/L | 60.4999 | 2019-01-03 | L1 | 0.91 |  | 1 | 1.7 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | SOC | 2031 | DALAPON | N | 1.3 | UG/L | 249.9999 | 2019-01-03 | WTP2 |  | 1.4999 |  |  | 1AM OF DALAPON AT WP3 BAHAMA BLVD. - LATE REPORTING TO DEPARTMENT RCVD 5/6/19_RLB
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | D | 0.14 | MG/L | 10.4999 | 2019-01-03 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | D | 0 | MG/L | 1.4999 | 2019-01-03 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1040 | NITRATE | D | 0.14 | MG/L | 10.4999 | 2019-01-03 | WTP3
3590879 | WINTER SPRINGS CITY OF (3 WPS) | INOR | 1041 | NITRITE | D | 0 | MG/L | 1.4999 | 2019-01-03 | WTP1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.5 |  |  | 2019-01-16 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-16 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2019-01-16 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.8 |  |  | 2019-01-16 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-01-16 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-01-16 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2019-01-16 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-16 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 19.4 |  |  | 2019-01-16 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2019-01-28 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.17 | LN(10) |  | 2019-01-28 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 17.4 |  |  | 2019-01-28 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-01-28 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.3 |  |  | 2019-01-28 | WTP2 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 20.4 |  |  | 2019-01-28 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-01-28 | WTP2 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-01-28 | WTP2 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-01-28 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.08 | MG/L |  | 2019-02-09 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-09 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.27 | MG/L |  | 2019-02-09 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.15 | LN(10) |  | 2019-02-09 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 20.3 |  |  | 2019-02-09 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.8 |  |  | 2019-02-09 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-02-09 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.8 |  |  | 2019-02-09 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.19 | MG/L |  | 2019-02-09 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-02-21 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.9 |  |  | 2019-02-21 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.24 | MG/L |  | 2019-02-21 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.02 | MG/L |  | 2019-02-21 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23.9 |  |  | 2019-02-21 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-02-21 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-02-21 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-02-21 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.3 |  |  | 2019-02-21 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-06 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-06 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2019-03-06 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-03-06 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.2 |  |  | 2019-03-06 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-03-06 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.3 |  |  | 2019-03-06 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2019-03-06 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.5 |  |  | 2019-03-06 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-03-19 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2019-03-19 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.8 |  |  | 2019-03-19 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2019-03-19 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-03-19 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.6 |  |  | 2019-03-19 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-03-19 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2019-03-19 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.8 |  |  | 2019-03-19 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-04-02 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.5 | UG/L | 60.4999 | 2019-04-02 | L1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 58.45 | UG/L | 80.4999 | 2019-04-02 | L1
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.41 | MG/L |  | 2019-04-02 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.8 |  |  | 2019-04-02 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.3 | LN(10) |  | 2019-04-02 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.14 | MG/L |  | 2019-04-02 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.2 |  |  | 2019-04-02 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-04-02 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-04-02 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.6 |  |  | 2019-04-02 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 58.16 | UG/L | 80.4999 | 2019-04-02 | L4 |  |  | 4 | 2.07 | 2950-STG 1 MRT WP3 410 SANDRINGHAM / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.79 | UG/L | 60.4999 | 2019-04-02 | L4 |  |  | 4 | 2.07 | 2950-STG 1 MRT WP3 410 SANDRINGHAM / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 50.36 | UG/L | 80.4999 | 2019-04-02 | L3 |  |  | 3 | 1.21 | 2950-STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.) / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.32 | UG/L | 60.4999 | 2019-04-02 | L3 |  |  | 3 | 1.21 | 2950-STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.) / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 43.61 | UG/L | 80.4999 | 2019-04-02 | L2 |  |  | 2 | 1.56 | 2950-SM-4 606 MORGAN / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.7 | UG/L | 60.4999 | 2019-04-02 | L2 |  |  | 2 | 1.56 | 2950-SM-4 606 MORGAN / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 58.45 | UG/L | 80.4999 | 2019-04-02 | L1 |  |  | 1 | 1.16 | 2950-SM-6 1626 WRENTHAM / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.5 | UG/L | 60.4999 | 2019-04-02 | L1 |  |  | 1 | 1.16 | 2950-SM-6 1626 WRENTHAM / SUBCONTRACT LABS E84589 E82535
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.16 | MG/L |  | 2019-04-18 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-18 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2019-04-18 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.03 | LN(10) |  | 2019-04-18 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23.7 |  |  | 2019-04-18 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.3 |  |  | 2019-04-18 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-04-18 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23.7 |  |  | 2019-04-18 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.06 | MG/L |  | 2019-04-18 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.1 |  |  | 2019-05-03 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-03 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-05-03 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-05-03 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2019-05-03 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.8 |  |  | 2019-05-03 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2019-05-03 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 26.5 |  |  | 2019-05-03 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.4 | LN(10) |  | 2019-05-03 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2019-05-15 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.4 | LN(10) |  | 2019-05-15 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.3 |  |  | 2019-05-15 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-05-15 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-15 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.4 |  |  | 2019-05-15 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.9 |  |  | 2019-05-15 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.9 | MG/L |  | 2019-05-15 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-15 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-05-28 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 27.1 |  |  | 2019-05-28 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2019-05-28 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-28 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.9 |  |  | 2019-05-28 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-05-28 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-05-28 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.5 |  |  | 2019-05-28 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2019-05-28 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-06 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.3 |  |  | 2019-06-06 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.06 | MG/L |  | 2019-06-06 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.4 |  |  | 2019-06-06 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-06 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2019-06-06 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.8 |  |  | 2019-06-06 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-06 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.51 | MG/L |  | 2019-06-06 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAY)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.21 | MG/L |  | 2019-06-17 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.8 |  |  | 2019-06-17 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-17 | WTP1 |  |  |  |  | WP2 (SHEOAH BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 25.1 |  |  | 2019-06-17 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 7.9 | LN(10) |  | 2019-06-17 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2019-06-17 | WTP3 |  |  |  |  | WP1 TUSKAWILLA (851 NORTHERN WAT)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 24.2 |  |  | 2019-06-17 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.17 | MG/L |  | 2019-06-17 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2019-06-17 | WTP2 |  |  |  |  | WP3 (BAHAMA BLVD.)
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.95 | UG/L | 60.4999 | 2019-07-02 | L2 |  |  | 2 | 0.61 | SM-4 606 MORGAN / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM =50.97; HAA5 =12.62]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.97 | UG/L | 60.4999 | 2019-07-02 | L4 |  |  | 4 | 1.77 | STG 1 MRT WP3 410 SANDRINGHAM / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM = 62.34;HAA5 =27.38]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.78 | UG/L | 60.4999 | 2019-07-02 | L1 |  |  | 1 | 0.38 | SM-6 1626 WRENTHAM / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM = 59.78; HAA5 = 13.23]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 51.47 | UG/L | 80.4999 | 2019-07-02 | L1 |  |  | 1 | 0.38 | SM-6 1626 WRENTHAM / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM = 59.78; HAA5 = 13.23]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 62.88 | UG/L | 80.4999 | 2019-07-02 | L4 |  |  | 4 | 1.77 | STG 1 MRT WP3 410 SANDRINGHAM / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM = 62.34;HAA5 =27.38]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 27.06 | UG/L | 80.4999 | 2019-07-02 | L2 |  |  | 2 | 0.61 | SM-4 606 MORGAN / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM =50.97; HAA5 =12.62]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.05 | UG/L | 60.4999 | 2019-07-02 | L3 |  |  | 3 | 0.3 | STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.) / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM =49.28;HAA5 =11.65]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 45.61 | UG/L | 80.4999 | 2019-07-02 | L3 |  |  | 3 | 0.3 | STG 1 MRT WP1 674 ONEIDA LN. (NOT CT.) / SUBCONTRACT LABS E82574 E82535 [LRAA TTHM =49.28;HAA5 =11.65]
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 1.85 | UG/L | 80.4999 | 2019-10-01 | L1 | 0.39 |  | 1 | 0.9 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 60.76 | UG/L | 80.4999 | 2019-10-01 | L4 | 0.39 |  | 4 | 1.6 | 410 SANDRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.91 | UG/L | 60.4999 | 2019-10-01 | L2 | 0.91 |  | 2 | 1.5 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 3.06 | UG/L | 80.4999 | 2019-10-01 | L2 | 0.39 |  | 2 | 1.5 | 606 MORGAN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.28 | UG/L | 60.4999 | 2019-10-01 | L3 | 0.91 |  | 3 | 0.5 | 674 ONEIDA LN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | D | 37.19 | UG/L | 80.4999 | 2019-10-01 | L3 | 0.39 |  | 3 | 0.5 | 674 ONEIDA LN
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.21 | UG/L | 60.4999 | 2019-10-01 | L1 | 0.91 |  | 1 | 0.9 | 1626 WRENTHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.43 | UG/L | 60.4999 | 2019-10-01 | L4 | 0.91 |  | 4 | 1.6 | 410 SANDRINGHAM
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 62.71 | UG/L | 80.4999 | 2019-12-11 | L2 | 0.39 |  | 1 | 1.6
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 53.41 | UG/L | 60.4999 | 2019-12-11 | L1 | 0.39 |  | 1 | 1.5
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 53.41 | UG/L | 80.4999 | 2019-12-11 | L1 | 0.39 |  | 1 | 1.5
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 40.79 | UG/L | 80.4999 | 2019-12-11 | L3 | 0.39 |  | 1 | 1.6
3590879 | WINTER SPRINGS CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | S | 70.91 | UG/L | 80.4999 | 2019-12-11 | L4 | 0.39 |  | 1 | 2
3590912 | OAKLAND SHORES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-18 | AAA |  | 6.4999 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0.65 | UG/L | 449.9999 | 2015-02-18 | AAA |  | 0.6499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 2.4999 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-18 | AAA |  | 0.0749 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0.86 | UG/L | 6.4999 | 2015-02-18 | AAA |  | 0.6499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-18 | AAA |  | 0.9499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.1499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-18 | AAA |  | 0.0449 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SEC | 1095 | ZINC | N | 0.0118 | MG/L | 5.4999 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.92 | LN(10) |  | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 276 | MG/L | 500.4999 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1052 | SODIUM | N | 30.2 | MG/L | 160.4999 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 1.4999 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 1.4999 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-18 | AAA |  | 0.4499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-18 | AAA |  | 0.2499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.1499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.0449 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-18 | AAA |  | 0.1499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-18 | AAA |  | 0.0149 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 4.6 | PCI/L | 15.4999 | 2015-02-18 | AAA |  |  |  |  | RADS DUE 2021
3590912 | OAKLAND SHORES | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-02-18 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590912 | OAKLAND SHORES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-02-18 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590912 | OAKLAND SHORES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1010 | BARIUM | N | 0 | MG/L | 2.4999 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-18 | AAA |  |  |  |  | 15:ADIPATE .65 PHTHALATE .86 4QM/2035+2039 12/15>EM 10/29/15 TO SCOTT GOSNELL) ROUTINE (ANN.) T/H WEEK 2 AUG. 2015
3590912 | OAKLAND SHORES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1017 | CHLORIDE | N | 52.9 | MG/L | 250.4999 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1022 | COPPER | N | 0.0111 | MG/L | 1.4999 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1028 | IRON | N | 0.0238 | MG/L | 0.3499 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | SEC | 1055 | SULFATE | N | 9.14 | MG/L | 250.4999 | 2015-02-18 | AAA
3590912 | OAKLAND SHORES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590912 | OAKLAND SHORES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.0149 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 9.4999 |  |  | (7/31 EW HAS 2QM/2035+2039 FOR ENTRY-ALREADY IN OC) 3YR SOC (ADIPATE .65 PHTHALATE .86 2QM/2035+2039 6/15>EM 3/20/15 TO SCOTT GOSNELL) EM REMINDER 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE-BB
3590912 | OAKLAND SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-06-17 | AAA |  | 0.6499 |  |  | 2QM/2035+2039 (3QM/2035+2039 9/15) EM 3/20/15 & 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE (**10/29/15 EW HAS 9/15 2035+2039 FOR ENTRY)
3590912 | OAKLAND SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-06-17 | AAA |  | 0.6499 |  |  | 2QM/2035+2039 (3QM/2035+2039 9/15) EM 3/20/15 & 6/19/15 TO SCOTT GOSNELL & BRYAN GONGRE (**10/29/15 EW HAS 9/15 2035+2039 FOR ENTRY)
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 57.3 | UG/L | 60.4999 | 2015-08-12 | L1 |  |  |  | 1.6 | 605 ENDSLEY COURT (NO LRAA MCLS OR OE EXCEEDANCES) >500
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 56.4 | UG/L | 80.4999 | 2015-08-12 | L1 |  |  |  | 1.6 | 605 ENDSLEY COURT (NO LRAA MCLS OR OE EXCEEDANCES) >500
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 52.1 | UG/L | 60.4999 | 2015-08-12 | L2 |  |  |  | 1 | 517 OAK LANE (NO LRAA MCLS OR OE EXCEEDANCES) >500
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 62.4 | UG/L | 80.4999 | 2015-08-12 | L2 |  |  |  | 1 | 517 OAK LANE (NO LRAA MCLS OR OE EXCEEDANCES) >500
3590912 | OAKLAND SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-09-23 | AAA |  | 0.6499 |  |  | ****12/21/15 EW HAS 11/15 ADIPATE & PHTHALATE&12/21/15EM>SUSAN DIPASQUALE&BKGONGRE FOR 1Q 2016 AM BOTH**) 3QM/2035+2039 (4QM/2035+2039 12/15) EM REMINDER FOR 12/15 2035+2039 SENT 10/29/15
3590912 | OAKLAND SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-09-23 | AAA |  | 0.6499 |  |  | ****12/21/15 EW HAS 11/15 ADIPATE & PHTHALATE&12/21/15EM>SUSAN DIPASQUALE&BKGONGRE FOR 1Q 2016 AM BOTH**) 3QM/2035+2039 (4QM/2035+2039 12/15) EM REMINDER FOR 12/15 2035+2039 SENT 10/29/15
3590912 | OAKLAND SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-11-24 | AAA |  | 0.6499 |  |  | 4QM/2035+2039 (1AM/2035+2039 1Q 2016>EM 12/21/15>SMDIPASQUALE@UIWATER.COM) "LISA AUGUST-SENDER FR. UT INC." ***2/22/16 EW HAS 1/16 2035+2039 RSLTS BY EM
3590912 | OAKLAND SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-11-24 | AAA |  | 0.6499 |  |  | 4QM/2035+2039 (1AM/2035+2039 1Q 2016>EM 12/21/15>SMDIPASQUALE@UIWATER.COM) "LISA AUGUST-SENDER FR. UT INC." ***2/22/16 EW HAS 1/16 2035+2039 RSLTS BY EM
3590912 | OAKLAND SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2016-01-07 | AAA |  | 0.6499 |  |  | 1AM/2035+2039 1Q 2016 (2AM/2035+2039 DUE 1Q 2017>>>ADD THIS TO MONIT. SCHEDULE)
3590912 | OAKLAND SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2016-01-07 | AAA |  | 0.6499 |  |  | 1AM/2035+2039 1Q 2016 (2AM/2035+2039 DUE 1Q 2017>>>ADD THIS TO MONIT. SCHEDULE)
3590912 | OAKLAND SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3590912 | OAKLAND SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45.1 | UG/L | 60.4999 | 2016-08-10 | L2 |  |  |  | 0.6 | 517 OAK LANE (CONT. ANNUAL MONITORING)
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 48.6 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 0.4 | 605 ENDSLEY COURT (CONT. ANNUAL MONITORING)
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 45.2 | UG/L | 80.4999 | 2016-08-10 | L2 |  |  |  | 0.6 | 517 OAK LANE (CONT. ANNUAL MONITORING)
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.4 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 0.4 | 605 ENDSLEY COURT (CONT. ANNUAL MONITORING)
3590912 | OAKLAND SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-01-12 | AAA | 0.6 | 0.6499 |  |  | 2AM/2035+2039 (3AM/2035+2039 DUE 1Q 2018>>>PUT THIS IN 2017 MONIT SCHEDULE)
3590912 | OAKLAND SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-01-12 | AAA | 0.6 | 0.6499 |  |  | 2AM/2035+2039 (3AM/2035+2039 DUE 1Q 2018>>>PUT THIS IN 2017 MONIT SCHEDULE)
3590912 | OAKLAND SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590912 | OAKLAND SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 59 | UG/L | 80.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 1.7 | 517 OAK LANE (H>60 L2 T>80 L1 TEST QUARTERLY NOW BOTH SITES) HYPERLINKED TO BW 9/20/17. MUST NOTIFY OWNER & OPERATOR. BB
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 69 | UG/L | 60.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 1.7 | 517 OAK LANE (H>60 L2 T>80 L1 TEST QUARTERLY NOW BOTH SITES) HYPERLINKED TO BW 9/20/17. MUST NOTIFY OWNER & OPERATOR. BB
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 47.3 | UG/L | 60.4999 | 2017-08-11 | L1 | 0.5 |  |  | 1.5 | 605 ENDSLEY COURT (T>80 L1 H>60 L2) HYPERLINKED 9/20/17 TO BW. HYPERLINKED TO BW 9/20/17. MUST NOTIFY OWNER & OPERATOR. BB
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 98.5 | UG/L | 80.4999 | 2017-08-11 | L1 | 0.5 |  |  | 1.5 | 605 ENDSLEY COURT (T>80 L1 H>60 L2) HYPERLINKED 9/20/17 TO BW. HYPERLINKED TO BW 9/20/17. MUST NOTIFY OWNER & OPERATOR. BB
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.9 | UG/L | 60.4999 | 2017-11-22 | L1 | 0.5 |  | 1 | 2.8 | 2QM-605 ENDSLEY COURT
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 50.8 | UG/L | 80.4999 | 2017-11-22 | L2 | 0.5 |  | 2 | 2.2 | 2QM-517 OAK LANE (HYPERLINKED TO BW 12/26/17 - BB) MUST COMPUTE LRAAS
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.2 | UG/L | 60.4999 | 2017-11-22 | L2 | 0.5 |  | 2 | 2.2 | 2QM-517 OAK LANE (HYPERLINKED TO BW 12/26/17 - BB) MUST COMPUTE LRAAS
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 39.1 | UG/L | 80.4999 | 2017-11-22 | L1 | 0.5 |  | 1 | 2.8 | 2QM-605 ENDSLEY COURT
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.4 | UG/L | 60.4999 | 2018-02-07 | L1 | 0.5 |  | 1 | 2.4 | 3QM-605 ENDSLEY COURT (**LRAAS MUST BE COMPUTED**)
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 35.2 | UG/L | 80.4999 | 2018-02-07 | L1 | 0.5 |  | 1 | 2.4 | 3QM-605 ENDSLEY COURT (**LRAAS MUST BE COMPUTED**)
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33 | UG/L | 60.4999 | 2018-02-07 | L2 | 0.5 |  | 2 | 2.4 | 3QM-517 OAK LANE (4/19/18 HYPERLINKED TO BW - BB) **LRAAS MUST BE COMPUTED**
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 38.4 | UG/L | 80.4999 | 2018-02-07 | L2 | 0.5 |  | 2 | 2.4 | 3QM-517 OAK LANE (4/19/18 HYPERLINKED TO BW - BB) **LRAAS MUST BE COMPUTED**
3590912 | OAKLAND SHORES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-20 | AAA | 0.2 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-20 | AAA | 0.001 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1010 | BARIUM | N | 0.0044 | MG/L | 2.4999 | 2018-02-20 | AAA | 0.002 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-20 | AAA | 0.001 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-20 | AAA | 0.001 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-20 | AAA | 0.005 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-02-20 | AAA | 0.2 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-20 | AAA | 0.001 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-20 | AAA | 2e-05 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-20 | AAA | 0.001 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-20 | AAA | 0.002 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1052 | SODIUM | N | 37 | MG/L | 160.4999 | 2018-02-20 | AAA | 0.5 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-20 | AAA | 0.001 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-20 | AAA | 0.0005 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-20 | AAA | 0.001 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-02-20 | AAA | 0.2 |  |  |  | UTILS INC. (ALL OK)
3590912 | OAKLAND SHORES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-20 | AAA | 0.02
3590912 | OAKLAND SHORES | SEC | 1017 | CHLORIDE | N | 57.8 | MG/L | 250.4999 | 2018-02-20 | AAA | 0.4
3590912 | OAKLAND SHORES | SEC | 1022 | COPPER | N | 0.0094 | MG/L | 1.4999 | 2018-02-20 | AAA | 0.001
3590912 | OAKLAND SHORES | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-02-20 | AAA | 0.4
3590912 | OAKLAND SHORES | SEC | 1028 | IRON | N | 0.0253 | MG/L | 0.3499 | 2018-02-20 | AAA | 0.01
3590912 | OAKLAND SHORES | SEC | 1032 | MANGANESE | N | 0.011 | MG/L | 0.0549 | 2018-02-20 | AAA | 0.01
3590912 | OAKLAND SHORES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-20 | AAA | 0.0005
3590912 | OAKLAND SHORES | SEC | 1055 | SULFATE | N | 14 | MG/L | 250.4999 | 2018-02-20 | AAA | 1
3590912 | OAKLAND SHORES | SEC | 1095 | ZINC | N | 0.0186 | MG/L | 5.4999 | 2018-02-20 | AAA | 0.01
3590912 | OAKLAND SHORES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-20 | AAA | 5
3590912 | OAKLAND SHORES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-20 | AAA | 1
3590912 | OAKLAND SHORES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.99 | LN(10) |  | 2018-02-20 | AAA | 0.01
3590912 | OAKLAND SHORES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-02-20 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-02-20 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-02-20 | AAA | 0.05 | 0.1499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-02-20 | AAA | 0.5 | 1.4999 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-02-20 | AAA | 0.1 | 1.4999 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-02-20 | AAA | 0.4 | 0.4499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-02-20 | AAA | 9 | 9.4999 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-02-20 | AAA | 6 | 6.4999 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-02-20 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-02-20 | AAA | 2 | 2.4999 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-02-20 | AAA | 0.07 | 0.0749 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-02-20 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-02-20 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-02-20 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-02-20 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-02-20 | AAA | 0.9 | 0.9499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-02-20 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-02-20 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-02-20 | AAA | 0.01 | 0.0449 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-02-20 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-02-20 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-02-20 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-02-20 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-02-20 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-02-20 | AAA | 0.04 | 0.0449 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-02-20 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-02-20 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-02-20 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-02-20 | AAA | 0.01 | 0.2499 |  |  | 3YR SOC & 3AM/2035+2039 DUE 1Q 2018 (MAY END THE AM/2035+2039 LAST 3 YRS -0- DURING 2016-2017-2018 - BB)
3590912 | OAKLAND SHORES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 326 | MG/L | 500.4999 | 2018-02-20 | AAA | 2.5
3590912 | OAKLAND SHORES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-20 | AAA | 0.2
3590912 | OAKLAND SHORES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-20 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-20 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 38.2 | UG/L | 80.4999 | 2018-05-08 | L1 |  |  |  | 2.4 | 605 ENDSLEY COURT
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.8 | UG/L | 60.4999 | 2018-05-08 | L2 |  |  |  | 2 | 517 OAK LANE
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.4 | UG/L | 60.4999 | 2018-05-08 | L1 |  |  |  | 2.4 | 605 ENDSLEY COURT
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 38 | UG/L | 80.4999 | 2018-05-08 | L2 |  |  |  | 2 | 517 OAK LANE
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45.1 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 1.9
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 47.8 | UG/L | 60.4999 | 2018-08-07 | L2 | 0.5 |  | 1 | 2.4
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 54.8 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 1.9
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 44.9 | UG/L | 80.4999 | 2018-08-07 | L2 | 0.5 |  | 1 | 2.4
3590912 | OAKLAND SHORES | INOR | 1040 | NITRATE | N | 0.0582 | MG/L | 10.4999 | 2019-02-26 | AAA
3590912 | OAKLAND SHORES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | AAA
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.8 | UG/L | 60.4999 | 2019-08-12 | L2 | 1 |  | 2 | 2.5 | 517 OAK LANE
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 50.6 | UG/L | 80.4999 | 2019-08-12 | L1 | 0.5 |  | 1 | 2.6 | 605 ENDSLEY COURT
3590912 | OAKLAND SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.7 | UG/L | 60.4999 | 2019-08-12 | L1 | 1 |  | 1 | 2.6 | 605 ENDSLEY COURT
3590912 | OAKLAND SHORES | DBP | 2950 | TOTAL THMS | D | 53.1 | UG/L | 80.4999 | 2019-08-12 | L2 | 0.5 |  | 2 | 2.5 | 517 OAK LANE
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 19.29 | UG/L | 80.4999 | 2015-05-13 | L3 |  |  |  | 2.2 | (6/8 EW HAS 5/16 ANN. T/H-RSLTS LOW-EM 6/8/16 FOR STG2 ANN. FORM-GREG PUT RSLTS ON STG1 FORM) 1223 TWIN RIVERS BLVD. (R.M. T/H MAY) (ON R.M. EFFEC. 10/1/14-REMAIN ON R.M.) ANNUAL STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.03 | UG/L | 60.4999 | 2015-05-13 | L3 |  |  |  | 2.2 | (6/8 EW HAS 5/16 ANN. T/H-RSLTS LOW-EM 6/8/16 FOR STG2 ANN. FORM-GREG PUT RSLTS ON STG1 FORM) 1223 TWIN RIVERS BLVD. (R.M. T/H MAY) (ON R.M. EFFEC. 10/1/14-REMAIN ON R.M.) ANNUAL STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 18.2 | UG/L | 80.4999 | 2015-05-13 | L4 |  |  |  | 0.8 | 804 PALMETTO TERR. (R.M. T/H MAY)(ON R.M. EFFEC. 10/1/14-REMAIN ON R.M.) ANNUAL STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.12 | UG/L | 60.4999 | 2015-05-13 | L4 |  |  |  | 0.8 | 804 PALMETTO TERR. (R.M. T/H MAY)(ON R.M. EFFEC. 10/1/14-REMAIN ON R.M.) ANNUAL STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-08-13 | WTP3 |  |  |  |  | W. MITCHELL HAMMOCK WP
3590970 | OVIEDO CITY OF | INOR | 1040 | NITRATE | N | 0.14 | MG/L | 10.4999 | 2015-08-13 | WTP3 |  |  |  |  | W. MITCHELL HAMMOCK WP
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 17.54 | UG/L | 80.4999 | 2016-05-18 | L3 |  |  |  | 0.8 | 1223 TWIN RIVERS BLVD. (R.M. T/H BOTH SITES IN MAY 2016) (6/16 ANNUAL DBF RCVD & IN OC ON ANNUAL 2 SITES 2Q 2016 RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.19 | UG/L | 60.4999 | 2016-05-18 | L3 |  |  |  | 0.8 | 1223 TWIN RIVERS BLVD. (R.M. T/H BOTH SITES IN MAY 2016) (6/16 ANNUAL DBF RCVD & IN OC ON ANNUAL 2 SITES 2Q 2016 RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.57 | UG/L | 60.4999 | 2016-05-18 | L4 |  |  |  | 1.5 | 804 PALMETTO TERR. (R.M. T/H MAY) (ON ANNUAL RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 17.25 | UG/L | 80.4999 | 2016-05-18 | L4 |  |  |  | 1.5 | 804 PALMETTO TERR. (R.M. T/H MAY) (ON ANNUAL RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC
3590970 | OVIEDO CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-25 | WTP3
3590970 | OVIEDO CITY OF | INOR | 1040 | NITRATE | N | 0.15 | MG/L | 10.4999 | 2016-05-25 | WTP3
3590970 | OVIEDO CITY OF | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-11 | WTP3 | 0.26 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-11 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-11 | WTP3 | 0.12 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-11 | WTP3 | 0.24 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-11 | WTP3 | 0.12 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-11 | WTP3 | 0.17 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-11 | WTP3 | 0.22 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-11 | WTP3 | 0.17 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-11 | WTP3 | 0.39 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-11 | WTP3 | 0.0069 | 0.0149 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-11 | WTP3 | 0.0071 | 0.0249 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-11 | WTP3 | 0.0068 | 0.1499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-11 | WTP3 | 0.12 | 1.4999 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-11 | WTP3 | 1 | 1.4999 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-11 | WTP3 | 7.6 | 0.4499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-11 | WTP3 | 1.2 | 9.4999 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-11 | WTP3 | 6.5 | 6.4999 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-11 | WTP3 | 0.97 | 0.6499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-11 | WTP3 | 0.57 | 2.4999 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-11 | WTP3 | 0.19 | 0.0749 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-11 | WTP3 | 1.5 | 0.6499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-11 | WTP3 | 0.23 | 0.1499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-11 | WTP3 | 0.86 | 0.2499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-11 | WTP3 | 0.012 | 0.1499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-11 | WTP3 | 0.28 | 0.9499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-11 | WTP3 | 0.16 | 0.1499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-11 | WTP3 | 0.27 | 0.2499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-11 | WTP3 | 0.006 | 0.0449 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-11 | WTP3 | 0.0052 | 0.0249 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-11 | WTP3 | 1.5 | 0.1499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-11 | WTP3 | 0.32 | 0.2499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-11 | WTP3 | 0.0063 | 0.1499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-11 | WTP3 | 0.098 | 0.0249 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-11 | WTP3 | 0.069 | 0.0449 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-11 | WTP3 | 0.11 | 0.1499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-11 | WTP3 | 0.0061 | 0.0249 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-11 | WTP3 | 0.0063 | 0.0149 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-11 | WTP3 | 0.053 | 0.2499 |  |  | 1Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS
3590970 | OVIEDO CITY OF | INOR | 1040 | NITRATE | N | 0.22 | MG/L | 10.4999 | 2017-04-11 | WTP3 | 0.051 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-04-11 | WTP3 | 0.053 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1005 | ARSENIC | N | 0.0003 | MG/L | 0.0104 | 2017-04-11 | WTP3 | 8e-05 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1010 | BARIUM | N | 0.017 | MG/L | 2.4999 | 2017-04-11 | WTP3 | 0.00028 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-04-11 | WTP3 | 3e-05 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-04-11 | WTP3 | 0.00011 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-04-11 | WTP3 | 0.0048 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1025 | FLUORIDE | N | 0.4 | MG/L | 4.0499 | 2017-04-11 | WTP3 | 0.075 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-04-11 | WTP3 | 6e-05 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-04-11 | WTP3 | 0.061 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1017 | CHLORIDE | N | 68 | MG/L | 250.4999 | 2017-04-11 | WTP3 | 0.78 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1022 | COPPER | N | 0.011 | MG/L | 1.4999 | 2017-04-11 | WTP3 | 0.00011 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1025 | FLUORIDE | N | 0.4 | MG/L | 2.0499 | 2017-04-11 | WTP3 | 0.075 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-04-11 | WTP3 | 0.03 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1032 | MANGANESE | N | 0.0028 | MG/L | 0.0549 | 2017-04-11 | WTP3 | 6e-05 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-04-11 | WTP3 | 3e-05 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1055 | SULFATE | N | 12 | MG/L | 250.4999 | 2017-04-11 | WTP3 | 0.52 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1095 | ZINC | N | 0.013 | MG/L | 5.4999 | 2017-04-11 | WTP3 | 0.002 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-04-11 | WTP3 | 5 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-04-11 | WTP3 | 1 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.24 | LN(10) |  | 2017-04-11 | WTP3 |  |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-11 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | INOR | 1030 | LEAD | N | 0.0005 | MG/L | 0.0154 | 2017-04-11 | WTP3 | 0.00024 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-04-11 | WTP3 | 1e-05 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1036 | NICKEL | N | 0.0001 | MG/L | 0.1499 | 2017-04-11 | WTP3 | 0.00011 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-04-11 | WTP3 | 0.00058 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1052 | SODIUM | N | 39 | MG/L | 160.4999 | 2017-04-11 | WTP3 | 0.16 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-04-11 | WTP3 | 5e-05 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-04-11 | WTP3 | 0.00013 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 270 | MG/L | 500.4999 | 2017-04-11 | WTP3 | 10 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | SEC | 2905 | FOAMING AGENTS | N | 0.042 |  | 0.5499 | 2017-04-11 | WTP3 | 0.04 |  |  |  | W. MITCHELL HAMMOCK WP (THE ONLY WP IN SYSTEM) NO MCLS
3590970 | OVIEDO CITY OF | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-11 | WTP3 | 0.32 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-11 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-11 | WTP3 | 0.44 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-11 | WTP3 | 0.46 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-11 | WTP3 | 0.26 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-11 | WTP3 | 0.2 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-11 | WTP3 | 0.18 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-11 | WTP3 | 0.28 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-11 | WTP3 | 0.35 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-11 | WTP3 | 0.39 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-11 | WTP3 | 0.23 | 0.5499 |  |  | 3YR VOC/W. M. HAMMOCK WP (THE ONLY WP IN SYSTEM NOW) NO DETECTIONS
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.26 | UG/L | 60.4999 | 2017-05-04 | L3 | 0.5 |  | 2 | 1.4 | 1223 TWIN RIVERS BLVD. (R.M. T/H BOTH SITES DUE MAY 2018) (6/17 ANNUAL DBF RCVD ON ANNUAL 2 SITES 2Q 2017 RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC. HYPERLINKED TO BW 6/28/17-BB
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 14.47 | UG/L | 80.4999 | 2017-05-04 | L4 | 0.14 |  | 1 | 1.6 | 804 PALMETTO TERR. (R.M. T/H BOTH SITES DUE MAY 2018) (6/17 ANNUAL DBF RCVD ON ANNUAL 2 SITES 2Q 2017 RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC.HYPERLINKED TO BW 6/28/17-BB
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.95 | UG/L | 60.4999 | 2017-05-04 | L4 | 0.5 |  | 1 | 1.6 | 804 PALMETTO TERR. (R.M. T/H BOTH SITES DUE MAY 2018) (6/17 ANNUAL DBF RCVD ON ANNUAL 2 SITES 2Q 2017 RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC.HYPERLINKED TO BW 6/28/17-BB
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 14.67 | UG/L | 80.4999 | 2017-05-04 | L3 | 0.14 |  | 2 | 1.4 | 1223 TWIN RIVERS BLVD. (R.M. T/H BOTH SITES DUE MAY 2018) (6/17 ANNUAL DBF RCVD ON ANNUAL 2 SITES 2Q 2017 RESULTS LOW REMAIN ON R.M.) ANN. STG2 PLAN IN OC. HYPERLINKED TO BW 6/28/17-BB
3590970 | OVIEDO CITY OF | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-08-15 | WTP3 | 0.0069 | 0.0149 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-08-15 | WTP3 | 0.0071 | 0.0249 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-08-15 | WTP3 | 0.0068 | 0.1499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-08-15 | WTP3 | 0.12 | 1.4999 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-08-15 | WTP3 | 1 | 1.4999 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-08-15 | WTP3 | 7.6 | 0.4499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-08-15 | WTP3 | 1.2 | 9.4999 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-08-15 | WTP3 | 6.5 | 6.4999 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-08-15 | WTP3 | 0.95 | 0.6499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-08-15 | WTP3 | 0.57 | 2.4999 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-08-15 | WTP3 | 0.19 | 0.0749 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-08-15 | WTP3 | 1.5 | 0.6499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-08-15 | WTP3 | 0.23 | 0.1499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-08-15 | WTP3 | 0.86 | 0.2499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-08-15 | WTP3 | 0.012 | 0.1499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-08-15 | WTP3 | 0.28 | 0.9499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-08-15 | WTP3 | 0.16 | 0.1499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-08-15 | WTP3 | 0.26 | 0.2499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-08-15 | WTP3 | 0.006 | 0.0449 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-08-15 | WTP3 | 0.0052 | 0.0249 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-08-15 | WTP3 | 1.5 | 0.1499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-08-15 | WTP3 | 0.32 | 0.2499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-08-15 | WTP3 | 0.0063 | 0.1499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-08-15 | WTP3 | 0.096 | 0.0249 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-08-15 | WTP3 | 0.069 | 0.0449 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-08-15 | WTP3 | 0.11 | 0.1499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-08-15 | WTP3 | 0.006 | 0.0249 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-08-15 | WTP3 | 0.0062 | 0.0149 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-08-15 | WTP3 | 0.053 | 0.2499 |  |  | 2Q SOC/W. MITCHELL HAMMOCK WP (THE ONLY WP IN THE SYSTEM) NO DETECTIONS (9/25/17 PLACED IN FINAL CHEM HOLDING FOLDER 9/25/17 - BB)
3590970 | OVIEDO CITY OF | INOR | 1040 | NITRATE | N | 0.22 | MG/L | 10.4999 | 2018-05-14 | WTP3 |  |  |  |  | W. MITCHELL HAMMOCK WP
3590970 | OVIEDO CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-14 | WTP3 |  |  |  |  | W. MITCHELL HAMMOCK WP
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 25 | UG/L | 80.4999 | 2018-05-14 | L3 |  |  |  | 1.2 | 1223 TWIN RIVERS BLVD. (R.M. T/H MAY)
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 25.47 | UG/L | 80.4999 | 2018-05-14 | L4 |  |  |  | 1 | 804 PALMETTO TERR. (R.M. T/H MAY)
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.02 | UG/L | 60.4999 | 2018-05-14 | L3 |  |  |  | 1.2 | 1223 TWIN RIVERS BLVD. (R.M. T/H MAY)
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.82 | UG/L | 60.4999 | 2018-05-14 | L4 |  |  |  | 1 | 804 PALMETTO TERR. (R.M. T/H MAY)
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.99 | UG/L | 60.4999 | 2019-05-13 | L4 |  |  | 1 | 2.2 | 804 PALMETTO TERR. (R.M. T/H MAY) / SUBCONTRACT LABS E82535 E84589
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 21.34 | UG/L | 80.4999 | 2019-05-13 | L4 |  |  | 1 | 2.2 | 804 PALMETTO TERR. (R.M. T/H MAY) / SUBCONTRACT LABS E82535 E84589
3590970 | OVIEDO CITY OF | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.95 | UG/L | 60.4999 | 2019-05-13 | L3 |  |  | 2 | 1.8 | 1223 TWIN RIVERS BLVD. (R.M. T/H MAY) / SUBCONTRACT LABS E82535 E84589
3590970 | OVIEDO CITY OF | DBP | 2950 | TOTAL THMS | D | 20.03 | UG/L | 80.4999 | 2019-05-13 | L3 |  |  | 2 | 1.8 | 1223 TWIN RIVERS BLVD. (R.M. T/H MAY) / SUBCONTRACT LABS E82535 E84589
3590970 | OVIEDO CITY OF | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-16 | WTP3 |  |  |  |  | W. MITCHELL HAMMOCK WP
3590970 | OVIEDO CITY OF | INOR | 1040 | NITRATE | N | 0.47 | MG/L | 10.4999 | 2019-05-16 | WTP3 |  |  |  |  | W. MITCHELL HAMMOCK WP
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.6 | PCI/L | 15.4999 | 2015-01-28 | AAA |  |  |  |  | RADS DUE 2021
3590988 | PALM VALLEY MOBILE HOME PARK | RAD | 4020 | RADIUM-226 | N | 0.8 | PCI/L | 3.4999 | 2015-01-28 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590988 | PALM VALLEY MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | N | 0.8 | PCI/L | 2.4999 | 2015-01-28 | AAA |  | 1.4999 |  |  | RADS DUE 2021
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.012 | MG/L | 2.4999 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.15 | MG/L | 4.0499 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 16 | MG/L | 160.4999 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-01-28 | AAA |  |  |  |  | NO MCLS IN TRIENNIALS (TRIENNIALS INCLUDING REVISED SECONDARIES PAGE FOR F.AG ALL IN OC)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 25 | MG/L | 250.4999 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.15 | MG/L | 2.0499 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0026 | MG/L | 0.0549 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 1.7 | MG/L | 250.4999 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0.011 | MG/L | 5.4999 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.1 | LN(10) |  | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 200 | MG/L | 500.4999 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0.084 |  | 0.5499 | 2015-01-28 | AAA |  |  |  |  | REVISED SECONDARIES & ALL TRIENNIALS IN OC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-01-28 | AAA |  | 0.5499 |  |  | 3YR VOC
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 78.81 | UG/L | 80.4999 | 2015-02-19 | L2 | 0.31 |  | 1 | 1 | (RCVD 3/15 OE REPORT T L2 SITE ONLY 95.2825 AS RQRD-IN OC) 744 PRINCESS PALM PLACE (AFTER 3 QTRS ONLY L2 LRR/T=75.58 LRAA/H=41.035) OE LEVEL 95.2825 FOR TTHMS ND. OE REPORT>EM 3/20/15>US WTR
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45.91 | UG/L | 60.4999 | 2015-02-19 | L1 | 0.52 |  | 2 | 1.2 | 3401 HUNT LANE (AFTER 3 QTRS ONLY L1 3/15 LRAA/T=61.4125 LRAA/H=31.925) OE LEVEL 80.1225 (JUST AT MCL BUT NOT EXCEEDING)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 47.96 | UG/L | 60.4999 | 2015-02-19 | L2 | 0.52 |  | 1 | 1 | (RCVD 3/15 OE REPORT T L2 SITE ONLY 95.2825 AS RQRD-IN OC) 744 PRINCESS PALM PLACE (AFTER 3 QTRS ONLY L2 LRR/T=75.58 LRAA/H=41.035) OE LEVEL 95.2825 FOR TTHMS ND. OE REPORT>EM 3/20/15>US WTR
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 74.84 | UG/L | 80.4999 | 2015-02-19 | L1 | 0.31 |  | 2 | 1.2 | 3401 HUNT LANE (AFTER 3 QTRS ONLY L1 3/15 LRAA/T=61.4125 LRAA/H=31.925) OE LEVEL 80.1225 (JUST AT MCL BUT NOT EXCEEDING)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 53.2 | UG/L | 60.4999 | 2015-05-21 | L2 | 0.52 |  | 2 | 1 | L2 OE RCVD)744 PR.PLM PL.(AFT.4QTRS L2:6/15 LRAA/T=101.2775 LRAA/H=54.335)H/E82574 T/E84589 EM 6/18/15>US WTR JF AW ADVISING OF 7/14-5/15 TTHMS MCL VIOS@BOTH SITES.CA PN RQRD W/IN30DAYS IF NO EX.TSTS
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 102.79 | UG/L | 80.4999 | 2015-05-21 | L2 | 0.31 |  | 2 | 1 | L2 OE RCVD)744 PR.PLM PL.(AFT.4QTRS L2:6/15 LRAA/T=101.2775 LRAA/H=54.335)H/E82574 T/E84589 EM 6/18/15>US WTR JF AW ADVISING OF 7/14-5/15 TTHMS MCL VIOS@BOTH SITES.CA PN RQRD W/IN30DAYS IF NO EX.TSTS
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 93.07 | UG/L | 80.4999 | 2015-05-21 | L1 | 0.31 |  | 1 | 1.2 | 3401 HUNT LANE (AFT. 4 QTRS L1: 6/15 LRAA/T 84.68 LRAA/H=50.5975) H/E82574 T/E84589 (T OE VALUE 79.135 L1)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 74.69 | UG/L | 60.4999 | 2015-05-21 | L1 | 0.52 |  | 1 | 1.2 | 3401 HUNT LANE (AFT. 4 QTRS L1: 6/15 LRAA/T 84.68 LRAA/H=50.5975) H/E82574 T/E84589 (T OE VALUE 79.135 L1)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.74 | UG/L | 60.4999 | 2015-08-19 | L1 |  |  |  | 0.5 | 3401 HUNT LANE (9/15 LRAA/T=75.17 LRAA/H=49.7575)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.8 | UG/L | 60.4999 | 2015-08-19 | L2 |  |  |  | 0.2 | 744 PPP(9/15 LRAA/T=90.1775 LRAA/H=44.3425)2ND LRAA/T MCLVIO-10/29/15PN.RCVD 9/15 T OE RPRT92.895-IN OC.EM9/21/15>US WTR OWNR W/NEW DRAFT PN.EM9/22/15>CD&JF(10/20BW CASE MGR-WL WRT C.O
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 77.21 | UG/L | 80.4999 | 2015-08-19 | L1 |  |  |  | 0.5 | 3401 HUNT LANE (9/15 LRAA/T=75.17 LRAA/H=49.7575)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 94.99 | UG/L | 80.4999 | 2015-08-19 | L2 |  |  |  | 0.2 | 744 PPP(9/15 LRAA/T=90.1775 LRAA/H=44.3425)2ND LRAA/T MCLVIO-10/29/15PN.RCVD 9/15 T OE RPRT92.895-IN OC.EM9/21/15>US WTR OWNR W/NEW DRAFT PN.EM9/22/15>CD&JF(10/20BW CASE MGR-WL WRT C.O
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 85.09 | UG/L | 80.4999 | 2015-11-24 | L2 |  |  |  | 0.8 | 744 PRINCESS PALM PL(12/15 LRAA/T=90.42 LRAA/H=40.01)PN ISSUED 1/19/16(US HAS PARTIAL PN DRAFT 1/12/16)EM1/12/16>BW JF CD W/UPDATE.MELISA SNT 12/31/15 C.O.1/12/16EM.12/15 T OE REPORT 91.99 IN OC.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.08 | UG/L | 60.4999 | 2015-11-24 | L2 |  |  |  | 0.8 | 744 PRINCESS PALM PL(12/15 LRAA/T=90.42 LRAA/H=40.01)PN ISSUED 1/19/16(US HAS PARTIAL PN DRAFT 1/12/16)EM1/12/16>BW JF CD W/UPDATE.MELISA SNT 12/31/15 C.O.1/12/16EM.12/15 T OE REPORT 91.99 IN OC.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 69.93 | UG/L | 80.4999 | 2015-11-24 | L1 |  |  |  | 1 | 3401 HUNT LANE (12/15 LRAA/T=78.7625 LRAA/H=49.6175) NEXT EM DUE 1/29/16 IF ABOVE MCLS
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.13 | UG/L | 60.4999 | 2015-11-24 | L1 |  |  |  | 1 | 3401 HUNT LANE (12/15 LRAA/T=78.7625 LRAA/H=49.6175) NEXT EM DUE 1/29/16 IF ABOVE MCLS
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.2 | MG/L | 10.4999 | 2016-02-08 | AAA |  |  |  |  | NN (US WTR)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-08 | AAA |  |  |  |  | NN (US WTR)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 63.57 | UG/L | 80.4999 | 2016-02-11 | L2 |  |  |  | 0.5 | 744 PRINCESS PALM PL(3/16 LRAA/T=86.61 LRAA/H=36.715)3/16OE/T=76.805 OE/H<MCL(NO OE RPRT NDD 3/16QTR)4/7/16EM>BW CD JF W/3/16 QTR UPDT L2 SITE MCL.4/7/16MELISA HAS APPRVD PN-PN ISSUED 4/18/16.1/27C.O.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 21.04 | UG/L | 80.4999 | 2016-02-11 | L1 |  |  |  | 0.38 | 3401 HUNT LANE(3/16 LRAA;T=65.3125 LRAA/H=41.745)3/16 OE/T<MCL OE/H<MCL(NO OE RPRT NDD 3/16 QTR)4/7/16 EM>BW CD JF W/3/16 QTR UPDATE L2 SITE MCL.4/7/16MELISA HAS APPRVD PN-ISSUE BY 4/19/16.1/27/16C.O.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.42 | UG/L | 60.4999 | 2016-02-11 | L1 |  |  |  | 0.38 | 3401 HUNT LANE(3/16 LRAA;T=65.3125 LRAA/H=41.745)3/16 OE/T<MCL OE/H<MCL(NO OE RPRT NDD 3/16 QTR)4/7/16 EM>BW CD JF W/3/16 QTR UPDATE L2 SITE MCL.4/7/16MELISA HAS APPRVD PN-ISSUE BY 4/19/16.1/27/16C.O.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.78 | UG/L | 60.4999 | 2016-02-11 | L2 |  |  |  | 0.5 | 744 PRINCESS PALM PL(3/16 LRAA/T=86.61 LRAA/H=36.715)3/16OE/T=76.805 OE/H<MCL(NO OE RPRT NDD 3/16QTR)4/7/16EM>BW CD JF W/3/16 QTR UPDT L2 SITE MCL.4/7/16MELISA HAS APPRVD PN-PN ISSUED 4/18/16.1/27C.O.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.02 | UG/L | 60.4999 | 2016-05-25 | L1 |  |  |  | 0.5 | 3401 HUNT LANE (6/16 LRAA/T=58.4225 LRAA/H=29.0775) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 65.51 | UG/L | 80.4999 | 2016-05-25 | L1 |  |  |  | 0.5 | 3401 HUNT LANE (6/16 LRAA/T=58.4225 LRAA/H=29.0775) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.58 | UG/L | 60.4999 | 2016-05-25 | L2 |  |  |  | 0.25 | 744 PRINCESS PALM PLACE (6/16 LRAA/T=74.8525 LRAA/H=27.31) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 55.76 | UG/L | 80.4999 | 2016-05-25 | L2 |  |  |  | 0.25 | 744 PRINCESS PALM PLACE (6/16 LRAA/T=74.8525 LRAA/H=27.31) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.03 | UG/L | 60.4999 | 2016-08-22 | L1 |  |  |  | 0.35 | 3401 HUNT LANE (9/16 LRAA/T=54.8025 LRAA/H=25.65) CONT. QM/T+H EM SENT TO US WATER 9/15/16 EW
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 79.86 | UG/L | 80.4999 | 2016-08-22 | L2 |  |  |  | 0.25 | 744 PRINCESS PALM PLACE (9/16 LRAA/T=71.07 LRAA/H=23.4225) CONT. QM/T+H EM SENT TO US WATER 9/15/16 EW. MELISA OF US WATER KNOWS THAT NO PUBLIC NOTICE IS NEEDED FOR THE 9/16 QUARTER.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.25 | UG/L | 60.4999 | 2016-08-22 | L2 |  |  |  | 0.25 | 744 PRINCESS PALM PLACE (9/16 LRAA/T=71.07 LRAA/H=23.4225) CONT. QM/T+H EM SENT TO US WATER 9/15/16 EW. MELISA OF US WATER KNOWS THAT NO PUBLIC NOTICE IS NEEDED FOR THE 9/16 QUARTER.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 62.73 | UG/L | 80.4999 | 2016-08-22 | L1 |  |  |  | 0.35 | 3401 HUNT LANE (9/16 LRAA/T=54.8025 LRAA/H=25.65) CONT. QM/T+H EM SENT TO US WATER 9/15/16 EW
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.51 | UG/L | 60.4999 | 2016-11-17 | L2 |  |  |  | 0.6 | 744 PRINCESS PALM PLACE (12/16 LRAA/T=63.4075 LRAA/H=18.03) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 50.18 | UG/L | 80.4999 | 2016-11-17 | L1 |  |  |  | 0.8 | 3401 HUNT LANE (12/16 LRAA/T=49.865 LRAA/H=20.22) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.41 | UG/L | 60.4999 | 2016-11-17 | L1 |  |  |  | 0.8 | 3401 HUNT LANE (12/16 LRAA/T=49.865 LRAA/H=20.22) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 54.44 | UG/L | 80.4999 | 2016-11-17 | L2 |  |  |  | 0.6 | 744 PRINCESS PALM PLACE (12/16 LRAA/T=63.4075 LRAA/H=18.03) CONT. QM/T+H
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.72 | UG/L | 60.4999 | 2017-02-27 | L1 | 0.2 |  | 1 | 1.1 | 3401 HUNT LANE
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 75.46 | UG/L | 80.4999 | 2017-02-27 | L1 | 0.14 |  | 1 | 1.1 | 3401 HUNT LANE
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.05 | UG/L | 60.4999 | 2017-02-27 | L2 | 0.2 |  | 2 | 0.85 | 744 PRINCESS PALM PL. (HYPERLINKED 4/18/17 TO BW - BB) CONTINUE QTRLY MONITORING (3/17 LRAA/T=67.7525)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 80.95 | UG/L | 80.4999 | 2017-02-27 | L2 | 0.14 |  | 2 | 0.85 | 744 PRINCESS PALM PL. (HYPERLINKED 4/18/17 TO BW - BB) CONTINUE QTRLY MONITORING (3/17 LRAA/T=67.7525)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 71.88 | UG/L | 80.4999 | 2017-05-18 | L1 | 0.14 |  | 1 | 1.2 | 3401 HUNT LANE (CONT. QM/T+H) NO LRAA MCL VIOLS OR OE EXCEEDANCES (HYPERLINKED 6/16/17 TO BW - BB)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.95 | UG/L | 60.4999 | 2017-05-18 | L1 | 0.5 |  | 1 | 1.2 | 3401 HUNT LANE (CONT. QM/T+H) NO LRAA MCL VIOLS OR OE EXCEEDANCES (HYPERLINKED 6/16/17 TO BW - BB)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.16 | UG/L | 60.4999 | 2017-05-18 | L2 | 0.5 |  | 2 | 1 | 744 PRINCESS PALM(6/17LRAA/T=76.1925)CONT.QM/T+H(6/17OE VAL/T=78.6075)NO LRAA MCL VIOLS OR OE EXCDNCS(HYPRLNKD 6/16/17 TO BW-GAVE ADVICE TO LET JF&CD KNOW@LATEST 80S RSLTS&TO TELL SYS TO TK ACTION-BB)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 89.52 | UG/L | 80.4999 | 2017-05-18 | L2 | 0.14 |  | 2 | 1 | 744 PRINCESS PALM(6/17LRAA/T=76.1925)CONT.QM/T+H(6/17OE VAL/T=78.6075)NO LRAA MCL VIOLS OR OE EXCDNCS(HYPRLNKD 6/16/17 TO BW-GAVE ADVICE TO LET JF&CD KNOW@LATEST 80S RSLTS&TO TELL SYS TO TK ACTION-BB)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.18 | MG/L | 10.4999 | 2017-08-23 | AAA | 0.051 |  |  |  | NN (PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-08-23 | AAA | 0.053 |  |  |  | NN (PLACED IN FINAL CHEM HOLDING FOLDER 10-23-17 - BB)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 82.96 | UG/L | 80.4999 | 2017-08-23 | L2 | 0.14 |  | 2 | 4.6 | ON QM - 744 PRINCESS PALM PLACE (HYPERLINKED TO BW 9/29/17 - BB) COMPUTE LRAAS TO SEE IF THERE'S AN MCL VIOL. OE EXCEEDANCE L2 SITE 9/17. 9/17 LRAA/T=76.9675 L2 SITE.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.3 | UG/L | 60.4999 | 2017-08-23 | L2 | 0.5 |  | 2 | 4.6 | ON QM - 744 PRINCESS PALM PLACE (HYPERLINKED TO BW 9/29/17 - BB) COMPUTE LRAAS TO SEE IF THERE'S AN MCL VIOL. OE EXCEEDANCE L2 SITE 9/17. 9/17 LRAA/T=76.9675 L2 SITE.
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 77.92 | UG/L | 80.4999 | 2017-08-23 | L1 | 0.14 |  | 1 | 0.4 | ON QM - 3401 HUNT LANE
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.4 | UG/L | 60.4999 | 2017-08-23 | L1 | 0.5 |  | 1 | 0.4 | ON QM - 3401 HUNT LANE
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 25.19 | UG/L | 80.4999 | 2017-11-20 | L2 | 0.14 |  | 2 | 0.3 | ON QM-744 PRINCESS PALM PLACE (MUST CONTINUE QM/DBPS) HYPERLINKED 12/22/17 TO BW - BB (12/22/17 3Q17 OE REPORT FOR TTHMS FOR L2 SITE MAY NOT HV BEEN RCVD - EMAILED BW - BB) LRAA/T=69.655
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.64 | UG/L | 60.4999 | 2017-11-20 | L2 | 0.5 |  | 2 | 0.3 | ON QM-744 PRINCESS PALM PLACE (MUST CONTINUE QM/DBPS) HYPERLINKED 12/22/17 TO BW - BB (12/22/17 3Q17 OE REPORT FOR TTHMS FOR L2 SITE MAY NOT HV BEEN RCVD - EMAILED BW - BB) LRAA/T=69.655
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 64.62 | UG/L | 80.4999 | 2017-11-20 | L1 | 0.14 |  | 1 | 0.3 | ON QM-3401 HUNT LANE (LRAA/T=72.47)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.96 | UG/L | 60.4999 | 2017-11-20 | L1 | 0.5 |  | 1 | 0.3 | ON QM-3401 HUNT LANE (LRAA/T=72.47)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-14 | AAA | 0.0004 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.36 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.23 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-14 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-14 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-14 | AAA | 0.24 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-14 | AAA | 0.12 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-14 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-14 | AAA | 0.22 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-14 | AAA | 0.17 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-14 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.16 | MG/L | 10.4999 | 2018-02-14 | AAA | 0.051 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-14 | AAA | 0.053 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-02-14 | AAA | 8e-05 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1010 | BARIUM | N | 0.012 | MG/L | 2.4999 | 2018-02-14 | AAA | 0.00083 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-14 | AAA | 6e-05 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-14 | AAA | 0.0016 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-14 | AAA | 0.0048 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1025 | FLUORIDE | N | 0.27 | MG/L | 4.0499 | 2018-02-14 | AAA | 0.075 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-14 | AAA | 0.00024 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-14 | AAA | 5e-05 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-14 | AAA | 0.006 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-14 | AAA | 0.00058 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1052 | SODIUM | N | 12 | MG/L | 160.4999 | 2018-02-14 | AAA | 0.34 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-14 | AAA | 0.00011 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-14 | AAA | 0.39 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-14 | AAA | 6e-05 |  |  |  | E53076/NN FL E84589/CY HG (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-14 | AAA | 0.028 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1017 | CHLORIDE | N | 19 | MG/L | 250.4999 | 2018-02-14 | AAA | 0.78 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-02-14 | AAA | 0.0032 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1025 | FLUORIDE | N | 0.27 | MG/L | 2.0499 | 2018-02-14 | AAA | 0.075 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-02-14 | AAA | 0.1 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1032 | MANGANESE | N | 0.0025 | MG/L | 0.0549 | 2018-02-14 | AAA | 0.0019 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-14 | AAA | 0.0001 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1055 | SULFATE | N | 4.9 | MG/L | 250.4999 | 2018-02-14 | AAA | 0.52 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-02-14 | AAA | 0.033 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-14 | AAA | 5 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-14 | AAA | 1 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.11 | LN(10) |  | 2018-02-14 | AAA |  |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 180 | MG/L | 500.4999 | 2018-02-14 | AAA | 10 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-14 | AAA | 0.04 |  |  |  | E53076/CHL FL SULF COL OD PH TDS E82001/F.AG. (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-14 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-14 | AAA | 0.32 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-14 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-14 | AAA | 0.44 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-14 | AAA | 0.46 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-14 | AAA | 0.26 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-14 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-14 | AAA | 0.18 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-14 | AAA | 0.28 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 49.61 | UG/L | 80.4999 | 2018-03-09 | L2 | 0.14 |  | 2 | 0.8 | 744 PRINCESS PALM PL. (3/18 LRAA/T = 61.82)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.55 | UG/L | 60.4999 | 2018-03-09 | L1 | 0.5 |  | 1 | 0.5 | 3401 HUNT LANE (LRAA/T = 65.785)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.91 | UG/L | 60.4999 | 2018-03-09 | L2 | 0.5 |  | 2 | 0.8 | 744 PRINCESS PALM PL. (3/18 LRAA/T = 61.82)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 48.72 | UG/L | 80.4999 | 2018-03-09 | L1 | 0.14 |  | 1 | 0.5 | 3401 HUNT LANE (LRAA/T = 65.785)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.5 | UG/L | 60.4999 | 2018-05-17 | L2 |  |  |  | 1
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 64.93 | UG/L | 80.4999 | 2018-05-17 | L1 |  |  |  | 1.1 | 3401 HUNT LANE TTHM
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.06 | UG/L | 60.4999 | 2018-05-17 | L1 |  |  |  |  | 3401 HUNT LANE
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 65.9 | UG/L | 80.4999 | 2018-05-17 | L2 |  |  |  | 1
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.63 | UG/L | 60.4999 | 2018-08-16 | L1 | 0.91 |  | 1 | 1.1
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 65.31 | UG/L | 80.4999 | 2018-08-16 | L2 | 0.39 |  | 2 | 1.5
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 45.32 | UG/L | 60.4999 | 2018-08-16 | L2 | 0.91 |  | 2 | 1.5
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 63.89 | UG/L | 80.4999 | 2018-08-16 | L1 | 0.39 |  | 1 | 1.1
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 58.55 | UG/L | 80.4999 | 2018-11-20 | L1 |  |  | 2 | 0.87 | 2950-3401 HUNT LANE / SUBCONTRACT LAB E84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.99 | UG/L | 60.4999 | 2018-11-20 | L2 |  |  | 1 | 0.81 | 2950-744 PRINCESS PALM PLACE / SUBCONTRACT LAB W84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 67.51 | UG/L | 80.4999 | 2018-11-20 | L2 |  |  | 1 | 0.81 | 2950-744 PRINCESS PALM PLACE / SUBCONTRACT LAB W84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.86 | UG/L | 60.4999 | 2018-11-20 | L1 |  |  | 2 | 0.87 | 2950-3401 HUNT LANE / SUBCONTRACT LAB E84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.54 | UG/L | 60.4999 | 2019-02-21 | L2 | 0.91 |  | 1 | 0.53 | 744 PRINCESS PALM PLACE (E53076 SUBC E82535 T E84589 H)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.24 | UG/L | 60.4999 | 2019-02-21 | L1 | 0.91 |  | 2 | 0.9 | 3401 HUNT LANE (E53076 SUBC E82535 T E84589 H) HLKD
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 56.83 | UG/L | 80.4999 | 2019-02-21 | L1 | 0.39 |  | 2 | 0.9 | 3401 HUNT LANE (E53076 SUBC E82535 T E84589 H) HLKD
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 66.95 | UG/L | 80.4999 | 2019-02-21 | L2 | 0.39 |  | 1 | 0.53 | 744 PRINCESS PALM PLACE (E53076 SUBC E82535 T E84589 H)
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.02 | UG/L | 60.4999 | 2019-05-20 | L1 |  |  | 2 | 0.72 | 3401 HUNT LANE / SUBCONTRACT LABS E82535 E84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 77.21 | UG/L | 80.4999 | 2019-05-20 | L2 |  |  | 1 | 0.47 | 744 PRINCESS PALM PLACE / SUBCONTRACT LABS E82535 E84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.01 | UG/L | 60.4999 | 2019-05-20 | L2 |  |  | 1 | 0.47 | 744 PRINCESS PALM PLACE / SUBCONTRACT LABS E82535 E84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 66.95 | UG/L | 80.4999 | 2019-05-20 | L1 |  |  | 2 | 0.72 | 3401 HUNT LANE / SUBCONTRACT LABS E82535 E84589
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.33 | UG/L | 60.4999 | 2019-08-20 | L2 |  |  | 1 | 0.45 | 744 PRINCESS PALM PLACE H LRAA = 38.9675; T LRAA = 66.225
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 29.21 | UG/L | 80.4999 | 2019-08-20 | L1 |  |  | 2 | 0.73 | 3401 HUNT LANE H LRAA= 38.095; T LRAA = 52.885
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 41.26 | UG/L | 60.4999 | 2019-08-20 | L1 |  |  | 2 | 0.73 | 3401 HUNT LANE H LRAA= 38.095; T LRAA = 52.885
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 53.23 | UG/L | 80.4999 | 2019-08-20 | L2 |  |  | 1 | 0.45 | 744 PRINCESS PALM PLACE H LRAA = 38.9675; T LRAA = 66.225
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-10-14 | AAA | 0.13 |  |  |  | NITRITE J QUALIFIER: LCS OK 86%/87% MS/MSD RECOVERIES - ACCEPTABLE
3590988 | PALM VALLEY MOBILE HOME PARK | INOR | 1040 | NITRATE | N | 0.27 | MG/L | 10.4999 | 2019-10-14 | AAA | 0.051 |  |  |  | NITRITE J QUALIFIER: LCS OK 86%/87% MS/MSD RECOVERIES - ACCEPTABLE
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 68.11 | UG/L | 80.4999 | 2019-11-19 | L1 | 0.39 |  | 2 | 0.63 | 3401 HUNT LN
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.92 | UG/L | 60.4999 | 2019-11-19 | L1 | 0.91 |  | 2 | 0.63 | 3401 HUNT LN
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | D | 74.68 | UG/L | 80.4999 | 2019-11-19 | L2 | 0.39 |  | 1 | 0.6 | 744 PRINCESS PALM
3590988 | PALM VALLEY MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.51 | UG/L | 60.4999 | 2019-11-19 | L2 | 0.91 |  | 1 | 0.6 | 744 PRINCESS PALM
3590993 | PARK RIDGE | INOR | 1010 | BARIUM | N | 0.0086 | MG/L | 2.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1052 | SODIUM | N | 41.8 | MG/L | 160.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 272 | MG/L | 500.4999 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1017 | CHLORIDE | N | 68.7 | MG/L | 250.4999 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1028 | IRON | N | 0.0186 | MG/L | 0.3499 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1055 | SULFATE | N | 5.12 | MG/L | 250.4999 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1905 | COLOR | N | 10 | COLOR UNITS | 15.4999 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.09 | LN(10) |  | 2015-02-18 | AAA |  |  |  |  | NO MCLS
3590993 | PARK RIDGE | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 0.5499 |  |  | 3YR VOC
3590993 | PARK RIDGE | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.0149 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 1.4999 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 1.4999 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-18 | AAA |  | 0.4499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-18 | AAA |  | 9.4999 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-18 | AAA |  | 6.4999 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-02-18 | AAA |  | 0.6499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-18 | AAA |  | 2.4999 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-18 | AAA |  | 0.0749 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-02-18 | AAA |  | 0.6499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-18 | AAA |  | 0.9499 |  |  | 3YR SOC
3590993 | PARK RIDGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-02-18 | AAA |  |  |  |  | (NO MCLS IN 2015 TRIENNIALS)15DON/16:3QM/T+H 3/16 NN RADS 2018 (SCOTT GOSNELL AREA MGR)
3590993 | PARK RIDGE | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-18 | AAA |  | 0.0449 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-18 | AAA |  | 0.0449 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-18 | AAA |  | 0.1499 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | AAA |  | 0.0249 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-18 | AAA |  | 0.0149 |  |  | 3YR SOC
3590993 | PARK RIDGE | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-18 | AAA |  | 0.2499 |  |  | 3YR SOC
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29 | UG/L | 60.4999 | 2015-08-12 | L1 |  |  |  | 1.2 | 161 CANAL STREET (QM/T+H 12/15>EM 9/18/15>GONGRE T>80) **SEE GONGRE'S 9/3/15 EM: T 93.8 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 93.8 | UG/L | 80.4999 | 2015-08-12 | L1 |  |  |  | 1.2 | 161 CANAL STREET (QM/T+H 12/15>EM 9/18/15>GONGRE T>80) **SEE GONGRE'S 9/3/15 EM: T 93.8 FOR 3RD QTR 2015 - HE KNOWS TO TEST QTRLY (SEE EM>GONGRE 9/4/15)
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.6 | UG/L | 60.4999 | 2015-11-11 | L1 |  |  |  | 0.9 | 161 CANAL STREET (12/15 LRAA/T=41.45 LRAA/H=12.15) NO OE EXCEEDANCE ("LISA AUGUST" SENDS DBPS NOW 3/3/16) 3/3 EW HAS 2/16 DBPS
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 72 | UG/L | 80.4999 | 2015-11-11 | L1 |  |  |  | 0.9 | 161 CANAL STREET (12/15 LRAA/T=41.45 LRAA/H=12.15) NO OE EXCEEDANCE ("LISA AUGUST" SENDS DBPS NOW 3/3/16) 3/3 EW HAS 2/16 DBPS
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 80.7 | UG/L | 80.4999 | 2016-02-09 | L1 |  |  |  | 1.5 | 161 CANAL STREET (AFT. 3 QTRS 3/16 LRAA/T=61.625 LRAA/H=22.1) 3/16 OE VALUE = 81.8 OE REPORT RQRD>EM 3/3/16>BKGONGRE. 3/16 OE REPORT IN OC. (8/18 EW HAS 5/16 T/H FOR ENTRY IN PWS-ALREADY IN OC)
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.8 | UG/L | 60.4999 | 2016-02-09 | L1 |  |  |  | 1.5 | 161 CANAL STREET (AFT. 3 QTRS 3/16 LRAA/T=61.625 LRAA/H=22.1) 3/16 OE VALUE = 81.8 OE REPORT RQRD>EM 3/3/16>BKGONGRE. 3/16 OE REPORT IN OC. (8/18 EW HAS 5/16 T/H FOR ENTRY IN PWS-ALREADY IN OC)
3590993 | PARK RIDGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3590993 | PARK RIDGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 70.4 | UG/L | 80.4999 | 2016-05-10 | L1 |  |  |  | 0.6 | 161 CANAL STREET (6/16 LRAA/T=79.225 LRAA/H=30.75)CONT.QM/T+H>8/18/16EM TO PEGGY HANKS B.GONGRE S.GOSNELL. 6/16 OE VAL=73.275 T (6/16 OE REPORT NOT NDD)
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.6 | UG/L | 60.4999 | 2016-05-10 | L1 |  |  |  | 0.6 | 161 CANAL STREET (6/16 LRAA/T=79.225 LRAA/H=30.75)CONT.QM/T+H>8/18/16EM TO PEGGY HANKS B.GONGRE S.GOSNELL. 6/16 OE VAL=73.275 T (6/16 OE REPORT NOT NDD)
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 68.5 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 0.9 | 161 CANAL STREET (3RD QTR 2016 LRAA/T=72.9 LRAA/H33.3) CONT. QTR MONITORING EM SENT TO UTILITIES INC. 9/12/16 EW
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 0.9 | 161 CANAL STREET (3RD QTR 2016 LRAA/T=72.9 LRAA/H33.3) CONT. QTR MONITORING EM SENT TO UTILITIES INC. 9/12/16 EW
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 41 | UG/L | 80.4999 | 2016-11-08 | L1 |  |  |  | 1.4 | 161 CANAL STREET (LRAA TTHM = 65.15 HAA5 = 40.075) TEST QUARTERLY STILL-CAN GO TO ROUTINE WHEN LRAA IS < 60 TTHM AND <45 HAA5 (REVISION RCVD 4/21/17 & HYPERLINKED 4/24/17 ADDRESS ALL CORRECTED)
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 46.9 | UG/L | 60.4999 | 2016-11-08 | L1 |  |  |  | 1.4 | 161 CANAL STREET (LRAA TTHM = 65.15 HAA5 = 40.075) TEST QUARTERLY STILL-CAN GO TO ROUTINE WHEN LRAA IS < 60 TTHM AND <45 HAA5 (REVISION RCVD 4/21/17 & HYPERLINKED 4/24/17 ADDRESS ALL CORRECTED)
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2017-01-04 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-01-04 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 141 | MG/L |  | 2017-01-04 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-01-17 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2017-01-17 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 144 | MG/L |  | 2017-01-17 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-02-01 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 144 | MG/L |  | 2017-02-01 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.3 | MG/L |  | 2017-02-01 | AAA
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 48.6 | UG/L | 80.4999 | 2017-02-07 | L1 | 0.5 |  | 1 | 1.2 | 161 CANAL (3/17 LRAA/T=57.125 LRAA/H=33.325) LRAAS FOR T<60 H<45. MAY STOP QM/T&H. NEXT ANNUAL DBPS DUE 7-9/2017 SPECIF. 2ND WEEK 8/17 - BW/BB. HYPERLINKED TO BW 3/3/17 - BB
3590993 | PARK RIDGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590993 | PARK RIDGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-07 | AAA | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.8 | UG/L | 60.4999 | 2017-02-07 | L1 | 0.5 |  | 1 | 1.2 | 161 CANAL (3/17 LRAA/T=57.125 LRAA/H=33.325) LRAAS FOR T<60 H<45. MAY STOP QM/T&H. NEXT ANNUAL DBPS DUE 7-9/2017 SPECIF. 2ND WEEK 8/17 - BW/BB. HYPERLINKED TO BW 3/3/17 - BB
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-02-15 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-02-15 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 136 | MG/L |  | 2017-02-15 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2017-03-01 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-03-01 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 144 | MG/L |  | 2017-03-01 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-03-15 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 160 | MG/L |  | 2017-03-15 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.5 | MG/L |  | 2017-03-15 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-03-28 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2017-03-28 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 141 | MG/L |  | 2017-03-28 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-04-11 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-04-11 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 136 | MG/L |  | 2017-04-11 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 136 | MG/L |  | 2017-04-26 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-04-26 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-04-26 | AAA
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 59.1 | UG/L | 80.4999 | 2017-05-08 | L1 | 0.5 |  | 1 | 1.6 | ANNUAL TTHMS PER LOC CODE SCREEN - 161 CANAL STREET (HYPERLINKED 6/9/17 TO BW - BB) SYSTEM WENT OFF QUARTERLY TESTING AFTER 3/17 QTR.
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.5 | UG/L | 60.4999 | 2017-05-08 | L1 | 0.5 |  | 1 | 1.6 | ANNUAL TTHMS PER LOC CODE SCREEN - 161 CANAL STREET (HYPERLINKED 6/9/17 TO BW - BB) SYSTEM WENT OFF QUARTERLY TESTING AFTER 3/17 QTR.
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 136 | MG/L |  | 2017-05-10 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-05-10 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-05-10 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-05-23 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-05-23 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 136 | MG/L |  | 2017-05-23 | AAA
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 136 | MG/L |  | 2017-06-06 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-06-06 | AAA
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-06-06 | AAA
3590993 | PARK RIDGE | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-06-22 | AAA |  |  |  |  | REPORT HAS 1.36 NOT 136 FOR TOTAL ALKALINITY FOR 6/22/17. IT'S PROBABLY 136 BUT NO REVISION WAS RECEIVED IF REQUESTED BY INSPECTOR. RESULTS ENTERED AS REPORTED - BB
3590993 | PARK RIDGE | WQP | 1924 | pH (FIELD) | N | 8 | LN(10) |  | 2017-06-22 | AAA |  |  |  |  | REPORT HAS 1.36 NOT 136 FOR TOTAL ALKALINITY FOR 6/22/17. IT'S PROBABLY 136 BUT NO REVISION WAS RECEIVED IF REQUESTED BY INSPECTOR. RESULTS ENTERED AS REPORTED - BB
3590993 | PARK RIDGE | WQP | 1927 | TOTAL ALKALINITY | N | 1.36 | MG/L |  | 2017-06-22 | AAA |  |  |  |  | REPORT HAS 1.36 NOT 136 FOR TOTAL ALKALINITY FOR 6/22/17. IT'S PROBABLY 136 BUT NO REVISION WAS RECEIVED IF REQUESTED BY INSPECTOR. RESULTS ENTERED AS REPORTED - BB
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 68.6 | UG/L | 80.4999 | 2017-11-08 | L1 | 0.5 |  | 1 | 0.6 | ANNUAL HAA5S PER LOC CODE SCREEN - 161 CANAL (LOC DESCRIPTION KEEPS REVERTING BACK TO "161 CANAL STREET (TTHMS)" NO MATTER HOW MANY TIMES THE RESULTS ARE ENTERED UNDER "161 CANAL STREET (HAA5S)"
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.5 | UG/L | 60.4999 | 2017-11-08 | L1 | 0.5 |  | 1 | 0.6 | ANNUAL HAA5S PER LOC CODE SCREEN - 161 CANAL (LOC DESCRIPTION KEEPS REVERTING BACK TO "161 CANAL STREET (TTHMS)" NO MATTER HOW MANY TIMES THE RESULTS ARE ENTERED UNDER "161 CANAL STREET (HAA5S)"
3590993 | PARK RIDGE | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.12 | LN(10) |  | 2018-03-07 | AAA | 0.01 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 326 | MG/L | 500.4999 | 2018-03-07 | AAA | 2.5 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-03-07 | AAA | 0.2 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-03-07 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-03-07 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-03-07 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-03-07 | AAA | 0.05 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.5 | 1.4999 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-03-07 | AAA | 0.1 | 1.4999 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-07 | AAA | 0.4 | 0.4499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-03-07 | AAA | 9 | 9.4999 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-07 | AAA | 6 | 6.4999 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-03-07 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-07 | AAA | 2 | 2.4999 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-03-07 | AAA | 0.07 | 0.0749 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-03-07 | AAA | 0.6 | 0.6499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-07 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-07 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-03-07 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-03-07 | AAA | 0.9 | 0.9499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-03-07 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-03-07 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-03-07 | AAA | 0.01 | 0.0449 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-03-07 | AAA | 0.01 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-07 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-07 | AAA | 0.2 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-03-07 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-03-07 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-07 | AAA | 0.04 | 0.0449 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-03-07 | AAA | 0.1 | 0.1499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-07 | AAA | 0.02 | 0.0249 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-07 | AAA | 0.01 | 0.0149 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-03-07 | AAA | 0.01 | 0.2499 |  |  | 3YR SOC (ALL OK)
3590993 | PARK RIDGE | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-03-07 | AAA | 2.1 |  |  |  | ALL OK
3590993 | PARK RIDGE | RAD | 4020 | RADIUM-226 | N | 1.2 | PCI/L | 3.4999 | 2018-03-07 | AAA | 0.4 | 1.4999 |  |  | ALL OK
3590993 | PARK RIDGE | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-03-07 | AAA | 0.7 | 1.4999 |  |  | ALL OK
3590993 | PARK RIDGE | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-03-07 | AAA | 0.2 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-03-07 | AAA | 0.2 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-03-07 | AAA | 0.001 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1010 | BARIUM | N | 0.0092 | MG/L | 2.4999 | 2018-03-07 | AAA | 0.002 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-03-07 | AAA | 0.001 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1020 | CHROMIUM | N | 0.0011 | MG/L | 0.1499 | 2018-03-07 | AAA | 0.001 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-03-07 | AAA | 0.005 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-03-07 | AAA | 2 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-03-07 | AAA | 0.001 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-03-07 | AAA | 2e-05 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-03-07 | AAA | 0.001 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-03-07 | AAA | 0.002 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1052 | SODIUM | N | 47.1 | MG/L | 160.4999 | 2018-03-07 | AAA | 0.5 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-03-07 | AAA | 0.001 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-03-07 | AAA | 0.0005 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-03-07 | AAA | 0.001 |  |  |  | UTILS INC. (NO MCLS IN THESE RESULTS)
3590993 | PARK RIDGE | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-03-07 | AAA | 0.02 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1017 | CHLORIDE | N | 76.3 | MG/L | 250.4999 | 2018-03-07 | AAA | 0.4 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1022 | COPPER | N | 0.007 | MG/L | 1.4999 | 2018-03-07 | AAA | 0.001 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-03-07 | AAA | 0.4 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1028 | IRON | N | 0.0113 | MG/L | 0.3499 | 2018-03-07 | AAA | 0.01 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-03-07 | AAA | 0.01 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-03-07 | AAA | 0.0005 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1055 | SULFATE | N | 4.95 | MG/L | 250.4999 | 2018-03-07 | AAA | 1 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1095 | ZINC | N | 0.013 | MG/L | 5.4999 | 2018-03-07 | AAA | 0.01 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-03-07 | AAA | 5 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-03-07 | AAA | 1 |  |  |  | NO MCLS IN THESE RESULTS
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 64.7 | UG/L | 80.4999 | 2018-05-08 | L1 |  |  |  | 1.5 | 161 CANAL STREET (TTHMS)
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 44.3 | UG/L | 60.4999 | 2018-05-08 | L1 |  |  |  | 1.5 | 161 CANAL STREET (TTHMS)
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.6 | UG/L | 60.4999 | 2018-11-07 | L1 |  |  |  | 1.6 | 2950-161 CANAL STREET (TTHMS)
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 81.3 | UG/L | 80.4999 | 2018-11-07 | L1 |  |  |  | 1.6 | 2950-161 CANAL STREET (TTHMS)
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 69.1 | UG/L | 80.4999 | 2019-02-05 | L1 | 0.5 |  | 2 |  | 161 CANAL TTHM
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.5 | UG/L | 60.4999 | 2019-02-05 | L1 | 1 |  | 1 | 1.5 | 161 CANAL HAA5
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 69.1 | UG/L | 80.4999 | 2019-02-05 | L1
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.5 | UG/L | 60.4999 | 2019-02-05 | L1
3590993 | PARK RIDGE | INOR | 1040 | NITRATE | N | 0.0139 | MG/L | 10.4999 | 2019-02-26 | AAA
3590993 | PARK RIDGE | INOR | 1041 | NITRITE | N | 0.0208 | MG/L | 1.4999 | 2019-02-26 | AAA
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 68.3 | UG/L | 60.4999 | 2019-05-04 | L1 |  |  |  | 1.4
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 54.4 | UG/L | 80.4999 | 2019-05-04 | L1 |  |  |  | 1.4
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.6 | UG/L | 60.4999 | 2019-08-05 | L1 | 1 |  | 1 | 0.5 | 161 CANAL STREET
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 68.5 | UG/L | 80.4999 | 2019-08-05 | L1 | 0.5 |  | 1 | 0.5 | 161 CANAL STREET
3590993 | PARK RIDGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.9 | UG/L | 60.4999 | 2019-11-05 | L1 | 1 |  | 1 | 1.5
3590993 | PARK RIDGE | DBP | 2950 | TOTAL THMS | D | 60.5 | UG/L | 80.4999 | 2019-11-05 | L1 | 0.5 |  | 1 | 1.5
3591061 | RAVENNA PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-18 | WP1 |  | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-18 | WP1 |  | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-18 | WP1 |  | 0.9499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-18 | WP1 |  | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-18 | WP1 |  | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-18 | WP1 |  | 0.0449 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-18 | WP1 |  | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-18 | WP1 |  | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-18 | WP1 |  | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | WP1 |  | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-18 | WP1 |  | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-18 | WP1 |  | 0.0449 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-18 | WP1 |  | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | WP1 |  | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-18 | WP1 |  | 0.0149 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-18 | WP1 |  | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.1 | PCI/L | 15.4999 | 2015-02-18 | WP1 |  |  |  |  | RADS DUE 2021
3591061 | RAVENNA PARK | RAD | 4020 | RADIUM-226 | N | 0.8 | PCI/L | 3.4999 | 2015-02-18 | WP1 |  | 1.4999 |  |  | RADS DUE 2021
3591061 | RAVENNA PARK | RAD | 4030 | RADIUM-228 | N | 1.4 | PCI/L | 2.4999 | 2015-02-18 | WP1 |  | 1.4999 |  |  | RADS DUE 2021
3591061 | RAVENNA PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1010 | BARIUM | N | 0.009 | MG/L | 2.4999 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1052 | SODIUM | N | 17.5 | MG/L | 160.4999 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-18 | WP1 |  |  |  |  | 15DON/16:NN ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016 RADS 2021 (SCOTT GOSNELL AREA MGR)
3591061 | RAVENNA PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1017 | CHLORIDE | N | 30.5 | MG/L | 250.4999 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1028 | IRON | N | 0.0353 | MG/L | 0.3499 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1055 | SULFATE | N | 8.48 | MG/L | 250.4999 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.11 | LN(10) |  | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 534 | MG/L | 500.4999 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-02-18 | WP1 |  |  |  |  | TDS 534 - TAKE 3 TDS RECHECKS>>3/20/15 & 4/2/15 EM SENT TO SCOTT GOSNELL (4/21 EW HAS 3/15 TDS - ON 3 CONSEC. DAYS)
3591061 | RAVENNA PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-18 | WP1 |  | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-18 | WP1 |  | 0.0149 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-18 | WP1 |  | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-18 | WP1 |  | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-18 | WP1 |  | 1.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-02-18 | WP1 |  | 1.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-18 | WP1 |  | 0.4499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-18 | WP1 |  | 9.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-18 | WP1 |  | 6.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-02-18 | WP1 |  | 0.6499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-18 | WP1 |  | 2.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-18 | WP1 |  | 0.0749 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-02-18 | WP1 |  | 0.6499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-18 | WP1 |  | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 240 | MG/L | 500.4999 | 2015-03-25 | WP1 |  |  |  |  | TDS (RESULT) RESULTS SATISFACTORY
3591061 | RAVENNA PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 240 | MG/L | 500.4999 | 2015-03-26 | WP1 |  |  |  |  | TDS (RESULT) RESULTS SATISFACTORY
3591061 | RAVENNA PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 236 | MG/L | 500.4999 | 2015-03-27 | WP1 |  |  |  |  | TDS (RESULT) RESULTS SATISFACTORY
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 48.9 | UG/L | 80.4999 | 2015-08-12 | L2 |  |  |  | 1.3 | (NEW STG2 PLAN IN OC APPRVD 5/3/16-2900 TRUMAN-R.PK & 155 FAIRWAY DR. **C.LK-R.PK. ACQUIRED C.LK. 3/16**) 101 IDYWILDE DRIVE (NO LRAA MCLS OR OE EXCEEDANCES) ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29 | UG/L | 60.4999 | 2015-08-12 | L2 |  |  |  | 1.3 | (NEW STG2 PLAN IN OC APPRVD 5/3/16-2900 TRUMAN-R.PK & 155 FAIRWAY DR. **C.LK-R.PK. ACQUIRED C.LK. 3/16**) 101 IDYWILDE DRIVE (NO LRAA MCLS OR OE EXCEEDANCES) ANN. T/H-2 SITES-DUE 2ND WK AUG. 2016
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 61.8 | UG/L | 80.4999 | 2015-08-12 | L1 |  |  |  | 1.1 | 2900 TRUMAN BLVD. (NO LRAA MCLS OR OE EXCEEDANCES)
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.7 | UG/L | 60.4999 | 2015-08-12 | L1 |  |  |  | 1.1 | 2900 TRUMAN BLVD. (NO LRAA MCLS OR OE EXCEEDANCES)
3591061 | RAVENNA PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-25 | WP1 |  |  |  |  | 2016 NN
3591061 | RAVENNA PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-25 | WP1 |  |  |  |  | 2016 NN
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 41.4 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 1.2 | 2900 TRUMAN BLVD.- CONT. ANNUAL MONITORING FOR BOTH
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.3 | UG/L | 60.4999 | 2016-08-10 | L3 |  |  |  | 1.8 | 155 FAIRWAY DR.- CONT. ANNUAL MONITORING FOR BOTH (5/3/16 NEW STG2 SITE )
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 35.9 | UG/L | 80.4999 | 2016-08-10 | L3 |  |  |  | 1.8 | 155 FAIRWAY DR.- CONT. ANNUAL MONITORING FOR BOTH (5/3/16 NEW STG2 SITE )
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.3 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 1.2 | 2900 TRUMAN BLVD.- CONT. ANNUAL MONITORING FOR BOTH
3591061 | RAVENNA PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-07 | WP1 | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3591061 | RAVENNA PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-07 | WP1 | 0.2 |  |  |  | HYPERLINKED TO BW 3/3/17 - BB
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.12 | UG/L | 60.4999 | 2017-08-11 | L3 | 0.5 |  | 2 | 0.5 | 155 FAIRWAY (HYPERLINKED 9/28/17 TO BW - BB)
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 69.9 | UG/L | 80.4999 | 2017-08-11 | L3 | 0.5 |  | 2 | 0.5 | 155 FAIRWAY (HYPERLINKED 9/28/17 TO BW - BB)
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.8 | UG/L | 60.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 1.1 | 2900 TRUMAN (HYPERLINKED 9/28/17 TO BW - BB)
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 60.4 | UG/L | 80.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 1.1 | 2900 TRUMAN (HYPERLINKED 9/28/17 TO BW - BB)
3591061 | RAVENNA PARK | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | WP1 | 0.5 | 1.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-03-07 | WP1 | 0.1 | 1.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-03-07 | WP1 | 0.4 | 0.4499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-03-07 | WP1 | 9 | 9.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-03-07 | WP1 | 6 | 6.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-03-07 | WP1 | 0.6 | 0.6499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-03-07 | WP1 | 0.1 | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-03-07 | WP1 | 0.2 | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-03-07 | WP1 | 0.01 | 0.0449 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-03-07 | WP1 | 0.01 | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-03-07 | WP1 | 0.1 | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-03-07 | WP1 | 0.2 | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-03-07 | WP1 | 0.1 | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-03-07 | WP1 | 0.02 | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-03-07 | WP1 | 0.04 | 0.0449 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-03-07 | WP1 | 0.1 | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-03-07 | WP1 | 2 | 2.4999 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-03-07 | WP1 | 0.07 | 0.0749 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-03-07 | WP1 | 0.6 | 0.6499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-03-07 | WP1 | 0.1 | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-03-07 | WP1 | 0.2 | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-03-07 | WP1 | 0.1 | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-03-07 | WP1 | 0.9 | 0.9499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-03-07 | WP1 | 0.02 | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-03-07 | WP1 | 0.01 | 0.0149 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-03-07 | WP1 | 0.01 | 0.2499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-03-07 | WP1 | 0.2
3591061 | RAVENNA PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-03-07 | WP1 | 0.2
3591061 | RAVENNA PARK | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | INOR | 1010 | BARIUM | N | 0.009 | MG/L | 2.4999 | 2018-03-07 | WP1 | 0.002
3591061 | RAVENNA PARK | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | INOR | 1020 | CHROMIUM | N | 0.0016 | MG/L | 0.1499 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-03-07 | WP1 | 0.005
3591061 | RAVENNA PARK | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-03-07 | WP1 | 0.2
3591061 | RAVENNA PARK | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-03-07 | WP1 | 2e-05
3591061 | RAVENNA PARK | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-03-07 | WP1 | 0.002
3591061 | RAVENNA PARK | INOR | 1052 | SODIUM | N | 18.9 | MG/L | 160.4999 | 2018-03-07 | WP1 | 0.5
3591061 | RAVENNA PARK | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-03-07 | WP1 | 0.0005
3591061 | RAVENNA PARK | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-03-07 | WP1 | 0.02
3591061 | RAVENNA PARK | SEC | 1017 | CHLORIDE | N | 30.9 | MG/L | 250.4999 | 2018-03-07 | WP1 | 0.4
3591061 | RAVENNA PARK | SEC | 1022 | COPPER | N | 0.0103 | MG/L | 1.4999 | 2018-03-07 | WP1 | 0.001
3591061 | RAVENNA PARK | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-03-07 | WP1 | 0.4
3591061 | RAVENNA PARK | SEC | 1028 | IRON | N | 0.0209 | MG/L | 0.3499 | 2018-03-07 | WP1 | 0.01
3591061 | RAVENNA PARK | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-03-07 | WP1 | 0.01
3591061 | RAVENNA PARK | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-03-07 | WP1 | 0.0005
3591061 | RAVENNA PARK | SEC | 1055 | SULFATE | N | 7.49 | MG/L | 250.4999 | 2018-03-07 | WP1 | 1
3591061 | RAVENNA PARK | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-03-07 | WP1 | 0.01
3591061 | RAVENNA PARK | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-03-07 | WP1 | 5
3591061 | RAVENNA PARK | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-03-07 | WP1 | 1
3591061 | RAVENNA PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.04 | LN(10) |  | 2018-03-07 | WP1 | 0.01
3591061 | RAVENNA PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 206 | MG/L | 500.4999 | 2018-03-07 | WP1 | 2.5
3591061 | RAVENNA PARK | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-03-07 | WP1 | 0.2
3591061 | RAVENNA PARK | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-03-07 | WP1 | 0.2 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-03-07 | WP1 | 0.5 | 0.5499 |  |  | 3YR VOC
3591061 | RAVENNA PARK | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-03-07 | WP1 | 0.01 | 0.0149 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-03-07 | WP1 | 0.01 | 0.0249 |  |  | 3YR SOC
3591061 | RAVENNA PARK | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-03-07 | WP1 | 0.05 | 0.1499 |  |  | 3YR SOC
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2018-08-07 | L3 | 0.5 |  | 1 | 0.4
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-08-07 | L3 | 0.5 |  | 1 | 0.4
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.6 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 0.4
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 51.9 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 0.4
3591061 | RAVENNA PARK | INOR | 1040 | NITRATE | N | 0.023 | MG/L | 10.4999 | 2019-02-26 | WP1 |  |  |  |  | 3591008 WP/WELL MERGED TO 3591061 ON 2/13/2019
3591061 | RAVENNA PARK | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | WP1 |  |  |  |  | 3591008 WP/WELL MERGED TO 3591061 ON 2/13/2019
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.9 | UG/L | 60.4999 | 2019-08-12 | L1 | 1 |  | 1 | 1.5 | 2900 TRUMAN BLVD. (CANNOT ENTER 2ND SITE'S RESULTS - SITE NOT SET UP YET - NEW SITE 108 PAR PLACE)
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 68 | UG/L | 80.4999 | 2019-08-12 | L4 | 0.5 |  | 1 | 2
3591061 | RAVENNA PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.1 | UG/L | 60.4999 | 2019-08-12 | L4 | 1 |  | 1 | 2
3591061 | RAVENNA PARK | DBP | 2950 | TOTAL THMS | D | 75.7 | UG/L | 80.4999 | 2019-08-12 | L1 | 0.5 |  | 1 | 1.5 | 2900 TRUMAN BLVD. (CANNOT ENTER 2ND SITE'S RESULTS - SITE NOT SET UP YET - NEW SITE 108 PAR PLACE)
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-05 | WTP1 |  |  |  |  | DES PINAR WP
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-05 | WTP1 |  |  |  |  | DES PINAR WP
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-05 | WTP2 |  |  |  |  | KNOLLWOOD (FKA OVERSTREET) WP
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-05 | WTP2 |  |  |  |  | KNOLLWOOD (FKA OVERSTREET) WP
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-05 | WTP3 |  |  |  |  | WEKIVA HUNT CLUB WP
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-05 | WTP3 |  |  |  |  | WEKIVA HUNT CLUB WP
3591121 | SANLANDO (3 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-05 | WTP2 |  | 0.5499 |  |  | 1AM/XY+ETH - KNOLLWOOD WP (2AM/XY+ETH-KNOLLWOOD DUE 1Q 2016)
3591121 | SANLANDO (3 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-05 | WTP2 |  | 0.5499 |  |  | 1AM/XY+ETH - KNOLLWOOD WP (2AM/XY+ETH-KNOLLWOOD DUE 1Q 2016)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 75.4 | UG/L | 80.4999 | 2015-02-10 | L2 |  |  |  | 0.5 | 260 NEW WATERFORD PLACE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0.587 | UG/L | 60.4999 | 2015-02-10 | L3 |  |  |  | 3.5 | 118 CROWN POINT (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 46.1 | UG/L | 80.4999 | 2015-02-10 | L1 |  |  |  | 0.6 | 1557 REBECCA (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.7 | UG/L | 60.4999 | 2015-02-10 | L1 |  |  |  | 0.6 | 1557 REBECCA (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.9 | UG/L | 60.4999 | 2015-02-10 | L2 |  |  |  | 0.5 | 260 NEW WATERFORD PLACE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 18.1 | UG/L | 80.4999 | 2015-02-10 | L3 |  |  |  | 3.5 | 118 CROWN POINT (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 53.6 | UG/L | 60.4999 | 2015-02-10 | L4 |  |  |  | 2.5 | (6/19/15 EW HAS 5/15 DBPS & 6/15 DBF BY EM) 1532 SUNSHINE TREE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 35.4 | UG/L | 80.4999 | 2015-02-10 | L4 |  |  |  | 2.5 | (6/19/15 EW HAS 5/15 DBPS & 6/15 DBF BY EM) 1532 SUNSHINE TREE (SYS. DOES NOT QUALIFY FOR R.M.) NO LRAA OR OE EXCEEDANCES
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 26.5 | UG/L | 80.4999 | 2015-05-13 | L4 |  |  |  | 3 | 1532 SUNSHINE TREE (NO LRAA OR OE MCLS SYSTEM DOES NOT QUALIFY FOR REDUCED MONITORING) 5/15 DBPS & 6/15 DBF IN OC
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.5 | UG/L | 60.4999 | 2015-05-13 | L1 |  |  |  | 0.4 | 1557 REBECCA
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 60.8 | UG/L | 80.4999 | 2015-05-13 | L1 |  |  |  | 0.4 | 1557 REBECCA
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 33.3 | UG/L | 80.4999 | 2015-05-13 | L3 |  |  |  | 3.5 | 118 CROWN POINT
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.7 | UG/L | 60.4999 | 2015-05-13 | L4 |  |  |  | 3 | 1532 SUNSHINE TREE (NO LRAA OR OE MCLS SYSTEM DOES NOT QUALIFY FOR REDUCED MONITORING) 5/15 DBPS & 6/15 DBF IN OC
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 72.4 | UG/L | 60.4999 | 2015-05-13 | L3 |  |  |  | 3.5 | 118 CROWN POINT
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 33.1 | UG/L | 80.4999 | 2015-05-13 | L2 |  |  |  | 2.5 | 260 NEW WATERFORD PLACE
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.1 | UG/L | 60.4999 | 2015-05-13 | L2 |  |  |  | 2.5 | 260 NEW WATERFORD PLACE
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.2 | UG/L | 60.4999 | 2015-08-13 | L1 |  |  |  | 0.4 | 1557 REBECCA (RESULTS OKAY) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 28.7 | UG/L | 80.4999 | 2015-08-13 | L4 |  |  |  | 3 | (12/7 EW HAS 11/15 DBPS & DBF) 1532 SUNSHINE TREE (HAA5 OE EXCEEDANCE 65.9 - OE REPORT IN OCULUS) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 90.6 | UG/L | 60.4999 | 2015-08-13 | L4 |  |  |  | 3 | (12/7 EW HAS 11/15 DBPS & DBF) 1532 SUNSHINE TREE (HAA5 OE EXCEEDANCE 65.9 - OE REPORT IN OCULUS) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 34.7 | UG/L | 80.4999 | 2015-08-13 | L3 |  |  |  | 3 | 118 CROWN POINT (HAA5 OE EXCEEDANCE 61.6 UG/L - OE REPORT IN OCULUS) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 86.7 | UG/L | 60.4999 | 2015-08-13 | L3 |  |  |  | 3 | 118 CROWN POINT (HAA5 OE EXCEEDANCE 61.6 UG/L - OE REPORT IN OCULUS) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 101 | UG/L | 80.4999 | 2015-08-13 | L2 |  |  |  | 0.3 | 260 NEW WATERFORD PLACE (LAB REPORT OK) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS OE REPORT NOT RQRD - @ 77 FOR TTHMS FOR OE VALUE)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 59.1 | UG/L | 80.4999 | 2015-08-13 | L1 |  |  |  | 0.4 | 1557 REBECCA (RESULTS OKAY) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.9 | UG/L | 60.4999 | 2015-08-13 | L2 |  |  |  | 0.3 | 260 NEW WATERFORD PLACE (LAB REPORT OK) 9/15 DBF W/RSLTS (NO LRAA MCL VIOLS OE REPORT NOT RQRD - @ 77 FOR TTHMS FOR OE VALUE)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 18 | UG/L | 80.4999 | 2015-11-11 | L2 |  |  |  | 1.6 | 260 NEW WATERFORD PLACE (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.2 | UG/L | 60.4999 | 2015-11-11 | L4 |  |  |  | 3.2 | 1532 SUNSHINE TREE (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.) 3/3 EW HAS 2/16 DBPS
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.8 | UG/L | 60.4999 | 2015-11-11 | L1 |  |  |  | 1.8 | 1557 REBECCA (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.) CHANGE IN SITE 12/15/15 FROM 1557 REBECCA TO 1554 REBECCA DUE TO SOFTENER AT 1557 REBECCA) REVISED STG2 PLAN IN OC.
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 32.1 | UG/L | 80.4999 | 2015-11-11 | L1 |  |  |  | 1.8 | 1557 REBECCA (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.) CHANGE IN SITE 12/15/15 FROM 1557 REBECCA TO 1554 REBECCA DUE TO SOFTENER AT 1557 REBECCA) REVISED STG2 PLAN IN OC.
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.93 | UG/L | 60.4999 | 2015-11-11 | L2 |  |  |  | 1.6 | 260 NEW WATERFORD PLACE (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 27.7 | UG/L | 80.4999 | 2015-11-11 | L4 |  |  |  | 3.2 | 1532 SUNSHINE TREE (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.) 3/3 EW HAS 2/16 DBPS
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.66 | UG/L | 60.4999 | 2015-11-11 | L3 |  |  |  | 1.6 | 118 CROWN POINT (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 16.3 | UG/L | 80.4999 | 2015-11-11 | L3 |  |  |  | 1.6 | 118 CROWN POINT (NO LRAA MCLS NO OE EXCEEDANCES DOES NOT QUALIFY FOR R.M.)
3591121 | SANLANDO (3 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-01-07 | WTP2 |  | 0.5499 |  |  | 2AM/XY+ETH-KNOLLWOOD DUE 1Q 2016 (3AM/XY+ETH-KNOLLWOOD DUE 1Q 2017)
3591121 | SANLANDO (3 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-01-07 | WTP2 |  | 0.5499 |  |  | 2AM/XY+ETH-KNOLLWOOD DUE 1Q 2016 (3AM/XY+ETH-KNOLLWOOD DUE 1Q 2017)
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-09 | WTP1 |  |  |  |  | DES PINAR WP NN
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 30.3 | UG/L | 80.4999 | 2016-02-09 | L4 |  |  |  | 3.2 | 8/18EW HAS 5/16 DBPS 6/16DB RPRT IN OC)1532 SUNSHINE TREE(3/16DB RPRT IN OC DOES NOT QUAL.FOR R.M.DOES NOT HV OE EXCEEDANCE OR LRAA MCL)RQSTD3/16 DBF OF LISA AUGUST ON 3/3/16 BY EM&8/18TO S.GOSNELL-BB
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.3 | UG/L | 60.4999 | 2016-02-09 | L4 |  |  |  | 3.2 | 8/18EW HAS 5/16 DBPS 6/16DB RPRT IN OC)1532 SUNSHINE TREE(3/16DB RPRT IN OC DOES NOT QUAL.FOR R.M.DOES NOT HV OE EXCEEDANCE OR LRAA MCL)RQSTD3/16 DBF OF LISA AUGUST ON 3/3/16 BY EM&8/18TO S.GOSNELL-BB
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 36.7 | UG/L | 80.4999 | 2016-02-09 | L3 |  |  |  | 2.8 | 118 CROWN POINT (RQSTED 3/16 DBF OF LISA AUGUST ON 3/3/16 BY EMAIL) DOES NOT QUALIFY FOR R.M. DOES NOT HAVE OE EXCEEDANCE OR LRAA MCL
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.8 | UG/L | 60.4999 | 2016-02-09 | L3 |  |  |  | 2.8 | 118 CROWN POINT (RQSTED 3/16 DBF OF LISA AUGUST ON 3/3/16 BY EMAIL) DOES NOT QUALIFY FOR R.M. DOES NOT HAVE OE EXCEEDANCE OR LRAA MCL
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 21.6 | UG/L | 80.4999 | 2016-02-09 | L2 |  |  |  | 1.4 | 260 NEW WATERFORD PLACE (RQSTED 3/16 DBF OF LISA AUGUST ON 3/3/16 BY EMAIL) DOES NOT QUALIFY FOR R.M. DOES NOT HAVE OE EXCEEDANCE OR LRAA MCL
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.1 | UG/L | 60.4999 | 2016-02-09 | L2 |  |  |  | 1.4 | 260 NEW WATERFORD PLACE (RQSTED 3/16 DBF OF LISA AUGUST ON 3/3/16 BY EMAIL) DOES NOT QUALIFY FOR R.M. DOES NOT HAVE OE EXCEEDANCE OR LRAA MCL
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 39.3 | UG/L | 80.4999 | 2016-02-09 | L1 |  |  |  | 2.6 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER) (RQSTED 3/16 DBF OF LISA AUGUST ON 3/3/16 BY EMAIL) DOES NOT QUALIFY FOR R.M. DOES NOT HAVE OE EXCEEDANCE OR LRAA MCL
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.5 | UG/L | 60.4999 | 2016-02-09 | L1 |  |  |  | 2.6 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER) (RQSTED 3/16 DBF OF LISA AUGUST ON 3/3/16 BY EMAIL) DOES NOT QUALIFY FOR R.M. DOES NOT HAVE OE EXCEEDANCE OR LRAA MCL
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-09 | WTP1 |  |  |  |  | DES PINAR WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-09 | WTP2 |  |  |  |  | KNOLLWOOD (FKA OVERSTREET) WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-09 | WTP2 |  |  |  |  | KNOLLWOOD (FKA OVERSTREET) WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-09 | WTP3 |  |  |  |  | WEKIVA HUNT CLUB WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-09 | WTP3 |  |  |  |  | WEKIVA HUNT CLUB WP NN
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 30.1 | UG/L | 80.4999 | 2016-05-10 | L4 |  |  |  | 2.5 | 1532 SUNSHINE TREE (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.1 | UG/L | 60.4999 | 2016-05-10 | L4 |  |  |  | 2.5 | 1532 SUNSHINE TREE (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 33.8 | UG/L | 80.4999 | 2016-05-10 | L3 |  |  |  | 2.1 | 118 CROWN POINT (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.8 | UG/L | 60.4999 | 2016-05-10 | L3 |  |  |  | 2.1 | 118 CROWN POINT (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 24.4 | UG/L | 80.4999 | 2016-05-10 | L2 |  |  |  | 2 | 260 NEW WATERFORD PLACE (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15 | UG/L | 60.4999 | 2016-05-10 | L2 |  |  |  | 2 | 260 NEW WATERFORD PLACE (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 37.3 | UG/L | 80.4999 | 2016-05-10 | L1 |  |  |  | 1.2 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER) (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.1 | UG/L | 60.4999 | 2016-05-10 | L1 |  |  |  | 1.2 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER) (8/18 EM TO S.GOSNELL B.GONGRE PEGGY HANKS FOR 3/16 & 6/16 DB REPORTS HAD ALREADY RQSTD 3/16 DB REPORT OF LISA AUGUST IN 3/3/16 EM)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 41.8 | UG/L | 80.4999 | 2016-08-11 | L1 |  |  |  | 2 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER) (9/16 LRAA/T=37.6 LRAA/H=24.9)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.8 | UG/L | 60.4999 | 2016-08-11 | L2 |  |  |  | 2.4 | 260 NEW WATERFORD PLACE (9/16 LRAA/T=21.9 LRAA/H=15.5)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.3 | UG/L | 60.4999 | 2016-08-11 | L1 |  |  |  | 2 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER) (9/16 LRAA/T=37.6 LRAA/H=24.9)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 19.5 | UG/L | 80.4999 | 2016-08-11 | L4 |  |  |  | 3 | 1532 SUNSHINE TREE (9/16 LRAA/T=26.9 LRAA/H=18.2)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.2 | UG/L | 60.4999 | 2016-08-11 | L4 |  |  |  | 3 | 1532 SUNSHINE TREE (9/16 LRAA/T=26.9 LRAA/H=18.2)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 35 | UG/L | 80.4999 | 2016-08-11 | L3 |  |  |  | 2.2 | 118 CROWN POINT (9/16 LRAA/T=30.5 LRAA/H=17.3)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.7 | UG/L | 60.4999 | 2016-08-11 | L3 |  |  |  | 2.2 | 118 CROWN POINT (9/16 LRAA/T=30.5 LRAA/H=17.3)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 23.4 | UG/L | 80.4999 | 2016-08-11 | L2 |  |  |  | 2.4 | 260 NEW WATERFORD PLACE (9/16 LRAA/T=21.9 LRAA/H=15.5)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16 | UG/L | 60.4999 | 2016-11-07 | L4 |  |  |  | 1.2 | 1532 SUNSHINE TREE
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 14.8 | UG/L | 80.4999 | 2016-11-07 | L4 |  |  |  | 1.2 | 1532 SUNSHINE TREE
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 16.5 | UG/L | 80.4999 | 2016-11-07 | L3 |  |  |  | 2.6 | 118 CROWN POINT
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.3 | UG/L | 60.4999 | 2016-11-07 | L3 |  |  |  | 2.6 | 118 CROWN POINT
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 25.4 | UG/L | 80.4999 | 2016-11-07 | L2 |  |  |  | 2.8 | 260 NEW WATERFORD PLACE
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.1 | UG/L | 60.4999 | 2016-11-07 | L1 |  |  |  | 1.6 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 38.3 | UG/L | 80.4999 | 2016-11-07 | L1 |  |  |  | 1.6 | 1554 REBECCA (WAS 1557 REBECCA-SOFTENER)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.2 | UG/L | 60.4999 | 2016-11-07 | L2 |  |  |  | 2.8 | 260 NEW WATERFORD PLACE
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-01-06 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2017-01-06 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-01-06 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-01-12 | WTP2 | 0.5 | 0.5499 |  |  | 3AM/XY+ETH-KNOLLWOOD WP (STOP AM/XY+ETH LAST 3 YRS -0- FOR EACH) ANNUAL TESTING FOR XY+ETH COMPLETED
3591121 | SANLANDO (3 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-01-12 | WTP2 | 0.5 | 0.5499 |  |  | 3AM/XY+ETH-KNOLLWOOD WP (STOP AM/XY+ETH LAST 3 YRS -0- FOR EACH) ANNUAL TESTING FOR XY+ETH COMPLETED
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-01-17 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2017-01-17 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-01-17 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-02-01 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-02-01 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-02-01 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2017-02-15 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-02-15 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-02-15 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP3 | 0.1 | 0.1499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-21 | WTP3 | 0.2 | 0.2499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-21 | WTP2 | 0.6 | 1.4999 |  |  | KNOLLWOOD WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023 - KNOLLWOOD WP) RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-21 | WTP3 | 0.2 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-21 | WTP3 | 0.2 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1010 | BARIUM | N | 0.0089 | MG/L | 2.4999 | 2017-02-21 | WTP3 | 0.002 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-21 | WTP3 | 0.005 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2017-02-21 | WTP3 | 0.2 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-21 | WTP3 | 2e-05 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-21 | WTP3 | 0.002 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1052 | SODIUM | N | 11.1 | MG/L | 160.4999 | 2017-02-21 | WTP3 | 0.5 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-21 | WTP3 | 0.0005 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-21 | WTP3 | 0.02 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1017 | CHLORIDE | N | 14.6 | MG/L | 250.4999 | 2017-02-21 | WTP3 | 0.4 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1022 | COPPER | N | 0.0063 | MG/L | 1.4999 | 2017-02-21 | WTP3 | 0.001 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2017-02-21 | WTP3 | 0.2 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-21 | WTP3 | 0.01 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-21 | WTP3 | 0.01 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP3 | 0.0005 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1055 | SULFATE | N | 73.6 | MG/L | 250.4999 | 2017-02-21 | WTP3 | 1 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-21 | WTP3 | 0.01 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-21 | WTP3 | 5 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-21 | WTP3 | 1 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.13 | LN(10) |  | 2017-02-21 | WTP3 | 0.01 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 260 | MG/L | 500.4999 | 2017-02-21 | WTP3 | 2.5 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-21 | WTP3 | 0.2 |  |  |  | WEKIVA HUNT CLUB WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP3 | 0.2 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP3 | 0.0101 | 0.0149 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP3 | 0.0101 | 0.0249 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-21 | WTP3 | 0.0503 | 0.1499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP3 | 0.503 | 1.4999 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP3 | 0.1 | 1.4999 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-21 | WTP3 | 0.4 | 0.4499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP3 | 9 | 9.4999 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-21 | WTP3 | 6 | 6.4999 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-21 | WTP3 | 0.6 | 0.6499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP3 | 2 | 2.4999 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-21 | WTP3 | 0.07 | 0.0749 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-21 | WTP3 | 0.6 | 0.6499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-21 | WTP3 | 0.1 | 0.1499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-21 | WTP3 | 0.2 | 0.2499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-21 | WTP3 | 0.101 | 0.1499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-21 | WTP3 | 0.9 | 0.9499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP3 | 0.1 | 0.1499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP3 | 0.2 | 0.2499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-21 | WTP3 | 0.0101 | 0.0449 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP3 | 0.0101 | 0.0249 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SEC | 1022 | COPPER | N | 0.0053 | MG/L | 1.4999 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2017-02-21 | WTP2 | 0.2 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1028 | IRON | N | 0.106 | MG/L | 0.3499 | 2017-02-21 | WTP2 | 0.01 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-21 | WTP2 | 0.01 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP2 | 0.0005 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1055 | SULFATE | N | 28.9 | MG/L | 250.4999 | 2017-02-21 | WTP2 | 1 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1095 | ZINC | N | 0.042 | MG/L | 5.4999 | 2017-02-21 | WTP2 | 0.01 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-21 | WTP2 | 5 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-21 | WTP2 | 1 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.36 | LN(10) |  | 2017-02-21 | WTP2 | 0.01 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 212 | MG/L | 500.4999 | 2017-02-21 | WTP2 | 2.5 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-21 | WTP2 | 0.2 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP2 | 0.2 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP2 | 0.5 | 0.5499 |  |  | 3YR VOC/KNOLLWOOD WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP2 | 0.0101 | 0.0149 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP2 | 0.0101 | 0.0249 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-21 | WTP2 | 0.0504 | 0.1499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP2 | 0.504 | 1.4999 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP2 | 0.1 | 1.4999 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-21 | WTP2 | 0.4 | 0.4499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP2 | 9 | 9.4999 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP3 | 0.101 | 0.1499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP3 | 0.02 | 0.0249 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP3 | 0.04 | 0.0449 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-21 | WTP3 | 0.101 | 0.1499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP3 | 0.0201 | 0.0249 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-21 | WTP3 | 0.0101 | 0.0149 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP3 | 0.0101 | 0.2499 |  |  | 1Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-21 | WTP3 | 1.7 |  |  |  | WEKIVA HUNT CLUB WP (GA DUE 2026 R226+R228 DUE 2023 UR DUE 2023) MUST RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | RAD | 4020 | RADIUM-226 | N | 1.7 | PCI/L | 3.4999 | 2017-02-21 | WTP3 | 0.3 | 1.4999 |  |  | WEKIVA HUNT CLUB WP (GA DUE 2026 R226+R228 DUE 2023 UR DUE 2023) MUST RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | RAD | 4030 | RADIUM-228 | N | 0.6 | PCI/L | 2.4999 | 2017-02-21 | WTP3 | 0.6 | 1.4999 |  |  | WEKIVA HUNT CLUB WP (GA DUE 2026 R226+R228 DUE 2023 UR DUE 2023) MUST RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP2 | 0.2 | 0.2499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-21 | WTP2 | 0.0101 | 0.0449 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP2 | 0.0101 | 0.0249 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP2 | 0.1 | 0.1499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-21 | WTP2 | 0.2 | 0.2499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP2 | 0.101 | 0.1499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP2 | 0.02 | 0.0249 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP2 | 0.04 | 0.0449 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-21 | WTP2 | 0.101 | 0.1499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP2 | 0.0202 | 0.0249 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-21 | WTP2 | 0.0101 | 0.0149 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP2 | 0.0101 | 0.2499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-21 | WTP2 | 1.4 |  |  |  | KNOLLWOOD WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023 - KNOLLWOOD WP) RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | RAD | 4020 | RADIUM-226 | N | 0.9 | PCI/L | 3.4999 | 2017-02-21 | WTP2 | 0.4 | 1.4999 |  |  | KNOLLWOOD WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023 - KNOLLWOOD WP) RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP1 | 0.0101 | 0.0149 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP1 | 0.0101 | 0.0249 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-21 | WTP1 | 0.0506 | 0.1499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP1 | 0.506 | 1.4999 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP1 | 0.1 | 1.4999 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-21 | WTP1 | 0.4 | 0.4499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP1 | 9 | 9.4999 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-21 | WTP1 | 6 | 6.4999 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-21 | WTP1 | 0.6 | 0.6499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP1 | 2 | 2.4999 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-21 | WTP1 | 0.07 | 0.0749 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-21 | WTP1 | 0.6 | 0.6499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-21 | WTP1 | 0.1 | 0.1499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-21 | WTP1 | 0.2 | 0.2499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-21 | WTP1 | 0.101 | 0.1499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-21 | WTP1 | 0.9 | 0.9499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP1 | 0.1 | 0.1499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP1 | 0.2 | 0.2499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-21 | WTP1 | 0.0101 | 0.0449 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP1 | 0.0101 | 0.0249 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP1 | 0.1 | 0.1499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-21 | WTP1 | 0.2 | 0.2499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP1 | 0.101 | 0.1499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP1 | 0.02 | 0.0249 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP1 | 0.04 | 0.0449 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-21 | WTP1 | 0.101 | 0.1499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-21 | WTP3 | 0.5 | 0.5499 |  |  | 3YR VOC/WEKIVA HUNT CLUB WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-21 | WTP2 | 0.005 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2017-02-21 | WTP2 | 0.2 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-21 | WTP2 | 2e-05 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-21 | WTP2 | 0.002 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1052 | SODIUM | N | 16.9 | MG/L | 160.4999 | 2017-02-21 | WTP2 | 0.5 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-21 | WTP2 | 0.0005 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-21 | WTP2 | 0.02 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1017 | CHLORIDE | N | 23.4 | MG/L | 250.4999 | 2017-02-21 | WTP2 | 0.4 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-21 | WTP1 | 0.0202 | 0.0249 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-21 | WTP1 | 0.0101 | 0.0149 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-21 | WTP1 | 0.0101 | 0.2499 |  |  | 1Q SOC/DES PINAR WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.4 | PCI/L | 15.4999 | 2017-02-21 | WTP1 | 1.4 |  |  |  | DES PINAR WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023 - DES PINAR WP) RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | RAD | 4020 | RADIUM-226 | N | 0.7 | PCI/L | 3.4999 | 2017-02-21 | WTP1 | 0.4 | 1.4999 |  |  | DES PINAR WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023 - DES PINAR WP) RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-21 | WTP1 | 0.6 | 1.4999 |  |  | DES PINAR WP (GA DUE 2026 R226+R228 DUE 2026 UR DUE 2023 - DES PINAR WP) RESET RADS WVRS BASED ON 2017 RESULTS-BB
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-21 | WTP2 | 0.2 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-21 | WTP2 | 0.2 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-21 | WTP2 | 0.001 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1010 | BARIUM | N | 0.0135 | MG/L | 2.4999 | 2017-02-21 | WTP2 | 0.002 |  |  |  | KNOLLWOOD WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-21 | WTP1 | 0.2 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-21 | WTP1 | 0.2 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1010 | BARIUM | N | 0.0064 | MG/L | 2.4999 | 2017-02-21 | WTP1 | 0.002 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-21 | WTP1 | 0.005 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2017-02-21 | WTP1 | 0.2 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-21 | WTP1 | 2e-05 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-21 | WTP1 | 0.002 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1052 | SODIUM | N | 13.9 | MG/L | 160.4999 | 2017-02-21 | WTP1 | 0.5 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-21 | WTP1 | 0.0005 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-21 | WTP1 | 0.02 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1017 | CHLORIDE | N | 23 | MG/L | 250.4999 | 2017-02-21 | WTP1 | 0.4 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1022 | COPPER | N | 0.0184 | MG/L | 1.4999 | 2017-02-21 | WTP1 | 0.001 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2017-02-21 | WTP1 | 0.2 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1028 | IRON | N | 0.0243 | MG/L | 0.3499 | 2017-02-21 | WTP1 | 0.01 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-21 | WTP1 | 0.01 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-21 | WTP1 | 0.0005 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-21 | WTP2 | 6 | 6.4999 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-21 | WTP2 | 0.6 | 0.6499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-21 | WTP2 | 2 | 2.4999 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-21 | WTP2 | 0.07 | 0.0749 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-21 | WTP2 | 0.6 | 0.6499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-21 | WTP2 | 0.1 | 0.1499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-21 | WTP2 | 0.2 | 0.2499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-21 | WTP2 | 0.101 | 0.1499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-21 | WTP2 | 0.9 | 0.9499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-21 | WTP2 | 0.1 | 0.1499 |  |  | 1Q SOC/KNOLLWOOD WP (2 QTRS SOCS DUE IN 2017 PER WP AT LEAST 60 DAYS APART) NO DETECTIONS
3591121 | SANLANDO (3 WTPS) | SEC | 1055 | SULFATE | N | 20.1 | MG/L | 250.4999 | 2017-02-21 | WTP1 | 1 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-21 | WTP1 | 0.01 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-21 | WTP1 | 5 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-21 | WTP1 | 1 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.17 | LN(10) |  | 2017-02-21 | WTP1 | 0.01 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 210 | MG/L | 500.4999 | 2017-02-21 | WTP1 | 2.5 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-21 | WTP1 | 0.2 |  |  |  | DES PINAR WP (NO RESULTS ABOVE THE MCL)
3591121 | SANLANDO (3 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-21 | WTP1 | 0.2 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-21 | WTP1 | 0.5 | 0.5499 |  |  | 3YR VOC/DES PINAR WP (NO DETECTIONS)
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.4 | MG/L |  | 2017-03-01 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-03-01 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-03-01 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-03-15 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-03-15 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-03-15 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-03-28 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-03-28 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2017-03-28 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-04-11 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.1 | MG/L |  | 2017-04-11 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-04-11 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 0.8 | MG/L |  | 2017-04-26 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-04-26 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-04-26 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-04 | WTP3 | 0.9 | 0.9499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP3 | 0.1 | 0.1499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP3 | 0.2 | 0.2499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-04 | WTP3 | 0.01 | 0.0449 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP3 | 0.01 | 0.0249 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-04 | WTP3 | 0.1 | 0.1499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-04 | WTP3 | 0.2 | 0.2499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP3 | 0.1 | 0.1499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP3 | 0.02 | 0.0249 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP3 | 0.04 | 0.0449 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-04 | WTP3 | 0.1 | 0.1499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP3 | 0.02 | 0.0249 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-04 | WTP3 | 0.01 | 0.0149 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP3 | 0.01 | 0.2499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-04 | WTP1 | 2 | 2.4999 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-04 | WTP1 | 0.07 | 0.0749 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-04 | WTP1 | 0.6 | 0.6499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-04 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-04 | WTP1 | 0.2 | 0.2499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-04 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-04 | WTP1 | 0.9 | 0.9499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP1 | 0.2 | 0.2499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-04 | WTP1 | 0.01 | 0.0449 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP1 | 0.01 | 0.0249 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-04 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-04 | WTP1 | 0.2 | 0.2499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP1 | 0.02 | 0.0249 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP1 | 0.04 | 0.0449 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-04 | WTP1 | 0.1 | 0.1499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP1 | 0.02 | 0.0249 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-04 | WTP1 | 0.01 | 0.0149 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP1 | 0.01 | 0.2499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP2 | 0.01 | 0.0149 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP2 | 0.01 | 0.0249 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-04 | WTP2 | 0.05 | 0.1499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP2 | 0.5 | 1.4999 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-04 | WTP2 | 0.1 | 1.4999 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-04 | WTP2 | 0.4 | 0.4499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-04 | WTP2 | 9 | 9.4999 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-04 | WTP2 | 6 | 6.4999 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-04 | WTP2 | 0.6 | 0.6499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-04 | WTP2 | 2 | 2.4999 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-04 | WTP2 | 0.07 | 0.0749 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-04 | WTP2 | 0.6 | 0.6499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-04 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-04 | WTP2 | 0.2 | 0.2499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-04 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-04 | WTP2 | 0.9 | 0.9499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP2 | 0.2 | 0.2499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-04 | WTP2 | 0.01 | 0.0449 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP2 | 0.01 | 0.0249 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-04 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-04 | WTP2 | 0.2 | 0.2499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP2 | 0.02 | 0.0249 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP2 | 0.04 | 0.0449 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-04 | WTP2 | 0.1 | 0.1499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP2 | 0.02 | 0.0249 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-04 | WTP2 | 0.01 | 0.0149 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP2 | 0.01 | 0.2499 |  |  | 2Q SOC/KNOLLWOOD WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP3 | 0.01 | 0.0149 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP3 | 0.01 | 0.0249 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-04 | WTP3 | 0.05 | 0.1499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP3 | 0.5 | 1.4999 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-04 | WTP3 | 0.1 | 1.4999 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-04 | WTP3 | 0.4 | 0.4499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-04 | WTP3 | 9 | 9.4999 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-04 | WTP3 | 6 | 6.4999 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-04 | WTP3 | 0.6 | 0.6499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-04 | WTP3 | 2 | 2.4999 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-04 | WTP3 | 0.07 | 0.0749 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-04 | WTP3 | 0.6 | 0.6499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-04 | WTP3 | 0.1 | 0.1499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-04 | WTP3 | 0.2 | 0.2499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-04 | WTP3 | 0.1 | 0.1499 |  |  | 2Q SOC/WEKIVA HUNT CLUB WP (NO DETECTIONS) 2 QTRS SOCS DONE (5/17 SOCS-3WPS PLACED IN FINAL CHEM HOLDING FOLDER ON 6/29/17 PER LATEST SOP)
3591121 | SANLANDO (3 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-04 | WTP1 | 0.01 | 0.0149 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-04 | WTP1 | 0.01 | 0.0249 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-04 | WTP1 | 0.05 | 0.1499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP1 | 0.5 | 1.4999 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-04 | WTP1 | 0.1 | 1.4999 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-04 | WTP1 | 0.4 | 0.4499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-04 | WTP1 | 9 | 9.4999 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-04 | WTP1 | 6 | 6.4999 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-04 | WTP1 | 0.6 | 0.6499 |  |  | 2Q SOC/DES PINAR WP (NO DETECTIONS) 2 QTRS SOCS DONE
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2017-05-10 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2017-05-10 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-05-10 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-05-23 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-05-23 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-05-23 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-06-06 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.1 | LN(10) |  | 2017-06-06 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1.2 | MG/L |  | 2017-06-06 | WTP3 |  |  |  |  | WEKIVA WP
3591121 | SANLANDO (3 WTPS) | WQP | 1927 | TOTAL ALKALINITY | N | 132 | MG/L |  | 2017-06-22 | WTP3 |  |  |  |  | WEKIVA WP (JAN - JUNE 2017 POE WQPS FOR WEKIVA WP)
3591121 | SANLANDO (3 WTPS) | WQP | 1924 | pH (FIELD) | N | 8.2 | LN(10) |  | 2017-06-22 | WTP3 |  |  |  |  | WEKIVA WP (JAN - JUNE 2017 POE WQPS FOR WEKIVA WP)
3591121 | SANLANDO (3 WTPS) | WQP | 1044 | ORTHOPHOSPHATE | N | 1 | MG/L |  | 2017-06-22 | WTP3 |  |  |  |  | WEKIVA WP (JAN - JUNE 2017 POE WQPS FOR WEKIVA WP)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.5 | UG/L | 60.4999 | 2017-08-10 | L1 | 0.5 |  | 1 | 1.4 | 1554 REBECCA (HYPERLINKED TO BW 9/28/17 - BB)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 43 | UG/L | 80.4999 | 2017-08-10 | L1 | 0.5 |  | 1 | 1.4 | 1554 REBECCA (HYPERLINKED TO BW 9/28/17 - BB)
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21 | UG/L | 60.4999 | 2017-08-10 | L3 | 0.5 |  | 2 | 1.6 | 118 CROWN POINT (HYPERLINKED TO BW 9/28/17 - BB)
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 32.7 | UG/L | 80.4999 | 2017-08-10 | L3 | 0.5 |  | 2 | 1.6 | 118 CROWN POINT (HYPERLINKED TO BW 9/28/17 - BB)
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-30 | WTP3 | 0.2 |  |  |  | WEKIVA HUNT CLUB WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-30 | WTP2 | 0.2 |  |  |  | KNOLLWOOD WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-30 | WTP1 | 0.2 |  |  |  | DES PINAR WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-30 | WTP1 | 0.2 |  |  |  | DES PINAR WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-30 | WTP3 | 0.2 |  |  |  | WEKIVA HUNT CLUB WP NN
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-30 | WTP2 | 0.2 |  |  |  | KNOLLWOOD WP NN
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.5 | UG/L | 60.4999 | 2018-08-07 | L3 |  |  |  | 2.2
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 34.4 | UG/L | 80.4999 | 2018-08-07 | L3 |  |  |  | 2.2
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 48.3 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.1 | 1554 REBECCA
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.8 | UG/L | 60.4999 | 2018-08-07 | L1 |  |  | 1 | 2.1 | 1554 REBECCA
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-26 | WTP1 |  |  |  |  | DES PINAR WP
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | WTP1 |  |  |  |  | DES PINAR WP
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-26 | WTP3 |  |  |  |  | WEKIVA HUNT CLUB WP
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | WTP3 |  |  |  |  | WEKIVA HUNT CLUB WP
3591121 | SANLANDO (3 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-26 | WTP2 |  |  |  |  | KNOLLWOOD (FKA OVERSTREET) WP
3591121 | SANLANDO (3 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | WTP2 |  |  |  |  | KNOLLWOOD (FKA OVERSTREET) WP
3591121 | SANLANDO (3 WTPS) | SEC | 1032 | MANGANESE | N | 0.0238 | MG/L | 0.0549 | 2019-06-12 | WTP2
3591121 | SANLANDO (3 WTPS) | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2019-06-12 | WTP1
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.9 | UG/L | 60.4999 | 2019-08-12 | L1 | 1 |  | 2 | 1.2 | 1554 REBECCA PL.
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 50.4 | UG/L | 80.4999 | 2019-08-12 | L1 | 0.5 |  | 2 | 1.2 | 1554 REBECCA PL.
3591121 | SANLANDO (3 WTPS) | DBP | 2950 | TOTAL THMS | D | 18 | UG/L | 80.4999 | 2019-08-12 | L3 | 0.5 |  | 1 | 2.4 | 118 CROWN POINT
3591121 | SANLANDO (3 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.2 | UG/L | 60.4999 | 2019-08-12 | L3 | 1 |  | 1 | 2.4 | 118 CROWN POINT
3591248 | SPRING HAMMOCK MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.13 | UG/L | 60.4999 | 2015-10-01 | L1 |  |  |  | 1.7 | WWTP (MUST ISSUE PN SINCE OUT OF 7-9/15 TESTING PERIOD) REMAIN ON ANNUAL (AUSTIN DUNLAP) RCVD 1/7/16
3591248 | SPRING HAMMOCK MHP | DBP | 2950 | TOTAL THMS | D | 6.08 | UG/L | 80.4999 | 2015-10-01 | L1 |  |  |  | 1.7 | WWTP (MUST ISSUE PN SINCE OUT OF 7-9/15 TESTING PERIOD) REMAIN ON ANNUAL (AUSTIN DUNLAP) RCVD 1/7/16
3591248 | SPRING HAMMOCK MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-11-23 | AAA | 0.2 |  |  |  | 1/7<3300 - 1/29/16 EW HAS TRIENNIAL CHEMS & RADS (THIS NN COMPLETE IN OC)15:<3300>EM 9/29/15&EM12/23/15&12/29/15&PH CALL12/29/15>AUSTIN DUNLAP QWT FOR <3300 RADS 2015 T/H 9/15 PB/CU 9/15 - BB. IN OC.
3591248 | SPRING HAMMOCK MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-11-23 | AAA | 0.2 |  |  |  | 1/7<3300 - 1/29/16 EW HAS TRIENNIAL CHEMS & RADS (THIS NN COMPLETE IN OC)15:<3300>EM 9/29/15&EM12/23/15&12/29/15&PH CALL12/29/15>AUSTIN DUNLAP QWT FOR <3300 RADS 2015 T/H 9/15 PB/CU 9/15 - BB. IN OC.
3591248 | SPRING HAMMOCK MHP | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-12-29 | AAA |  | 0.0149 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-12-29 | AAA |  | 0.0249 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-12-29 | AAA |  | 0.1499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-12-29 | AAA |  | 1.4999 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-12-29 | AAA |  | 1.4999 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-12-29 | AAA |  | 0.4499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-12-29 | AAA |  | 9.4999 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-12-29 | AAA |  | 6.4999 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-12-29 | AAA |  | 0.6499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-12-29 | AAA |  | 2.4999 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-12-29 | AAA |  | 0.0749 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-12-29 | AAA |  | 0.6499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-12-29 | AAA |  | 0.1499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-12-29 | AAA |  | 0.2499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-12-29 | AAA |  | 0.1499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-12-29 | AAA |  | 0.9499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-12-29 | AAA |  | 0.1499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-12-29 | AAA |  | 0.2499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-12-29 | AAA |  | 0.0449 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-12-29 | AAA |  | 0.0249 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-12-29 | AAA |  | 0.1499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-12-29 | AAA |  | 0.2499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-12-29 | AAA |  | 0.1499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-12-29 | AAA |  | 0.0249 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-12-29 | AAA |  | 0.0449 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-12-29 | AAA |  | 0.1499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-12-29 | AAA |  | 0.0249 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-12-29 | AAA |  | 0.0149 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-12-29 | AAA |  | 0.2499 |  |  | 3YR SOC (ANALYSIS DATES ALL REVISED IN FINAL COPY IN OC)
3591248 | SPRING HAMMOCK MHP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.8 | PCI/L | 15.4999 | 2015-12-29 | AAA |  |  |  |  | RADS DUE 2018 (1.5+1.1=2.6 OVER 50% OF MCL OF 5 R226+R228 DUE 2018) PROGRAMMING MAY USE 2.5 + 1.1 = 3.9 - EITHER WAY THE SYSTEM MUST TEST IN 2018. BB
3591248 | SPRING HAMMOCK MHP | RAD | 4030 | RADIUM-228 | N | 1.1 | PCI/L | 2.4999 | 2015-12-29 | AAA |  | 1.4999 |  |  | RADS DUE 2018 (1.5+1.1=2.6 OVER 50% OF MCL OF 5 R226+R228 DUE 2018) PROGRAMMING MAY USE 2.5 + 1.1 = 3.9 - EITHER WAY THE SYSTEM MUST TEST IN 2018. BB
3591248 | SPRING HAMMOCK MHP | INOR | 1040 | NITRATE | N | 4.97 | MG/L | 10.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1010 | BARIUM | N | 0.0191 | MG/L | 2.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1025 | FLUORIDE | N | 0.376 | MG/L | 4.0499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1036 | NICKEL | N | 0.0032 | MG/L | 0.1499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1052 | SODIUM | N | 12.1 | MG/L | 160.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1017 | CHLORIDE | N | 21 | MG/L | 250.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1022 | COPPER | N | 0.0028 | MG/L | 1.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1025 | FLUORIDE | N | 0.376 | MG/L | 2.0499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1028 | IRON | N | 0.0978 | MG/L | 0.3499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1055 | SULFATE | N | 16.7 | MG/L | 250.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1095 | ZINC | N | 0.0756 | MG/L | 5.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.44 | LN(10) |  | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 206 | MG/L | 500.4999 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-12-29 | AAA |  |  |  |  | NO MCLS
3591248 | SPRING HAMMOCK MHP | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-12-29 | AAA |  | 0.5499 |  |  | 3YR VOC
3591248 | SPRING HAMMOCK MHP | DBP | 2950 | TOTAL THMS | S | 1.86 | UG/L | 80.4999 | 2016-09-30 | L1 | 0.5 |  | 1 |  | XXX UNACCEPTABLE XXX-BIOMETRICS RETESTING. "MRT" (NO SITE GVN) SMPLS TKN TO LAB 13 DAYS AFTER COLLECTION ANALYZED OVER HOLDING TIME-Q QUALIFIERS. NO DISINF RESID GVN PG1 COMPLETELY BLANK.
3591248 | SPRING HAMMOCK MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | S | 0 | UG/L | 60.4999 | 2016-09-30 | L1 | 0.5 |  | 1 |  | XXX UNACCEPTABLE XXX-BIOMETRICS RETESTING. "MRT" (NO SITE GVN) SMPLS TKN TO LAB 13 DAYS AFTER COLLECTION ANALYZED OVER HOLDING TIME-Q QUALIFIERS. NO DISINF RESID GVN PG1 COMPLETELY BLANK.
3591248 | SPRING HAMMOCK MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-11-28 | AAA | 0.2 |  |  |  | (REPORT W/O PG1 SIGNATURE IS IN OCULUS)CHANGED "S" TO "N" FOR SMP TYPE PER RFP AND AW_JMF
3591248 | SPRING HAMMOCK MHP | INOR | 1040 | NITRATE | N | 0.769 | MG/L | 10.4999 | 2016-11-28 | AAA | 0.2 |  |  |  | (REPORT W/O PG1 SIGNATURE IS IN OCULUS)CHANGED "S" TO "N" FOR SMP TYPE PER RFP AND AW_JMF
3591248 | SPRING HAMMOCK MHP | DBP | 2950 | TOTAL THMS | D | 30.1 | UG/L | 80.4999 | 2016-12-16 | L1 |  |  | 1 | 0.4 | MAKE UP SAMPLES 3Q 2016 HELD OUTSIDE HOLD TIME. SAMPLE DURING 3Q 2017 (KEEP ON ANNUAL TESTING SINCE TESTING CONDUCTED OUTSIDE NORMAL 7-9/16 TESTING PERIOD)
3591248 | SPRING HAMMOCK MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11 | UG/L | 60.4999 | 2016-12-16 | L1 |  |  | 1 | 0.4 | MAKE UP SAMPLES 3Q 2016 HELD OUTSIDE HOLD TIME. SAMPLE DURING 3Q 2017 (KEEP ON ANNUAL TESTING SINCE TESTING CONDUCTED OUTSIDE NORMAL 7-9/16 TESTING PERIOD)
3591248 | SPRING HAMMOCK MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-06-06 | AAA | 0.025 |  |  |  | RCVD 11-6-17 FROM BW FOR BY EMAIL FOR ENTRY - BB (PLACED IN FINAL CHEM HOLDING FOLDER 11/16/17 - BB) THESE 6/6/17 NN WERE 1ST RCVD 11/6/17 BY BW FROM LAUREN COWLES OF BIOMETRICS BY EMAIL - BB.
3591248 | SPRING HAMMOCK MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-06-06 | AAA | 0.025 |  |  |  | RCVD 11-6-17 FROM BW FOR BY EMAIL FOR ENTRY - BB (PLACED IN FINAL CHEM HOLDING FOLDER 11/16/17 - BB) THESE 6/6/17 NN WERE 1ST RCVD 11/6/17 BY BW FROM LAUREN COWLES OF BIOMETRICS BY EMAIL - BB.
3591248 | SPRING HAMMOCK MHP | DBP | 2950 | TOTAL THMS | D | 56.2 | UG/L | 80.4999 | 2017-08-15 | L1 | 0.32 |  | 1 | 0.7 | WWTP (HYPERLINKED TO BW FOR RESOLUTION OF THE 9/17 QTR REPORTING VIOL - BB) RESULTS RCVD LATE 11/6/17 - BW/BB
3591248 | SPRING HAMMOCK MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.6 | UG/L | 60.4999 | 2017-08-15 | L1 | 0.48 |  | 1 | 0.7 | WWTP (HYPERLINKED TO BW FOR RESOLUTION OF THE 9/17 QTR REPORTING VIOL - BB) RESULTS RCVD LATE 11/6/17 - BW/BB
3591248 | SPRING HAMMOCK MHP | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1010 | BARIUM | N | 0.007 | MG/L | 2.4999 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1025 | FLUORIDE | N | 0.19 | MG/L | 4.0499 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1030 | LEAD | N | 0.0007 | MG/L | 0.0154 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1052 | SODIUM | N | 18.2 | MG/L | 160.4999 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1022 | COPPER | N | 0.0039 | MG/L | 1.4999 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1025 | FLUORIDE | N | 0.19 | MG/L | 2.0499 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.1 | LN(10) |  | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 155 | MG/L | 500.4999 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 2905 | FOAMING AGENTS | N | 0.47 |  | 0.5499 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | SEC | 1017 | CHLORIDE | N | 24.7 | MG/L | 250.4999 | 2018-04-10 | AAA |  |  |  |  | CHLORIDE J QUALIFIER - RECOVERY WITHIN CONTROL_RLB
3591248 | SPRING HAMMOCK MHP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-04-10 | AAA
3591248 | SPRING HAMMOCK MHP | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-04-10 | AAA |  | 1.4999
3591248 | SPRING HAMMOCK MHP | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-10 | AAA |  | 0.5499
3591248 | SPRING HAMMOCK MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.2 | UG/L | 60.4999 | 2018-08-14 | L1 |  |  |  | 0.3
3591248 | SPRING HAMMOCK MHP | DBP | 2950 | TOTAL THMS | D | 41 | UG/L | 80.4999 | 2018-08-14 | L1 |  |  |  | 0.3
3591248 | SPRING HAMMOCK MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.9 | UG/L | 60.4999 | 2019-08-08 | L1 |  |  | 1 | 1 | WASTEWATER TRTMNT PLANT (WWTP)
3591248 | SPRING HAMMOCK MHP | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-08-08 | AAA
3591248 | SPRING HAMMOCK MHP | DBP | 2950 | TOTAL THMS | D | 48.9 | UG/L | 80.4999 | 2019-08-08 | L1 |  |  | 1 | 1 | WASTEWATER TRTMNT PLANT (WWTP)
3591248 | SPRING HAMMOCK MHP | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-08-08 | AAA
3591248 | SPRING HAMMOCK MHP | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2019-10-08 | AAA | 0.16 | 0.2499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2019-10-08 | AAA | 0.094 | 0.1499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2019-10-08 | AAA | 0.67 | 0.9499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2019-10-08 | AAA | 0.06 | 0.2499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2019-10-08 | AAA | 0.0092 | 0.0449 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2019-10-08 | AAA | 0.0066 | 0.0249 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2019-10-08 | AAA | 0.081 | 0.1499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2019-10-08 | AAA | 0.16 | 0.2499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2019-10-08 | AAA | 0.023 | 0.1499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2019-10-08 | AAA | 0.012 | 0.0249 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2019-10-08 | AAA | 0.03 | 0.0449 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2019-10-08 | AAA | 0.076 | 0.1499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2019-10-08 | AAA | 0.0061 | 0.0249 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2019-10-08 | AAA | 0.0072 | 0.0149 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2019-10-08 | AAA | 0.045 | 0.2499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2019-10-08 | AAA | 0.034 | 0.0249 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2019-10-08 | AAA | 0.055 | 0.1499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2019-10-08 | AAA | 0.58 | 1.4999 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-10-08 | AAA | 0.89 | 1.4999 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2019-10-08 | AAA | 0.15 | 0.4499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2019-10-08 | AAA | 3.3 | 9.4999 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2019-10-08 | AAA | 4.2 | 6.4999 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2019-10-08 | AAA | 0.36 | 0.6499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2019-10-08 | AAA | 0.44 | 2.4999 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2019-10-08 | AAA | 0.045 | 0.0749 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2019-10-08 | AAA | 0.47 | 0.6499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591248 | SPRING HAMMOCK MHP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2019-10-08 | AAA | 0.016 | 0.1499 |  |  | 2018 MISSED MAKE UP SAMPLES.
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.0449 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1005 | ARSENIC | N | 0.0014 | MG/L | 0.0104 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1010 | BARIUM | N | 0.0097 | MG/L | 2.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1020 | CHROMIUM | N | 0.011 | MG/L | 0.1499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1025 | FLUORIDE | N | 0.068 | MG/L | 4.0499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1036 | NICKEL | N | 0.0024 | MG/L | 0.1499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1045 | SELENIUM | N | 0.0013 | MG/L | 0.0549 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-11 | AAA |  | 0.0149 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1052 | SODIUM | N | 31 | MG/L | 160.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS) 15:TEST ANN. (ROUTINE) T/H DUE 8/11/15 - 8/15/15 2 SITES>>EM 12/4/14 TO FELTON
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1017 | CHLORIDE | N | 35 | MG/L | 250.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1022 | COPPER | N | 0.0023 | MG/L | 1.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1025 | FLUORIDE | N | 0.068 | MG/L | 2.0499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1028 | IRON | N | 0.1 | MG/L | 0.3499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1032 | MANGANESE | N | 0.011 | MG/L | 0.0549 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1055 | SULFATE | N | 1.5 | MG/L | 250.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1095 | ZINC | N | 0.0034 | MG/L | 5.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.2 | LN(10) |  | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 130 | MG/L | 500.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | SEC | 2905 | FOAMING AGENTS | N | 0.07 |  | 0.5499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOC (ALL OK)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-11 | AAA |  | 0.0149 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 1.4999 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2031 | DALAPON | N | 0.88 | UG/L | 249.9999 | 2015-02-11 | AAA |  | 1.4999 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-11 | AAA |  | 0.4499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 9.4999 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-11 | AAA |  | 6.4999 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-02-11 | AAA |  | 0.6499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-11 | AAA |  | 2.4999 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-11 | AAA |  | 0.0749 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-02-11 | AAA |  | 0.6499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-11 | AAA |  | 0.9499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-11 | AAA |  | 0.0449 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOC (DALAPON 0.88 NO QM OR REC RQRD <RDL 1.4999)
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2950 | TOTAL THMS | D | 31.2 | UG/L | 80.4999 | 2015-09-03 | L2 |  |  |  | 0.4 | #2 348B (QUALIFIES FOR R.M. AT 1 SITE LOT 122 - NEXT T/H DUE 8/11/16 - 8/15/16>EM 5/20/16>FELTON&OWNER) 500 POP. (MUST UPDATE WVR & SITE SCREEN)
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24 | UG/L | 60.4999 | 2015-09-03 | L1 |  |  |  | 0.2 | ANN. T/H-LOT 122 (NEED 2ND T/H AT LOT 348B - 2ND SITE - FOR 2015) EM 9/25/15 TO FELTON FOR 2ND SITE.
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22 | UG/L | 60.4999 | 2015-09-03 | L2 |  |  |  | 0.4 | #2 348B (QUALIFIES FOR R.M. AT 1 SITE LOT 122 - NEXT T/H DUE 8/11/16 - 8/15/16>EM 5/20/16>FELTON&OWNER) 500 POP. (MUST UPDATE WVR & SITE SCREEN)
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2950 | TOTAL THMS | D | 33.7 | UG/L | 80.4999 | 2015-09-03 | L1 |  |  |  | 0.2 | ANN. T/H-LOT 122 (NEED 2ND T/H AT LOT 348B - 2ND SITE - FOR 2015) EM 9/25/15 TO FELTON FOR 2ND SITE.
3591395 | TWELVE OAKS R.V.RESORT | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-10-19 | AAA |  | 1.4999 |  |  | DUE 2021
3591395 | TWELVE OAKS R.V.RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.9 | PCI/L | 15.4999 | 2015-10-19 | AAA |  |  |  |  | DUE 2021
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1040 | NITRATE | N | 0.228 | MG/L | 10.4999 | 2016-01-26 | AAA | 0.2
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-26 | AAA | 0.2
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2950 | TOTAL THMS | D | 11.7 | UG/L | 80.4999 | 2016-11-30 | L1 |  |  | 1 |  | MAKE UP FOR MISSED 3RD Q. NO CL2 RESIDUAL. ASKED FOR AMENDED REPORT 1/12/17_JMF
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.7 | UG/L | 60.4999 | 2016-11-30 | L1 |  |  | 1 |  | MAKE UP FOR MISSED 3RD Q. NO CL2 RESIDUAL. ASKED FOR AMENDED REPORT 1/12/17_JMF
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-18 | AAA | 0.2 |  |  |  | PLACED IN FINAL CHEM HOLDING FOLDER FOR OC 5/31/17-BB
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-05-18 | AAA | 0.2 |  |  |  | PLACED IN FINAL CHEM HOLDING FOLDER FOR OC 5/31/17-BB
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2950 | TOTAL THMS | D | 52.3 | UG/L | 80.4999 | 2017-08-30 | L1 | 0.32 |  | 1 | 1 | LOT 122 (HYPERLINKED TO BW 9/29/17 - BB)
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.1 | UG/L | 60.4999 | 2017-08-30 | L1 | 0.48 |  | 1 | 1 | LOT 122 (HYPERLINKED TO BW 9/29/17 - BB)
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA | 0.0005
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1032 | MANGANESE | N | 0.0196 | MG/L | 0.0549 | 2018-05-15 | AAA | 0.01
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1095 | ZINC | N | 0.122 | MG/L | 5.4999 | 2018-05-15 | AAA | 0.01
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-15 | AAA | 5
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-05-15 | AAA | 1
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.33 | LN(10) |  | 2018-05-15 | AAA | 0.01
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 262 | MG/L | 500.4999 | 2018-05-15 | AAA | 2.5
3591395 | TWELVE OAKS R.V.RESORT | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-15 | AAA | 0.2
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA | 0.2 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2955 | TOT XYLENE | N | 0.71 | UG/L | 10499.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA | 0.5 | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-15 | AAA | 0.2
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | AAA | 0.2
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1010 | BARIUM | N | 0.0103 | MG/L | 2.4999 | 2018-05-15 | AAA | 0.002
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1020 | CHROMIUM | N | 0.0038 | MG/L | 0.1499 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA | 0.005
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-05-15 | AAA | 0.2
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-15 | AAA | 2e-05
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1036 | NICKEL | N | 0.0013 | MG/L | 0.1499 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA | 0.002
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1052 | SODIUM | N | 27.8 | MG/L | 160.4999 | 2018-05-15 | AAA | 0.5
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-15 | AAA | 0.0005
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA | 0.02
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1017 | CHLORIDE | N | 44.5 | MG/L | 250.4999 | 2018-05-15 | AAA | 0.4
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1022 | COPPER | N | 0.0092 | MG/L | 1.4999 | 2018-05-15 | AAA | 0.001
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-05-15 | AAA | 0.2
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1028 | IRON | N | 0.391 | MG/L | 0.3499 | 2018-05-15 | AAA | 0.01
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1055 | SULFATE | N | 0 | MG/L | 250.4999 | 2018-05-15 | AAA | 1
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 39.7 | UG/L | 60.4999 | 2018-08-22 | L1 | 0.5 |  | 1 | 1
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2950 | TOTAL THMS | D | 50.4 | UG/L | 80.4999 | 2018-08-22 | L1 | 0.5 |  | 1 | 1
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-21 | AAA |  | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-10-30 | AAA |  | 0.5499
3591395 | TWELVE OAKS R.V.RESORT | SEC | 1028 | IRON | N | 0.33 | MG/L | 0.3499 | 2018-10-30 | AAA
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-02-27 | AAA | 0.5 | 0.5499 |  |  | 4QM/XY (HLKD)
3591395 | TWELVE OAKS R.V.RESORT | VOC | 2955 | TOT XYLENE | N | 1.5 | UG/L | 10499.9999 | 2019-05-29 | AAA | 0.5 | 0.5499 |  |  | 1AM/XYLENES
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2950 | TOTAL THMS | D | 4.74 | UG/L | 80.4999 | 2019-08-29 | L1 |  |  | 1 | 0.4 | #1 - LOT 122 (R.M. SITE EFFEC. 9/16)
3591395 | TWELVE OAKS R.V.RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 4.81 | UG/L | 60.4999 | 2019-08-29 | L1 |  |  | 1 | 0.4 | #1 - LOT 122 (R.M. SITE EFFEC. 9/16)
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-09-10 | AAA
3591395 | TWELVE OAKS R.V.RESORT | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-09-10 | AAA
3591451 | WEATHERSFIELD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-17 | AAA |  |  |  |  | NN (OK) EM 4/22/16 TO SCOTT GOSNELL W/2016 RQRMNTS
3591451 | WEATHERSFIELD | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-17 | AAA |  |  |  |  | NN (OK) EM 4/22/16 TO SCOTT GOSNELL W/2016 RQRMNTS
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 59.7 | UG/L | 80.4999 | 2015-08-12 | L2 |  |  |  | 0.8 | 187 RONNIE DRIVE (NO LRAA MCLS OR OE EXCEEDANCES) POP. 4 221 - EM 4/22/16 TO SCOTT GOSNELL W/2016 RQRMNTS
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 54.5 | UG/L | 60.4999 | 2015-08-12 | L2 |  |  |  | 0.8 | 187 RONNIE DRIVE (NO LRAA MCLS OR OE EXCEEDANCES) POP. 4 221 - EM 4/22/16 TO SCOTT GOSNELL W/2016 RQRMNTS
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 57.1 | UG/L | 80.4999 | 2015-08-12 | L1 |  |  |  | 2 | 496 DOGWOOD DRIVE (NO LRAA MCLS OR OE EXCEEDANCES)
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 48.3 | UG/L | 60.4999 | 2015-08-12 | L1 |  |  |  | 2 | 496 DOGWOOD DRIVE (NO LRAA MCLS OR OE EXCEEDANCES)
3591451 | WEATHERSFIELD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3591451 | WEATHERSFIELD | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-02-25 | AAA |  |  |  |  | 2016 NN
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 85.2 | UG/L | 80.4999 | 2016-08-10 | L2 |  |  |  | 0.6 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 56.6 | UG/L | 80.4999 | 2016-08-10 | L1 |  |  |  | 0.6 | 496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.3 | UG/L | 60.4999 | 2016-08-10 | L1 |  |  |  | 0.6 | 496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 43.1 | UG/L | 60.4999 | 2016-08-10 | L2 |  |  |  | 0.6 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.8 | UG/L | 60.4999 | 2016-11-08 | L2 |  |  |  | 1.4 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 39.6 | UG/L | 80.4999 | 2016-11-08 | L2 |  |  |  | 1.4 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 37.2 | UG/L | 80.4999 | 2016-11-08 | L1 |  |  |  | 1.4 | 496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.14 | UG/L | 60.4999 | 2016-11-08 | L1 |  |  |  | 1.4 | 496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.6 | UG/L | 60.4999 | 2017-02-07 | L2 | 0.5 |  | 2 | 1.6 | 187 RONNIE (AFT. 3 QTRS LRAA/T IN 30S LRAA/H LOW) NO MCL VIOLS NO OE EXCEEDANCES (HYPERLINKED 3/3/17 TO BW)
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 31.5 | UG/L | 80.4999 | 2017-02-07 | L1 | 0.5 |  | 1 | 1.8 | 496 DOGWOOD DRIVE (AFT. 3 QTRS LRAA/T IN 30S LRAA/H LOW) NO MCL VIOLS NO OE EXCEEDANCES
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.6 | UG/L | 60.4999 | 2017-02-07 | L1 | 0.5 |  | 1 | 1.8 | 496 DOGWOOD DRIVE (AFT. 3 QTRS LRAA/T IN 30S LRAA/H LOW) NO MCL VIOLS NO OE EXCEEDANCES
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 30.8 | UG/L | 80.4999 | 2017-02-07 | L2 | 0.5 |  | 2 | 1.6 | 187 RONNIE (AFT. 3 QTRS LRAA/T IN 30S LRAA/H LOW) NO MCL VIOLS NO OE EXCEEDANCES (HYPERLINKED 3/3/17 TO BW)
3591451 | WEATHERSFIELD | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-24 | AAA | 0.04 | 0.0449 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-24 | AAA | 0.101 | 0.1499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-24 | AAA | 0.0202 | 0.0249 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-24 | AAA | 0.0101 | 0.0149 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-24 | AAA | 0.0101 | 0.2499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-24 | AAA | 0.0101 | 0.0149 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-24 | AAA | 0.0101 | 0.0249 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-24 | AAA | 0.0506 | 0.1499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-24 | AAA | 0.506 | 1.4999 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-24 | AAA | 0.1 | 1.4999 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-24 | AAA | 0.4 | 0.4499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-24 | AAA | 9 | 9.4999 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-24 | AAA | 6 | 6.4999 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-24 | AAA | 0.6 | 0.6499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-24 | AAA | 2 | 2.4999 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-24 | AAA | 0.07 | 0.0749 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-24 | AAA | 0.6 | 0.6499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-24 | AAA | 0.1 | 0.1499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-24 | AAA | 0.2 | 0.2499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-24 | AAA | 0.101 | 0.1499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-24 | AAA | 0.9 | 0.9499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-24 | AAA | 0.1 | 0.1499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-24 | AAA | 0.2 | 0.2499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-24 | AAA | 2.5 |  |  |  | SET UP RADS WVR BASED ON 2017 RESULTS (UR ON 6-YR SCHEDULE - RADS DUE 2023) R226+R228 6YR STRICTEST INTERPRETATION & UR 6 YR
3591451 | WEATHERSFIELD | RAD | 4020 | RADIUM-226 | N | 1.4 | PCI/L | 3.4999 | 2017-02-24 | AAA | 0.3 | 1.4999 |  |  | SET UP RADS WVR BASED ON 2017 RESULTS (UR ON 6-YR SCHEDULE - RADS DUE 2023) R226+R228 6YR STRICTEST INTERPRETATION & UR 6 YR
3591451 | WEATHERSFIELD | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-24 | AAA | 0.7 | 1.4999 |  |  | SET UP RADS WVR BASED ON 2017 RESULTS (UR ON 6-YR SCHEDULE - RADS DUE 2023) R226+R228 6YR STRICTEST INTERPRETATION & UR 6 YR
3591451 | WEATHERSFIELD | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-02-24 | AAA | 0.2 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-24 | AAA | 0.2 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1010 | BARIUM | N | 0.0063 | MG/L | 2.4999 | 2017-02-24 | AAA | 0.002 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1024 | CYANIDE | N | 0.0122 | MG/L | 0.2499 | 2017-02-24 | AAA | 0.005 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2017-02-24 | AAA | 0.2 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-24 | AAA | 2e-05 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-24 | AAA | 0.002 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1052 | SODIUM | N | 2.27 | MG/L | 160.4999 | 2017-02-24 | AAA | 0.5 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-24 | AAA | 0.0005 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN PRIM INORG
3591451 | WEATHERSFIELD | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-24 | AAA | 0.02 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1017 | CHLORIDE | N | 22.8 | MG/L | 250.4999 | 2017-02-24 | AAA | 0.4 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1022 | COPPER | N | 0.0298 | MG/L | 1.4999 | 2017-02-24 | AAA | 0.001 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2017-02-24 | AAA | 0.2 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1028 | IRON | N | 0.106 | MG/L | 0.3499 | 2017-02-24 | AAA | 0.01 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-24 | AAA | 0.01 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-24 | AAA | 0.0005 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1055 | SULFATE | N | 8.21 | MG/L | 250.4999 | 2017-02-24 | AAA | 1 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1095 | ZINC | N | 0.131 | MG/L | 5.4999 | 2017-02-24 | AAA | 0.01 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-24 | AAA | 5 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-24 | AAA | 1 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8.56 | LN(10) |  | 2017-02-24 | AAA | 0.01 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 176 | MG/L | 500.4999 | 2017-02-24 | AAA | 2.5 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-24 | AAA | 0.2 |  |  |  | NO MCLS IN SECONDARIES
3591451 | WEATHERSFIELD | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-24 | AAA | 0.2 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-24 | AAA | 0.5 | 0.5499 |  |  | 3YR VOC (ALL OK)
3591451 | WEATHERSFIELD | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-24 | AAA | 0.0101 | 0.0449 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-24 | AAA | 0.0101 | 0.0249 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-24 | AAA | 0.1 | 0.1499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-24 | AAA | 0.2 | 0.2499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-24 | AAA | 0.101 | 0.1499 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-24 | AAA | 0.02 | 0.0249 |  |  | 1Q SOC (NEED 2 QTRS OF SOCS IN 2017 AT LEAST 60 DAYS APART) ALL OK
3591451 | WEATHERSFIELD | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-08 | AAA | 0.01 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 49.3 | UG/L | 80.4999 | 2017-05-08 | L2 | 0.5 |  | 2 | 1.5 | 187 RONNIE DRIVE (AFT. 4 QTRS 6/17 LRAA/T=51.225 LRAA/H=33.225) HYPERLINKED TO BW ON 6/29/17 - BB (NOW LRAA/T<60 LRAA/H<45) RETURN TO ROUTINE (ANNUAL) DBP TESTING & MUST TEST DUAL SAMPLES.
3591451 | WEATHERSFIELD | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-08 | AAA | 0.5 | 1.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-08 | AAA | 0.1 | 1.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-08 | AAA | 0.4 | 0.4499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-08 | AAA | 9 | 9.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-08 | AAA | 6 | 6.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-08 | AAA | 0.6 | 0.6499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-08 | AAA | 2 | 2.4999 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-08 | AAA | 0.07 | 0.0749 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-08 | AAA | 0.6 | 0.6499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-08 | AAA | 0.1 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-08 | AAA | 0.2 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-08 | AAA | 0.1 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-08 | AAA | 0.9 | 0.9499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-08 | AAA | 0.1 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-08 | AAA | 0.2 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-08 | AAA | 0.01 | 0.0449 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-08 | AAA | 0.01 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-08 | AAA | 0.1 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-08 | AAA | 0.2 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-08 | AAA | 0.1 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-08 | AAA | 0.02 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-08 | AAA | 0.04 | 0.0449 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-08 | AAA | 0.1 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-08 | AAA | 0.02 | 0.0249 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-08 | AAA | 0.01 | 0.0149 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-08 | AAA | 0.01 | 0.2499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-08 | AAA | 0.05 | 0.1499 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.4 | UG/L | 60.4999 | 2017-05-08 | L2 | 0.5 |  | 2 | 1.5 | 187 RONNIE DRIVE (AFT. 4 QTRS 6/17 LRAA/T=51.225 LRAA/H=33.225) HYPERLINKED TO BW ON 6/29/17 - BB (NOW LRAA/T<60 LRAA/H<45) RETURN TO ROUTINE (ANNUAL) DBP TESTING & MUST TEST DUAL SAMPLES.
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 48.7 | UG/L | 80.4999 | 2017-05-08 | L1 | 0.5 |  | 1 | 1.2 | 496 DOGWOOD DRIVE (AFT. 4 QTRS 6/17 LRAA/T=43.5 LRAA/H=25.835) HYPERLINKED TO BW ON 6/29/17 - BB (NOW LRAA/T<60 LRAA/H<45) RETURN TO ROUTINE (ANNUAL) DBP TESTING & MUST TEST DUAL SAMPLES.
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.3 | UG/L | 60.4999 | 2017-05-08 | L1 | 0.5 |  | 1 | 1.2 | 496 DOGWOOD DRIVE (AFT. 4 QTRS 6/17 LRAA/T=43.5 LRAA/H=25.835) HYPERLINKED TO BW ON 6/29/17 - BB (NOW LRAA/T<60 LRAA/H<45) RETURN TO ROUTINE (ANNUAL) DBP TESTING & MUST TEST DUAL SAMPLES.
3591451 | WEATHERSFIELD | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-08 | AAA | 0.01 | 0.0149 |  |  | 2Q SOC (NO DETECTIONS IN THESE SOCS) 2 QTRS SOCS DONE FOR 2017
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.6 | UG/L | 60.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.4 | ON ANNUAL - 496 DOGWOOD DRIVE (HYPERLINKED 9/28/17 TO BW - BB) OTHER SITE'S HAA5 64.4 (MCL = 60)
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 57.2 | UG/L | 80.4999 | 2017-08-11 | L1 | 0.5 |  | 1 | 2.4 | ON ANNUAL - 496 DOGWOOD DRIVE (HYPERLINKED 9/28/17 TO BW - BB) OTHER SITE'S HAA5 64.4 (MCL = 60)
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 64.4 | UG/L | 60.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 2 | ON ANNUAL - 187 RONNIE (HYPERLINKED 9/28/17 TO BW - BB) HAA5S 64.4 (MCL = 60)
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 71.4 | UG/L | 80.4999 | 2017-08-11 | L2 | 0.5 |  | 2 | 2 | ON ANNUAL - 187 RONNIE (HYPERLINKED 9/28/17 TO BW - BB) HAA5S 64.4 (MCL = 60)
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 43 | UG/L | 80.4999 | 2017-11-08 | L1 | 0.5 |  | 1 | 2.6 | 2QM - 496 DOGWOOD DR. (12/17 DB REPORT SBMITTD W/RSLTS - NOT RQRD & INCORRECT) MUST TEST QTRLY 3/18 & 6/18 MINIMUM.
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 38.3 | UG/L | 60.4999 | 2017-11-08 | L1 | 0.5 |  | 1 | 2.6 | 2QM - 496 DOGWOOD DR. (12/17 DB REPORT SBMITTD W/RSLTS - NOT RQRD & INCORRECT) MUST TEST QTRLY 3/18 & 6/18 MINIMUM.
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 54.1 | UG/L | 80.4999 | 2017-11-08 | L2 | 0.5 |  | 2 | 2.4 | 2QM - 187 RONNIE DR. (12/17 DB REPORT SBMITTD W/RSLTS - NOT RQRD & INCORRECT) MUST TEST QTRLY 3/18 & 6/18 MINIMUM.
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.2 | UG/L | 60.4999 | 2017-11-08 | L2 | 0.5 |  | 2 | 2.4 | 2QM - 187 RONNIE DR. (12/17 DB REPORT SBMITTD W/RSLTS - NOT RQRD & INCORRECT) MUST TEST QTRLY 3/18 & 6/18 MINIMUM.
3591451 | WEATHERSFIELD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-01-30 | AAA | 0.2 |  |  |  | NN
3591451 | WEATHERSFIELD | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-01-30 | AAA | 0.2 |  |  |  | NN
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.3 | UG/L | 60.4999 | 2018-02-07 | L1 | 0.5 |  | 1 | 2.6 | 3QM-496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 31.2 | UG/L | 80.4999 | 2018-02-07 | L1 | 0.5 |  | 1 | 2.6 | 3QM-496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.4 | UG/L | 60.4999 | 2018-02-07 | L2 | 0.5 |  | 2 | 2.4 | 3QM-187 RONNIE (3/18 VOLUN. DISINF BYP RPRT RCVD W/RSLTS IS INCORRECT FOR LRAAS) HYPRLNKD TO BW 4/18/18 - BB
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 39.1 | UG/L | 80.4999 | 2018-02-07 | L2 | 0.5 |  | 2 | 2.4 | 3QM-187 RONNIE (3/18 VOLUN. DISINF BYP RPRT RCVD W/RSLTS IS INCORRECT FOR LRAAS) HYPRLNKD TO BW 4/18/18 - BB
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 44 | UG/L | 80.4999 | 2018-05-08 | L1 |  |  |  | 1.4 | 496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.9 | UG/L | 60.4999 | 2018-05-08 | L2 |  |  |  | 0.7 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 23 | UG/L | 80.4999 | 2018-05-08 | L2 |  |  |  | 0.7 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28 | UG/L | 60.4999 | 2018-05-08 | L1 |  |  |  | 1.4 | 496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 38.7 | UG/L | 80.4999 | 2018-08-07 | L2 | 0.5 |  | 1 | 1.8
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.1 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.2
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 21.7 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.5 |  | 1 | 2.2
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.3 | UG/L | 60.4999 | 2018-08-07 | L2 | 0.5 |  | 1 | 1.8
3591451 | WEATHERSFIELD | INOR | 1040 | NITRATE | N | 0.018 | MG/L | 10.4999 | 2019-02-26 | AAA
3591451 | WEATHERSFIELD | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-26 | AAA
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 74.1 | UG/L | 80.4999 | 2019-08-12 | L2 | 0.5 |  | 2 | 3.5 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 52.6 | UG/L | 60.4999 | 2019-08-12 | L2 | 1 |  | 2 | 3.5 | 187 RONNIE DRIVE
3591451 | WEATHERSFIELD | DBP | 2950 | TOTAL THMS | D | 47.4 | UG/L | 80.4999 | 2019-08-12 | L1 | 0.5 |  | 1 | 3.8 | 496 DOGWOOD DRIVE
3591451 | WEATHERSFIELD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.4 | UG/L | 60.4999 | 2019-08-12 | L1 | 1 |  | 1 | 3.8 | 496 DOGWOOD DRIVE
3594050 | SEMINOLE WOODS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1005 | ARSENIC | N | 0.0019 | MG/L | 0.0104 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1010 | BARIUM | N | 0.024 | MG/L | 2.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1020 | CHROMIUM | N | 0.0066 | MG/L | 0.1499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1025 | FLUORIDE | N | 0.028 | MG/L | 4.0499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 140 | MG/L | 500.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1095 | ZINC | N | 0.002 | MG/L | 5.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.2 | LN(10) |  | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 0.5499 |  |  | 3YR VOCS (ALL OK)
3594050 | SEMINOLE WOODS | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-02-11 | AAA |  | 0.0149 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 1.4999 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2031 | DALAPON | N | 0.86 | UG/L | 249.9999 | 2015-02-11 | AAA |  | 1.4999 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-02-11 | AAA |  | 0.4499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-02-11 | AAA |  | 9.4999 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-02-11 | AAA |  | 6.4999 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-02-11 | AAA |  | 0.6499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-02-11 | AAA |  | 2.4999 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-02-11 | AAA |  | 0.0749 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-02-11 | AAA |  | 0.6499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-02-11 | AAA |  | 0.9499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-02-11 | AAA |  | 0.0449 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-02-11 | AAA |  | 0.0449 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-02-11 | AAA |  | 0.1499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-02-11 | AAA |  | 0.0249 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-02-11 | AAA |  | 0.0149 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-02-11 | AAA |  | 0.2499 |  |  | 3YR SOCS (DALAPON 0.86 NO QM RQRD < RDL OF 1 UG/L)
3594050 | SEMINOLE WOODS | INOR | 1040 | NITRATE | N | 0.02 | MG/L | 10.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1036 | NICKEL | N | 0.0022 | MG/L | 0.1499 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1045 | SELENIUM | N | 0.0014 | MG/L | 0.0549 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1052 | SODIUM | N | 13 | MG/L | 160.4999 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1075 | BERYLLIUM | N | 0.0002 | MG/L | 0.0045 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-02-11 | AAA |  |  |  |  | (NO MCLS IN TRIENNIALS)15:(R.M.) T/H DUE @ 8/11 - 8/15 IN 2016) >500 NN RADS 2018 (TOM FELTON)
3594050 | SEMINOLE WOODS | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1017 | CHLORIDE | N | 16 | MG/L | 250.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1022 | COPPER | N | 0.0016 | MG/L | 1.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1025 | FLUORIDE | N | 0.028 | MG/L | 2.0499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | SEC | 1055 | SULFATE | N | 6.8 | MG/L | 250.4999 | 2015-02-11 | AAA |  |  |  |  | NO MCLS
3594050 | SEMINOLE WOODS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.42 | UG/L | 60.4999 | 2015-09-03 | L2 |  |  |  | 0.4 | LOT 257 (NEED 2ND SITE TESTED LOT 221>>>EM 9/27/15 TO TOM FELTON C A MACEACHERN GEN UTILS) POP. 780
3594050 | SEMINOLE WOODS | DBP | 2950 | TOTAL THMS | D | 20.4 | UG/L | 80.4999 | 2015-09-03 | L1 |  |  |  | 0.5 | #1-221 (QUALIFIES FOR R.M. - NEXT T/H DUE @ 8/11 - 8/15 IN 2016) >500
3594050 | SEMINOLE WOODS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.67 | UG/L | 60.4999 | 2015-09-03 | L1 |  |  |  | 0.5 | #1-221 (QUALIFIES FOR R.M. - NEXT T/H DUE @ 8/11 - 8/15 IN 2016) >500
3594050 | SEMINOLE WOODS | DBP | 2950 | TOTAL THMS | D | 20.7 | UG/L | 80.4999 | 2015-09-03 | L2 |  |  |  | 0.4 | LOT 257 (NEED 2ND SITE TESTED LOT 221>>>EM 9/27/15 TO TOM FELTON C A MACEACHERN GEN UTILS) POP. 780
3594050 | SEMINOLE WOODS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-01-27 | AAA | 0.2
3594050 | SEMINOLE WOODS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-27 | AAA | 0.2
3594050 | SEMINOLE WOODS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.44 | UG/L | 60.4999 | 2016-09-13 | L2 |  |  |  | 1 | ON REDUCED ANNUAL MONITORING. SAMPLE L1 Q3 2017. BW
3594050 | SEMINOLE WOODS | DBP | 2950 | TOTAL THMS | D | 28.7 | UG/L | 80.4999 | 2016-09-13 | L2 |  |  |  | 1 | ON REDUCED ANNUAL MONITORING. SAMPLE L1 Q3 2017. BW
3594050 | SEMINOLE WOODS | DBP | 2950 | TOTAL THMS | D | 26.5 | UG/L | 80.4999 | 2016-09-13 | L1 |  |  |  | 1.2 | #1-221 (10/24/16 FORWARDED 2ND SET T/H 10/24/16 RCVD FROM GEN UTILS TO AA & BW-BB)
3594050 | SEMINOLE WOODS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.73 | UG/L | 60.4999 | 2016-09-13 | L1 |  |  |  | 1.2 | #1-221 (10/24/16 FORWARDED 2ND SET T/H 10/24/16 RCVD FROM GEN UTILS TO AA & BW-BB)
3594050 | SEMINOLE WOODS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-18 | AAA | 0.2 |  |  |  | PLACED IN FINAL CHEM HOLDING FOLDER FOR OC 5/31/17-BB
3594050 | SEMINOLE WOODS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2017-05-18 | AAA | 0.2 |  |  |  | PLACED IN FINAL CHEM HOLDING FOLDER FOR OC 5/31/17-BB
3594050 | SEMINOLE WOODS | DBP | 2950 | TOTAL THMS | D | 28.6 | UG/L | 80.4999 | 2017-08-30 | L1 | 0.32 |  | 1 | 1 | LOT 221 (HYPERLINKED 9/29/17 TO BW - BB)
3594050 | SEMINOLE WOODS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.6 | UG/L | 60.4999 | 2017-08-30 | L1 | 0.48 |  | 1 | 1 | LOT 221 (HYPERLINKED 9/29/17 TO BW - BB)
3594050 | SEMINOLE WOODS | SEC | 1055 | SULFATE | N | 9.76 | MG/L | 250.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 366 | MG/L | 500.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3594050 | SEMINOLE WOODS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1010 | BARIUM | N | 0.0252 | MG/L | 2.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1020 | CHROMIUM | N | 0.002 | MG/L | 0.1499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.83 | LN(10) |  | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1052 | SODIUM | N | 12.5 | MG/L | 160.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1017 | CHLORIDE | N | 21.3 | MG/L | 250.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1022 | COPPER | N | 0.0023 | MG/L | 1.4999 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1028 | IRON | N | 0.0166 | MG/L | 0.3499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3594050 | SEMINOLE WOODS | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2018-05-24 | AAA
3594050 | SEMINOLE WOODS | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-05-24 | AAA |  | 1.4999
3594050 | SEMINOLE WOODS | DBP | 2950 | TOTAL THMS | D | 20.6 | UG/L | 80.4999 | 2018-08-23 | L1 | 0.5 |  | 1 | 1
3594050 | SEMINOLE WOODS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.1 | UG/L | 60.4999 | 2018-08-23 | L1 | 0.5 |  | 1 | 1
3594050 | SEMINOLE WOODS | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-09-11 | AAA
3594050 | SEMINOLE WOODS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-09-11 | AAA
3594050 | SEMINOLE WOODS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.9 | UG/L | 60.4999 | 2019-09-27 | L1 |  |  |  | 0.2 | #1-221
3594050 | SEMINOLE WOODS | DBP | 2950 | TOTAL THMS | D | 9.23 | UG/L | 80.4999 | 2019-09-27 | L1 |  |  |  | 0.2 | #1-221
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 21.4 | UG/L | 10.4999 | 2015-01-08 | L5 |  |  |  |  | 1/08/15 BROMATE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-01-08 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.53 | UG/L | 60.4999 | 2015-01-14 | L4 |  |  |  | 0.9 | NW 40 8196 NARROW LEAF PT. (***LAST TEST AT THIS SITE - CHANGE IN SMP LOC TO 4965 SR 46 DUE TO INACTIVATION OF WPS IN THE SYSTEM WHICH MADE THE NEW SITE A BETTER CHOICE FOR THE STG2 SITE PER DEP RQST)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 54.19 | UG/L | 80.4999 | 2015-01-14 | L4 |  |  |  | 0.9 | NW 40 8196 NARROW LEAF PT. (***LAST TEST AT THIS SITE - CHANGE IN SMP LOC TO 4965 SR 46 DUE TO INACTIVATION OF WPS IN THE SYSTEM WHICH MADE THE NEW SITE A BETTER CHOICE FOR THE STG2 SITE PER DEP RQST)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 65.86 | UG/L | 80.4999 | 2015-01-14 | L1 |  |  |  | 0.9 | NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.77 | UG/L | 60.4999 | 2015-01-14 | L1 |  |  |  | 0.9 | NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 55.91 | UG/L | 80.4999 | 2015-01-14 | L2 |  |  |  | 0.75 | NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.93 | UG/L | 60.4999 | 2015-01-14 | L2 |  |  |  | 0.75 | NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 67.58 | UG/L | 80.4999 | 2015-01-14 | L3 |  |  |  | 0.89 | NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.13 | UG/L | 60.4999 | 2015-01-14 | L3 |  |  |  | 0.89 | NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-01-28 | L5 |  |  |  |  | 1/28/15 BROMATE - MARKHAM REGIONAL WP (1/15 MONTHLY BROMATE AVG=10.7)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | WTP4 |  |  |  |  | MARKHAM REGIONAL WP (5/20/15 HEA WP'S 4 HIGH SVC PUMPS HAVE BEEN SEVERED (PHOTOS) FROM 3594107 & WLS 2 4 5 TO BE RE-ROUTED TO MARKHAM REG.WP. 5/27/15 EM FROM DAV RQSTS INFO-SEE EM IN OC>SMPLNG/BACTES)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-11 | WTP1 |  |  |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-02-11 | WTP1 |  |  |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-02-11 | WTP4 |  |  |  |  | MARKHAM REGIONAL WP (5/20/15 HEA WP'S 4 HIGH SVC PUMPS HAVE BEEN SEVERED (PHOTOS) FROM 3594107 & WLS 2 4 5 TO BE RE-ROUTED TO MARKHAM REG.WP. 5/27/15 EM FROM DAV RQSTS INFO-SEE EM IN OC>SMPLNG/BACTES)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-02-11 | L5 |  |  |  |  | 2/15 BROMATE - MARKHAM REGIONAL WP (SEE 4/13/15 EM FROM "WILLIAMS ELISA" WHERE STG2 SITES CHANGING PER DECOMMISSIONING-NEW STG2 PLAN IN EM TO CK & RESPOND TO ELISA-BB)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-02-12 | WTP1 |  | 0.5499 |  |  | SPECIAL VOC MONITORING HEA POE (9/4/15 CONTAMINATED HEA WL/WLS HEA WL 6 BEING RE-ROUTED TO MARKHAM>EM GOING OUT IN S.S. BY CJ&JF ASKING FOR QTRLY 1 1-DIC & TCE AT POE/D MARKHAM ONCE THAT HAPPENS.)BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | D | 0 | UG/L | 10.4999 | 2015-03-03 | L5 | 1 |  | 1 | 1.23 | 3/15 BROMATE - MARKHAM REG. WP (C.R. NOT RQRD BUT GVN) IN OC (REVISED 3/15 BROMATE RAA IN OC - 3/15 BROMATE RAA 4/14-3/15 = 0.89)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-04-06 | L5 |  |  |  |  | (6/15 RAA IN OC)4/15 BROM-MAR WP(HEA WP'S 4 HIGH SVC PUMPS SEVERD FR.3594107 PER 5/20/15 LTR FR.S.MCFARLAND. DAV ASKD FOR MORE INFO ON WELLS IN 5/27/15EM IN BAC/SMPLNG IN OC-EM INCLUD.5/20/15 LTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 80.9 | UG/L | 80.4999 | 2015-04-14 | L3 |  |  |  | 0.82 | NW 64 1924 BRIDGEWATER DR.(T LRAA=79.8125VERIFIED HAA5 LOW)(IN OC)**8/3/15 EM TO E.WMS S.MCFARLAND SITE 64 BRIDGEWATER HAS 7/15 TTHM LRAA MCL VIOL-ENCOURAGD TO DO COREC ACTION & RESMPL BY 9/30)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.97 | UG/L | 60.4999 | 2015-04-14 | L2 |  |  |  | 0.55 | NW 56 1799 ASTOR FARMS PL. (T LRAA = 62.0875 HAA5 LOW)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | N | 76.03 | UG/L | 80.4999 | 2015-04-14 | L1 |  |  |  | 0.87 | NW 39 8507 CYPRESS HOLLOW CT. (T LRAA = 70.0525 HAA5 LOW)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | N | 24.44 | UG/L | 60.4999 | 2015-04-14 | L1 |  |  |  | 0.87 | NW 39 8507 CYPRESS HOLLOW CT. (T LRAA = 70.0525 HAA5 LOW)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 61.66 | UG/L | 80.4999 | 2015-04-14 | L6 |  |  |  | 0.75 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (SITE REPLACES 8196 NARROW LEAF CT.-BRAND NEW LRAA BEGINS 4/15-2 SITES NOT CLOSE TO EACH OTHER?NEW SITE CHOSEN DUE TO MAR & HEA WP INACTIVATIONS?DEP RQSTD CHANGE)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.99 | UG/L | 60.4999 | 2015-04-14 | L6 |  |  |  | 0.75 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (SITE REPLACES 8196 NARROW LEAF CT.-BRAND NEW LRAA BEGINS 4/15-2 SITES NOT CLOSE TO EACH OTHER?NEW SITE CHOSEN DUE TO MAR & HEA WP INACTIVATIONS?DEP RQSTD CHANGE)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.45 | UG/L | 60.4999 | 2015-04-14 | L3 |  |  |  | 0.82 | NW 64 1924 BRIDGEWATER DR.(T LRAA=79.8125VERIFIED HAA5 LOW)(IN OC)**8/3/15 EM TO E.WMS S.MCFARLAND SITE 64 BRIDGEWATER HAS 7/15 TTHM LRAA MCL VIOL-ENCOURAGD TO DO COREC ACTION & RESMPL BY 9/30)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 81.32 | UG/L | 80.4999 | 2015-04-14 | L2 |  |  |  | 0.55 | NW 56 1799 ASTOR FARMS PL. (T LRAA = 62.0875 HAA5 LOW)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-05-18 | L5 |  |  |  |  | 5/15 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-06-02 | L5 |  |  |  |  | 6/15 BROMATE - MAR WP (**PER WMS ELISA 8/5/15 WL. TEST 7/14 T/H & ADDITIONALLY FOR ALL SITES FOR THE 3594107 BY 9/30/15 DUE TO EXCEEDANCES 7/14/15-SHE WL. SEND SUMMARY THEN. BB)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 90.45 | UG/L | 80.4999 | 2015-07-14 | L3 |  |  |  | 0.94 | (NW 64 1924 BRIDGEWATER DR.) 9/15 AVG(2)= 85.86 T 18.09 H. RSLTS W/9/15 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.92 | UG/L | 60.4999 | 2015-07-14 | L3 |  |  |  | 0.94 | (NW 64 1924 BRIDGEWATER DR.) 9/15 AVG(2)= 85.86 T 18.09 H. RSLTS W/9/15 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 99.13 | UG/L | 80.4999 | 2015-07-14 | L2 |  |  |  | 1.11 | (NW 56 1799 ASTOR FARMS PL.) RCVD 9/15 OE REPORT T ASTOR FARMS SITE=83.8725 - IN OC (EM 11/3/15>ELSA WMS) NO LRAA MCL VIOLS T OE EXCEEDANCES=83.8725
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.5 | UG/L | 60.4999 | 2015-07-14 | L2 |  |  |  | 1.11 | (NW 56 1799 ASTOR FARMS PL.) RCVD 9/15 OE REPORT T ASTOR FARMS SITE=83.8725 - IN OC (EM 11/3/15>ELSA WMS) NO LRAA MCL VIOLS T OE EXCEEDANCES=83.8725
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 85.19 | UG/L | 80.4999 | 2015-07-14 | L1 |  |  |  | 1.12 | (NW 39 8507 CYPRESS HOLLOW CT.) RSLTS W/9/15 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.91 | UG/L | 60.4999 | 2015-07-14 | L1 |  |  |  | 1.12 | (NW 39 8507 CYPRESS HOLLOW CT.) RSLTS W/9/15 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.77 | UG/L | 60.4999 | 2015-07-14 | L6 |  |  |  | 0.93 | (NW 79 4965 S.R. 46 (NEW SITE 4/1/15)) RSLTS W/915 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 66.3 | UG/L | 80.4999 | 2015-07-14 | L6 |  |  |  | 0.93 | (NW 79 4965 S.R. 46 (NEW SITE 4/1/15)) RSLTS W/915 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-07-15 | L5 |  |  |  |  | 7/15 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-08-05 | L5 |  |  |  |  | 8/15 BROMATE - MAR WP >>ASKED ELISA FOR 9/15 BROMATE-MAR BY EM 11/20/15 - SHE SENT AVGS INSTEAD OF LAB REPORT BY MISTAKE. BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 81.27 | UG/L | 80.4999 | 2015-08-31 | L3 |  |  |  | 1.27 | (NW 64 1924 BRIDGEWATER DR.) 9/15 AVG(2)=85.86 T 18.09 H. RSLTS W/9/15 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.26 | UG/L | 60.4999 | 2015-08-31 | L3 |  |  |  | 1.27 | (NW 64 1924 BRIDGEWATER DR.) 9/15 AVG(2)=85.86 T 18.09 H. RSLTS W/9/15 DBF NO LRAA MCL VIOLS NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-09-03 | L5 |  |  |  |  | 9/15 BROMATE - MAR WP (9/15 BROMATE RAA IN OC)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-10-12 | L5 |  |  |  |  | 10/15 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 47.79 | UG/L | 80.4999 | 2015-10-15 | L3 |  |  |  | 0.96 | NW 64 1924 BRIDGEWATER DR. (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.77 | UG/L | 60.4999 | 2015-10-15 | L3 |  |  |  | 0.96 | NW 64 1924 BRIDGEWATER DR. (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 46.38 | UG/L | 80.4999 | 2015-10-15 | L6 |  |  |  | 1.33 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.57 | UG/L | 60.4999 | 2015-10-15 | L6 |  |  |  | 1.33 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 61.75 | UG/L | 80.4999 | 2015-10-15 | L1 |  |  |  | 1.23 | NW 39 8507 CYPRESS HOLLOW CT. (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.41 | UG/L | 60.4999 | 2015-10-15 | L1 |  |  |  | 1.23 | NW 39 8507 CYPRESS HOLLOW CT. (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 69.31 | UG/L | 80.4999 | 2015-10-15 | L2 |  |  |  | 1.43 | NW 56 1799 ASTOR FARMS PL. (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.04 | UG/L | 60.4999 | 2015-10-15 | L2 |  |  |  | 1.43 | NW 56 1799 ASTOR FARMS PL. (DOES NOT QUALIFY FOR R.M.) CK LRAAS
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 22 | UG/L | 10.4999 | 2015-11-02 | L5 |  |  |  |  | 11/15 BROMATE - MAR WP (BROMATE 22 UG/L) **12/15 BROMATE RAAS ARE IN OC & EW HAS 12/15 BROMATE 2/24/16 - BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-11-17 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2015-12-01 | L5 |  |  |  |  | 12/15 BROMATE - MAR WP (12/15 BROMATE RAA IN OC)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-12-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-01-07 | L5 |  |  |  |  | 1/16 BROMATE - MAR WP (4/26 EW HAS 3/16 & 2/16 BROMATE)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-01-12 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.31 | UG/L | 60.4999 | 2016-01-14 | L6 |  |  |  | 1.29 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 35.44 | UG/L | 80.4999 | 2016-01-14 | L2 |  |  |  | 1.24 | NW 56 1799 ASTOR FARMS PL. (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.82 | UG/L | 60.4999 | 2016-01-14 | L3 |  |  |  | 1.14 | NW 64 1924 BRIDGEWATER DR. (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 41.4 | UG/L | 80.4999 | 2016-01-14 | L3 |  |  |  | 1.14 | NW 64 1924 BRIDGEWATER DR. (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 25.19 | UG/L | 80.4999 | 2016-01-14 | L6 |  |  |  | 1.29 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.65 | UG/L | 60.4999 | 2016-01-14 | L2 |  |  |  | 1.24 | NW 56 1799 ASTOR FARMS PL. (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.37 | UG/L | 60.4999 | 2016-01-14 | L1 |  |  |  | 1.26 | NW 39 8507 CYPRESS HOLLOW CT. (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 36.2 | UG/L | 80.4999 | 2016-01-14 | L1 |  |  |  | 1.26 | NW 39 8507 CYPRESS HOLLOW CT. (NO LRAA OR OE EXCEEDANCES ON DB REPORT) DOES NOT QUALIFY FOR R.M.
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-01-21 | WTP4 |  |  |  |  | MAR WP (J4 QUAL NO3: MS/MSD BOTH 112% RECOV BIASED HIGH ACCEPTABLE LCS OK)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-21 | WTP4 |  |  |  |  | MAR WP (J4 QUAL NO3: MS/MSD BOTH 112% RECOV BIASED HIGH ACCEPTABLE LCS OK)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 7.7 | UG/L | 10.4999 | 2016-02-10 | L5 |  |  |  |  | 2/16 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-02-10 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-03-09 | L5 |  |  |  |  | 3/16 BROMATE - MAR WP (3/16 BROMATE & 3/16 BROMATE RAA IN OC) 3/16 RAA/BROMATE = 2.48 PER REPORT (7/11 EW HAS 4/16 DBPS & 6/16 DB REPORT>NO LRAA MCLS OR OE EXCEEDANCES)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-03-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-04-04 | L5 |  |  |  |  | 4/16 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-04-04 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 61.61 | UG/L | 80.4999 | 2016-04-13 | L3 |  |  |  | 1.5 | NW 64 1924 BRIDGEWATER DR. (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 48.75 | UG/L | 80.4999 | 2016-04-13 | L1 |  |  |  | 1.69 | NW 39 8507 CYPRESS HOLLOW CT. (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.12 | UG/L | 60.4999 | 2016-04-13 | L1 |  |  |  | 1.69 | NW 39 8507 CYPRESS HOLLOW CT. (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 37.84 | UG/L | 80.4999 | 2016-04-13 | L6 |  |  |  | 1.74 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.12 | UG/L | 60.4999 | 2016-04-13 | L6 |  |  |  | 1.74 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.81 | UG/L | 60.4999 | 2016-04-13 | L3 |  |  |  | 1.5 | NW 64 1924 BRIDGEWATER DR. (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 61.84 | UG/L | 80.4999 | 2016-04-13 | L2 |  |  |  | 1.58 | NW 56 1799 ASTOR FARMS PL. (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.65 | UG/L | 60.4999 | 2016-04-13 | L2 |  |  |  | 1.58 | NW 56 1799 ASTOR FARMS PL. (NO LRAA MCLS NO OE EXCEEDANCES 6/16 QTR)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-05-09 | L5 |  |  |  |  | 5/16 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-05-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-06-13 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-06-13 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-06-13 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-06-13 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-06-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-06-13 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-06-13 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-06-13 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-06-13 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-06-13 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-06-13 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-06-13 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-06-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-06-13 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-06-13 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-06-13 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-06-13 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | D | 12 | UG/L | 10.4999 | 2016-06-13 | L5 | 1 |  | 1 | 1.85 | 6/16 BROMATE - MAR WP (IN OC) (6/16 BROMATE & 6/16 BROMATE RAA IN OC) 6/16 RAA/BROMATE = 3.48 PER REPORT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-06-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-06-13 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-06-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-06-13 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-07-11 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-07-11 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-07-11 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-07-11 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-07-11 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-07-11 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-07-11 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-07-11 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-07-11 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-07-11 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-07-11 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-07-11 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-07-11 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-07-11 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-07-11 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-07-11 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-07-11 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-07-11 | L5 | 1 |  | 1 | 1.66 | 7/16 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 66.31 | UG/L | 80.4999 | 2016-07-14 | L1 |  |  |  | 1.39 | NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.71 | UG/L | 60.4999 | 2016-07-14 | L2 |  |  |  | 1.36 | NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 67.95 | UG/L | 80.4999 | 2016-07-14 | L2 |  |  |  | 1.36 | NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.81 | UG/L | 60.4999 | 2016-07-14 | L3 |  |  |  | 1.15 | NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 79.38 | UG/L | 80.4999 | 2016-07-14 | L3 |  |  |  | 1.15 | NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.85 | UG/L | 60.4999 | 2016-07-14 | L6 |  |  |  | 1.82 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 46.95 | UG/L | 80.4999 | 2016-07-14 | L6 |  |  |  | 1.82 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.21 | UG/L | 60.4999 | 2016-07-14 | L1 |  |  |  | 1.39 | NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-08-11 | L5 |  |  |  |  | 8/16 BROMATE - MAR WP (****7/14/16 DBPS & 3RD QTR DISINF BYP REPORT IN OCULUS*** NOT YET ENT'D)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-08-11 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 1.7 | UG/L | 10499.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0.23 | UG/L | 749.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-09-15 | L5 |  |  |  | 1.51 | 9/16 BROMATE MAR WP (ROUTINE BROMATE DUE MONTHLY BROMATE RAA DUE QUARTERLY) 9/16 BROMATE RAA RCVD & IN OC - 9/16 BROMATE RAA REPORTED AS 3.48 UG/L (SINCE <10 OK) THESE NOTES ADDED FOR BW ON 2/13/17
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0.31 | UG/L | 10499.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-09-15 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 59.22 | UG/L | 80.4999 | 2016-10-13 | L1 |  |  |  | 1.55 | NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 32.72 | UG/L | 80.4999 | 2016-10-13 | L6 |  |  |  | 1.77 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 5.65 | UG/L | 60.4999 | 2016-10-13 | L6 |  |  |  | 1.77 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 56.35 | UG/L | 80.4999 | 2016-10-13 | L3 |  |  |  | 1.62 | NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.52 | UG/L | 60.4999 | 2016-10-13 | L3 |  |  |  | 1.62 | NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 47.31 | UG/L | 80.4999 | 2016-10-13 | L2 |  |  |  | 1.82 | NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.99 | UG/L | 60.4999 | 2016-10-13 | L2 |  |  |  | 1.82 | NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.81 | UG/L | 60.4999 | 2016-10-13 | L1 |  |  |  | 1.55 | NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-10-18 | L5 |  |  |  | 1.52 | 10/18/16 BROMATE MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-10-18 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-10-18 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | S | 0 | UG/L | 7.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | S | 0 | UG/L | 249.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | S | 0 | UG/L | 3.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP (WELL #6)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-11-10 | L5 |  |  |  | 1.5 | 11/16 BROMATE MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-11-10 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | S | 0 | UG/L | 5.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | S | 0 | UG/L | 649.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | S | 0 | UG/L | 75.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | S | 0 | UG/L | 1.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | S | 0 | UG/L | 1.4999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | S | 0 | UG/L | 1499.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | S | 0 | UG/L | 749.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | S | 0 | UG/L | 149.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #2)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | S | 0 | UG/L | 74.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | S | 0 | UG/L | 74.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | S | 0 | UG/L | 10499.9999 | 2016-11-10 | WTP1 |  | 0.5499 |  |  | SPEC.VOC MON-HEATHROW WP (WELL #5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2016-12-13 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2016-12-13 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2016-12-13 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2016-12-13 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2016-12-13 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-12-13 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2016-12-13 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2016-12-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2016-12-13 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2016-12-13 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2016-12-13 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2016-12-13 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2016-12-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2016-12-13 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2016-12-13 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2016-12-13 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2016-12-13 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-12-13 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2016-12-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2016-12-13 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2016-12-13 | L5 | 1 |  | 1 | 1.79 | 12/16 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2016-12-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.34 | UG/L | 60.4999 | 2017-01-11 | L1 | 0.2 |  | 1 | 1.42 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 49.02 | UG/L | 80.4999 | 2017-01-11 | L6 | 0.14 |  | 4 | 1.47 | 4965 S.R. 46 (3/17 LRAA/T FOR 4 SITES = @ 40 - 66 UG/L LRAA/H=LOW) 3/17 DB REPORT RCVD. NO OE EXCEEDANCES. DOES NOT QUALIFY FOR REDUCED MONITORING.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.42 | UG/L | 60.4999 | 2017-01-11 | L6 | 0.2 |  | 4 | 1.47 | 4965 S.R. 46 (3/17 LRAA/T FOR 4 SITES = @ 40 - 66 UG/L LRAA/H=LOW) 3/17 DB REPORT RCVD. NO OE EXCEEDANCES. DOES NOT QUALIFY FOR REDUCED MONITORING.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 69.6 | UG/L | 80.4999 | 2017-01-11 | L3 | 0.14 |  | 3 | 1.3 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 67.48 | UG/L | 80.4999 | 2017-01-11 | L1 | 0.14 |  | 1 | 1.42 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.1 | UG/L | 60.4999 | 2017-01-11 | L2 | 0.2 |  | 2 | 1.44 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 62.52 | UG/L | 80.4999 | 2017-01-11 | L2 | 0.14 |  | 2 | 1.44 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.24 | UG/L | 60.4999 | 2017-01-11 | L3 | 0.2 |  | 3 | 1.3 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-01-12 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-01-12 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-01-12 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-01-12 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-01-12 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-01-12 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-12 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-01-12 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-01-12 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-01-12 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-01-12 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-01-12 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-01-12 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-01-12 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-01-12 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-01-12 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-01-12 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-01-12 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-01-12 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-01-12 | L5 | 1 |  | 1 | 1.38 | 1/17 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-01-12 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-01-12 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP4 | 0.28 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP4 | 0.32 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-06 | WTP4 | 0.28 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP4 | 0.44 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-06 | WTP4 | 0.46 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-06 | WTP4 | 0.26 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP4 | 0.2 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-06 | WTP4 | 0.18 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP4 | 0.28 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP4 | 0.36 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP4 | 0.39 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP4 | 0.23 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP4 | 0.26 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP4 | 0.28 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-06 | WTP4 | 0.12 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP4 | 0.24 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP4 | 0.12 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP4 | 0.17 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-06 | WTP4 | 0.22 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1025 | FLUORIDE | N | 0.42 | MG/L | 2.0499 | 2017-02-06 | WTP4 | 0.075 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-06 | WTP4 | 0.03 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-02-06 | WTP4 | 0.00024 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-06 | WTP4 | 0.17 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP4 | 0.39 | 0.5499 |  |  | 3YR VOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP4 | 0.0069 | 0.0149 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP4 | 0.0071 | 0.0249 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-06 | WTP4 | 0.0068 | 0.1499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP4 | 0.12 | 1.4999 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP4 | 1 | 1.4999 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-06 | WTP4 | 7.6 | 0.4499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-06 | WTP4 | 1.2 | 9.4999 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-06 | WTP4 | 6.5 | 6.4999 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-06 | WTP4 | 0.95 | 0.6499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-06 | WTP4 | 0.57 | 2.4999 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-06 | WTP4 | 0.19 | 0.0749 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-06 | WTP4 | 1.5 | 0.6499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-06 | WTP4 | 0.23 | 0.1499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-06 | WTP4 | 0.86 | 0.2499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-06 | WTP4 | 0.012 | 0.1499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-06 | WTP4 | 0.28 | 0.9499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-06 | WTP4 | 0.16 | 0.1499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP4 | 0.26 | 0.2499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-06 | WTP4 | 0.006 | 0.0449 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP4 | 0.0052 | 0.0249 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-06 | WTP4 | 1.5 | 0.1499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-06 | WTP4 | 0.32 | 0.2499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP4 | 0.0063 | 0.1499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP4 | 0.096 | 0.0249 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-06 | WTP4 | 0.069 | 0.0449 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-06 | WTP4 | 0.11 | 0.1499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-06 | WTP4 | 0.0061 | 0.0249 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-06 | WTP4 | 0.0063 | 0.0149 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-06 | WTP4 | 0.053 | 0.2499 |  |  | 1Q SOC/MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 7.8 | PCI/L | 15.4999 | 2017-02-06 | WTP4 | 1.8 |  |  |  | MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | RAD | 4020 | RADIUM-226 | N | 1.3 | PCI/L | 3.4999 | 2017-02-06 | WTP4 | 0.4 | 1.4999 |  |  | MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-06 | WTP4 | 0.6 | 1.4999 |  |  | MAR WP (HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1025 | FLUORIDE | N | 0.42 | MG/L | 4.0499 | 2017-02-06 | WTP4 | 0.075 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-06 | WTP4 | 0.00024 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-06 | WTP4 | 1e-05 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP4 | 0.0011 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-06 | WTP4 | 0.00058 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1052 | SODIUM | N | 33 | MG/L | 160.4999 | 2017-02-06 | WTP4 | 0.16 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-06 | WTP4 | 5e-05 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-06 | WTP4 | 0.00013 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-06 | WTP4 | 6e-05 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-06 | WTP4 | 0.061 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1017 | CHLORIDE | N | 65 | MG/L | 250.4999 | 2017-02-06 | WTP4 | 0.78 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2017-02-06 | WTP4 | 0.0025 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1040 | NITRATE | N | 0.17 | MG/L | 10.4999 | 2017-02-06 | WTP4 | 0.051 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-06 | WTP4 | 0.053 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2017-02-06 | WTP4 | 8e-05 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1010 | BARIUM | N | 0.0094 | MG/L | 2.4999 | 2017-02-06 | WTP4 | 0.00028 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-06 | WTP4 | 0.00032 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP4 | 0.0005 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-06 | WTP4 | 0.0048 |  |  |  | MAR WP (TRIENNIAL CHEMS HYPERLINKED 3/8/17)
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-02-06 | WTP4 | 3e-05 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1055 | SULFATE | N | 18 | MG/L | 250.4999 | 2017-02-06 | WTP4 | 0.52 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-06 | WTP4 | 0.002 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-06 | WTP4 | 5 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-06 | WTP4 | 1 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.82 | LN(10) |  | 2017-02-06 | WTP4 |  |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 300 | MG/L | 500.4999 | 2017-02-06 | WTP4 | 10 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-06 | WTP4 | 0.04 |  |  |  | MAR WP (HYPERLINKED 3/8/17) MAR WELL 2 RETURN TO SERVICE APPROVAL GRANTED 3/20/17-ELSA WMS WL TAKE POE TDS BECAUSE RAW WELL 2 HAD HIGH TDS - BB
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1040 | NITRATE | N | 0.17 | MG/L | 10.4999 | 2017-02-08 | WTP4 | 0.051 |  |  |  | MAR WP (NO2 J4: MS 88%/MSD 89%) RESULTS HYPERLINKED TO BW 3/8/17-BB
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-08 | WTP4 | 0.053 |  |  |  | MAR WP (NO2 J4: MS 88%/MSD 89%) RESULTS HYPERLINKED TO BW 3/8/17-BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-16 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-16 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-16 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-16 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-16 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-16 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-16 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-16 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-16 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-16 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-16 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-16 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-16 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-16 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-16 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-16 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-16 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-16 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 15 | UG/L | 10.4999 | 2017-02-16 | L5 | 1 |  | 1 | 1.57 | 2/17 BROMATE - MAR WP (HYPERLINKED 3/8/17 TO BW-BB) MCL = 10 UG/L
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-09 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-09 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-09 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-09 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-09 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-09 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-09 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-09 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-09 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-09 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-09 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 7.7 | UG/L | 10.4999 | 2017-03-09 | L5 | 1 |  | 1 | 1.89 | 3/17 BROMATE - MAR WP (HYPERLINKED 4/4/17 TO BW-BB) ORIG 3/17 BROMATE RAA RCVD (HYPERLINKED 4/4/17 - BB) & 3/17 BROMATE RAA REVISION RCVD 6/1/17 (HYPERLINKED 6/19/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-09 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-09 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-09 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-09 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-09 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-09 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-09 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-09 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-09 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-09 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 76.09 | UG/L | 80.4999 | 2017-04-11 | L3 | 0.14 |  | 3 | 1.13 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 68.51 | UG/L | 80.4999 | 2017-04-11 | L1 | 0.14 |  | 1 | 1.21 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.09 | UG/L | 60.4999 | 2017-04-11 | L1 | 0.52 |  | 1 | 1.21 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.66 | UG/L | 60.4999 | 2017-04-11 | L6 | 0.52 |  | 4 | 1.35 | 4965 S.R. 46 (NEW SITE 4/1/15) 6/17 DB REPORT RCVD: 6/17 LRAAS/T 4 SITES @ 46 - 70 LRAAS/H 4 SITES @ 7 - 11 (DOES NOT QUALIFY FOR REDUCED MONITORING NO OE EXCEEDANCES)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 56.16 | UG/L | 80.4999 | 2017-04-11 | L6 | 0.14 |  | 4 | 1.35 | 4965 S.R. 46 (NEW SITE 4/1/15) 6/17 DB REPORT RCVD: 6/17 LRAAS/T 4 SITES @ 46 - 70 LRAAS/H 4 SITES @ 7 - 11 (DOES NOT QUALIFY FOR REDUCED MONITORING NO OE EXCEEDANCES)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.21 | UG/L | 60.4999 | 2017-04-11 | L3 | 0.52 |  | 3 | 1.13 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.95 | UG/L | 60.4999 | 2017-04-11 | L2 | 0.52 |  | 2 | 1.14 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 71.88 | UG/L | 80.4999 | 2017-04-11 | L2 | 0.14 |  | 2 | 1.14 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP4 | 0.007 | 0.0149 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-04-13 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-04-13 | WTP4 | 0.0069 | 0.1499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP4 | 0.12 | 1.4999 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-04-13 | WTP4 | 1 | 1.4999 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-04-13 | WTP4 | 7.6 | 0.4499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-04-13 | WTP4 | 1.2 | 9.4999 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-04-13 | WTP4 | 6.5 | 6.4999 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-04-13 | WTP4 | 0.96 | 0.6499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-04-13 | WTP4 | 0.57 | 2.4999 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-04-13 | WTP4 | 0.19 | 0.0749 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-04-13 | WTP4 | 1.5 | 0.6499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-04-13 | WTP4 | 0.23 | 0.1499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-04-13 | WTP4 | 0.86 | 0.2499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-04-13 | WTP4 | 0.013 | 0.1499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-04-13 | WTP4 | 0.28 | 0.9499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP4 | 0.16 | 0.1499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP4 | 0.26 | 0.2499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-04-13 | WTP4 | 0.0061 | 0.0449 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP4 | 0.0053 | 0.0249 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-04-13 | WTP4 | 1.5 | 0.1499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-04-13 | WTP4 | 0.32 | 0.2499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP4 | 0.0064 | 0.1499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP4 | 0.097 | 0.0249 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP4 | 0.069 | 0.0449 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-04-13 | WTP4 | 0.11 | 0.1499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP4 | 0.0061 | 0.0249 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-04-13 | WTP4 | 0.0063 | 0.0149 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-04-13 | WTP4 | 0.054 | 0.2499 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-04-13 | L5 | 1 |  | 1 | 1.28 | 4/17 BROMATE - MAR WP (RESULTS HYPERLINKED 5/31/17 TO BW-BB)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-04-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-04-13 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-04-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-04-13 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-04-13 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-04-13 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-04-13 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-04-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-04-13 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-04-13 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-04-13 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-04-13 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-04-13 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-04-13 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-04-13 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-04-13 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-04-13 | WTP4 | 0.0072 | 0.0249 |  |  | 2Q SOC/MAR WP (NO DETECTIONS)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP4 | 0.31 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 7.9 | UG/L | 10.4999 | 2017-05-04 | L5 | 1 |  | 1 | 1.45 | 5/17 BROMATE - MAR WP (RESULTS HYPERLINKED 6/16/17 TO BW - BB)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP4 | 0.3 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-05-04 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP4 | 0.15 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-05-04 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-05-04 | WTP4 | 0.21 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-05-04 | WTP4 | 0.14 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-05-04 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-05-04 | WTP4 | 0.29 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-05-04 | WTP4 | 0.38 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-05-04 | WTP4 | 0.25 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-05-04 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-05-04 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-05-04 | WTP4 | 0.13 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-05-04 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-05-04 | WTP4 | 0.38 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP4 | 0.27 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-05-04 | WTP4 | 0.21 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-05-04 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-05-04 | WTP4 | 0.15 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-05-04 | WTP4 | 0.35 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 1.6 | UG/L | 10.4999 | 2017-06-05 | L5 | 1 |  | 1 | 1.39 | 6/17 BROMATE - MAR WP (6/17 BROMATE RAA RCVD RAA REPORTED AS 2.68)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-06-05 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-06-05 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-06-05 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-06-05 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-06-05 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-06-05 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-06-05 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-06-05 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-06-05 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-06-05 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-06-05 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-06-05 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-06-05 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-06-05 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-06-05 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-06-05 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-06-05 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-06-05 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-06-05 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-06-05 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-06-05 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.47 | UG/L | 60.4999 | 2017-07-13 | L1 | 0.5 |  | 1 | 1.38 | 8507 CYPRESS HOLLOW CT. (9/17 LRAA/T=65.6 LRAA/H=11.6775) NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 67.19 | UG/L | 80.4999 | 2017-07-13 | L1 | 0.14 |  | 1 | 1.38 | 8507 CYPRESS HOLLOW CT. (9/17 LRAA/T=65.6 LRAA/H=11.6775) NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.52 | UG/L | 60.4999 | 2017-07-13 | L2 | 0.5 |  | 2 | 1.47 | 1799 ASTOR FARMS PL. (9/17 LRAA/T=59.315 LRAA/H=12.39) NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 55.55 | UG/L | 80.4999 | 2017-07-13 | L2 | 0.14 |  | 2 | 1.47 | 1799 ASTOR FARMS PL. (9/17 LRAA/T=59.315 LRAA/H=12.39) NO OE EXCEEDANCE THIS SITE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9 | UG/L | 60.4999 | 2017-07-13 | L3 | 0.5 |  | 3 | 1.11 | 1924 BRIDGEWATER DR. (9/17 LRAA/T=72.7025 LRAA/H=10.4925) **9/17 T OE VAL=80.8075 - 9/17 QTR OE REPORT RCVD & IN OC. BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 88.77 | UG/L | 80.4999 | 2017-07-13 | L3 | 0.14 |  | 3 | 1.11 | 1924 BRIDGEWATER DR. (9/17 LRAA/T=72.7025 LRAA/H=10.4925) **9/17 T OE VAL=80.8075 - 9/17 QTR OE REPORT RCVD & IN OC. BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.09 | UG/L | 60.4999 | 2017-07-13 | L6 | 0.5 |  | 4 | 1.58 | 4965 S.R. 46(9/17 QTR DB RPRT RCVD-NO 9/17 QTR LRAA MCL VIOLS 9/17 LRAA/T=44.4075 9/17 LRAA/H=7.705)NO OE EXCEEDANCE THIS SITE(9/17 QTR OE EXCEEDANCE BRIDGEWATER SITE-OE REPORT IN OC)HYPRLNKD 8/28/17
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 39.73 | UG/L | 80.4999 | 2017-07-13 | L6 | 0.14 |  | 4 | 1.58 | 4965 S.R. 46(9/17 QTR DB RPRT RCVD-NO 9/17 QTR LRAA MCL VIOLS 9/17 LRAA/T=44.4075 9/17 LRAA/H=7.705)NO OE EXCEEDANCE THIS SITE(9/17 QTR OE EXCEEDANCE BRIDGEWATER SITE-OE REPORT IN OC)HYPRLNKD 8/28/17
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-07-17 | L5 | 1 |  | 1 | 1.5 | 7/17 BROMATE - MAR WP (HYPERLINKED 8/25/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-07-17 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-07-17 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-07-17 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-07-17 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-07-17 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-07-17 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-07-17 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-07-17 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-07-17 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-07-17 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-07-17 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-07-17 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-07-17 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-07-17 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-07-17 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-07-17 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-07-17 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-07-17 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-07-17 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-07-17 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-07-17 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MARKHAM WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>S.S. BY CJ&JF ASKS FOR QTRLY 1 1-DIC&TCE AT POE MARKHAM ONCE HEA WELLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-08-08 | L5 | 1 |  | 1 | 1.76 | 8/17 BROMATE - MARKHAM WP (HYPERLINKED 9/15/17)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-08-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-08-08 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-08-08 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-08-08 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-08-08 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-08-08 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-08-08 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-08-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-08-08 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-08-08 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-08-08 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-08-08 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-08-08 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-08-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-08-08 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-08-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-08-08 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-08-08 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-08-08 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-08-08 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-08-08 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MAR WP(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(ONLY POE NDS ENTRY)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-09-18 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-09-18 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-09-18 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-09-18 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-18 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-09-18 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-09-18 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-09-18 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 1 | UG/L | 749.9999 | 2017-09-18 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-09-18 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-09-18 | L5 | 1 |  | 1 | 1.6 | 9/17 BROMATE - MAR WP (9/17 BROMATE RAA RCVD RAA REPORTED AS 2.68) HYPERLINKED 10/19/17 TO BW - BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-09-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-09-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 1.9 | UG/L | 10499.9999 | 2017-09-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-09-18 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-09-18 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-09-18 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-09-18 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-09-18 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-09-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-09-18 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-09-18 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0(11/15 CONTAMINATED HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 31.88 | UG/L | 80.4999 | 2017-10-12 | L6 | 0.31 |  | 4 | 1.28 | 4965 S.R. 46 (NEW SITE 4/1/15) 10/17 DBPS RCVD W/ 12/17 DISINF BYP REPORT (DOES NOT QUALIFY FOR REDUCED MONITORING NO EXCEEDANCES) HYPERLINKED 12/22/17 TO BW - BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.45 | UG/L | 60.4999 | 2017-10-12 | L6 | 0.5 |  | 4 | 1.28 | 4965 S.R. 46 (NEW SITE 4/1/15) 10/17 DBPS RCVD W/ 12/17 DISINF BYP REPORT (DOES NOT QUALIFY FOR REDUCED MONITORING NO EXCEEDANCES) HYPERLINKED 12/22/17 TO BW - BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 63 | UG/L | 80.4999 | 2017-10-12 | L3 | 0.31 |  | 3 | 0.93 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.28 | UG/L | 60.4999 | 2017-10-12 | L3 | 0.5 |  | 3 | 0.93 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 72.39 | UG/L | 80.4999 | 2017-10-12 | L2 | 0.31 |  | 2 | 0.94 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.35 | UG/L | 60.4999 | 2017-10-12 | L2 | 0.5 |  | 2 | 0.94 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.44 | UG/L | 60.4999 | 2017-10-12 | L1 | 0.5 |  | 1 | 1.28 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 53.34 | UG/L | 80.4999 | 2017-10-12 | L1 | 0.31 |  | 1 | 1.28 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-10-18 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-10-18 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2017-10-18 | L5 | 1 |  | 1 | 1.74 | 10/17 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-10-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-10-18 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-10-18 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-10-18 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-10-18 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-10-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-10-18 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-10-18 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-10-18 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-10-18 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-10-18 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-10-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-10-18 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-10-18 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-10-18 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-10-18 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-10-18 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-10-18 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-10-18 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-MAR WP-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-11-06 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-11-06 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-11-06 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-11-06 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-11-06 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-11-06 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-06 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-11-06 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-11-06 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-11-06 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-11-06 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-11-06 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-11-06 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-11-06 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-11-06 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-11-06 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-11-06 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 4.2 | UG/L | 10.4999 | 2017-11-06 | L5 | 1 |  | 1 | 1.62 | 11/17 BROMATE - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-11-06 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-11-06 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-11-06 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-11-06 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-12-07 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-12-07 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-12-07 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-12-07 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-12-07 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-12-07 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-12-07 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-12-07 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-12-07 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-12-07 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-12-07 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-12-07 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 8.2 | UG/L | 10.4999 | 2017-12-07 | L5 | 1 |  | 1 | 1.91 | 12/17 BROMATE - MAR WP (12/17 BROMATE RAA RCVD RAA REPORTED AS 3.72) HYPERLINKED 10/19/17 TO BW - BB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-12-07 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-12-07 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-12-07 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-12-07 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-12-07 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-12-07 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-12-07 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-12-07 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-12-07 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-01-10 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-01-10 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-01-10 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-01-10 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-01-10 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-01-10 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-01-10 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-01-10 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-01-10 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-01-10 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-01-10 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-01-10 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 17 | UG/L | 10.4999 | 2018-01-10 | L5 | 1 |  | 1 | 1.79 | 1/18 BROMATE - MAR WP (ELEVATED RESULTS-HYPERLINKED 2/26/18 TO BW - BB) RAA NOT CURRENTLY OVER 10 UG/L THE MCL
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-01-10 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-01-10 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-01-10 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-01-10 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-01-10 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-01-10 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-01-10 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-01-10 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-01-10 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.91 | UG/L | 60.4999 | 2018-01-11 | L6 | 0.5 |  | 4 | 1.29 | 4965 S.R. 46 (1/18 RSLTS RCVD WITH 3/18 DISINF BYP REPORT) HYPERLINKED 3/5/18 TO BW - BB (CONT. QM/DBPS)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 51.71 | UG/L | 80.4999 | 2018-01-11 | L6 | 0.14 |  | 4 | 1.29 | 4965 S.R. 46 (1/18 RSLTS RCVD WITH 3/18 DISINF BYP REPORT) HYPERLINKED 3/5/18 TO BW - BB (CONT. QM/DBPS)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.21 | UG/L | 60.4999 | 2018-01-11 | L1 | 0.5 |  | 1 | 0.88 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 71.47 | UG/L | 80.4999 | 2018-01-11 | L1 | 0.14 |  | 1 | 0.88 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.55 | UG/L | 60.4999 | 2018-01-11 | L2 | 0.5 |  | 2 | 1.03 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 72.49 | UG/L | 80.4999 | 2018-01-11 | L2 | 0.14 |  | 2 | 1.03 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.87 | UG/L | 60.4999 | 2018-01-11 | L3 | 0.5 |  | 3 | 1.13 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 67.44 | UG/L | 80.4999 | 2018-01-11 | L3 | 0.14 |  | 3 | 1.13 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 12 | UG/L | 10.4999 | 2018-02-08 | L5 | 1 |  | 1 | 1.84 | 2/18 BROMATE - MAR WP (4/19/18 HYPERLINKED TO BW - BB) BROMATE > MCL 2/18 AND 1/18 SINGLE SMP RESULTS
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-08 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-08 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-08 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-08 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-08 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-08 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-08 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-08 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-08 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-08 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-08 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-08 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-08 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-08 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-08 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-08 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1040 | NITRATE | N | 0.15 | MG/L | 10.4999 | 2018-02-08 | WTP4 | 0.051 |  |  |  | NN - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-08 | WTP4 | 0.053 |  |  |  | NN - MAR WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-08 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-03-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 8.4 | UG/L | 10.4999 | 2018-03-08 | L5 | 1 |  | 1 | 1.45 | 3/18 BROMATE - MAR WP (4/23/18 RSLTS & RAA HYPERLINKED TO BW - BB) BROMATE 8.4 (BROMATE>MCL 2/18 & 1/18 SINGLE SMP RESULTS)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-03-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-03-08 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-03-08 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-03-08 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-03-08 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-03-08 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-03-08 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-03-08 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-08 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-03-08 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-03-08 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-03-08 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-03-08 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-03-08 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-03-08 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-03-08 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-04-09 | WTP4 |  | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 17 | UG/L | 10.4999 | 2018-04-09 | L5 | 1 |  | 1 | 1.72 | 4/18 BROMATE - MAR WP (5/30/18 HLK'D - BB)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.04 | UG/L | 60.4999 | 2018-04-12 | L2 | 0.5 |  | 2 | 1.19 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.95 | UG/L | 60.4999 | 2018-04-12 | L3 | 0.5 |  | 3 | 0.91 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 68.22 | UG/L | 80.4999 | 2018-04-12 | L3 | 0.14 |  | 3 | 0.91 | 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 55.36 | UG/L | 80.4999 | 2018-04-12 | L1 | 0.14 |  | 1 | 1.25 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.97 | UG/L | 60.4999 | 2018-04-12 | L1 | 0.5 |  | 1 | 1.25 | 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 38.12 | UG/L | 80.4999 | 2018-04-12 | L6 | 0.14 |  | 4 | 1.35 | 4965 S.R. 46 (6/18 DISINF BYP RPRT RCVD W/RSLTS) HLKD RSLTS & LRAAS TO RLB 6/21/18 - BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.64 | UG/L | 60.4999 | 2018-04-12 | L6 | 0.5 |  | 4 | 1.35 | 4965 S.R. 46 (6/18 DISINF BYP RPRT RCVD W/RSLTS) HLKD RSLTS & LRAAS TO RLB 6/21/18 - BB
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 60.01 | UG/L | 80.4999 | 2018-04-12 | L2 | 0.14 |  | 2 | 1.19 | 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-05-08 | WTP4 | 0.39 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-05-08 | WTP4 | 0.12 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-08 | WTP4 | 0.24 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-05-08 | WTP4 | 0.12 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-05-08 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-05-08 | WTP4 | 0.26 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-05-08 | WTP4 | 0.23 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-05-08 | WTP4 | 0.39 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-05-08 | WTP4 | 0.36 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-05-08 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-05-08 | WTP4 | 0.18 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-05-08 | WTP4 | 0.2 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-05-08 | WTP4 | 0.26 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-05-08 | WTP4 | 0.46 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-05-08 | WTP4 | 0.17 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-05-08 | WTP4 | 0.22 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-05-08 | WTP4 | 0.17 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-05-08 | L5 | 1 |  |  | 1.49
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-05-08 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-05-08 | WTP4 | 0.32 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-05-08 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-05-08 | WTP4 | 0.44 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-06-06 | WTP4 | 0.17 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-06-06 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-06-06 | WTP4 | 0.26 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-06-06 | WTP4 | 0.23 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-06-06 | WTP4 | 0.39 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-06-06 | WTP4 | 0.36 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-06-06 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-06-06 | WTP4 | 0.18 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-06-06 | WTP4 | 0.2 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-06-06 | WTP4 | 0.26 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-06-06 | WTP4 | 0.46 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-06-06 | WTP4 | 0.44 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-06-06 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-06-06 | WTP4 | 0.32 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-06-06 | WTP4 | 0.28 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-06-06 | L5 | 1 |  | 1 | 1.46 | BROMATE (6/18 BROMATE RAA RCVD RAA REPORTED WAS 5.57)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-06-06 | WTP4 | 0.39 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-06-06 | WTP4 | 0.17 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-06-06 | WTP4 | 0.22 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-06-06 | WTP4 | 0.24 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-06-06 | WTP4 | 0.12 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-06-06 | WTP4 | 0.12 | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-07-11 | L5 |  |  |  | 1.87 | 07/2018 BROMATE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-07-11 | WTP4 | 0.44 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-07-11 | WTP4 | 0.46 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-07-11 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-07-11 | WTP4 | 0.2 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-07-11 | WTP4 | 0.18 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-07-11 | WTP4 | 0.36 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-07-11 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-07-11 | WTP4 | 0.23 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-07-11 | WTP4 | 0.26 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-07-11 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-07-11 | WTP4 | 0.24 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-07-11 | WTP4 | 0.12 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-07-11 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-07-11 | WTP4 | 0.22 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-07-11 | WTP4 | 0.17 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-07-11 | WTP4 | 0.39 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-07-11 | WTP4 | 0.28 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-07-11 | WTP4 | 0.32 | 0.5499 |  |  | SPEC.VOC MON-XY1.9 ETH1.0 9/17(11/15 CONTAM.HEA WL/WLS HEA WL 6 RE-ROUTED TO MARKHAM>QLY 1 1-DIC&TCE DUE FROM POE MARKHAM NOW SINCE HEA WLS RE-ROUTED)WLS 2 5 6 IN SVC WLS 1 4 NOT YET(POE ENTD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.56 | UG/L | 60.4999 | 2018-07-12 | L1 | 0.91 |  | 1 | 1.04 | NW 39 8507 CYPRESS HOLLOW CT. (E84589/HAA5)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 58 | UG/L | 80.4999 | 2018-07-12 | L6 | 0.14 |  | 4 | 1.05 | NW 79 4965 S.R. 46 (WAS A NEW SITE 4/1/15) E84589/HAA5
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.73 | UG/L | 60.4999 | 2018-07-12 | L6 | 0.91 |  | 4 | 1.05 | NW 79 4965 S.R. 46 (WAS A NEW SITE 4/1/15) E84589/HAA5
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 88.68 | UG/L | 80.4999 | 2018-07-12 | L3 | 0.14 |  | 3 | 0.66 | NW 64 1924 BRIDGEWATER DR. (E84589/HAA5)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.93 | UG/L | 60.4999 | 2018-07-12 | L3 | 0.91 |  | 3 | 0.66 | NW 64 1924 BRIDGEWATER DR. (E84589/HAA5)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 70.58 | UG/L | 80.4999 | 2018-07-12 | L2 | 0.14 |  | 2 | 0.97 | NW 56 1799 ASTOR FARMS PL. (E84589/HAA5)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.82 | UG/L | 60.4999 | 2018-07-12 | L2 | 0.91 |  | 2 | 0.97 | NW 56 1799 ASTOR FARMS PL. (E84589/HAA5)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 90.41 | UG/L | 80.4999 | 2018-07-12 | L1 | 0.14 |  | 1 | 1.04 | NW 39 8507 CYPRESS HOLLOW CT. (E84589/HAA5)
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-08-07 | L5 | 5 |  | 1 | 1.35
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-07 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-09-13 | L5
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-09-13 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-09-13 | L5 | 1 |  | 1 | 1.84 | BROMATE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-09-13 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-10-08 | L5 | 1 |  |  | 1.4 | BROMATE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-10-08 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP2 |  | 0.5499 |  |  | HANOVER WOODS WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-10-08 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 82.08 | UG/L | 80.4999 | 2018-10-11 | L2 |  |  |  | 0.99 | 2950-NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.88 | UG/L | 60.4999 | 2018-10-11 | L3 |  |  |  | 0.3 | 2950-NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 74.4 | UG/L | 80.4999 | 2018-10-11 | L3 |  |  |  | 0.3 | 2950-NW 64 1924 BRIDGEWATER DR.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.47 | UG/L | 60.4999 | 2018-10-11 | L2 |  |  |  | 0.99 | 2950-NW 56 1799 ASTOR FARMS PL.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 68.66 | UG/L | 80.4999 | 2018-10-11 | L1 |  |  |  | 1.21 | 2950-NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.54 | UG/L | 60.4999 | 2018-10-11 | L1 |  |  |  | 1.21 | 2950-NW 39 8507 CYPRESS HOLLOW CT.
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.47 | UG/L | 60.4999 | 2018-10-11 | L6 |  |  | 4 | 1.16 | NW 79 4965 SR 46
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 57.1 | UG/L | 80.4999 | 2018-10-11 | L6 |  |  | 4 | 1.16 | NW 79 4965 SR 46
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-11-06 | L5 | 1 |  | 1 | 1.23 | 11-2018 BROMATE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-11-06 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-11-06 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-11-06 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2018-12-04 | L5 |  |  |  |  | J4 QUALIFIER ACCEPTED_RLB
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2018-12-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-12-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-01-09 | WTP4 | 17 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-01-09 | WTP4 | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-01-09 | L5 | 1.6 |  | 1 | 1.56 | BROMATE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-01-09 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-01-09 | WTP4 | 0.32 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-01-09 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-01-09 | WTP4 | 0.44 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-01-09 | WTP4 | 0.46 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-01-09 | WTP4 | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-01-09 | WTP4 | 0.2 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-01-09 | WTP4 | 0.18 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-01-09 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-01-09 | WTP4 | 0.36 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-01-09 | WTP4 | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-01-09 | WTP4 | 0.23 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-01-09 | WTP4 | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-01-09 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-01-09 | WTP4 | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-01-09 | WTP4 | 0.24 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-01-09 | WTP4 | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-01-09 | WTP4 | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-01-09 | WTP4 | 0.22 | 0.5499 |  |  | SPECIAL VOC MONITORING
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 37.56 | UG/L | 80.4999 | 2019-01-10 | L6 | 0.39 |  | 4 | 1.3 | SR 46
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.38 | UG/L | 60.4999 | 2019-01-10 | L6 | 0.91 |  | 4 | 1.3 | SR 46
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 55.82 | UG/L | 80.4999 | 2019-01-10 | L1
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.65 | UG/L | 60.4999 | 2019-01-10 | L3 | 0.91 |  | 3 | 1.23 | BRIDGEWATER DR
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 52.72 | UG/L | 80.4999 | 2019-01-10 | L2 | 0.39 |  | 2 | 0.85 | ASTOR FARMS PL
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.03 | UG/L | 60.4999 | 2019-01-10 | L2 | 0.91 |  | 2 | 0.85 | ASTOR FARMS PL
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 55.82 | UG/L | 80.4999 | 2019-01-10 | L1 | 0.39 |  | 1 | 1.26 | CYPRESS HOLLOW
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.62 | UG/L | 60.4999 | 2019-01-10 | L1 | 0.91 |  | 1 | 1.26 | CYPRESS HOLLOW
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 37.56 | UG/L | 80.4999 | 2019-01-10 | L6
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 13.62 | UG/L | 60.4999 | 2019-01-10 | L1
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 58.89 | UG/L | 80.4999 | 2019-01-10 | L3 | 0.39 |  | 3 | 1.23 | BRIDGEWATER DR
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 15.03 | UG/L | 60.4999 | 2019-01-10 | L2
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 57.72 | UG/L | 80.4999 | 2019-01-10 | L2
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 13.65 | UG/L | 60.4999 | 2019-01-10 | L3
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 58.59 | UG/L | 80.4999 | 2019-01-10 | L3
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 11.38 | UG/L | 60.4999 | 2019-01-10 | L6
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-02-07 | WTP4 | 0.23 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-02-07 | WTP4 | 0.32 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-02-07 | WTP4 | 0.36 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-02-07 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-02-07 | WTP4 | 0.18 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-02-07 | WTP4 | 0.2 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-02-07 | WTP4 | 0.26 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-02-07 | WTP4 | 0.46 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-02-07 | WTP4 | 0.26 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-02-07 | WTP4 | 0.44 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-02-07 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-02-07 | WTP4 | 0.17 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-02-07 | WTP4 | 0.12 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-02-07 | WTP4 | 0.24 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-02-07 | WTP4 | 0.12 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-02-07 | WTP4 | 0.39 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-02-07 | WTP4 | 0.17 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-02-07 | WTP4 | 0.22 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-02-07 | WTP4 | 0.39 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-02-07 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-02-07 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONT
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-02-07 | L5 | 1.6 |  | 1 | 1.84 | BROMATE - MAR WP (HLKD)
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1040 | NITRATE | N | 0.45 | MG/L | 10.4999 | 2019-02-19 | WTP4 |  |  |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-19 | WTP4 |  |  |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-03-05 | L5 | 1.6 |  | 1 | 1.89 | 3/19 BROMATE - MAR WP (HLKD) 3/19 BROMATE RAA RCVD W/RSLTS
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-03-14 | WTP4 |  | 0.5499 |  |  | MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-03-14 | WTP1 |  | 0.5499 |  |  | HEATHROW WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-04-04 | L5 |  |  |  | 1.51 | 2019-04 BROMATE - MAR POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP3 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-04-04 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-04-04 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 65.77 | UG/L | 80.4999 | 2019-04-11 | L3
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.67 | UG/L | 60.4999 | 2019-04-11 | L6 |  |  | 4 | 0.93 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 72.11 | UG/L | 80.4999 | 2019-04-11 | L6 |  |  | 4 | 0.93 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.79 | UG/L | 60.4999 | 2019-04-11 | L1 |  |  | 3 | 1.32 | NW 39 8507 CYPRESS HOLLOW CT. / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 61.2 | UG/L | 80.4999 | 2019-04-11 | L1 |  |  | 3 | 1.32 | NW 39 8507 CYPRESS HOLLOW CT. / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.02 | UG/L | 60.4999 | 2019-04-11 | L2 |  |  | 2 | 0.87 | NW 56 1799 ASTOR FARMS PL. / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 61.02 | UG/L | 80.4999 | 2019-04-11 | L2 |  |  | 2 | 0.87 | NW 56 1799 ASTOR FARMS PL. / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.3 | UG/L | 60.4999 | 2019-04-11 | L3 |  |  | 1 | 0.78 | NW 64 1924 BRIDGEWATER DR. / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 65.77 | UG/L | 80.4999 | 2019-04-11 | L3 |  |  | 1 | 0.78 | NW 64 1924 BRIDGEWATER DR. / SUBCONTACT LABS E82535 AND E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 15.3 | UG/L | 60.4999 | 2019-04-11 | L3
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 61.02 | UG/L | 80.4999 | 2019-04-11 | L2
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 12.02 | UG/L | 60.4999 | 2019-04-11 | L2
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 61.2 | UG/L | 80.4999 | 2019-04-11 | L1
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 11.79 | UG/L | 60.4999 | 2019-04-11 | L1
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 12.67 | UG/L | 60.4999 | 2019-04-11 | L6
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | M | 72.11 | UG/L | 80.4999 | 2019-04-11 | L6
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-05-06 | L5 |  |  |  | 1.64 | 2019-05 BROMATE / MAR POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-05-08 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-05-08 | WTP4 | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-05-08 | WTP4 | 0.24 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-05-08 | WTP4 | 0.12 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-05-08 | WTP4 | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-05-08 | WTP4 | 0.22 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-05-08 | WTP4 | 0.17 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-05-08 | WTP4 | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-05-08 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-05-08 | WTP4 | 0.32 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-05-08 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-05-08 | WTP4 | 0.44 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-05-08 | WTP4 | 0.46 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-05-08 | WTP4 | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-05-08 | WTP4 | 0.2 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-05-08 | WTP4 | 0.18 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-05-08 | WTP4 | 0.28 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-05-08 | WTP4 | 0.36 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-05-08 | WTP4 | 0.39 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-05-08 | WTP4 | 0.23 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-05-08 | WTP4 | 0.26 | 0.5499 |  |  | SPECIAL VOC MONITORING - MAR POE - MARKHAM REGIONAL WP
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-06-03 | L5 |  |  |  | 1.49 | 2019-06 BROMATE / MAR POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-06-12 | WTP2 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-06-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-06-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-07-02 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-07-02 | L5 | 1.6 |  | 1 | 1.82 | BROMATE - MAR WP (HLKD)
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-07-02 | L5 |  |  |  | 1.64 | 2019 08 - BROMATE ¦ 07/19 BROMATE GC
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-07-02 | L5 |  |  |  | 1.64 | 2019 08 - BROMATE ¦ 07/19 BROMATE GC
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 57.9 | UG/L | 80.4999 | 2019-07-11 | L3 |  |  | 3 | 0.68 | NW 64 1924 BRIDGEWATER DR. / SUBCONTRACT LABS E82535 E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.3 | UG/L | 60.4999 | 2019-07-11 | L6 |  |  | 4 | 0.96 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) / SUBCONTRACT LABS E82535 E84589 [LRAA TTHM = 69.2250; OEL = 82.4825; HAA5 TTHM = 11.9550]
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 40.25 | UG/L | 80.4999 | 2019-07-11 | L1 |  |  | 1 | 1.32 | NW 39 8507 CYPRESS HOLLOW CT. / SUBCONTRACT LABS E82535 E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.46 | UG/L | 60.4999 | 2019-07-11 | L2 |  |  | 2 | 1.65 | NW 56 1799 ASTOR FARMS PL. / SUBCONTRACT LABS E82535 E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 110.13 | UG/L | 80.4999 | 2019-07-11 | L6 |  |  | 4 | 0.96 | NW 79 4965 S.R. 46 (NEW SITE 4/1/15) / SUBCONTRACT LABS E82535 E84589 [LRAA TTHM = 69.2250; OEL = 82.4825; HAA5 TTHM = 11.9550]
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.18 | UG/L | 60.4999 | 2019-07-11 | L1 |  |  | 1 | 1.32 | NW 39 8507 CYPRESS HOLLOW CT. / SUBCONTRACT LABS E82535 E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 56.27 | UG/L | 80.4999 | 2019-07-11 | L2 |  |  | 2 | 1.65 | NW 56 1799 ASTOR FARMS PL. / SUBCONTRACT LABS E82535 E84589
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.09 | UG/L | 60.4999 | 2019-07-11 | L3 |  |  | 3 | 0.68 | NW 64 1924 BRIDGEWATER DR. / SUBCONTRACT LABS E82535 E84589
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-08-08 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-08-08 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-09-11 | L5 |  |  |  | 1.41 | 2019 09 BROMATE - MAR POE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-09-11 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 76.19 | UG/L | 80.4999 | 2019-10-10 | L1 | 0.39 |  | 1 | 1.21 | 8507 CYPRESS HOLLOW
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.37 | UG/L | 60.4999 | 2019-10-10 | L1 | 0.91 |  | 1 | 1.21 | 8507 CYPRESS HOLLOW
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-10-10 | L5 | 1.6 |  | 1 | 1.6 | BROMATE
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.86 | UG/L | 60.4999 | 2019-10-10 | L2 | 0.91 |  | 2 | 1.45 | 1799 ASTOR FARMS PL
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 69.99 | UG/L | 80.4999 | 2019-10-10 | L6 | 0.39 |  | 5 | 1.26 | 4965 SR 46 TTHM LRAA =72.44
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 65.67 | UG/L | 80.4999 | 2019-10-10 | L2 | 0.39 |  | 2 | 1.45 | 1799 ASTOR FARMS PL
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.51 | UG/L | 60.4999 | 2019-10-10 | L3 | 0.91 |  | 3 | 1.07 | 1924 BRIDGEWATER DR TTHM LRAA = 68.425
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2950 | TOTAL THMS | D | 91.44 | UG/L | 80.4999 | 2019-10-10 | L3 | 0.39 |  | 3 | 1.07 | 1924 BRIDGEWATER DR TTHM LRAA = 68.425
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.69 | UG/L | 60.4999 | 2019-10-10 | L6 | 0.91 |  | 5 | 1.26 | 4965 SR 46 TTHM LRAA =72.44
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-10-16 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | DBP | 1011 | BROMATE | N | 0 | UG/L | 10.4999 | 2019-11-07 | L5 | 1.6 |  | 1 | 1.6 | BROMATE
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-11-07 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | R | 0 | UG/L | 5.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | R | 0 | UG/L | 5.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | R | 0 | UG/L | 3.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | R | 0 | UG/L | 149.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | R | 0 | UG/L | 1.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | R | 0 | UG/L | 1499.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | R | 0 | UG/L | 749.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | R | 0 | UG/L | 149.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-12-12 | WTP4 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | R | 0 | UG/L | 74.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | R | 0 | UG/L | 74.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2955 | TOT XYLENE | R | 0 | UG/L | 10499.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2964 | DICHLOROMETHANE | R | 0 | UG/L | 5.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2968 | 1 2-DICHLOROBENZENE | R | 0 | UG/L | 649.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2969 | P-DICHLOROBENZENE | R | 0 | UG/L | 75.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2976 | VINYL CHLORIDE | R | 0 | UG/L | 1.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2977 | 1 1-DICHLOROETHENE | R | 0 | UG/L | 7.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | R | 0 | UG/L | 149.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2980 | 1 2-DICHLOROETHANE | R | 0 | UG/L | 3.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2981 | 1 1 1-TRICHLOROETHANE | R | 0 | UG/L | 249.9999 | 2019-12-12 | WTP1 |  | 0.5499
3594107 | SEMINOLE COUNTY NORTHWEST | VOC | 2982 | CARBON TETRACHLORIDE | R | 0 | UG/L | 3.4999 | 2019-12-12 | WTP1 |  | 0.5499
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.91 | UG/L | 60.4999 | 2015-08-14 | L1 |  |  |  | 2.68 | (6/1-7/27/16 CHLORINE BURN BY OVIEDO-PN ALREADY GVN BY BOTH OVIEDO & SCES)BH 7 2364 GENOVA DR. (QUALIFIES FOR R.M. - NEXT ANNUAL TEST DUE FOR 1 SITE ONLY 2364 GENOVA DR. @ 2ND WEEK AUGUST 2016) >500
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 17.36 | UG/L | 80.4999 | 2015-08-14 | L2 |  |  |  | 2.82 | BH 6 3703 PALM AVE. (QUALIFIES FOR R.M. - NEXT ANNUAL TEST DUE FOR 1 SITE ONLY 2364 GENOVA DR. @ 2ND WEEK AUGUST 2016) >500
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 20.05 | UG/L | 80.4999 | 2015-08-14 | L1 |  |  |  | 2.68 | (6/1-7/27/16 CHLORINE BURN BY OVIEDO-PN ALREADY GVN BY BOTH OVIEDO & SCES)BH 7 2364 GENOVA DR. (QUALIFIES FOR R.M. - NEXT ANNUAL TEST DUE FOR 1 SITE ONLY 2364 GENOVA DR. @ 2ND WEEK AUGUST 2016) >500
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.59 | UG/L | 60.4999 | 2015-08-14 | L2 |  |  |  | 2.82 | BH 6 3703 PALM AVE. (QUALIFIES FOR R.M. - NEXT ANNUAL TEST DUE FOR 1 SITE ONLY 2364 GENOVA DR. @ 2ND WEEK AUGUST 2016) >500
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 16.14 | UG/L | 80.4999 | 2016-08-11 | L1 |  |  |  | 2.88 | BH 7 2364 GENOVA DR. (8/16 LRAA/T=16.14* LRAA/H=10.61) *CHANGED TTHM RESULT FROM 18.14. ERROR DISCOVERED DURING CCR REVIEW. BW
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.27 | UG/L | 60.4999 | 2016-08-11 | L2 |  |  |  | 2.46 | BH 6 3703 PALM AVE. (8/16 LRAA/T=16.49 LRAA/H=11.27)
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 10.61 | UG/L | 60.4999 | 2016-08-11 | L1 |  |  |  | 2.88 | BH 7 2364 GENOVA DR. (8/16 LRAA/T=16.14* LRAA/H=10.61) *CHANGED TTHM RESULT FROM 18.14. ERROR DISCOVERED DURING CCR REVIEW. BW
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 16.49 | UG/L | 80.4999 | 2016-08-11 | L2 |  |  |  | 2.46 | BH 6 3703 PALM AVE. (8/16 LRAA/T=16.49 LRAA/H=11.27)
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.62 | UG/L | 60.4999 | 2017-08-10 | L2 | 0.5 |  | 2 | 2.8 | 3703 PALM AVE. (HYPERLINKED 9/25/17 TO BW PER SOP - BB)
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 25.71 | UG/L | 80.4999 | 2017-08-10 | L1 | 0.14 |  | 1 | 2.6 | 2364 GENOVA DR.
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.51 | UG/L | 60.4999 | 2017-08-10 | L1 | 0.5 |  | 1 | 2.6 | 2364 GENOVA DR.
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 20.68 | UG/L | 80.4999 | 2017-08-10 | L2 | 0.14 |  | 2 | 2.8 | 3703 PALM AVE. (HYPERLINKED 9/25/17 TO BW PER SOP - BB)
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 18.06 | UG/L | 80.4999 | 2018-08-09 | L1 | 0.39 |  | 1 | 1.78 | 2364 GENOVA DR
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.19 | UG/L | 60.4999 | 2018-08-09 | L1 | 0.91 |  | 1 | 1.78 | 2364 GENOVA DR
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2950 | TOTAL THMS | D | 24.54 | UG/L | 80.4999 | 2019-08-08 | L1 |  |  |  | 0.65 | BH 7 2364 GENOVA DR.
3594186 | BLACK HAMMOCK -MSBU(CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12 | UG/L | 60.4999 | 2019-08-08 | L1 |  |  |  | 0.65 | BH 7 2364 GENOVA DR.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.98 | UG/L | 60.4999 | 2015-01-14 | L2 |  |  |  | 0.8 | (7/22 EW HAS 4/15 DBPS) CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) *****MUST CONT. QM AFTER 6/15 QTR RSLTS (T LRAA>60)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 40.54 | UG/L | 80.4999 | 2015-01-14 | L2 |  |  |  | 0.8 | (7/22 EW HAS 4/15 DBPS) CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) *****MUST CONT. QM AFTER 6/15 QTR RSLTS (T LRAA>60)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.11 | UG/L | 60.4999 | 2015-01-14 | L1 |  |  | 0.98 |  | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 41.91 | UG/L | 80.4999 | 2015-01-14 | L1 |  |  | 0.98 |  | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 68.93 | UG/L | 80.4999 | 2015-04-15 | L1 |  |  |  | 0.9 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (LRAAS/T BOTH SITES > 60 UG/L CONT. QM/T+H UFN>EM 7/22/15 TO E. WMS SCES)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.04 | UG/L | 60.4999 | 2015-04-15 | L1 |  |  |  | 0.9 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (LRAAS/T BOTH SITES > 60 UG/L CONT. QM/T+H UFN>EM 7/22/15 TO E. WMS SCES)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 57.91 | UG/L | 80.4999 | 2015-04-15 | L2 |  |  |  | 1.19 | (>3300) CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (LRAAS/T BOTH SITES > 60 UG/L CONT. QM/T+H UFN>EM 7/22/15 TO E. WMS SCES) IN OC
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.26 | UG/L | 60.4999 | 2015-04-15 | L2 |  |  |  | 1.19 | (>3300) CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (LRAAS/T BOTH SITES > 60 UG/L CONT. QM/T+H UFN>EM 7/22/15 TO E. WMS SCES) IN OC
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 79.66 | UG/L | 80.4999 | 2015-07-14 | L1 |  |  |  | 0.73 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (>3300) CONT. QM/T+H AT THE 2 SITES UFN (9/15 LRAA/T=62.5 LRAA/H=22.8325) NO LRAA OR OE EXCEEDANCES. CONT. QM/T+H SINCE LRAA/T>60 9/15 QTR FOR 1 SITE.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.69 | UG/L | 60.4999 | 2015-07-14 | L1 |  |  |  | 0.73 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (>3300) CONT. QM/T+H AT THE 2 SITES UFN (9/15 LRAA/T=62.5 LRAA/H=22.8325) NO LRAA OR OE EXCEEDANCES. CONT. QM/T+H SINCE LRAA/T>60 9/15 QTR FOR 1 SITE.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.27 | UG/L | 60.4999 | 2015-07-14 | L2 |  |  |  | 0.6 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (>3300) 9/15 LRAA/T=52.04 LRAA/H=24.7725) CONT. QM/T+H AT THE 2 SITES UFN (1 SITE L1 SITE LRAA/T>60 NO LRAA OR OE EXCEEDANCES) VOLUN REVISED 9/15 DBF IN OC
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 50.48 | UG/L | 80.4999 | 2015-07-14 | L2 |  |  |  | 0.6 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (>3300) 9/15 LRAA/T=52.04 LRAA/H=24.7725) CONT. QM/T+H AT THE 2 SITES UFN (1 SITE L1 SITE LRAA/T>60 NO LRAA OR OE EXCEEDANCES) VOLUN REVISED 9/15 DBF IN OC
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.32 | UG/L | 60.4999 | 2015-10-15 | L2 |  |  |  | 0.87 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (12/15 LRAA/T=52.8475 LRAA/H=23.2075) NO OE EXCEEDANCE AT THIS SITE BUT 1 AT L1 SITE
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 62.46 | UG/L | 80.4999 | 2015-10-15 | L2 |  |  |  | 0.87 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (12/15 LRAA/T=52.8475 LRAA/H=23.2075) NO OE EXCEEDANCE AT THIS SITE BUT 1 AT L1 SITE
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 103.25 | UG/L | 80.4999 | 2015-10-15 | L1 |  |  |  | 0.52 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (12/15 LRAA/T=73.4375 LRAA/H=22.3075) 12/15 T OE VALUE=88.7725 (OE REPORT RCVD & IN OC) CONT. QM/T+H UFN SINCE LRAA/T>60.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.39 | UG/L | 60.4999 | 2015-10-15 | L1 |  |  |  | 0.52 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (12/15 LRAA/T=73.4375 LRAA/H=22.3075) 12/15 T OE VALUE=88.7725 (OE REPORT RCVD & IN OC) CONT. QM/T+H UFN SINCE LRAA/T>60.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.11 | UG/L | 60.4999 | 2016-01-14 | L1 |  |  |  | 0.95 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE) 7/11 EW HAS 4/16 T/H & 6/16 QTR DB REPORT (NO LRAA EXCEEDANCES 6/16 QTR)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 51.94 | UG/L | 80.4999 | 2016-01-14 | L2 |  |  |  | 1.05 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 13.44 | UG/L | 60.4999 | 2016-01-14 | L2 |  |  |  | 1.05 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 58.5 | UG/L | 80.4999 | 2016-01-14 | L1 |  |  |  | 0.95 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (NO 3/16 QTR LRAA OR OE EXCEEDANCES EITHER SITE) 7/11 EW HAS 4/16 T/H & 6/16 QTR DB REPORT (NO LRAA EXCEEDANCES 6/16 QTR)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.82 | UG/L | 60.4999 | 2016-04-13 | L1 |  |  |  | 0.53 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (6/16 LRAA/T=77.3375 LRAA/H=21.7525)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.22 | UG/L | 60.4999 | 2016-04-13 | L2 |  |  |  | 0.81 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (6/16 LRAA/T=56.4475 LRAA/H=17.8125)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 60.91 | UG/L | 80.4999 | 2016-04-13 | L2 |  |  |  | 0.81 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) (6/16 LRAA/T=56.4475 LRAA/H=17.8125)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 67.94 | UG/L | 80.4999 | 2016-04-13 | L1 |  |  |  | 0.53 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (6/16 LRAA/T=77.3375 LRAA/H=21.7525)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 15.43 | UG/L | 60.4999 | 2016-07-14 | L1 | 0.2 |  | 1 | 0.75 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (9/16 LRAA/T=76.4475 LRAA/H=19.1875) CONT. QM/T+H BOTH SITES (LRAA/T>60) CANNOT STOP QM. 9/16/16 EM TO ELISA WILLIAMS TO CONTINUE QM/T+H - BB
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.37 | UG/L | 60.4999 | 2016-07-14 | L2 | 0.2 |  | 2 | 1.02 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) 6/16 LRAA/T=54.8175 LRAA/H=14.3375 (CONT. QM/T+H DUE TO LRAA/T>60 OTHER SITE) 9/16/16 EM TO ELISA WILLIAMS TO CONTINUE QM/T+H - BB
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 76.1 | UG/L | 80.4999 | 2016-07-14 | L1 | 0.14 |  | 1 | 0.75 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) (9/16 LRAA/T=76.4475 LRAA/H=19.1875) CONT. QM/T+H BOTH SITES (LRAA/T>60) CANNOT STOP QM. 9/16/16 EM TO ELISA WILLIAMS TO CONTINUE QM/T+H - BB
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 43.96 | UG/L | 80.4999 | 2016-07-14 | L2 | 0.14 |  | 2 | 1.02 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) 6/16 LRAA/T=54.8175 LRAA/H=14.3375 (CONT. QM/T+H DUE TO LRAA/T>60 OTHER SITE) 9/16/16 EM TO ELISA WILLIAMS TO CONTINUE QM/T+H - BB
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 76.28 | UG/L | 80.4999 | 2016-10-13 | L1 |  |  |  | 0.87 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) 12/16 LRAA/T=69.705 LRAA/H=LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.62 | UG/L | 60.4999 | 2016-10-13 | L1 |  |  |  | 0.87 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) 12/16 LRAA/T=69.705 LRAA/H=LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 72.05 | UG/L | 80.4999 | 2016-10-13 | L2 |  |  |  | 0.88 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) 12/16 LRAA/T=57.215 LRAA/H=LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.06 | UG/L | 60.4999 | 2016-10-13 | L2 |  |  |  | 0.88 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) 12/16 LRAA/T=57.215 LRAA/H=LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.87 | UG/L | 60.4999 | 2017-01-11 | L1 | 0.2 |  | 1 | 1.13 | CG 5 2999 GREENWOOD SPRINGS LOOP (3/17 LRAA/T=76.0375 LRAA/H=LOW) 3/17 OE VALUE/T=80.01 OE/H LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 83.83 | UG/L | 80.4999 | 2017-01-11 | L1 | 0.14 |  | 1 | 1.13 | CG 5 2999 GREENWOOD SPRINGS LOOP (3/17 LRAA/T=76.0375 LRAA/H=LOW) 3/17 OE VALUE/T=80.01 OE/H LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.91 | UG/L | 60.4999 | 2017-01-11 | L2 | 0.2 |  | 2 | 0.94 | CG 9 2874 SNOWY OWL CT. (3/17 LRAA/T=65.5875 LRAA/H=LOW) 3/17 OE VALUE/T=71.7175 OE VALUE/H LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 85.43 | UG/L | 80.4999 | 2017-01-11 | L2 | 0.14 |  | 2 | 0.94 | CG 9 2874 SNOWY OWL CT. (3/17 LRAA/T=65.5875 LRAA/H=LOW) 3/17 OE VALUE/T=71.7175 OE VALUE/H LOW
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.25 | UG/L | 60.4999 | 2017-04-11 | L2 | 0.52 |  | 2 | 1.46 | 2874 SNOWY OWL CT. - RESULTS HYPERLINKED 5/4/17. THERE'S NO 3/17 OE EXCEEDANCE FOR SNOWY OWL SITE.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 70.61 | UG/L | 80.4999 | 2017-04-11 | L2 | 0.14 |  | 2 | 1.46 | 2874 SNOWY OWL CT. - RESULTS HYPERLINKED 5/4/17. THERE'S NO 3/17 OE EXCEEDANCE FOR SNOWY OWL SITE.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 81.72 | UG/L | 80.4999 | 2017-04-11 | L1 | 0.14 |  | 1 | 1.3 | 2999 GREENWOOD SPRINGS LOOP - TTHMS 6/17 OE VALUE=80.8875 & OE REPORT RCVD WITH THESE RESULTS BY EMAIL 5/4/17. RESULTS HYPERLINKED 5/4/17.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.72 | UG/L | 60.4999 | 2017-04-11 | L1 | 0.52 |  | 1 | 1.3 | 2999 GREENWOOD SPRINGS LOOP - TTHMS 6/17 OE VALUE=80.8875 & OE REPORT RCVD WITH THESE RESULTS BY EMAIL 5/4/17. RESULTS HYPERLINKED 5/4/17.
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 73.14 | UG/L | 80.4999 | 2017-07-13 | L2 | 0.14 |  | 2 | 1.27 | 2874 SNOWY OWL CT. (9/17 LRAA/T=75.3075 LRAA/H=21.0025) 9/17 OE VAL/T=75.58 (H LOW)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 79.88 | UG/L | 80.4999 | 2017-07-13 | L1 | 0.14 |  | 1 | 0.83 | 2999 GREENWOOD SPRINGS LOOP(9/17 LRAA/T=80.4275-JUST AT MCL-NOT MCL VIOL LRAA/H=21.84)9/17 OE VAL/T=81.3275(9/17 OE REPORT RCVD & PLACED IN OC-ADVISED BW BY EM 8/9/17 SO OE/OI CODES CD BE ENTD-BB)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.15 | UG/L | 60.4999 | 2017-07-13 | L1 | 0.5 |  | 1 | 0.83 | 2999 GREENWOOD SPRINGS LOOP(9/17 LRAA/T=80.4275-JUST AT MCL-NOT MCL VIOL LRAA/H=21.84)9/17 OE VAL/T=81.3275(9/17 OE REPORT RCVD & PLACED IN OC-ADVISED BW BY EM 8/9/17 SO OE/OI CODES CD BE ENTD-BB)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.79 | UG/L | 60.4999 | 2017-07-13 | L2 | 0.5 |  | 2 | 1.27 | 2874 SNOWY OWL CT. (9/17 LRAA/T=75.3075 LRAA/H=21.0025) 9/17 OE VAL/T=75.58 (H LOW)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 67.82 | UG/L | 80.4999 | 2017-10-12 | L2 | 0.31 |  | 2 | 1.13 | 2874 SNOWY OWL CT. (HIGH T LRAA) 12/17 LRAA/T=74.25 LRAA/H=21.7275 (NO OE EXCEEDANCES CONTINUE QM/DBPS)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.96 | UG/L | 60.4999 | 2017-10-12 | L2 | 0.5 |  | 2 | 1.13 | 2874 SNOWY OWL CT. (HIGH T LRAA) 12/17 LRAA/T=74.25 LRAA/H=21.7275 (NO OE EXCEEDANCES CONTINUE QM/DBPS)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 72.14 | UG/L | 80.4999 | 2017-10-12 | L1 | 0.31 |  | 1 | 0.82 | 2999 GREENWOOD SPRINGS LOOP (HI H) 12/17 LRAA/T=79.3925 LRAA/H=22.4025 (NO OE EXCEEDANCES CONTINUE QM/DBPS)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.87 | UG/L | 60.4999 | 2017-10-12 | L1 | 0.5 |  | 1 | 0.82 | 2999 GREENWOOD SPRINGS LOOP (HI H) 12/17 LRAA/T=79.3925 LRAA/H=22.4025 (NO OE EXCEEDANCES CONTINUE QM/DBPS)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 69.15 | UG/L | 80.4999 | 2018-01-11 | L2 | 0.14 |  | 2 | 1.24 | 2874 SNOWY OWL CT. (3/18 LRAA/T=70.18 LRAA/H LOW) CONT. QM/T+H (NO OE EXCEEDANCES 3/18 QTR)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.64 | UG/L | 60.4999 | 2018-01-11 | L2 | 0.5 |  | 2 | 1.24 | 2874 SNOWY OWL CT. (3/18 LRAA/T=70.18 LRAA/H LOW) CONT. QM/T+H (NO OE EXCEEDANCES 3/18 QTR)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 64.48 | UG/L | 80.4999 | 2018-01-11 | L1 | 0.14 |  | 1 | 1.39 | 2999 GREENWOOD SPGS LOOP (3/18 LRAA/T=74.555 H LOW) CONT. QM/T+H (NO OE EXCEEDANCES 3/18 QTR)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.52 | UG/L | 60.4999 | 2018-01-11 | L1 | 0.5 |  | 1 | 1.39 | 2999 GREENWOOD SPGS LOOP (3/18 LRAA/T=74.555 H LOW) CONT. QM/T+H (NO OE EXCEEDANCES 3/18 QTR)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 71.82 | UG/L | 80.4999 | 2018-04-12 | L1 |  |  |  | 1 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.93 | UG/L | 60.4999 | 2018-04-12 | L1 |  |  |  | 1 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 68.26 | UG/L | 80.4999 | 2018-04-12 | L2 |  |  |  | 1.01 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.9 | UG/L | 60.4999 | 2018-04-12 | L2 |  |  |  | 1.01 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.23 | UG/L | 60.4999 | 2018-07-12 | L1 | 0.91 |  | 1 | 1.17 | 2999 GREENWOOD SPRINGS LOOP
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 56.75 | UG/L | 80.4999 | 2018-07-12 | L1 | 0.14 |  | 1 | 1.17 | 2999 GREENWOOD SPRINGS LOOP
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.78 | UG/L | 60.4999 | 2018-07-12 | L2 | 0.91 |  | 2 | 1.33 | 2874 SNOWY OWL CT. (HLKD 8-24-18)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 70.51 | UG/L | 80.4999 | 2018-07-12 | L2 | 0.14 |  | 2 | 1.33 | 2874 SNOWY OWL CT. (HLKD 8-24-18)
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.63 | UG/L | 60.4999 | 2018-10-11 | L2 | 0.91 |  | 2 | 0.97 | 2874 SNOWY OWL
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 74.64 | UG/L | 80.4999 | 2018-10-11 | L1 | 0.56 |  | 1 | 1.15 | 2999 GREENWOOD
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.74 | UG/L | 60.4999 | 2018-10-11 | L1 | 0.91 |  | 1 | 1.15 | 2999 GREENWOOD
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 50.39 | UG/L | 80.4999 | 2018-10-11 | L2 | 0.56 |  | 2 | 0.97 | 2874 SNOWY OWL
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 52.23 | UG/L | 80.4999 | 2019-01-10 | L2 | 0.39 |  | 1 | 1.33 | SNOWY OWL CT
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.84 | UG/L | 60.4999 | 2019-01-10 | L2 | 0.91 |  | 1 | 1.33 | SNOWY OWL CT
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 18.19 | UG/L | 60.4999 | 2019-01-10 | L1
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | M | 52.23 | UG/L | 80.4999 | 2019-01-10 | L2
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 17.84 | UG/L | 60.4999 | 2019-01-10 | L2
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 17.84 | UG/L | 60.4999 | 2019-01-10 | L2
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.19 | UG/L | 60.4999 | 2019-01-10 | L1 | 0.91 |  | 2 | 0.92 | GREENWOOD SPRINGS LOOP
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 55.38 | UG/L | 80.4999 | 2019-01-10 | L1 | 0.39 |  | 2 | 0.92 | GREENWOOD SPRINGS LOOP
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | M | 55.38 | UG/L | 80.4999 | 2019-01-10 | L1
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.21 | UG/L | 60.4999 | 2019-04-11 | L1 |  |  | 1 | 0.79 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) / SUBCONTRACT LABS E82535 AND E84589
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | M | 79.42 | UG/L | 80.4999 | 2019-04-11 | L1
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 19.21 | UG/L | 60.4999 | 2019-04-11 | L1
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 62.22 | UG/L | 80.4999 | 2019-04-11 | L2 |  |  | 2 | 1.01 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) / SUBCONTRACT LABS E82535 AND E84589
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 79.42 | UG/L | 80.4999 | 2019-04-11 | L1 |  |  | 1 | 0.79 | CG 5 2999 GREENWOOD SPRINGS LOOP (HI H) / SUBCONTRACT LABS E82535 AND E84589
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.15 | UG/L | 60.4999 | 2019-04-11 | L2 |  |  | 2 | 1.01 | CG 9 2874 SNOWY OWL CT. (HIGH T LRAA) / SUBCONTRACT LABS E82535 AND E84589
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.31 | UG/L | 60.4999 | 2019-07-11 | L1 | 0.91 |  | 1 | 0.84 | CG 5 2999 GREENWOOD SPRINGS LOOP THH: LRAA = 70.1
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 70.85 | UG/L | 80.4999 | 2019-07-11 | L1 | 0.39 |  | 1 | 0.84 | CG 5 2999 GREENWOOD SPRINGS LOOP THH: LRAA = 70.1
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 57.42 | UG/L | 80.4999 | 2019-07-11 | L2 | 0.39 |  | 2 | 0.74 | CG 9 2874 SNOWY OWL CT. (HLKD) TTHM LRAA = 55.56
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.2 | UG/L | 60.4999 | 2019-07-11 | L2 | 0.91 |  | 2 | 0.74 | CG 9 2874 SNOWY OWL CT. (HLKD) TTHM LRAA = 55.56
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 22.6 | UG/L | 60.4999 | 2019-10-10 | L2 |  |  |  | 0.78 | 2874 SNOWY OWL CT. [LRAA TTHM=62.45; HAA5=18.70]
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 77.92 | UG/L | 80.4999 | 2019-10-10 | L2 |  |  |  | 0.78 | 2874 SNOWY OWL CT. [LRAA TTHM=62.45; HAA5=18.70]
3594214 | CHASE GROVES(CONSEC.) | DBP | 2950 | TOTAL THMS | D | 100.69 | UG/L | 80.4999 | 2019-10-10 | L1 | 0.39 |  | 1 | 0.46 | 2999 GREENWOOD TTHM LRAA = 76.585 OE=87.91. NEED OE REPORT; HAA5=21.21
3594214 | CHASE GROVES(CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.15 | UG/L | 60.4999 | 2019-10-10 | L1 | 0.91 |  | 1 | 0.46 | 2999 GREENWOOD TTHM LRAA = 76.585 OE=87.91. NEED OE REPORT; HAA5=21.21
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.99 | UG/L | 60.4999 | 2015-08-18 | L2 |  |  |  | 1.65 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/16 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 50.23 | UG/L | 80.4999 | 2015-08-18 | L2 |  |  |  | 1.65 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/16 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.39 | UG/L | 60.4999 | 2015-08-18 | L1 |  |  |  | 1.43 | SS 4 SUNBRANCH LN @ HWY 17-92 (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/16 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 63.2 | UG/L | 80.4999 | 2015-08-18 | L1 |  |  |  | 1.43 | SS 4 SUNBRANCH LN @ HWY 17-92 (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/16 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 57.8 | UG/L | 80.4999 | 2016-08-18 | L2 |  |  |  | 0.46 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/17 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.39 | UG/L | 60.4999 | 2016-08-18 | L2 |  |  |  | 0.46 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/17 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 68 | UG/L | 80.4999 | 2016-08-18 | L1 |  |  |  | 0.59 | SS 4 SUNBRANCH LN @ HWY 17-92 (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/17 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.83 | UG/L | 60.4999 | 2016-08-18 | L1 |  |  |  | 0.59 | SS 4 SUNBRANCH LN @ HWY 17-92 (REMAIN ON ROUTINE T/H - NEXT ANNUAL TEST DUE 3RD WEEK 8/17 AT SAME 2 SITES >500) NO LRAA OR OE EXCEEDANCES
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 81.43 | UG/L | 80.4999 | 2017-08-17 | L1 | 0.14 |  | 1 | 0.83 | SS 4 SUNBRANCH LN @ HWY 17-92 (T>80 START QM) HYPERLINKED 9/7/17 (9/7/17 E. WMS. EMAILED THAT SHE WOULD TEST QTRLY TO BW-BB)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.72 | UG/L | 60.4999 | 2017-08-17 | L1 | 0.5 |  | 1 | 0.83 | SS 4 SUNBRANCH LN @ HWY 17-92 (T>80 START QM) HYPERLINKED 9/7/17 (9/7/17 E. WMS. EMAILED THAT SHE WOULD TEST QTRLY TO BW-BB)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27 | UG/L | 60.4999 | 2017-08-17 | L2 | 0.5 |  | 2 | 0.95 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) HYPERLINKED 9/7/17 TO BW - BB (9/7/17 PER EM FROM E. WMS SHE WL TEST QTRLY FOR T/H DUE TO T>80 AT L1 SITE. BB)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 70.89 | UG/L | 80.4999 | 2017-08-17 | L2 | 0.14 |  | 2 | 0.95 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) HYPERLINKED 9/7/17 TO BW - BB (9/7/17 PER EM FROM E. WMS SHE WL TEST QTRLY FOR T/H DUE TO T>80 AT L1 SITE. BB)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 22 | UG/L | 80.4999 | 2017-11-16 | L1 | 0.14 |  | 1 | 0.48 | 2QM-SUNBRANCH LN @ HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.49 | UG/L | 60.4999 | 2017-11-16 | L2 | 0.5 |  | 2 | 0.58 | 2QM-1750 SUNCREST LOOP (WINN-DIXIE)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 59.95 | UG/L | 80.4999 | 2017-11-16 | L2 | 0.14 |  | 2 | 0.58 | 2QM-1750 SUNCREST LOOP (WINN-DIXIE)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.74 | UG/L | 60.4999 | 2017-11-16 | L1 | 0.5 |  | 1 | 0.48 | 2QM-SUNBRANCH LN @ HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 55.44 | UG/L | 80.4999 | 2018-02-22 | L2 | 0.14 |  | 1 | 0.87 | 3QM-1750 SUNCREST LOOP (WINN-DIXIE)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.77 | UG/L | 60.4999 | 2018-02-22 | L2 | 0.5 |  | 1 | 0.87 | 3QM-1750 SUNCREST LOOP (WINN-DIXIE)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 58.91 | UG/L | 80.4999 | 2018-02-22 | L1 | 0.14 |  | 2 | 1.04 | 3QM-SUNBRANCH LN & HWY 17-92 (4/13/18 HYPRLNKD TO BW-BB) CONTINUE QM/DBPS
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.39 | UG/L | 60.4999 | 2018-02-22 | L1 | 0.5 |  | 2 | 1.04 | 3QM-SUNBRANCH LN & HWY 17-92 (4/13/18 HYPRLNKD TO BW-BB) CONTINUE QM/DBPS
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.65 | UG/L | 60.4999 | 2018-05-16 | L1 | 0.91 |  |  | 0.97 | SUNBRANCH LANE @ HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 78.53 | UG/L | 80.4999 | 2018-05-16 | L2 | 0.14 |  |  |  | 1750 SUNCREST LOOP
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 71.95 | UG/L | 80.4999 | 2018-05-16 | L1 | 0.14 |  |  | 0.97 | SUNBRANCH LANE @ HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 34.08 | UG/L | 60.4999 | 2018-05-16 | L2 | 0.91 |  |  |  | 1750 SUNCREST LOOP
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 35.33 | UG/L | 60.4999 | 2018-08-16 | L1 | 0.91 |  | 1 | 1.01 | SUNBRANCH LN
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 55.16 | UG/L | 80.4999 | 2018-08-16 | L1 | 0.39 |  | 1 | 1.01 | SUNBRANCH LN
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.93 | UG/L | 60.4999 | 2018-08-16 | L2 | 0.91 |  | 2 | 0.65 | SUNCREST LOOP
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 55.1 | UG/L | 80.4999 | 2018-08-16 | L2 | 0.39 |  | 2 | 0.65 | SUNCREST LOOP
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 51.04 | UG/L | 80.4999 | 2018-11-15 | L2 | 0.56 |  | 2 | 0.42
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.63 | UG/L | 60.4999 | 2018-11-15 | L2 | 0.91 |  | 2 | 0.42
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 51.21 | UG/L | 80.4999 | 2018-11-15 | L1 | 0.56 |  | 1 | 0.73
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.62 | UG/L | 60.4999 | 2018-11-15 | L1 | 0.91 |  | 1 | 0.73
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 40.03 | UG/L | 60.4999 | 2019-02-14 | L1 | 0.91 |  | 1 | 0.64 | HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 61.68 | UG/L | 80.4999 | 2019-02-14 | L1 | 0.39 |  | 1 | 0.64 | HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 42.01 | UG/L | 60.4999 | 2019-02-14 | L2 | 0.91 |  | 2 | 0.29 | WINN DIXIE
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 56.59 | UG/L | 80.4999 | 2019-02-14 | L2 | 0.39 |  | 2 | 0.29 | WINN DIXIE
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | M | 61.98 | UG/L | 80.4999 | 2019-02-14 | L1
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | M | 40.03 | UG/L | 60.4999 | 2019-02-14 | L1
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 58.97 | UG/L | 80.4999 | 2019-05-16 | L2 |  |  | 2 | 0.93 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) / SUBCONTRACT LABS E82535 E84589
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.85 | UG/L | 60.4999 | 2019-05-16 | L2 |  |  | 2 | 0.93 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE) / SUBCONTRACT LABS E82535 E84589
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 88.05 | UG/L | 80.4999 | 2019-05-16 | L1 |  |  | 1 | 0.64 | SS 4 SUNBRANCH LN @ HWY 17-92 / SUBCONTRACT LABS E82535 E84589
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.88 | UG/L | 60.4999 | 2019-05-16 | L1 |  |  | 1 | 0.64 | SS 4 SUNBRANCH LN @ HWY 17-92 / SUBCONTRACT LABS E82535 E84589
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 57.82 | UG/L | 80.4999 | 2019-08-15 | L2 |  |  | 2 | 0.51 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.01 | UG/L | 60.4999 | 2019-08-15 | L2 |  |  | 2 | 0.51 | SS 6 1750 SUNCREST LOOP (WINN-DIXIE)
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 68.35 | UG/L | 80.4999 | 2019-08-15 | L1 |  |  | 1 | 0.6 | SS 4 SUNBRANCH LN @ HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.59 | UG/L | 60.4999 | 2019-08-15 | L1 |  |  | 1 | 0.6 | SS 4 SUNBRANCH LN @ HWY 17-92
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 59.41 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.39 |  | 2 | 0.66 | SUNBRANCH LN
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2950 | TOTAL THMS | D | 53.19 | UG/L | 80.4999 | 2019-11-20 | L2 | 0.39 |  | 1 | 0.78 | 1750 SUNCREST LOOP
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.98 | UG/L | 60.4999 | 2019-11-20 | L2 | 0.91 |  | 1 | 0.78 | 1750 SUNCREST LOOP
3594216 | SUNSHADOW APARTMENTS (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.9 | UG/L | 60.4999 | 2019-11-20 | L1 | 0.91 |  | 2 | 0.66 | SUNBRANCH LN
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.1 | UG/L | 60.4999 | 2015-09-02 | L1 |  |  |  | 1.2 | 2040 SIPES AVE. (HOUSE) STG 2 PLAN REVISED FOR 3RD QTR 2015-SITE MOVING 1 BLOCK AWAY-APPROVED (MOVED FROM CHURCH AT 2140 SIPES TO HOUSE AT 2040 SIPES-LOW WTR USAGE AT CHURCH)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 37.2 | UG/L | 80.4999 | 2015-09-02 | L2 |  |  |  | 1.4 | 2310 JITWAY (WATER ASSOCIATION OFFC)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.7 | UG/L | 60.4999 | 2015-09-02 | L2 |  |  |  | 1.4 | 2310 JITWAY (WATER ASSOCIATION OFFC)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 49.5 | UG/L | 80.4999 | 2015-09-02 | L1 |  |  |  | 1.2 | 2040 SIPES AVE. (HOUSE) STG 2 PLAN REVISED FOR 3RD QTR 2015-SITE MOVING 1 BLOCK AWAY-APPROVED (MOVED FROM CHURCH AT 2140 SIPES TO HOUSE AT 2040 SIPES-LOW WTR USAGE AT CHURCH)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.8 | UG/L | 60.4999 | 2016-08-30 | L1 | 0.5 |  | 2 | 0.7 | 2040 SIPES AVE.
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 30.2 | UG/L | 60.4999 | 2016-08-30 | L2 | 0.5 |  | 1 | 0.9 | 2310 JITWAY AVE.
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 76.3 | UG/L | 80.4999 | 2016-08-30 | L2 | 0.5 |  | 1 | 0.9 | 2310 JITWAY AVE.
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 85.8 | UG/L | 80.4999 | 2016-08-30 | L1 | 0.5 |  | 2 | 0.7 | 2040 SIPES AVE.
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 45.4 | UG/L | 80.4999 | 2017-06-19 | L1 | 0.5 |  | 2 | 1.4 | 2040 SIPES AVE. (HYPERLINKED 7/24/17) CONTINUE QM/DBPS (8/16 T>80 ONE SITE MISSED QTRS 4Q'16 & 1Q'17)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 9.29 | UG/L | 60.4999 | 2017-06-19 | L1 | 0.5 |  | 2 | 1.4 | 2040 SIPES AVE. (HYPERLINKED 7/24/17) CONTINUE QM/DBPS (8/16 T>80 ONE SITE MISSED QTRS 4Q'16 & 1Q'17)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.97 | UG/L | 60.4999 | 2017-06-19 | L2 | 0.5 |  | 1 | 1.4 | 2310 JITWAY
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 46.5 | UG/L | 80.4999 | 2017-06-19 | L2 | 0.5 |  | 1 | 1.4 | 2310 JITWAY
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.9 | UG/L | 60.4999 | 2017-08-03 | L2 | 0.5 |  | 1 | 1.4 | ON QM-2310 JITWAY
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 46 | UG/L | 80.4999 | 2017-08-03 | L2 | 0.5 |  | 1 | 1.4 | ON QM-2310 JITWAY
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.2 | UG/L | 60.4999 | 2017-08-03 | L1 | 0.5 |  | 2 | 1.4 | ON QM-2040 SIPES AVE. (HYPERLINKED 8/30/17 TO BW - BB) 8/16 T>80 ONE SITE MISSED QTRS 4Q'16 & 1Q'17
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 51.5 | UG/L | 80.4999 | 2017-08-03 | L1 | 0.5 |  | 2 | 1.4 | ON QM-2040 SIPES AVE. (HYPERLINKED 8/30/17 TO BW - BB) 8/16 T>80 ONE SITE MISSED QTRS 4Q'16 & 1Q'17
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.6 | UG/L | 60.4999 | 2017-12-07 | L2 | 0.5 |  | 2 | 1.5 | 2310 JITWAY AVE(HYPRLNKD 12/28/17 TO BW-BB)MUST TEST QTRLY AT LEAST THRU 3/31/18 QTR(4-10-18 PWS WILL NOT ALLOW ENTRY OF 2/18 DBPS-TOO MANY LOC CODES AUTO-CREATED BY PWS-HYPRLNKD 4-10-18 BB&NO PN YET)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 51 | UG/L | 80.4999 | 2017-12-07 | L1 | 0.5 |  | 1 | 1.4 | 2040 SIPES AVE.
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.3 | UG/L | 60.4999 | 2017-12-07 | L1 | 0.5 |  | 1 | 1.4 | 2040 SIPES AVE.
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 48.4 | UG/L | 80.4999 | 2017-12-07 | L2 | 0.5 |  | 2 | 1.5 | 2310 JITWAY AVE(HYPRLNKD 12/28/17 TO BW-BB)MUST TEST QTRLY AT LEAST THRU 3/31/18 QTR(4-10-18 PWS WILL NOT ALLOW ENTRY OF 2/18 DBPS-TOO MANY LOC CODES AUTO-CREATED BY PWS-HYPRLNKD 4-10-18 BB&NO PN YET)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 18.7 | UG/L | 60.4999 | 2018-02-27 | L2 | 0.5 |  | 1 | 1.4 | 2310 JITWAY
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 50.8 | UG/L | 80.4999 | 2018-02-27 | L2 | 0.5 |  | 1 | 1.4 | 2310 JITWAY
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.1 | UG/L | 60.4999 | 2018-02-27 | L1 | 0.5 |  | 2 | 1.1 | 2040 SIPES AVE. (4-10-18 PWS WOULD NOT ALLOW ENTRY OF 2/18 DBPS AT 1ST-TOO MANY LOC CODES AUTO-CREATED BY PWS-HYPRLNKD 4-10-18 BB&NO PN YET) RSLTS ENT'D 4/26/18 AFTER DBP MONIT LOCS FIXED BY HQS. BB
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 56.1 | UG/L | 80.4999 | 2018-02-27 | L1 | 0.5 |  | 2 | 1.1 | 2040 SIPES AVE. (4-10-18 PWS WOULD NOT ALLOW ENTRY OF 2/18 DBPS AT 1ST-TOO MANY LOC CODES AUTO-CREATED BY PWS-HYPRLNKD 4-10-18 BB&NO PN YET) RSLTS ENT'D 4/26/18 AFTER DBP MONIT LOCS FIXED BY HQS. BB
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.9 | UG/L | 60.4999 | 2018-06-12 | L2 |  |  |  | 1.3 | 2310 JITWAY (WATER ASSOCIATION OFFC)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 69.1 | UG/L | 80.4999 | 2018-06-12 | L2 |  |  |  | 1.3 | 2310 JITWAY (WATER ASSOCIATION OFFC)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 21.5 | UG/L | 60.4999 | 2018-06-12 | L1 |  |  |  | 1.1 | 2040 SIPES AVE. (HOUSE) WAS 2140 (CH)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 63.7 | UG/L | 80.4999 | 2018-06-12 | L1 |  |  |  | 1.1 | 2040 SIPES AVE. (HOUSE) WAS 2140 (CH)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.8 | UG/L | 60.4999 | 2019-05-20 | L2 |  |  | 1 | 1.3 | 2310 JITWAY (WATER ASSOCIATION OFFC)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 39.4 | UG/L | 80.4999 | 2019-05-20 | L2 |  |  | 1 | 1.3 | 2310 JITWAY (WATER ASSOCIATION OFFC)
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.9 | UG/L | 60.4999 | 2019-05-20 | L1 |  |  | 2 | 1.1 | 2040 SIPES AVE. (HOUSE) WAS 2140 (CH) NEED SAMPLING PLAN SAMPLE 2Q_JB
3594230 | MIDWAY-CANAAN WATER ASSOCIATION (CONSEC) | DBP | 2950 | TOTAL THMS | D | 50.4 | UG/L | 80.4999 | 2019-05-20 | L1 |  |  | 2 | 1.1 | 2040 SIPES AVE. (HOUSE) WAS 2140 (CH) NEED SAMPLING PLAN SAMPLE 2Q_JB
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 74.45 | UG/L | 80.4999 | 2015-09-02 | L1 |  |  |  | 1.8 | 1ST FLOOR MEN'S BATHROOM SINK (REMAIN ON ANNUAL ROUTINE DBP SAMPLING W/NEXT T/H DUE @ 9/2/16)
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.1 | UG/L | 60.4999 | 2015-09-02 | L1 |  |  |  | 1.8 | 1ST FLOOR MEN'S BATHROOM SINK (REMAIN ON ANNUAL ROUTINE DBP SAMPLING W/NEXT T/H DUE @ 9/2/16)
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.91 | UG/L | 60.4999 | 2016-09-12 | L1 |  |  |  | 1.4 | T>40 REMAIN ON ROUTINE TESTING WAS NEXT DUE 9/17. MISSED 2017 SAMPLING. WILL GO BACK TO ROUTINE IN 3Q 2018.
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 56.01 | UG/L | 80.4999 | 2016-09-12 | L1 |  |  |  | 1.4 | T>40 REMAIN ON ROUTINE TESTING WAS NEXT DUE 9/17. MISSED 2017 SAMPLING. WILL GO BACK TO ROUTINE IN 3Q 2018.
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.25 | UG/L | 60.4999 | 2018-01-03 | L1
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 71.42 | UG/L | 80.4999 | 2018-01-03 | L1
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 102.87 | UG/L | 80.4999 | 2018-07-02 | L1 |  |  |  | 0.2 | 1ST FLOOR MEN'S BATHROOM SINK / E82535 TTHM / FIRST TIME EXCEEDANCE START QUARTERLY MONITORING
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.3 | UG/L | 60.4999 | 2018-07-02 | L1 |  |  |  | 0.2 | 1ST FLOOR MEN'S BATHROOM SINK / E82535 TTHM / FIRST TIME EXCEEDANCE START QUARTERLY MONITORING
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 89.35 | UG/L | 80.4999 | 2018-07-02 | L2 |  |  |  | 0.52 | BEGIN Q MONITORING_JMF
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.18 | UG/L | 60.4999 | 2018-07-02 | L2 |  |  |  | 0.52 | BEGIN Q MONITORING_JMF
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 37.55 | UG/L | 60.4999 | 2018-10-02 | L1 | 0.91 |  | 1 | 0.9 | 3000 DOVERA DR
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 117.15 | UG/L | 80.4999 | 2018-10-02 | L1 | 1 |  | 1 | 0.9 | 3000 DOVERA DR
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 92.01 | UG/L | 80.4999 | 2018-10-02 | L2 | 1 |  | 2 | 0.9 | 701 AMBERLY JEWEL WAY
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.14 | UG/L | 60.4999 | 2018-10-02 | L2 | 0.91 |  | 2 | 0.9 | 701 AMBERLY JEWEL WAY
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | S | 50.33 | UG/L | 80.4999 | 2018-12-14 | L1 |  |  | 1 | 1 | 2950-3000 DOVERA DRIVE OUTSIDE SAMPLE TAP / SUBCONTRACT LAB 82535
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | S | 49.2 | UG/L | 80.4999 | 2018-12-14 | L2 |  |  | 2 | 0.9 | 2950-701 AMBERLY JEWEL WAY / SUBCONTRACT LAB E82535
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 33.25 | UG/L | 60.4999 | 2019-01-03 | L1 | 0.91 |  | 1 | 0.4 | 3000 DOVERA DR
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 71.42 | UG/L | 80.4999 | 2019-01-03 | L1 | 0.39 |  | 1 | 0.4 | 3000 DOVERA DR
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 47.51 | UG/L | 80.4999 | 2019-01-03 | L2
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.32 | UG/L | 60.4999 | 2019-01-03 | L2 | 0.91 |  | 2 | 1.2 | 701 AMBERLY JEWEL
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 47.51 | UG/L | 80.4999 | 2019-01-03 | L2 | 0.39 |  | 2 | 1.2 | 701 AMBERLY JEWEL
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 20.32 | UG/L | 60.4999 | 2019-01-03 | L2
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 31.37 | UG/L | 60.4999 | 2019-04-02 | L1 |  |  |  | 0.82 | 2950-3000 DOVERA DRIVE OUTSIDE SAMPLE TAP / SUBCONTRACT LABS E84589 E82535
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 82.78 | UG/L | 80.4999 | 2019-04-02 | L1 |  |  |  | 0.82 | 2950-3000 DOVERA DRIVE OUTSIDE SAMPLE TAP / SUBCONTRACT LABS E84589 E82535
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 64.8 | UG/L | 80.4999 | 2019-04-02 | L2 |  |  |  | 1.08 | 2950-701 AMBERLY JEWEL WAY / SUBCONTRACT LABS E84589 E82535
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.88 | UG/L | 60.4999 | 2019-04-02 | L2 |  |  |  | 1.08 | 2950-701 AMBERLY JEWEL WAY / SUBCONTRACT LABS E84589 E82535
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 14.69 | UG/L | 60.4999 | 2019-07-02 | L1 |  |  | 1 | 1.33 | 3000 DOVERA DRIVE OUTSIDE SAMPLE TAP / SUBCONTRACT LABS E82574 E82535
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 46.87 | UG/L | 80.4999 | 2019-07-02 | L2 |  |  | 2 | 1.33 | 701 AMBERLY JEWEL WAY / SUBCONTRACT LABS E82574 E82535 [TTHM LRAA=52.01]_VP
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 17.51 | UG/L | 60.4999 | 2019-07-02 | L2 |  |  | 2 | 1.33 | 701 AMBERLY JEWEL WAY / SUBCONTRACT LABS E82574 E82535 [TTHM LRAA=52.01]_VP
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 42.39 | UG/L | 80.4999 | 2019-07-02 | L1 |  |  | 1 | 1.33 | 3000 DOVERA DRIVE OUTSIDE SAMPLE TAP / SUBCONTRACT LABS E82574 E82535
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.04 | UG/L | 60.4999 | 2019-10-01 | L2 | 0.91 |  | 2 | 1.1 | 701 AMBERLY
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 11.07 | UG/L | 80.4999 | 2019-10-01 | L2 | 0.39 |  | 2 | 1.1 | 701 AMBERLY
3594240 | DOVERA (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.06 | UG/L | 60.4999 | 2019-10-01 | L1 | 0.91 |  | 1 | 1.3 | 3000 DOVERA DR
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 54.76 | UG/L | 80.4999 | 2019-10-01 | L1 | 0.39 |  | 1 | 1.3 | 3000 DOVERA DR
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 75.59 | UG/L | 80.4999 | 2019-12-11 | L1 | 0.39 |  | 1 | 1
3594240 | DOVERA (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 63.38 | UG/L | 80.4999 | 2019-12-11 | L2 | 0.39 |  | 1 | 1.2
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 57.43 | UG/L | 80.4999 | 2016-09-14 | L1 |  |  |  | 1.2 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.22 | UG/L | 60.4999 | 2016-09-14 | L1 |  |  |  | 1.2 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 57.39 | UG/L | 80.4999 | 2016-09-14 | L2 |  |  |  | 1.4 | 1400 OVIEDO MALL BLVD.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 27.06 | UG/L | 60.4999 | 2016-09-14 | L2 |  |  |  | 1.4 | 1400 OVIEDO MALL BLVD.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.7 | UG/L | 60.4999 | 2017-07-26 | L2 | 0.5 |  | 2 | 0.8 | 1400 OVIEDO MALL BLVD. (L1 SITE TTHMS>MCL OF 80 UG/L START QM/DBPS BOTH SITES) HYPERLINKED 8/28/17 TO BW - BB
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 72.98 | UG/L | 80.4999 | 2017-07-26 | L2 | 0.14 |  | 2 | 0.8 | 1400 OVIEDO MALL BLVD. (L1 SITE TTHMS>MCL OF 80 UG/L START QM/DBPS BOTH SITES) HYPERLINKED 8/28/17 TO BW - BB
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 29.14 | UG/L | 60.4999 | 2017-07-26 | L1 | 0.5 |  | 1 | 1 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 82.94 | UG/L | 80.4999 | 2017-07-26 | L1 | 0.14 |  | 1 | 1 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 52.52 | UG/L | 80.4999 | 2017-10-18 | L1 | 0.14 |  | 1 | 1 | 2QM-1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.71 | UG/L | 60.4999 | 2017-10-18 | L2 | 0.5 |  | 1 | 1.2 | 2QM-1400 OVIEDO MALL BLVD. (HYPERLINKED TO BW 12/22/17 - BB) REMAIN ON QM/DBPS
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 49.1 | UG/L | 80.4999 | 2017-10-18 | L2 | 0.14 |  | 1 | 1.2 | 2QM-1400 OVIEDO MALL BLVD. (HYPERLINKED TO BW 12/22/17 - BB) REMAIN ON QM/DBPS
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.93 | UG/L | 60.4999 | 2017-10-18 | L1 | 0.5 |  | 1 | 1 | 2QM-1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 28.36 | UG/L | 80.4999 | 2018-02-13 | L1 | 0.14 |  | 1 | 0.8 | 1740 GARDEN SAGE
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.75 | UG/L | 60.4999 | 2018-02-13 | L2 | 0.5 |  | 2 | 1 | 1400 OVIEDO MALL
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 57.59 | UG/L | 80.4999 | 2018-02-13 | L2 | 0.14 |  | 2 | 1 | 1400 OVIEDO MALL
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.54 | UG/L | 60.4999 | 2018-02-13 | L1 | 0.5 |  | 1 | 0.8 | 1740 GARDEN SAGE
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 70.52 | UG/L | 80.4999 | 2018-05-14 | L2 |  |  |  | 0.8 | 1400 OVIEDO MALL BLVD.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.09 | UG/L | 60.4999 | 2018-05-14 | L1 |  |  |  | 1 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 75.17 | UG/L | 80.4999 | 2018-05-14 | L1 |  |  |  | 1 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 36.36 | UG/L | 60.4999 | 2018-05-14 | L2 |  |  |  | 0.8 | 1400 OVIEDO MALL BLVD.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.5 | UG/L | 60.4999 | 2018-08-13 | L2 | 0.91 |  | 2 | 1.2 | 1400 OVIEDO MALL BLVD
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 40.31 | UG/L | 80.4999 | 2018-08-13 | L1 | 0.39 |  | 1 | 1 | 1740 GARDEN SAGE
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 19.67 | UG/L | 60.4999 | 2018-08-13 | L1 | 0.91 |  | 1 | 1 | 1740 GARDEN SAGE
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 44.72 | UG/L | 80.4999 | 2018-08-13 | L2 | 0.39 |  | 2 | 1.2 | 1400 OVIEDO MALL BLVD
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 49.57 | UG/L | 80.4999 | 2018-11-14 | L1 |  |  |  | 1 | 2950-1740 GARDEN SAGE DR. / SUBCONTRACT LAB E84589
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.95 | UG/L | 60.4999 | 2018-11-14 | L2 |  |  |  | 0.09 | 2950-1400 OVIEDO MALL BLVD. / SUBCONTRACT LAB E84589
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 47.93 | UG/L | 80.4999 | 2018-11-14 | L2 |  |  |  | 0.09 | 2950-1400 OVIEDO MALL BLVD. / SUBCONTRACT LAB E84589
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 26.6 | UG/L | 60.4999 | 2018-11-14 | L1 |  |  |  | 1 | 2950-1740 GARDEN SAGE DR. / SUBCONTRACT LAB E84589
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 58.09 | UG/L | 80.4999 | 2019-02-13 | L1
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.46 | UG/L | 60.4999 | 2019-02-13 | L1 | 0.91 |  | 1 | 0.9 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 58.09 | UG/L | 80.4999 | 2019-02-13 | L1 | 0.39 |  | 1 | 0.9 | 1740 GARDEN SAGE DR.
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 28.2 | UG/L | 60.4999 | 2019-02-13 | L2 | 0.91 |  | 2 | 0.8 | 1400 OVIEDO MALL BLVD. (HLKD)
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 66.23 | UG/L | 80.4999 | 2019-02-13 | L2 | 0.39 |  | 2 | 0.8 | 1400 OVIEDO MALL BLVD. (HLKD)
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 25.46 | UG/L | 60.4999 | 2019-02-13 | L1
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 53.58 | UG/L | 80.4999 | 2019-07-23 | L1 |  |  | 1 | 1.32 | 1740 GARDEN SAGE DR. / SUBCONTRACT LABS E84589 E82535
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 24.51 | UG/L | 60.4999 | 2019-07-23 | L1 |  |  | 1 | 1.32 | 1740 GARDEN SAGE DR. / SUBCONTRACT LABS E84589 E82535
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 30.69 | UG/L | 80.4999 | 2019-07-23 | L2 |  |  | 2 | 1.28 | 1400 OVIEDO MALL BLVD. / SUBCONTRACT LABS E84589 E82535
3594241 | OVIEDO MARKETPLACE (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 23.64 | UG/L | 60.4999 | 2019-07-23 | L2 |  |  | 2 | 1.28 | 1400 OVIEDO MALL BLVD. / SUBCONTRACT LABS E84589 E82535
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2950 | TOTAL THMS | D | 24.36 | UG/L | 80.4999 | 2017-04-27 | L1 | 0.14 |  | 1 | 6.13 | 3180 MOYER LOOP (NO STAGE 2 PLAN YET - MUST TEST INITIALLY DURING JULY - SEPT. 2017)
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2950 | TOTAL THMS | D | 29.26 | UG/L | 80.4999 | 2017-04-27 | L2 | 0.14 |  | 2 | 1.69 | 3414 MOYER LOOP (NO STAGE 2 PLAN RCVD YET - MUST TEST INITIALLY DURING JULY - SEPT. 2017) HYPERLINKED TO RLB 5/26/17-ASKED RLB TO TELL DEANNA THAT THEY HAD TO TEST DBPS DURING JULY-SEPT. 2017-BB
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.78 | UG/L | 60.4999 | 2017-04-27 | L2 | 0.5 |  | 2 | 1.69 | 3414 MOYER LOOP (NO STAGE 2 PLAN RCVD YET - MUST TEST INITIALLY DURING JULY - SEPT. 2017) HYPERLINKED TO RLB 5/26/17-ASKED RLB TO TELL DEANNA THAT THEY HAD TO TEST DBPS DURING JULY-SEPT. 2017-BB
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.13 | UG/L | 60.4999 | 2017-04-27 | L1 | 0.5 |  | 1 | 6.13 | 3180 MOYER LOOP (NO STAGE 2 PLAN YET - MUST TEST INITIALLY DURING JULY - SEPT. 2017)
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.77 | UG/L | 60.4999 | 2017-08-17 | L2 | 0.5 |  | 2 | 1.34 | 3414 MOYER LOOP (QUALIFIES FOR REDUCED AT 1 SITE 3414 MOYER LOOP ONLY DURING AUG. 2018 ASSUMING ORIG. 2 SITES ARE OK - NO STG2 PLAN YET) T<40 H<30 BOTH SITES
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2950 | TOTAL THMS | D | 24.02 | UG/L | 80.4999 | 2017-08-17 | L1 | 0.14 |  | 1 | 1.22 | 3180 MOYER LOOP (T<40 H<30 QUALIFIES FOR REDUCED AT 1 SITE L2 SITE DURING AUG. 2018 ASSUMING ORIG. STG2 PLAN APPROVED)
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 6.55 | UG/L | 60.4999 | 2017-08-17 | L1 | 0.5 |  | 1 | 1.22 | 3180 MOYER LOOP (T<40 H<30 QUALIFIES FOR REDUCED AT 1 SITE L2 SITE DURING AUG. 2018 ASSUMING ORIG. STG2 PLAN APPROVED)
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2950 | TOTAL THMS | D | 28.52 | UG/L | 80.4999 | 2017-08-17 | L2 | 0.14 |  | 2 | 1.34 | 3414 MOYER LOOP (QUALIFIES FOR REDUCED AT 1 SITE 3414 MOYER LOOP ONLY DURING AUG. 2018 ASSUMING ORIG. 2 SITES ARE OK - NO STG2 PLAN YET) T<40 H<30 BOTH SITES
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2950 | TOTAL THMS | D | 25.87 | UG/L | 80.4999 | 2018-05-15 | L2 |  |  |  | 1.13 | 3414 MOYER LOOP
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.85 | UG/L | 60.4999 | 2018-05-15 | L2 |  |  |  | 1.13 | 3414 MOYER LOOP
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2950 | TOTAL THMS | D | 20.74 | UG/L | 80.4999 | 2019-05-08 | L2 |  |  |  | 1.34 | SUBCONTRACT LABS 382535 E84589
3600007 | VILLAGE OF PINE RIDGE (CONSEC) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 8.2 | UG/L | 60.4999 | 2019-05-08 | L2 |  |  |  | 1.34 | SUBCONTRACT LABS 382535 E84589
3600009 | SOUTH SUMTER UTILITIES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 230 | MG/L | 500.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1040 | NITRATE | N | 0.73 | MG/L | 10.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1010 | BARIUM | N | 0.0093 | MG/L | 2.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1025 | FLUORIDE | N | 0.42 | MG/L | 4.0499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1052 | SODIUM | N | 7.7 | MG/L | 160.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2019-08-01 | POE |  | 0.0149
3600009 | SOUTH SUMTER UTILITIES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2019-08-01 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2019-08-01 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2019-08-01 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-08-01 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2019-08-01 | POE |  | 0.4499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2019-08-01 | POE |  | 9.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2019-08-01 | POE |  | 6.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2019-08-01 | POE |  | 0.6499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2019-08-01 | POE |  | 2.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2019-08-01 | POE |  | 0.0749
3600009 | SOUTH SUMTER UTILITIES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 16.3 | UG/L | 60.4999 | 2019-08-01 | L2 |  |  |  | 1.34 | 1QM 2264 GORDON PATH
3600009 | SOUTH SUMTER UTILITIES | DBP | 2950 | TOTAL THMS | D | 35.92 | UG/L | 80.4999 | 2019-08-01 | L2 |  |  |  | 1.34 | 1QM 2264 GORDON PATH
3600009 | SOUTH SUMTER UTILITIES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 32.34 | UG/L | 60.4999 | 2019-08-01 | L1 |  |  |  | 1.53 | 1QM 2162 FENNEY WAY
3600009 | SOUTH SUMTER UTILITIES | DBP | 2950 | TOTAL THMS | D | 40.78 | UG/L | 80.4999 | 2019-08-01 | L1 |  |  |  | 1.53 | 1QM 2162 FENNEY WAY
3600009 | SOUTH SUMTER UTILITIES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2019-08-01 | POE |  | 0.6499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2019-08-01 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2019-08-01 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2019-08-01 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2019-08-01 | POE |  | 0.9499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2019-08-01 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2019-08-01 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2019-08-01 | POE |  | 0.0449
3600009 | SOUTH SUMTER UTILITIES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2019-08-01 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2019-08-01 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2019-08-01 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2019-08-01 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2019-08-01 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2019-08-01 | POE |  | 0.0449
3600009 | SOUTH SUMTER UTILITIES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2019-08-01 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2019-08-01 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2019-08-01 | POE |  | 0.0149
3600009 | SOUTH SUMTER UTILITIES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2019-08-01 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-08-01 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1017 | CHLORIDE | N | 16 | MG/L | 250.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1025 | FLUORIDE | N | 0.42 | MG/L | 2.0499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1055 | SULFATE | N | 71 | MG/L | 250.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.93 | LN(10) |  | 2019-08-01 | POE
3600009 | SOUTH SUMTER UTILITIES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2019-08-05 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | RAD | 4020 | RADIUM-226 | N | 0.7 | PCI/L | 3.4999 | 2019-08-05 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2019-08-05 | POE
3600009 | SOUTH SUMTER UTILITIES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2019-11-20 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2019-11-20 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | INOR | 1040 | NITRATE | N | 0.44 | MG/L | 10.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2019-11-20 | POE |  | 0.9499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2019-11-20 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2019-11-20 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2063 | DIOXIN (NG/L) | N | 0 | NG/L | 0.0349 | 2019-11-20 | POE |  | 0.0055
3600009 | SOUTH SUMTER UTILITIES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2019-11-20 | POE |  | 0.0449
3600009 | SOUTH SUMTER UTILITIES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2019-11-20 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2019-11-20 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2019-11-20 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2019-11-20 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2019-11-20 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2019-11-20 | POE |  | 0.0449
3600009 | SOUTH SUMTER UTILITIES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2019-11-20 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2019-11-20 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2019-11-20 | POE |  | 0.0149
3600009 | SOUTH SUMTER UTILITIES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2019-11-20 | POE |  | 0.2499
3600009 | SOUTH SUMTER UTILITIES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | RAD | 4020 | RADIUM-226 | N | 1 | PCI/L | 3.4999 | 2019-11-20 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2019-11-20 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1025 | FLUORIDE | N | 0.24 | MG/L | 4.0499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.98 | UG/L | 60.4999 | 2019-11-20 | L2 | 0.91 |  | 1 | 1.39 | 2264 GORDON PATH
3600009 | SOUTH SUMTER UTILITIES | DBP | 2950 | TOTAL THMS | D | 33.46 | UG/L | 80.4999 | 2019-11-20 | L2 | 0.39 |  | 1 | 1.39 | 2264 GORDON PATH
3600009 | SOUTH SUMTER UTILITIES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 12.12 | UG/L | 60.4999 | 2019-11-20 | L1 | 0.91 |  | 2 | 1.25 | 2162 FENNEY WAY
3600009 | SOUTH SUMTER UTILITIES | DBP | 2950 | TOTAL THMS | D | 32.29 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.39 |  | 2 | 1.25 | 2162 FENNEY WAY
3600009 | SOUTH SUMTER UTILITIES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1052 | SODIUM | N | 8.2 | MG/L | 160.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1017 | CHLORIDE | N | 14 | MG/L | 250.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1022 | COPPER | N | 0.025 | MG/L | 1.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1025 | FLUORIDE | N | 0.24 | MG/L | 2.0499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1055 | SULFATE | N | 79 | MG/L | 250.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.97 | LN(10) |  | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 230 | MG/L | 500.4999 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2019-11-20 | POE
3600009 | SOUTH SUMTER UTILITIES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2019-11-20 | POE |  | 0.5499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2019-11-20 | POE |  | 0.0149
3600009 | SOUTH SUMTER UTILITIES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2019-11-20 | POE |  | 0.0249
3600009 | SOUTH SUMTER UTILITIES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2019-11-20 | POE |  | 0.1499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2019-11-20 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2019-11-20 | POE |  | 1.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2019-11-20 | POE |  | 0.4499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2019-11-20 | POE |  | 9.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2019-11-20 | POE |  | 6.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2019-11-20 | POE |  | 0.6499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2019-11-20 | POE |  | 2.4999
3600009 | SOUTH SUMTER UTILITIES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2019-11-20 | POE |  | 0.0749
3600009 | SOUTH SUMTER UTILITIES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2019-11-20 | POE |  | 0.6499
3600009 | SOUTH SUMTER UTILITIES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2019-11-20 | POE |  | 0.1499
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2016-12-06 | L2 |  |  |  | 1.1 | LATE SAMPLING VP
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 1.77 | UG/L | 80.4999 | 2016-12-06 | L2 |  |  |  | 1.1 | LATE SAMPLING VP
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2016-12-06 | L1 |  |  |  | 1.1 | LATE SAMPLING VP
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2016-12-06 | L1 |  |  |  | 1.1 | LATE SAMPLING VP
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2017-08-21 | L2 |  |  |  | 1.1 | 7130 SW 64TH TERR BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2017-08-21 | L1 |  |  |  | 1.1 | HANDYWAY (KANGAROO) BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2017-08-21 | L1 |  |  |  | 1.1 | HANDYWAY (KANGAROO) BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2017-08-21 | L2 |  |  |  | 1.1 | 7130 SW 64TH TERR BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.89 |  | 1 | 1.1 | KANGAROO BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2018-08-07 | L2 | 0.39 |  | 1 | 1.1 | 7130 SW 64TH TERR BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-08-07 | L2 | 0.89 |  | 1 | 1.1 | 7130 SW 64TH TERR BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.39 |  | 1 | 1.1 | KANGAROO BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2019-08-07 | L2 |  |  | 2 | 1.1 | 7130 SW 64TH TERR BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2019-08-07 | L1 |  |  | 1 | 1.1 | HANDYWAY (KANGAROO) BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2019-08-07 | L1 |  |  | 1 | 1.1 | HANDYWAY (KANGAROO) BLOWOFF
6420103 | BAHIA OAKS (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2019-08-07 | L2 |  |  | 2 | 1.1 | 7130 SW 64TH TERR BLOWOFF
6420467 | DOGWOOD ACRES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 490 | MG/L | 500.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0.35 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6420467 | DOGWOOD ACRES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 3.7 | PCI/L | 15.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | RAD | 4020 | RADIUM-226 | N | 2 | PCI/L | 3.4999 | 2015-07-08 | AAA |  | 1.4999
6420467 | DOGWOOD ACRES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-07-08 | AAA |  | 1.4999
6420467 | DOGWOOD ACRES | INOR | 1040 | NITRATE | N | 0.82 | MG/L | 10.4999 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1005 | ARSENIC | N | 0.0005 | MG/L | 0.0104 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1010 | BARIUM | N | 0.0079 | MG/L | 2.4999 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1015 | CADMIUM | N | 0.0002 | MG/L | 0.0055 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1020 | CHROMIUM | N | 0.0006 | MG/L | 0.1499 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1025 | FLUORIDE | N | 0.35 | MG/L | 4.0499 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1036 | NICKEL | N | 0.0033 | MG/L | 0.1499 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1052 | SODIUM | N | 16 | MG/L | 160.4999 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1074 | ANTIMONY | N | 0.0012 | MG/L | 0.0065 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-08 | AAA |  |  |  |  | 15 DONE
6420467 | DOGWOOD ACRES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1017 | CHLORIDE | N | 31 | MG/L | 250.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1025 | FLUORIDE | N | 0.35 | MG/L | 2.0499 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1032 | MANGANESE | N | 0.0009 | MG/L | 0.0549 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1050 | SILVER | N | 0.0002 | MG/L | 0.1499 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1055 | SULFATE | N | 200 | MG/L | 250.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1095 | ZINC | N | 0.013 | MG/L | 5.4999 | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 6.9 | LN(10) |  | 2015-07-08 | AAA
6420467 | DOGWOOD ACRES | DBP | 2950 | TOTAL THMS | D | 1.68 | UG/L | 80.4999 | 2015-08-18 | L1 |  |  |  | 0.4 | REDUCED MONITORING SM C DUE 2018 VP
6420467 | DOGWOOD ACRES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.43 | UG/L | 60.4999 | 2015-08-18 | L1 |  |  |  | 0.4 | REDUCED MONITORING SM C DUE 2018 VP
6420467 | DOGWOOD ACRES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-08-24 | AAA |  |  |  |  | 16 DONE
6420467 | DOGWOOD ACRES | INOR | 1040 | NITRATE | N | 1.1 | MG/L | 10.4999 | 2016-08-24 | AAA |  |  |  |  | 16 DONE
6420467 | DOGWOOD ACRES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-05-24 | AAA
6420467 | DOGWOOD ACRES | INOR | 1040 | NITRATE | N | 1.1 | MG/L | 10.4999 | 2017-05-24 | AAA
6420467 | DOGWOOD ACRES | DBP | 2950 | TOTAL THMS | D | 5.47 | UG/L | 80.4999 | 2018-07-09 | L1 | 0.14 |  | 1 | 1 | CLUBHOUSE K. SINK (HLKD 8-16-18 - BB)
6420467 | DOGWOOD ACRES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-07-09 | L1 | 0.52 |  | 1 | 1 | CLUBHOUSE K. SINK (HLKD 8-16-18 - BB)
6420467 | DOGWOOD ACRES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1045 | SELENIUM | N | 0.0027 | MG/L | 0.0549 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1052 | SODIUM | N | 18 | MG/L | 160.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | SEC | 1002 | ALUMINUM | N | 0.036 | MG/L | 0.2499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1017 | CHLORIDE | N | 26 | MG/L | 250.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1022 | COPPER | N | 0.0063 | MG/L | 1.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1050 | SILVER | N | 0.0006 | MG/L | 0.1499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | SEC | 1095 | ZINC | N | 0.012 | MG/L | 5.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 6.55 | LN(10) |  | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 530 | MG/L | 500.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-11-28 | AAA |  | 0.5499 |  |  | POE / SUBCONTRACT LAB E82535
6420467 | DOGWOOD ACRES | INOR | 1040 | NITRATE | N | 1.1 | MG/L | 10.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1010 | BARIUM | N | 0.01 | MG/L | 2.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | INOR | 1005 | ARSENIC | N | 0.0003 | MG/L | 0.0104 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E82574 E84589
6420467 | DOGWOOD ACRES | SEC | 1055 | SULFATE | N | 210 | MG/L | 250.4999 | 2018-11-28 | AAA |  |  |  |  | POE / SUBCONTRACT LABS E84589 E82574
6420467 | DOGWOOD ACRES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-11-29 | AAA |  | 1.4999 |  |  | POE / SUBCONTRACT LAB E84025
6420467 | DOGWOOD ACRES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 5.1 | PCI/L | 15.4999 | 2018-11-29 | AAA |  |  |  |  | POE / SUBCONTRACT LAB E84025
6420467 | DOGWOOD ACRES | RAD | 4020 | RADIUM-226 | N | 2.5 | PCI/L | 3.4999 | 2019-04-04 | AAA |  | 1.4999
6420467 | DOGWOOD ACRES | INOR | 1040 | NITRATE | N | 0.86 | MG/L | 10.4999 | 2019-05-08 | AAA
6420467 | DOGWOOD ACRES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-08 | AAA
6420619 | FOXWOOD FARMS | INOR | 1010 | BARIUM | N | 0.0041 | MG/L | 2.4999 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1020 | CHROMIUM | N | 0.0064 | MG/L | 0.1499 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1025 | FLUORIDE | N | 0.26 | MG/L | 4.0499 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1036 | NICKEL | N | 0.0025 | MG/L | 0.1499 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1045 | SELENIUM | N | 0.0023 | MG/L | 0.0549 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1052 | SODIUM | N | 12 | MG/L | 160.4999 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1017 | CHLORIDE | N | 17 | MG/L | 250.4999 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1022 | COPPER | N | 0.0029 | MG/L | 1.4999 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1025 | FLUORIDE | N | 0.26 | MG/L | 2.0499 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1028 | IRON | N | 0.048 | MG/L | 0.3499 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1032 | MANGANESE | N | 0.0029 | MG/L | 0.0549 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1055 | SULFATE | N | 58 | MG/L | 250.4999 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1095 | ZINC | N | 0.0099 | MG/L | 5.4999 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.4 | LN(10) |  | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 380 | MG/L | 500.4999 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-06-24 | AAA |  |  |  |  | PER 7/29/15 EM FROM GEN UTI SYS CONTRACTED OUT MONIT TO OTHER COMPANY PRIOR TO THEM STARTING OPS. SECONDARIES MISSING ODOR SAMPLE. GEN UTI IS AWARE. AMA
6420619 | FOXWOOD FARMS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-06-24 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-06-24 | AAA |  | 0.0149
6420619 | FOXWOOD FARMS | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-06-24 | AAA |  | 0.0249
6420619 | FOXWOOD FARMS | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-06-24 | AAA |  | 0.1499
6420619 | FOXWOOD FARMS | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-06-24 | AAA |  | 1.4999
6420619 | FOXWOOD FARMS | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-06-24 | AAA |  | 1.4999
6420619 | FOXWOOD FARMS | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-06-24 | AAA |  | 0.4499
6420619 | FOXWOOD FARMS | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-06-24 | AAA |  | 9.4999
6420619 | FOXWOOD FARMS | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-06-24 | AAA |  | 6.4999
6420619 | FOXWOOD FARMS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-06-24 | AAA |  | 0.6499
6420619 | FOXWOOD FARMS | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-06-24 | AAA |  | 2.4999
6420619 | FOXWOOD FARMS | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-06-24 | AAA |  | 0.0749
6420619 | FOXWOOD FARMS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-06-24 | AAA |  | 0.6499
6420619 | FOXWOOD FARMS | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-06-24 | AAA |  | 0.1499
6420619 | FOXWOOD FARMS | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-06-24 | AAA |  | 0.2499
6420619 | FOXWOOD FARMS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-06-24 | AAA |  | 0.1499
6420619 | FOXWOOD FARMS | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-06-24 | AAA |  | 0.9499
6420619 | FOXWOOD FARMS | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-06-24 | AAA |  | 0.1499
6420619 | FOXWOOD FARMS | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-06-24 | AAA |  | 0.2499
6420619 | FOXWOOD FARMS | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-06-24 | AAA |  | 0.0449
6420619 | FOXWOOD FARMS | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-06-24 | AAA |  | 0.0249
6420619 | FOXWOOD FARMS | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-06-24 | AAA |  | 0.1499
6420619 | FOXWOOD FARMS | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-06-24 | AAA |  | 0.2499
6420619 | FOXWOOD FARMS | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-06-24 | AAA |  | 0.1499
6420619 | FOXWOOD FARMS | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-06-24 | AAA |  | 0.0249
6420619 | FOXWOOD FARMS | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-06-24 | AAA |  | 0.0449
6420619 | FOXWOOD FARMS | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-06-24 | AAA |  | 0.1499
6420619 | FOXWOOD FARMS | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-06-24 | AAA |  | 0.0249
6420619 | FOXWOOD FARMS | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-06-24 | AAA |  | 0.0149
6420619 | FOXWOOD FARMS | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-06-24 | AAA |  | 0.2499
6420619 | FOXWOOD FARMS | INOR | 1040 | NITRATE | N | 0.86 | MG/L | 10.4999 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | INOR | 1005 | ARSENIC | N | 0.0021 | MG/L | 0.0104 | 2015-06-24 | AAA
6420619 | FOXWOOD FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 11.21 | UG/L | 60.4999 | 2015-07-31 | L1 |  |  |  | 2.1 | SITE #13 LOT 328
6420619 | FOXWOOD FARMS | DBP | 2950 | TOTAL THMS | D | 15.39 | UG/L | 80.4999 | 2015-07-31 | L1 |  |  |  | 2.1 | SITE #13 LOT 328
6420619 | FOXWOOD FARMS | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-08-05 | AAA
6420619 | FOXWOOD FARMS | INOR | 1040 | NITRATE | N | 0.66 | MG/L | 10.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1010 | BARIUM | N | 0.0055 | MG/L | 2.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1025 | FLUORIDE | N | 0.28 | MG/L | 4.0499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1052 | SODIUM | N | 12 | MG/L | 160.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1005 | ARSENIC | N | 0.0006 | MG/L | 0.0104 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1017 | CHLORIDE | N | 19 | MG/L | 250.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1025 | FLUORIDE | N | 0.28 | MG/L | 2.0499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1055 | SULFATE | N | 64 | MG/L | 250.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.34 | LN(10) |  | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 350 | MG/L | 500.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-09-29 | AAA |  | 0.5499 |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-09-29 | AAA |  |  |  |  | EXTRA SAMPLES
6420619 | FOXWOOD FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-01-27 | AAA
6420619 | FOXWOOD FARMS | INOR | 1040 | NITRATE | N | 1.1 | MG/L | 10.4999 | 2016-01-27 | AAA
6420619 | FOXWOOD FARMS | INOR | 1040 | NITRATE | N | 0.31 | MG/L | 10.4999 | 2017-06-21 | AAA
6420619 | FOXWOOD FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-06-21 | AAA
6420619 | FOXWOOD FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-07-09 | L1 |  |  |  | 0.3 | SITE #13 LOT 328
6420619 | FOXWOOD FARMS | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2018-07-09 | L1 |  |  |  | 0.3 | SITE #13 LOT 328
6420619 | FOXWOOD FARMS | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | INOR | 1040 | NITRATE | N | 0.78 | MG/L | 10.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1005 | ARSENIC | N | 0.0008 | MG/L | 0.0104 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1010 | BARIUM | N | 0.0035 | MG/L | 2.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1020 | CHROMIUM | N | 0.0029 | MG/L | 0.1499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1024 | CYANIDE | N | 0.0055 | MG/L | 0.2499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1025 | FLUORIDE | N | 0.25 | MG/L | 4.0499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1045 | SELENIUM | N | 0.0012 | MG/L | 0.0549 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1052 | SODIUM | N | 7.5 | MG/L | 160.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1017 | CHLORIDE | N | 11 | MG/L | 250.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1022 | COPPER | N | 0.0073 | MG/L | 1.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1025 | FLUORIDE | N | 0.25 | MG/L | 2.0499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1055 | SULFATE | N | 3.6 | MG/L | 250.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1095 | ZINC | N | 0.015 | MG/L | 5.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.28 | LN(10) |  | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 290 | MG/L | 500.4999 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-10-29 | AAA
6420619 | FOXWOOD FARMS | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499
6420619 | FOXWOOD FARMS | RAD | 4006 | COMBINED URANIUM | N | 0.3 | PCI/L | 20.4999 | 2018-11-29 | AAA |  | 0.667
6420619 | FOXWOOD FARMS | RAD | 4020 | RADIUM-226 | N | 1.3 | PCI/L | 3.4999 | 2018-11-30 | AAA |  | 1.4999
6420619 | FOXWOOD FARMS | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.2 | PCI/L | 15.4999 | 2018-11-30 | AAA
6420619 | FOXWOOD FARMS | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-11-30 | AAA |  | 1.4999
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | D | 7.75 | LN(10) |  | 2019-03-22 | AAA |  |  |  |  | 2283 NW 47 CIR LOT 75
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | N | 220 | MG/L |  | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | N | 7.63 | LN(10) |  | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1919 | HARDNESS - CALCIUM | N | 92 | MG/L | 0 | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | D | 590 | MG/L | 0 | 2019-03-22 | AAA |  |  |  |  | 235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1919 | HARDNESS - CALCIUM | D | 93 | MG/L | 0 | 2019-03-22 | AAA |  |  |  |  | 235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | D | 7.67 | LN(10) |  | 2019-03-22 | AAA |  |  |  |  | 235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | D | 210 | MG/L |  | 2019-03-22 | AAA |  |  |  |  | 235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 24.2 |  |  | 2019-03-22 | AAA |  |  |  |  | 235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 20.3 |  |  | 2019-03-22 | AAA |  |  |  |  | 2283 NW 47 CIR LOT 75
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | D | 580 | MG/L | 0 | 2019-03-22 | AAA |  |  |  |  | 2283 NW 47 CIR LOT 75
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 21.8 |  |  | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1016 | CALCIUM | D | 91 | MG/L |  | 2019-03-22 | AAA |  |  |  |  | 2283 NW 47 CIR LOT 75
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | D | 220 | MG/L |  | 2019-03-22 | AAA |  |  |  |  | 2283 NW 47 CIR LOT 75
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | N | 580 | MG/L | 0 | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1919 | HARDNESS - CALCIUM | N | 94 | MG/L | 0 | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | N | 7.82 | LN(10) |  | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | N | 210 | MG/L |  | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 23.8 |  |  | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | N | 590 | MG/L | 0 | 2019-03-22 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | N | 200 | MG/L |  | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | N | 7.82 | LN(10) |  | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | D | 580 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | 2235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1919 | HARDNESS - CALCIUM | D | 97 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | 2235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | D | 7.67 | LN(10) |  | 2019-06-12 | AAA |  |  |  |  | 2235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | D | 210 | MG/L |  | 2019-06-12 | AAA |  |  |  |  | 2235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 22.5 |  |  | 2019-06-12 | AAA |  |  |  |  | 2235 NW 46 COURT RD LOT 20
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | D | 580 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | 2283 NW 47 CIR. LOT 75
6420619 | FOXWOOD FARMS | WQP | 1919 | HARDNESS - CALCIUM | D | 97 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | 2283 NW 47 CIR. LOT 75
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | D | 7.75 | LN(10) |  | 2019-06-12 | AAA |  |  |  |  | 2283 NW 47 CIR. LOT 75
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | D | 210 | MG/L |  | 2019-06-12 | AAA |  |  |  |  | 2283 NW 47 CIR. LOT 75
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | D | 22.5 |  |  | 2019-06-12 | AAA |  |  |  |  | 2283 NW 47 CIR. LOT 75
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | N | 570 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1919 | HARDNESS - CALCIUM | N | 96 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1924 | pH (FIELD) | N | 7.6 | LN(10) |  | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1927 | TOTAL ALKALINITY | N | 210 | MG/L |  | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.5 |  |  | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 19
6420619 | FOXWOOD FARMS | WQP | 1064 | CONDUCTIVITY | N | 580 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1919 | HARDNESS - CALCIUM | N | 96 | MG/L | 0 | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | WQP | 1996 | TEMPERATURE (Degrees C.) | N | 22.5 |  |  | 2019-06-12 | AAA |  |  |  |  | POE WELL SITE LOT 16
6420619 | FOXWOOD FARMS | INOR | 1040 | NITRATE | N | 0.43 | MG/L | 10.4999 | 2019-06-25 | AAA
6420619 | FOXWOOD FARMS | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-06-25 | AAA
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 6.6 | PCI/L | 15.4999 | 2015-02-12 | WTP6 |  |  |  |  | SUMMERGLEN WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-02-12 | WTP6 |  | 1.4999 |  |  | SUMMERGLEN WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4020 | RADIUM-226 | N | 0.8 | PCI/L | 3.4999 | 2015-02-12 | WTP6 |  | 1.4999 |  |  | SUMMERGLEN WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-20 | WTP3 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.93 | MG/L | 10.4999 | 2015-05-20 | WTP3 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-20 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.48 | MG/L | 10.4999 | 2015-05-20 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-20 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2015-05-20 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-05-20 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0.36 | MG/L | 10.4999 | 2015-05-20 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-06-18 | WTP6 |  |  |  |  | WP 6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.56 | MG/L | 10.4999 | 2015-06-18 | WTP6 |  |  |  |  | WP 6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.97 | UG/L | 60.4999 | 2015-10-19 | L1 |  |  |  | 1.3 | 1754 SW 134TH ST TRACTOR SUPPLY (211 MARION OAKS SLD HAVE BEEN SMPLD. MY ERROR INFORMED SYS OF WRONG SITE. ACCEPTING RSLTS) WILL SAMPLE CORRECT LOC NEXT MONIT PERIOD)11/18/15 EM TO MIKE BRYSON_AMA
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 6.16 | UG/L | 80.4999 | 2015-10-19 | L4 |  |  |  | 1.3 | 13581 SW 17TH CT LIFT STATION SONNY'S
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.66 | UG/L | 60.4999 | 2015-10-19 | L4 |  |  |  | 1.3 | 13581 SW 17TH CT LIFT STATION SONNY'S
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 5.52 | UG/L | 80.4999 | 2015-10-19 | L1 |  |  |  | 1.3 | 1754 SW 134TH ST TRACTOR SUPPLY (211 MARION OAKS SLD HAVE BEEN SMPLD. MY ERROR INFORMED SYS OF WRONG SITE. ACCEPTING RSLTS) WILL SAMPLE CORRECT LOC NEXT MONIT PERIOD)11/18/15 EM TO MIKE BRYSON_AMA
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.6 | MG/L | 10.4999 | 2016-05-17 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-17 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-17 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0.66 | MG/L | 10.4999 | 2016-05-17 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 2.19 | MG/L | 10.4999 | 2016-05-17 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-17 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0.88 | MG/L | 10.4999 | 2016-05-17 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-17 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2016-05-17 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-05-17 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 4.92 | UG/L | 80.4999 | 2016-10-24 | L4 |  |  |  | 1.1 | 13581 SW 17TH CT LIFT STATION SONNY'S
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0.2 | UG/L | 60.4999 | 2016-10-24 | L4 |  |  |  | 1.1 | 13581 SW 17TH CT LIFT STATION SONNY'S
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2016-10-24 | L2 |  |  |  | 1 | 211 MARION OAKS LANE
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2016-10-24 | L2 |  |  |  | 1 | 211 MARION OAKS LANE
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-28 | WTP7 |  | 0.9499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP7 |  | 0.1499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-28 | WTP7 |  | 0.2499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-28 | WTP7 |  | 0.0449 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP7 |  | 0.0249 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-28 | WTP7 |  | 0.1499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-28 | WTP7 |  | 0.2499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP7 |  | 0.1499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP7 |  | 0.0249 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP7 |  | 0.0449 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-28 | WTP7 |  | 0.1499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP7 |  | 0.0249 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-28 | WTP7 |  | 0.0149 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-28 | WTP7 |  | 0.2499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.38 | MG/L | 10.4999 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1005 | ARSENIC | N | 0.0004 | MG/L | 0.0104 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1010 | BARIUM | N | 0.0022 | MG/L | 2.4999 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1020 | CHROMIUM | N | 0.001 | MG/L | 0.1499 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1052 | SODIUM | N | 6.3 | MG/L | 160.4999 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-28 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1017 | CHLORIDE | N | 8 | MG/L | 250.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1022 | COPPER | N | 0.0007 | MG/L | 1.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1032 | MANGANESE | N | 0.0001 | MG/L | 0.0549 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1050 | SILVER | N | 0.0001 | MG/L | 0.1499 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1055 | SULFATE | N | 8.36 | MG/L | 250.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1095 | ZINC | N | 0.0048 | MG/L | 5.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-28 | WTP7 |  | 0.0149 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP7 |  | 0.0249 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-28 | WTP7 |  | 0.1499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP7 |  | 1.4999 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-02-28 | WTP3 |  | 0.0149 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP3 |  | 0.0249 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-02-28 | WTP3 |  | 0.1499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP3 |  | 1.4999 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-28 | WTP3 |  | 1.4999 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-28 | WTP3 |  | 0.4499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP3 |  | 9.4999 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-28 | WTP3 |  | 6.4999 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-28 | WTP3 |  | 0.6499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-28 | WTP3 |  | 2.4999 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-28 | WTP3 |  | 0.0749 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-28 | WTP3 |  | 0.6499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-28 | WTP3 |  | 0.1499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-28 | WTP3 |  | 0.2499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-28 | WTP3 |  | 0.1499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-02-28 | WTP3 |  | 0.9499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-02-28 | WTP3 |  | 0.1499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-02-28 | WTP3 |  | 0.2499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-02-28 | WTP3 |  | 0.0449 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP3 |  | 0.0249 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-02-28 | WTP3 |  | 0.1499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-02-28 | WTP3 |  | 0.2499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP3 |  | 0.1499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP3 |  | 0.0249 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.7 | LN(10) |  | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 150 | MG/L | 500.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-28 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-02-28 | WTP7 |  | 1.4999 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP7 |  | 0.5499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-02-28 | WTP7 |  | 1.4999 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-02-28 | WTP7 |  | 0.4499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-02-28 | WTP7 |  | 9.4999 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-02-28 | WTP7 |  | 6.4999 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-02-28 | WTP7 |  | 0.6499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-02-28 | WTP7 |  | 2.4999 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-02-28 | WTP7 |  | 0.0749 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-02-28 | WTP7 |  | 0.6499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-02-28 | WTP7 |  | 0.1499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-02-28 | WTP7 |  | 0.2499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-02-28 | WTP7 |  | 0.1499 |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP3 |  | 0.0449 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-02-28 | WTP3 |  | 0.1499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-02-28 | WTP3 |  | 0.0249 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-02-28 | WTP3 |  | 0.0149 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-02-28 | WTP3 |  | 0.2499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.93 | MG/L | 10.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1005 | ARSENIC | N | 0.0004 | MG/L | 0.0104 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1010 | BARIUM | N | 0.0045 | MG/L | 2.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1020 | CHROMIUM | N | 0.0013 | MG/L | 0.1499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1025 | FLUORIDE | N | 0.12 | MG/L | 4.0499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1045 | SELENIUM | N | 0.0006 | MG/L | 0.0549 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1052 | SODIUM | N | 6.1 | MG/L | 160.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6) MERCURY RESULT .000016
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1017 | CHLORIDE | N | 9.1 | MG/L | 250.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1022 | COPPER | N | 0.0007 | MG/L | 1.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1025 | FLUORIDE | N | 0.12 | MG/L | 2.0499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1032 | MANGANESE | N | 0.0001 | MG/L | 0.0549 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1050 | SILVER | N | 0.0001 | MG/L | 0.1499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1055 | SULFATE | N | 42.8 | MG/L | 250.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 224 | MG/L | 500.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0.042 |  | 0.5499 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2017-02-28 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4030 | RADIUM-228 | N | 0.7 | PCI/L | 2.4999 | 2017-02-28 | WTP3 |  | 1.4999 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-02-28 | WTP3 |  | 0.5499 |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-13 | WTP1 |  | 0.0149 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-13 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP1 |  | 1.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-13 | WTP1 |  | 1.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-13 | WTP1 |  | 0.4499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP1 |  | 9.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-13 | WTP1 |  | 6.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-13 | WTP1 |  | 0.6499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-13 | WTP1 |  | 2.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-03-13 | WTP1 |  | 0.0749 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-13 | WTP1 |  | 0.6499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-13 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-13 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-13 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-13 | WTP1 |  | 0.9499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-13 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-13 | WTP1 |  | 0.0449 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-13 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-13 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0.06 | MG/L | 10.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1005 | ARSENIC | N | 0.0023 | MG/L | 0.0104 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1010 | BARIUM | N | 0.0084 | MG/L | 2.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP2 |  | 0.5499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-13 | WTP2 |  | 0.0149 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-13 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP2 |  | 1.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-13 | WTP2 |  | 1.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-13 | WTP2 |  | 0.4499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP2 |  | 9.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-13 | WTP2 |  | 6.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-13 | WTP2 |  | 0.6499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-13 | WTP2 |  | 2.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1025 | FLUORIDE | N | 0.25 | MG/L | 4.0499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1052 | SODIUM | N | 6.2 | MG/L | 160.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1017 | CHLORIDE | N | 8.6 | MG/L | 250.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1022 | COPPER | N | 0.0004 | MG/L | 1.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1025 | FLUORIDE | N | 0.25 | MG/L | 2.0499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1032 | MANGANESE | N | 0.0056 | MG/L | 0.0549 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1050 | SILVER | N | 0.0007 | MG/L | 0.1499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1055 | SULFATE | N | 92.2 | MG/L | 250.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1095 | ZINC | N | 0.0095 | MG/L | 5.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.5 | LN(10) |  | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 315 | MG/L | 500.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0.059 |  | 0.5499 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 3.4 | PCI/L | 15.4999 | 2017-03-13 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4030 | RADIUM-228 | N | 0.8 | PCI/L | 2.4999 | 2017-03-13 | WTP1 |  | 1.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-03-13 | WTP2 |  | 0.0749 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-13 | WTP2 |  | 0.6499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-13 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-13 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-13 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-13 | WTP2 |  | 0.9499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-13 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-13 | WTP2 |  | 0.0449 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-13 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-13 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP2 |  | 0.0449 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-13 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-13 | WTP2 |  | 0.0149 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-13 | WTP1 |  | 0.5499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-13 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1017 | CHLORIDE | N | 9.6 | MG/L | 250.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1022 | COPPER | N | 0.0003 | MG/L | 1.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1025 | FLUORIDE | N | 0.16 | MG/L | 2.0499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1032 | MANGANESE | N | 0.002 | MG/L | 0.0549 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1050 | SILVER | N | 0.0002 | MG/L | 0.1499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-13 | WTP1 |  | 0.0449 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-13 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-13 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-13 | WTP1 |  | 0.0149 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-13 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.44 | MG/L | 10.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1005 | ARSENIC | N | 0.0005 | MG/L | 0.0104 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1010 | BARIUM | N | 0.0072 | MG/L | 2.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1020 | CHROMIUM | N | 0.001 | MG/L | 0.1499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1025 | FLUORIDE | N | 0.16 | MG/L | 4.0499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1045 | SELENIUM | N | 0.0006 | MG/L | 0.0549 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1052 | SODIUM | N | 6.7 | MG/L | 160.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1055 | SULFATE | N | 94.6 | MG/L | 250.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1095 | ZINC | N | 0.0048 | MG/L | 5.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.5 | LN(10) |  | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 310 | MG/L | 500.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0.05 |  | 0.5499 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.6 | PCI/L | 15.4999 | 2017-03-13 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4030 | RADIUM-228 | N | 1.9 | PCI/L | 2.4999 | 2017-03-13 | WTP2 |  | 1.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-03-14 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-03-14 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-03-14 | WTP6 |  | 0.0149 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-03-14 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1032 | MANGANESE | N | 0.0041 | MG/L | 0.0549 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1055 | SULFATE | N | 188 | MG/L | 250.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 8 | LN(10) |  | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 488 | MG/L | 500.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 2905 | FOAMING AGENTS | N | 0.055 |  | 0.5499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1017 | CHLORIDE | N | 14 | MG/L | 250.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1022 | COPPER | N | 0.0089 | MG/L | 1.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1025 | FLUORIDE | N | 0.24 | MG/L | 2.0499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0.59 | MG/L | 10.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1005 | ARSENIC | N | 0.0002 | MG/L | 0.0104 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1010 | BARIUM | N | 0.012 | MG/L | 2.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1020 | CHROMIUM | N | 0.0004 | MG/L | 0.1499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1025 | FLUORIDE | N | 0.24 | MG/L | 4.0499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1052 | SODIUM | N | 10 | MG/L | 160.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP (WTP6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 2.8 | PCI/L | 15.4999 | 2017-03-14 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2017-03-14 | WTP6 |  | 1.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2017-03-14 | WTP6 |  | 0.5499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-03-14 | WTP6 |  | 0.0149 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-03-14 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-03-14 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-03-14 | WTP6 |  | 1.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-03-14 | WTP6 |  | 1.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-03-14 | WTP6 |  | 0.4499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-03-14 | WTP6 |  | 9.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-03-14 | WTP6 |  | 6.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-03-14 | WTP6 |  | 0.6499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-03-14 | WTP6 |  | 2.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-03-14 | WTP6 |  | 0.0749 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-03-14 | WTP6 |  | 0.6499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-03-14 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-03-14 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-03-14 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-03-14 | WTP6 |  | 0.9499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-03-14 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-03-14 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-03-14 | WTP6 |  | 0.0449 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-03-14 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-03-14 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-03-14 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-03-14 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-03-14 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-03-14 | WTP6 |  | 0.0449 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP3 |  | 0.1499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP3 |  | 1.4999 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP3 |  | 1.4999 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-17 | WTP3 |  | 0.4499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-17 | WTP3 |  | 9.4999 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-17 | WTP3 |  | 6.4999 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-17 | WTP3 |  | 0.6499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP3 |  | 2.4999 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-17 | WTP3 |  | 0.0749 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-17 | WTP3 |  | 0.6499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-17 | WTP3 |  | 0.1499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-17 | WTP3 |  | 0.2499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP3 |  | 0.1499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP3 |  | 0.9499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP3 |  | 0.1499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP3 |  | 0.2499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-17 | WTP3 |  | 0.0449 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP3 |  | 0.0249 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-17 | WTP3 |  | 0.1499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP3 |  | 0.2499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP3 |  | 0.1499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP3 |  | 0.0249 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP3 |  | 0.0449 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-17 | WTP3 |  | 0.1499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP3 |  | 0.0249 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-17 | WTP7 |  | 0.0749 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP3 |  | 0.2499 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-17 | WTP7 |  | 0.6499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-17 | WTP7 |  | 0.1499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-17 | WTP7 |  | 0.2499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP7 |  | 0.1499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP7 |  | 0.9499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP7 |  | 0.1499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP7 |  | 0.2499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-17 | WTP7 |  | 0.0449 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP7 |  | 0.0249 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-17 | WTP7 |  | 0.1499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-17 | WTP7 |  | 0.2499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP7 |  | 0.1499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP7 |  | 0.0249 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-17 | WTP7 |  | 0.0449 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-17 | WTP7 |  | 0.1499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP7 |  | 0.0249 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-17 | WTP7 |  | 0.0149 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP7 |  | 0.2499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP7 |  | 0.0149 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP7 |  | 0.0249 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-17 | WTP7 |  | 0.1499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-17 | WTP7 |  | 1.4999 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP7 |  | 1.4999 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-17 | WTP7 |  | 0.4499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-17 | WTP7 |  | 9.4999 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-17 | WTP7 |  | 6.4999 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-17 | WTP7 |  | 0.6499 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-17 | WTP7 |  | 2.4999 |  |  | RECEIVED 2/20/18 (ORIGINAL SUBMITTAL LIKELY MISPLACED BY FDEP OFFICE -- ATR)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-17 | WTP3 |  | 0.0249 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-17 | WTP3 |  | 0.0149 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-17 | WTP3 |  | 0.0149 |  |  | WELL 6
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-18 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-18 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-18 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-18 | WTP6 |  | 0.9499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-18 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-18 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-18 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-18 | WTP6 |  | 0.6499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-18 | WTP6 |  | 0.0449 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-18 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-18 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-18 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-18 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-18 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-18 | WTP6 |  | 0.0449 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-18 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-18 | WTP6 |  | 0.0249 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-18 | WTP6 |  | 0.0149 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-18 | WTP6 |  | 0.2499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-18 | WTP6 |  | 0.0149 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-18 | WTP6 |  | 0.1499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-18 | WTP6 |  | 1.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-18 | WTP6 |  | 1.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-18 | WTP6 |  | 0.4499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-18 | WTP6 |  | 9.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-18 | WTP6 |  | 6.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-18 | WTP6 |  | 0.6499 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-18 | WTP6 |  | 2.4999 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-18 | WTP6 |  | 0.0749 |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-23 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-23 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-23 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-23 | WTP2 |  | 0.0449 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-23 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-23 | WTP2 |  | 0.0149 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-23 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-23 | WTP1 |  | 0.0149 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-23 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-23 | WTP1 |  | 1.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-23 | WTP1 |  | 1.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-23 | WTP1 |  | 0.4499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-23 | WTP1 |  | 9.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-23 | WTP1 |  | 6.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-23 | WTP1 |  | 0.6499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-23 | WTP1 |  | 2.4999 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-23 | WTP1 |  | 0.0749 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-23 | WTP1 |  | 0.6499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-23 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-23 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-23 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-23 | WTP1 |  | 0.9499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-23 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-23 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-23 | WTP1 |  | 0.0449 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2017-05-23 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2017-05-23 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2017-05-23 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2017-05-23 | WTP1 |  | 0.0449 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2017-05-23 | WTP1 |  | 0.1499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP1 |  | 0.0249 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2017-05-23 | WTP1 |  | 0.0149 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2017-05-23 | WTP1 |  | 0.2499 |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2017-05-23 | WTP2 |  | 0.0149 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2017-05-23 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2017-05-23 | WTP2 |  | 1.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2017-05-23 | WTP2 |  | 1.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2017-05-23 | WTP2 |  | 0.4499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2017-05-23 | WTP2 |  | 9.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2017-05-23 | WTP2 |  | 6.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2017-05-23 | WTP2 |  | 0.6499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2017-05-23 | WTP2 |  | 2.4999 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2017-05-23 | WTP2 |  | 0.0749 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2017-05-23 | WTP2 |  | 0.6499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2017-05-23 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2017-05-23 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2017-05-23 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2017-05-23 | WTP2 |  | 0.9499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2017-05-23 | WTP2 |  | 0.1499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2017-05-23 | WTP2 |  | 0.2499 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2017-05-23 | WTP2 |  | 0.0449 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2017-05-23 | WTP2 |  | 0.0249 |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 2.21 | UG/L | 80.4999 | 2017-10-18 | L2 |  |  |  | 1 | 211 MARION OAKS LANE
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 1.26 | UG/L | 60.4999 | 2017-10-18 | L4 |  |  |  | 0.8 | 13581 SW 17TH CT LIFT STATION SONNY'S
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 11.14 | UG/L | 80.4999 | 2017-10-18 | L4 |  |  |  | 0.8 | 13581 SW 17TH CT LIFT STATION SONNY'S
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2017-10-18 | L2 |  |  |  | 1 | 211 MARION OAKS LANE
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.46 | MG/L | 10.4999 | 2018-05-15 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | WTP6 |  |  |  |  | SUMMERGLEN C.C. WP
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.48 | MG/L | 10.4999 | 2018-05-15 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1 | MG/L | 10.4999 | 2018-05-15 | WTP7 |  |  |  |  | WP7 (TIMBERWALK)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 2.46 | MG/L | 10.4999 | 2018-05-15 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | WTP3 |  |  |  |  | WP6 (WELL 6)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2018-05-15 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | WTP1 |  |  |  |  | WP4 (WELL 4)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-05-15 | WTP2 |  |  |  |  | WP5 (WELL 5)
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-11-14 | L2 |  |  | 2 | 1 | 2950-211 MARION OAKS LANE / SUBCONTRACT LABS E82574 AND E82535
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 3.51 | UG/L | 80.4999 | 2018-11-14 | L4 |  |  | 1 | 1.1 | 2950-13581 SW 17TH CT LIFT STATION SONNY'S / SUBCONTRACT LABS E82574 AND E82535
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 0.49 | UG/L | 80.4999 | 2018-11-14 | L2 |  |  | 2 | 1 | 2950-211 MARION OAKS LANE / SUBCONTRACT LABS E82574 AND E82535
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.34 | UG/L | 60.4999 | 2018-11-14 | L4 |  |  | 1 | 1.1 | 2950-13581 SW 17TH CT LIFT STATION SONNY'S / SUBCONTRACT LABS E82574 AND E82535
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-14 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.59 | MG/L | 10.4999 | 2019-05-14 | WTP3
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-14 | WTP3
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-05-14 | WTP1
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-14 | WTP1
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 1.44 | MG/L | 10.4999 | 2019-05-14 | WTP2
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-14 | WTP2
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 2.66 | MG/L | 10.4999 | 2019-05-14 | WTP3
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-14 | WTP3
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | INOR | 1040 | NITRATE | N | 0.25 | MG/L | 10.4999 | 2019-05-14 | WTP7
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 5.84 | UG/L | 80.4999 | 2019-11-14 | L4 | 0.56 |  | 1 | 0.9 | 135881 SW 17TH CT
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.06 | UG/L | 60.4999 | 2019-11-14 | L4 | 0.91 |  | 1 | 0.9 | 135881 SW 17TH CT
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2950 | TOTAL THMS | D | 1.75 | UG/L | 80.4999 | 2019-11-14 | L2 | 0.56 |  | 1 | 1.1 | 211 MARION OAKS
6421144 | MARION OAKS SUBDIVISION (5 WTPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2019-11-14 | L2 | 0.91 |  | 1 | 1.1 | 211 MARION OAKS
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.73 | MG/L | 10.4999 | 2015-01-12 | 6421512-2 |  |  |  |  | WELL # 2 NORTH PLANT (WTP/WELL #6 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.94 | MG/L | 10.4999 | 2015-01-12 | 6421512-1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-12 | 6421512-1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-12 | 6421512-2 |  |  |  |  | WELL # 2 NORTH PLANT (WTP/WELL #6 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP2 |  | 0.1499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-08-18 | WTP2 |  | 0.2499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-08-18 | WTP2 |  | 0.0449 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP2 |  | 0.0249 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-08-18 | WTP1 |  | 0.0149 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP1 |  | 0.0249 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-08-18 | WTP1 |  | 0.1499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP1 |  | 1.4999 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-08-18 | WTP1 |  | 1.4999 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-08-18 | WTP1 |  | 0.4499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP1 |  | 9.4999 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-08-18 | WTP1 |  | 6.4999 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-08-18 | WTP1 |  | 0.6499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-08-18 | WTP1 |  | 2.4999 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-08-18 | WTP1 |  | 0.0749 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-08-18 | WTP1 |  | 0.6499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-08-18 | WTP1 |  | 0.1499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 1.4 | MG/L | 10.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1010 | BARIUM | N | 0.0048 | MG/L | 2.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1020 | CHROMIUM | N | 0.0016 | MG/L | 0.1499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.089 | MG/L | 4.0499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1036 | NICKEL | N | 0.0012 | MG/L | 0.1499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1052 | SODIUM | N | 4.2 | MG/L | 160.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 1 | MG/L | 10.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-08-18 | WTP2 |  | 0.1499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-08-18 | WTP2 |  | 0.2499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP2 |  | 0.1499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP2 |  | 0.0249 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP2 |  | 0.0449 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-08-18 | WTP2 |  | 0.1499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP2 |  | 0.0249 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-08-18 | WTP2 |  | 0.0149 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-08-18 | WTP2 |  | 0.2499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 5.7 | PCI/L | 15.4999 | 2015-08-18 | WTP2 |  |  |  |  | (CORRECTED WELL NAMES AND LOCATION DESCRIPTIONS IN PWS SYSTEM DATABASE 6/27/17 - AR)
6421512 | RIO VISTA (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-08-18 | WTP2 |  | 1.4999 |  |  | (CORRECTED WELL NAMES AND LOCATION DESCRIPTIONS IN PWS SYSTEM DATABASE 6/27/17 - AR)
6421512 | RIO VISTA (2 WPS) | RAD | 4020 | RADIUM-226 | N | 0.5 | PCI/L | 3.4999 | 2015-08-18 | WTP2 | 0.5 | 1.4999 |  |  | (CORRECTED WELL NAMES AND LOCATION DESCRIPTIONS IN PWS SYSTEM DATABASE 6/27/17 - AR)
6421512 | RIO VISTA (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1017 | CHLORIDE | N | 7.7 | MG/L | 250.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1022 | COPPER | N | 0.0024 | MG/L | 1.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.089 | MG/L | 2.0499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-08-18 | WTP1 |  | 0.2499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-08-18 | WTP1 |  | 0.1499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-08-18 | WTP1 |  | 0.9499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP1 |  | 0.1499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-08-18 | WTP1 |  | 0.2499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-08-18 | WTP1 |  | 0.0449 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP1 |  | 0.0249 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-08-18 | WTP1 |  | 0.1499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-08-18 | WTP1 |  | 0.2499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP1 |  | 0.1499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP1 |  | 0.0249 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP1 |  | 0.0449 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-08-18 | WTP1 |  | 0.1499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP1 |  | 0.0249 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-08-18 | WTP1 |  | 0.0149 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1028 | IRON | N | 0.34 | MG/L | 0.3499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1032 | MANGANESE | N | 0.026 | MG/L | 0.0549 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1055 | SULFATE | N | 26 | MG/L | 250.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1095 | ZINC | N | 0.035 | MG/L | 5.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.3 | LN(10) |  | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 130 | MG/L | 500.4999 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-08-18 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP2 |  | 0.5499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-08-18 | WTP2 |  | 0.0149 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-08-18 | WTP2 |  | 0.0249 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-08-18 | WTP2 |  | 0.1499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP2 |  | 1.4999 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-08-18 | WTP2 |  | 1.4999 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-08-18 | WTP2 |  | 0.4499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP2 |  | 9.4999 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-08-18 | WTP2 |  | 6.4999 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-08-18 | WTP2 |  | 0.6499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-08-18 | WTP2 |  | 2.4999 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-08-18 | WTP2 |  | 0.0749 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-08-18 | WTP2 |  | 0.6499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-08-18 | WTP2 |  | 0.1499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-08-18 | WTP2 |  | 0.2499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-08-18 | WTP2 |  | 0.1499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-08-18 | WTP2 |  | 0.9499 |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.06 | UG/L | 60.4999 | 2015-08-18 | L1 |  |  |  | 0.5 | 10300 SW 186TH AVE.
6421512 | RIO VISTA (2 WPS) | DBP | 2950 | TOTAL THMS | D | 12.22 | UG/L | 80.4999 | 2015-08-18 | L1 |  |  |  | 0.5 | 10300 SW 186TH AVE.
6421512 | RIO VISTA (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-08-18 | WTP1 |  | 0.2499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1010 | BARIUM | N | 0.0044 | MG/L | 2.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1020 | CHROMIUM | N | 0.0011 | MG/L | 0.1499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.096 | MG/L | 4.0499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1036 | NICKEL | N | 0.0011 | MG/L | 0.1499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1052 | SODIUM | N | 4.9 | MG/L | 160.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1 SOUTH PLANT (WTP/WELL #5 ON CHEM REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1017 | CHLORIDE | N | 8.6 | MG/L | 250.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.096 | MG/L | 2.0499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1028 | IRON | N | 0.065 | MG/L | 0.3499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1032 | MANGANESE | N | 0.0017 | MG/L | 0.0549 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1055 | SULFATE | N | 34 | MG/L | 250.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1095 | ZINC | N | 0.036 | MG/L | 5.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1905 | COLOR | N | 5.7 | COLOR UNITS | 15.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.4 | LN(10) |  | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 150 | MG/L | 500.4999 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-08-18 | WTP1 |  |  |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-08-18 | WTP1 |  | 0.5499 |  |  | WELL # 1
6421512 | RIO VISTA (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-08-19 | WTP1 |  |  |  |  | (CORRECTED WELL NAMES AND LOCATION DESCRIPTIONS IN PWS SYSTEM DATABASE 6/27/17 - AR)
6421512 | RIO VISTA (2 WPS) | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-08-19 | WTP1 |  | 1.4999 |  |  | (CORRECTED WELL NAMES AND LOCATION DESCRIPTIONS IN PWS SYSTEM DATABASE 6/27/17 - AR)
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-03-14 | WTP1 |  |  |  |  | WTP1 WELL # 1 WELL #5 ON CHEM REPORT
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.33 | MG/L | 10.4999 | 2016-03-14 | WTP1 |  |  |  |  | WTP1 WELL # 1 WELL #5 ON CHEM REPORT
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-04-04 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.28 | MG/L | 10.4999 | 2016-04-04 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2016-08-15 | L1 |  |  |  | 0.5 | 10300 SW 186TH AVE.
6421512 | RIO VISTA (2 WPS) | DBP | 2950 | TOTAL THMS | D | 1.17 | UG/L | 80.4999 | 2016-08-15 | L1 |  |  |  | 0.5 | 10300 SW 186TH AVE.
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.7 | MG/L | 10.4999 | 2017-03-06 | WTP1 |  |  |  |  | WTP1 WELL # 1 WELL #5 ON CHEM REPORT
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-06 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.64 | MG/L | 10.4999 | 2017-03-06 | WTP2 |  |  |  |  | WELL # 2 (WELL 6 ON REPORT)
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-06 | WTP1 |  |  |  |  | WTP1 WELL # 1 WELL #5 ON CHEM REPORT
6421512 | RIO VISTA (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2017-08-21 | L1 |  |  | RVT1 | 0.61 | 10300 SW 186TH AVE. (ENTERED 5/25/18--NOT REQUIRED TRI-ANNUAL WAIVER (ATR))
6421512 | RIO VISTA (2 WPS) | DBP | 2950 | TOTAL THMS | D | 1.01 | UG/L | 80.4999 | 2017-08-21 | L1 |  |  | RVT1 | 0.61 | 10300 SW 186TH AVE. (ENTERED 5/25/18--NOT REQUIRED TRI-ANNUAL WAIVER (ATR))
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 1 | MG/L | 10.4999 | 2018-02-05 | WTP1 |  |  |  |  | WELL # 5
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-05 | WTP1 |  |  |  |  | WELL # 5
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 1.1 | MG/L | 10.4999 | 2018-02-05 | WTP2
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-05 | WTP2
6421512 | RIO VISTA (2 WPS) | DBP | 2950 | TOTAL THMS | D | 1.18 | UG/L | 80.4999 | 2018-08-06 | L1 | 0.39 |  | 1 | 0.88 | 10300 SW 186TH AVE. (HLKD 8/27/18)
6421512 | RIO VISTA (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-08-06 | L1 | 0.89 |  | 1 | 0.88 | 10300 SW 186TH AVE. (HLKD 8/27/18)
6421512 | RIO VISTA (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-08-09 | WTP2 |  | 0.1499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP2 |  | 0.0249 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-08-09 | WTP2 |  | 0.0149 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-08-09 | WTP2 |  | 0.2499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1085 | THALLIUM | N | 0.0002 | MG/L | 0.0025 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1017 | CHLORIDE | N | 17 | MG/L | 250.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1022 | COPPER | N | 0.014 | MG/L | 1.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.19 | MG/L | 2.0499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1028 | IRON | N | 0.14 | MG/L | 0.3499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1032 | MANGANESE | N | 0.057 | MG/L | 0.0549 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1055 | SULFATE | N | 29 | MG/L | 250.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1095 | ZINC | N | 0.2 | MG/L | 5.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.84 | LN(10) |  | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 160 | MG/L | 500.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | INOR | 1005 | ARSENIC | N | 0.0004 | MG/L | 0.0104 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1010 | BARIUM | N | 0.0048 | MG/L | 2.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP2 |  | 0.5499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82535
6421512 | RIO VISTA (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-08-09 | WTP2 |  | 2.4999 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-08-09 | WTP2 |  | 0.0149 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP2 |  | 0.0249 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-08-09 | WTP2 |  | 0.1499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP2 |  | 1.4999 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-08-09 | WTP2 |  | 1.4999 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-08-09 | WTP2 |  | 0.4499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP2 |  | 9.4999 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-08-09 | WTP2 |  | 6.4999 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-08-09 | WTP2 |  | 0.6499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-08-09 | WTP2 |  | 0.0749 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-08-09 | WTP2 |  | 0.6499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-08-09 | WTP2 |  | 0.1499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-08-09 | WTP2 |  | 0.2499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-08-09 | WTP2 |  | 0.1499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-08-09 | WTP2 |  | 0.9499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP2 |  | 0.1499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-08-09 | WTP2 |  | 0.2499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-08-09 | WTP2 |  | 0.0449 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP2 |  | 0.0249 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-08-09 | WTP2 |  | 0.1499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-08-09 | WTP2 |  | 0.2499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP2 |  | 0.1499 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP2 |  | 0.0249 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP2 |  | 0.0449 |  |  | WELL # 6 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.62 | LN(10) |  | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 200 | MG/L | 500.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 2905 | FOAMING AGENTS | N | 0.04 |  | 0.5499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP1 |  | 0.5499 |  |  | WELL # 5 - SUBCONTRACT LAB E82535
6421512 | RIO VISTA (2 WPS) | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-08-09 | WTP1 |  | 0.1499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-08-09 | WTP1 |  | 0.2499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP1 |  | 0.1499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP1 |  | 0.0249 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-08-09 | WTP1 |  | 0.0449 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-08-09 | WTP1 |  | 0.1499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP1 |  | 0.0249 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-08-09 | WTP1 |  | 0.0149 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-08-09 | WTP1 |  | 0.2499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-08-09 | WTP1 |  | 0.0149 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP1 |  | 0.0249 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-08-09 | WTP1 |  | 0.1499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP1 |  | 1.4999 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-08-09 | WTP1 |  | 1.4999 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-08-09 | WTP1 |  | 0.4499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-08-09 | WTP1 |  | 9.4999 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-08-09 | WTP1 |  | 6.4999 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-08-09 | WTP1 |  | 0.6499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-08-09 | WTP1 |  | 2.4999 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-08-09 | WTP1 |  | 0.0749 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-08-09 | WTP1 |  | 0.6499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-08-09 | WTP1 |  | 0.1499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-08-09 | WTP1 |  | 0.2499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0.014 | UG/L | 54.9999 | 2018-08-09 | WTP1 |  | 0.1499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-08-09 | WTP1 |  | 0.9499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-08-09 | WTP1 |  | 0.1499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-08-09 | WTP1 |  | 0.2499 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-08-09 | WTP1 |  | 0.0449 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-08-09 | WTP1 |  | 0.0249 |  |  | WELL # 5 - SUBCONTRACTED LAB E82574
6421512 | RIO VISTA (2 WPS) | INOR | 1005 | ARSENIC | N | 0.0001 | MG/L | 0.0104 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1010 | BARIUM | N | 0.0077 | MG/L | 2.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1020 | CHROMIUM | N | 0.0002 | MG/L | 0.1499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.19 | MG/L | 4.0499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1030 | LEAD | N | 0.0011 | MG/L | 0.0154 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1052 | SODIUM | N | 10 | MG/L | 160.4999 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-08-09 | WTP2 |  |  |  |  | WELL # 6 - SUBCONTRACTED LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1020 | CHROMIUM | N | 0.0014 | MG/L | 0.1499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1025 | FLUORIDE | N | 0.22 | MG/L | 4.0499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1030 | LEAD | N | 0.0009 | MG/L | 0.0154 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1045 | SELENIUM | N | 0.0008 | MG/L | 0.0549 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1052 | SODIUM | N | 6.2 | MG/L | 160.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E84589 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1017 | CHLORIDE | N | 13 | MG/L | 250.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1022 | COPPER | N | 0.0058 | MG/L | 1.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1025 | FLUORIDE | N | 0.22 | MG/L | 2.0499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1028 | IRON | N | 0.1 | MG/L | 0.3499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1032 | MANGANESE | N | 0.0019 | MG/L | 0.0549 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1055 | SULFATE | N | 38 | MG/L | 250.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1095 | ZINC | N | 0.056 | MG/L | 5.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1905 | COLOR | N | 5 | COLOR UNITS | 15.4999 | 2018-08-09 | WTP1 |  |  |  |  | WELL # 5 - SUBCONTRACT LABS E82574 E53076
6421512 | RIO VISTA (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-08-21 | WTP2
6421512 | RIO VISTA (2 WPS) | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-08-21 | WTP1 |  |  |  |  | WELL # 5
6421512 | RIO VISTA (2 WPS) | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-08-30 | WTP1 |  |  |  |  | WELL # 5
6421512 | RIO VISTA (2 WPS) | SEC | 1032 | MANGANESE | N | 0.26 | MG/L | 0.0549 | 2018-08-30 | WTP2 |  |  |  |  | WELL # 6
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-05 | WTP2 |  |  |  |  | WELL #6
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-05 | WTP1 |  |  |  |  | WELL#5
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.69 | MG/L | 10.4999 | 2019-02-05 | WTP1 |  |  |  |  | WELL#5
6421512 | RIO VISTA (2 WPS) | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-05 | WTP1 |  |  |  |  | WELL#5
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.69 | MG/L | 10.4999 | 2019-02-05 | WTP1 |  |  |  |  | WELL#5
6421512 | RIO VISTA (2 WPS) | INOR | 1040 | NITRATE | N | 0.67 | MG/L | 10.4999 | 2019-02-05 | WTP2 |  |  |  |  | WELL #6
6421952 | MHP OCALA AIR LLC | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | RAD | 4020 | RADIUM-226 | N | 0.6 | PCI/L | 3.4999 | 2015-07-08 | AAA |  | 1.4999
6421952 | MHP OCALA AIR LLC | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-07-08 | AAA |  | 1.4999
6421952 | MHP OCALA AIR LLC | INOR | 1040 | NITRATE | N | 1.8 | MG/L | 10.4999 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1005 | ARSENIC | N | 0.0004 | MG/L | 0.0104 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1010 | BARIUM | N | 0.0048 | MG/L | 2.4999 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1020 | CHROMIUM | N | 0.0014 | MG/L | 0.1499 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1025 | FLUORIDE | N | 0.18 | MG/L | 4.0499 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1036 | NICKEL | N | 0.0019 | MG/L | 0.1499 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1052 | SODIUM | N | 10 | MG/L | 160.4999 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1074 | ANTIMONY | N | 0.0011 | MG/L | 0.0065 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-08 | AAA |  |  |  |  | 3YR OK
6421952 | MHP OCALA AIR LLC | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1017 | CHLORIDE | N | 17 | MG/L | 250.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1022 | COPPER | N | 0.0021 | MG/L | 1.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1025 | FLUORIDE | N | 0.18 | MG/L | 2.0499 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1032 | MANGANESE | N | 0.0004 | MG/L | 0.0549 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1055 | SULFATE | N | 72 | MG/L | 250.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1095 | ZINC | N | 0.014 | MG/L | 5.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 6.8 | LN(10) |  | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 300 | MG/L | 500.4999 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-08 | AAA
6421952 | MHP OCALA AIR LLC | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-08 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2015-08-19 | L1 |  |  |  | 0.52 | LOT #50
6421952 | MHP OCALA AIR LLC | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2015-08-19 | L1 |  |  |  | 0.52 | LOT #50
6421952 | MHP OCALA AIR LLC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-08-24 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1040 | NITRATE | N | 2 | MG/L | 10.4999 | 2016-08-24 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1040 | NITRATE | N | 1.5 | MG/L | 10.4999 | 2017-10-26 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-10-26 | AAA
6421952 | MHP OCALA AIR LLC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-07-10 | L1 | 0.52 |  | 1 | 0.7 | LOT #50 (HLKD 8-16-18 - BB)
6421952 | MHP OCALA AIR LLC | DBP | 2950 | TOTAL THMS | D | 0.88 | UG/L | 80.4999 | 2018-07-10 | L1 | 0.14 |  | 1 | 0.7 | LOT #50 (HLKD 8-16-18 - BB)
6421952 | MHP OCALA AIR LLC | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1025 | FLUORIDE | N | 0 | MG/L | 4.0499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1052 | SODIUM | N | 11 | MG/L | 160.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1017 | CHLORIDE | N | 13 | MG/L | 250.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1022 | COPPER | N | 0.0076 | MG/L | 1.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1025 | FLUORIDE | N | 0 | MG/L | 2.0499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1055 | SULFATE | N | 52 | MG/L | 250.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1095 | ZINC | N | 0.0078 | MG/L | 5.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 6.87 | LN(10) |  | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 330 | MG/L | 500.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-11-20 | AAA |  | 0.5499
6421952 | MHP OCALA AIR LLC | INOR | 1010 | BARIUM | N | 0.0039 | MG/L | 2.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1005 | ARSENIC | N | 0.0002 | MG/L | 0.0104 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1040 | NITRATE | N | 1.8 | MG/L | 10.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-11-20 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-08 | AAA
6421952 | MHP OCALA AIR LLC | INOR | 1040 | NITRATE | N | 1.9 | MG/L | 10.4999 | 2019-05-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1095 | ZINC | N | 0.022 | MG/L | 5.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 6.8 | LN(10) |  | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 340 | MG/L | 500.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-08 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 0 | PCI/L | 15.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | RAD | 4020 | RADIUM-226 | N | 1.1 | PCI/L | 3.4999 | 2015-07-08 | AAA |  | 1.4999
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-07-08 | AAA |  | 1.4999
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1040 | NITRATE | N | 1 | MG/L | 10.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1010 | BARIUM | N | 0.005 | MG/L | 2.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1020 | CHROMIUM | N | 0.0011 | MG/L | 0.1499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1025 | FLUORIDE | N | 0.31 | MG/L | 4.0499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1036 | NICKEL | N | 0.0025 | MG/L | 0.1499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1052 | SODIUM | N | 15 | MG/L | 160.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1074 | ANTIMONY | N | 0.0005 | MG/L | 0.0065 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1017 | CHLORIDE | N | 29 | MG/L | 250.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1022 | COPPER | N | 0.0029 | MG/L | 1.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1025 | FLUORIDE | N | 0.31 | MG/L | 2.0499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1032 | MANGANESE | N | 0.0004 | MG/L | 0.0549 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1055 | SULFATE | N | 52 | MG/L | 250.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 1.63 | UG/L | 60.4999 | 2015-08-18 | L1 |  |  |  | 0.4 | LOT 125
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | DBP | 2950 | TOTAL THMS | D | 20.09 | UG/L | 80.4999 | 2015-08-18 | L1 |  |  |  | 0.4 | LOT 125
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1040 | NITRATE | N | 1.3 | MG/L | 10.4999 | 2016-08-24 | AAA |  |  |  |  | 16 DONE
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-08-24 | AAA |  |  |  |  | 16 DONE
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-10-26 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1040 | NITRATE | N | 1.2 | MG/L | 10.4999 | 2017-10-26 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 310 | MG/L | 500.4999 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.38 | LN(10) |  | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 3 | PCI/L | 15.4999 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2018-02-27 | AAA |  | 1.4999
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1040 | NITRATE | N | 1.5 | MG/L | 10.4999 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1005 | ARSENIC | N | 0.0002 | MG/L | 0.0104 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1010 | BARIUM | N | 0.0049 | MG/L | 2.4999 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1025 | FLUORIDE | N | 0.21 | MG/L | 4.0499 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1052 | SODIUM | N | 12 | MG/L | 160.4999 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-02-27 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1017 | CHLORIDE | N | 25 | MG/L | 250.4999 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1025 | FLUORIDE | N | 0.21 | MG/L | 2.0499 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1055 | SULFATE | N | 44 | MG/L | 250.4999 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1095 | ZINC | N | 0 | MG/L | 5.4999 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-02-27 | AAA |  |  |  |  | FOAMING AGENTS NOT ENTERED NO LAB CERT# ON LAB REPORT- RCVD REVISION 5/15/18--FOAMING AGENTS UPDATED.
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 2.47 | UG/L | 60.4999 | 2018-07-10 | L1 | 0.52 |  | 1 | 1
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | DBP | 2950 | TOTAL THMS | D | 14.69 | UG/L | 80.4999 | 2018-07-10 | L1 | 0.14 |  | 1 | 1
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1040 | NITRATE | N | 1.6 | MG/L | 10.4999 | 2019-05-08 | AAA
6422359 | OAK TREE VILLAGE APTS & CAMPGROUND | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-05-08 | AAA
6422362 | ARROWHEAD CAMPSITES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-05-20 | AAA |  | 0.5499 |  |  | 1AM/DIC (3AM FOR 2014 WAS NOT DONE-MONITORING TO BEGIN AGAIN) (2AM 7-9/2016)
6422362 | ARROWHEAD CAMPSITES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 3.95 | UG/L | 60.4999 | 2015-08-19 | L1 |  |  |  | 0.77 | LOT #139
6422362 | ARROWHEAD CAMPSITES | DBP | 2950 | TOTAL THMS | D | 3.22 | UG/L | 80.4999 | 2015-08-19 | L1 |  |  |  | 0.77 | LOT #139
6422362 | ARROWHEAD CAMPSITES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1052 | SODIUM | N | 6.3 | MG/L | 160.4999 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1025 | FLUORIDE | N | 0.16 | MG/L | 4.0499 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1020 | CHROMIUM | N | 0.0014 | MG/L | 0.1499 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1005 | ARSENIC | N | 0.0004 | MG/L | 0.0104 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1040 | NITRATE | N | 1.13 | MG/L | 10.4999 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | INOR | 1010 | BARIUM | N | 0.0031 | MG/L | 2.4999 | 2015-09-28 | AAA |  |  |  |  | 3YR OK
6422362 | ARROWHEAD CAMPSITES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.6 | LN(10) |  | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 283 | MG/L | 500.4999 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1017 | CHLORIDE | N | 11 | MG/L | 250.4999 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1095 | ZINC | N | 0.034 | MG/L | 5.4999 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1055 | SULFATE | N | 27.9 | MG/L | 250.4999 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1022 | COPPER | N | 0.0017 | MG/L | 1.4999 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | SEC | 1025 | FLUORIDE | N | 0.15 | MG/L | 2.0499 | 2015-10-28 | AAA |  |  |  |  | 3YR OK (8/31/17 NOTE BY BB: NEW REPLACEMENT WEST WELL 3 ACCEPTANCE LETTER 6/1/17 ASKS FOR CHL IRON MANGANESE TESTS NO SOONER THAN 6 WKS AFTER PLACEMENT INTO SERVICE & BEFORE 6 MONTHS ENDS.)
6422362 | ARROWHEAD CAMPSITES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-11-30 | AAA |  | 1.4999 |  |  | DUE 2018
6422362 | ARROWHEAD CAMPSITES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 1.9 | PCI/L | 15.4999 | 2015-11-30 | AAA |  |  |  |  | DUE 2018
6422362 | ARROWHEAD CAMPSITES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2016-03-28 | AAA |  | 0.5499 |  |  | 2AM(3AM 7-9/2017) 8/31/17 NOTE ADDED BY BB: REPLACEMENT WEST WELL 3 CLRNC CHEMS (ACCEPTED FOR SVC 6/1/17) HAD DIC>MCL TCE>MCL BUT ACCEPTANCE LTR DID NOT ASK FOR ADDITIONAL TESTING FOR THESE.
6422362 | ARROWHEAD CAMPSITES | INOR | 1040 | NITRATE | N | 1.15 | MG/L | 10.4999 | 2016-12-27 | AAA |  |  |  |  | 16 DONE
6422362 | ARROWHEAD CAMPSITES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-12-27 | AAA |  |  |  |  | 16 DONE
6422362 | ARROWHEAD CAMPSITES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2017-10-25 | AAA |  | 0.5499 |  |  | 1025/17 IS 3RD YR NO DETECTIONS (ATR)
6422362 | ARROWHEAD CAMPSITES | SEC | 1017 | CHLORIDE | N | 5.4 | MG/L | 250.4999 | 2017-10-25 | AAA |  |  |  |  | CHLORIDE LAB E82001
6422362 | ARROWHEAD CAMPSITES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2017-10-25 | AAA |  |  |  |  | CHLORIDE LAB E82001
6422362 | ARROWHEAD CAMPSITES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2017-10-25 | AAA |  |  |  |  | CHLORIDE LAB E82001
6422362 | ARROWHEAD CAMPSITES | INOR | 1041 | NITRITE | S | 0 | MG/L | 1.4999 | 2018-02-21 | AAA |  |  |  |  | MAKE-UP SAMPLE FOR FAILURE TO MONITOR DURING 2017 (ATR)
6422362 | ARROWHEAD CAMPSITES | INOR | 1040 | NITRATE | S | 1.16 | MG/L | 10.4999 | 2018-02-21 | AAA |  |  |  |  | MAKE-UP SAMPLE FOR FAILURE TO MONITOR DURING 2017 (ATR)
6422362 | ARROWHEAD CAMPSITES | DBP | 2950 | TOTAL THMS | D | 22.12 | UG/L | 80.4999 | 2018-08-27 | L1 | 0.39 |  | 1 | 0.93
6422362 | ARROWHEAD CAMPSITES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 7.02 | UG/L | 60.4999 | 2018-08-27 | L1 | 0.89 |  | 1 | 0.93
6422362 | ARROWHEAD CAMPSITES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2018-11-07 | AAA |  | 0.0149
6422362 | ARROWHEAD CAMPSITES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2018-11-07 | AAA |  | 0.0249
6422362 | ARROWHEAD CAMPSITES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-11-07 | AAA |  | 0.1499
6422362 | ARROWHEAD CAMPSITES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 1.4999
6422362 | ARROWHEAD CAMPSITES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-11-07 | AAA |  | 1.4999
6422362 | ARROWHEAD CAMPSITES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-11-07 | AAA |  | 0.4499
6422362 | ARROWHEAD CAMPSITES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-11-07 | AAA |  | 9.4999
6422362 | ARROWHEAD CAMPSITES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2018-11-07 | AAA |  | 6.4999
6422362 | ARROWHEAD CAMPSITES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2018-11-07 | AAA |  | 0.6499
6422362 | ARROWHEAD CAMPSITES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2018-11-07 | AAA |  | 2.4999
6422362 | ARROWHEAD CAMPSITES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2018-11-07 | AAA |  | 0.0749
6422362 | ARROWHEAD CAMPSITES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2018-11-07 | AAA |  | 0.6499
6422362 | ARROWHEAD CAMPSITES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2018-11-07 | AAA |  | 0.1499
6422362 | ARROWHEAD CAMPSITES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2018-11-07 | AAA |  | 0.2499
6422362 | ARROWHEAD CAMPSITES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1017 | CHLORIDE | N | 9.2 | MG/L | 250.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1022 | COPPER | N | 0.0012 | MG/L | 1.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1025 | FLUORIDE | N | 0.19 | MG/L | 2.0499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1032 | MANGANESE | N | 0 | MG/L | 0.0549 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1055 | SULFATE | N | 24 | MG/L | 250.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1095 | ZINC | N | 0.026 | MG/L | 5.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.51 | LN(10) |  | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 293 | MG/L | 500.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | INOR | 1040 | NITRATE | N | 1.2 | MG/L | 10.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1005 | ARSENIC | N | 0.0004 | MG/L | 0.0104 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1010 | BARIUM | N | 0.0032 | MG/L | 2.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2018-11-07 | AAA |  | 0.1499
6422362 | ARROWHEAD CAMPSITES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2018-11-07 | AAA |  | 0.9499
6422362 | ARROWHEAD CAMPSITES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.1499
6422362 | ARROWHEAD CAMPSITES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2018-11-07 | AAA |  | 0.2499
6422362 | ARROWHEAD CAMPSITES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2018-11-07 | AAA |  | 0.0449
6422362 | ARROWHEAD CAMPSITES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2018-11-07 | AAA |  | 0.0249
6422362 | ARROWHEAD CAMPSITES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2018-11-07 | AAA |  | 0.1499
6422362 | ARROWHEAD CAMPSITES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2018-11-07 | AAA |  | 0.2499
6422362 | ARROWHEAD CAMPSITES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2018-11-07 | AAA |  | 0.1499
6422362 | ARROWHEAD CAMPSITES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2018-11-07 | AAA |  | 0.0249
6422362 | ARROWHEAD CAMPSITES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2018-11-07 | AAA |  | 0.0449
6422362 | ARROWHEAD CAMPSITES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2018-11-07 | AAA |  | 0.1499
6422362 | ARROWHEAD CAMPSITES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2018-11-07 | AAA |  | 0.0249
6422362 | ARROWHEAD CAMPSITES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2018-11-07 | AAA |  | 0.0149
6422362 | ARROWHEAD CAMPSITES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2018-11-07 | AAA |  | 0.2499
6422362 | ARROWHEAD CAMPSITES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-11-07 | AAA |  | 0.5499
6422362 | ARROWHEAD CAMPSITES | INOR | 1025 | FLUORIDE | N | 0.19 | MG/L | 4.0499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1052 | SODIUM | N | 8.2 | MG/L | 160.4999 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-11-07 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1040 | NITRATE | N | 0 | MG/L | 10.4999 | 2019-02-25 | AAA
6422362 | ARROWHEAD CAMPSITES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2019-02-25 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-01-12 | AAA |  |  |  |  | 15 DONE
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1040 | NITRATE | N | 0.32 | MG/L | 10.4999 | 2015-01-12 | AAA |  |  |  |  | 15 DONE
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2005 | ENDRIN | N | 0 | UG/L | 2.4999 | 2015-07-13 | AAA |  | 0.0149
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2010 | LINDANE | N | 0 | UG/L | 0.2499 | 2015-07-13 | AAA |  | 0.0249
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2015-07-13 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2015-07-13 | AAA |  | 1.4999
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2015-07-13 | AAA |  | 1.4999
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2015-07-13 | AAA |  | 0.4499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2015-07-13 | AAA |  | 9.4999
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2034 | GLYPHOSATE | N | 0 | UG/L | 749.9999 | 2015-07-13 | AAA |  | 6.4999
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | N | 0 | UG/L | 449.9999 | 2015-07-13 | AAA |  | 0.6499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2036 | OXAMYL (VYDATE) | N | 0 | UG/L | 249.9999 | 2015-07-13 | AAA |  | 2.4999
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2037 | SIMAZINE | N | 0 | UG/L | 4.4999 | 2015-07-13 | AAA |  | 0.0749
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | N | 0 | UG/L | 6.4999 | 2015-07-13 | AAA |  | 0.6499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2040 | PICLORAM | N | 0 | UG/L | 549.9999 | 2015-07-13 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2041 | DINOSEB | N | 0 | UG/L | 7.4999 | 2015-07-13 | AAA |  | 0.2499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | N | 0 | UG/L | 54.9999 | 2015-07-13 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2046 | CARBOFURAN | N | 0 | UG/L | 44.9999 | 2015-07-13 | AAA |  | 0.9499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2050 | ATRAZINE | N | 0 | UG/L | 3.4999 | 2015-07-13 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2051 | ALACHLOR (LASSO) | N | 0 | UG/L | 2.4999 | 2015-07-13 | AAA |  | 0.2499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2065 | HEPTACHLOR | N | 0 | UG/L | 0.4499 | 2015-07-13 | AAA |  | 0.0449
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2067 | HEPTACHLOR EPOXIDE | N | 0 | UG/L | 0.2499 | 2015-07-13 | AAA |  | 0.0249
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2105 | 2 4-D | N | 0 | UG/L | 74.9999 | 2015-07-13 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2110 | 2 4 5-TP (Silvex) | N | 0 | UG/L | 54.9999 | 2015-07-13 | AAA |  | 0.2499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2274 | HEXACHLOROBENZENE | N | 0 | UG/L | 1.4999 | 2015-07-13 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2306 | BENZO(A)PYRENE | N | 0 | UG/L | 0.2499 | 2015-07-13 | AAA |  | 0.0249
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2326 | PENTACHLOROPHENOL | N | 0 | UG/L | 1.4999 | 2015-07-13 | AAA |  | 0.0449
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | N | 0 | UG/L | 0.5499 | 2015-07-13 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | N | 0 | UG/L | 0.2499 | 2015-07-13 | AAA |  | 0.0249
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2946 | ETHYLENE DIBROMIDE | N | 0 | UG/L | 0.0249 | 2015-07-13 | AAA |  | 0.0149
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2959 | CHLORDANE | N | 0 | UG/L | 2.4999 | 2015-07-13 | AAA |  | 0.2499
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2015-07-13 | L1 |  |  |  | 0.7 | 9996 SW 188TH CIR.
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2950 | TOTAL THMS | D | 0.47 | UG/L | 80.4999 | 2015-07-13 | L1 |  |  |  | 0.7 | 9996 SW 188TH CIR.
6422679 | RAINBOW SPRINGS CC ESTATES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | N | 6.6 | PCI/L | 15.4999 | 2015-07-13 | AAA |  |  |  |  | DUE 2021 SIMPLIFIED. (GA & UR 2021 RADIUM 2024)
6422679 | RAINBOW SPRINGS CC ESTATES | RAD | 4020 | RADIUM-226 | N | 0 | PCI/L | 3.4999 | 2015-07-13 | AAA |  | 1.4999 |  |  | DUE 2021 SIMPLIFIED. (GA & UR 2021 RADIUM 2024)
6422679 | RAINBOW SPRINGS CC ESTATES | RAD | 4030 | RADIUM-228 | N | 0 | PCI/L | 2.4999 | 2015-07-13 | AAA |  | 1.4999 |  |  | DUE 2021 SIMPLIFIED. (GA & UR 2021 RADIUM 2024)
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1005 | ARSENIC | N | 0 | MG/L | 0.0104 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1010 | BARIUM | N | 0 | MG/L | 2.4999 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1020 | CHROMIUM | N | 0 | MG/L | 0.1499 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1025 | FLUORIDE | N | 0.078 | MG/L | 4.0499 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1036 | NICKEL | N | 0.004 | MG/L | 0.1499 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1052 | SODIUM | N | 2.8 | MG/L | 160.4999 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1074 | ANTIMONY | N | 0.0004 | MG/L | 0.0065 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2015-07-13 | AAA |  |  |  |  | MERCURY/E84589 J4 QUALIFIER. % RECOVERY MS/65% & MSD/72%. ACCEPTABLE FOR COMPLIANCE. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2015-07-13 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1040 | NITRATE | N | 0.69 | MG/L | 10.4999 | 2015-07-13 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2015-07-13 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1017 | CHLORIDE | N | 7.3 | MG/L | 250.4999 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1022 | COPPER | N | 0 | MG/L | 1.4999 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1025 | FLUORIDE | N | 0.078 | MG/L | 2.0499 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1032 | MANGANESE | N | 0.0005 | MG/L | 0.0549 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1050 | SILVER | N | 0 | MG/L | 0.1499 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1055 | SULFATE | N | 12 | MG/L | 250.4999 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1095 | ZINC | N | 0.014 | MG/L | 5.4999 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | N | 7.2 | LN(10) |  | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | N | 110 | MG/L | 500.4999 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-07-13 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001. ALL HAD Q QUALIFIERS. 8/24/15 EM TO JULIO GRANADOS TO RESAMPLE FOR EACH. AMA
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2015-07-13 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1920 | ODOR THRESHOLD | N | 0 |  | 3.4999 | 2015-09-09 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001 7/13/15 RESULTS Q QUALIFIERS
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1905 | COLOR | N | 0 | COLOR UNITS | 15.4999 | 2015-09-09 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001 7/13/15 RESULTS Q QUALIFIERS
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 2905 | FOAMING AGENTS | N | 0 |  | 0.5499 | 2015-09-09 | AAA |  |  |  |  | COLOR & ODOR/E84589 FOAMING AGENTS/E82001 7/13/15 RESULTS Q QUALIFIERS
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1040 | NITRATE | N | 0.33 | MG/L | 10.4999 | 2016-03-14 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2016-03-14 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2016-08-15 | L1 |  |  |  | 0.6 | 9996 SW 188TH CIR.
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2950 | TOTAL THMS | D | 0.42 | UG/L | 80.4999 | 2016-08-15 | L1 |  |  |  | 0.6 | 9996 SW 188TH CIR.
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2017-03-06 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1040 | NITRATE | N | 0.61 | MG/L | 10.4999 | 2017-03-06 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2950 | TOTAL THMS | D | 0 | UG/L | 80.4999 | 2017-08-21 | L1 |  |  |  | 1.17 | 9996 SW 188TH CIR.
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2017-08-21 | L1 |  |  |  | 1.17 | 9996 SW 188TH CIR.
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1041 | NITRITE | N | 0 | MG/L | 1.4999 | 2018-02-06 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1040 | NITRATE | N | 0.63 | MG/L | 10.4999 | 2018-02-06 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2950 | TOTAL THMS | D | 0.39 | UG/L | 80.4999 | 2018-08-06 | L1 | 0.39 |  | 1 | 1.17 | 9996 SW 188TH CIR. (HLKD 8-27-18)
6422679 | RAINBOW SPRINGS CC ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | D | 0 | UG/L | 60.4999 | 2018-08-06 | L1 | 0.89 |  | 1 | 1.17 | 9996 SW 188TH CIR. (HLKD 8-27-18)
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2378 | 1 2 4-TRICHLOROBENZENE | N | 0 | UG/L | 74.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2380 | CIS-1 2-DICHLOROETHYLENE | N | 0 | UG/L | 74.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2955 | TOT XYLENE | N | 0 | UG/L | 10499.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2964 | DICHLOROMETHANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2968 | 1 2-DICHLOROBENZENE | N | 0 | UG/L | 649.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2969 | P-DICHLOROBENZENE | N | 0 | UG/L | 75.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2976 | VINYL CHLORIDE | N | 0 | UG/L | 1.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2977 | 1 1-DICHLOROETHENE | N | 0 | UG/L | 7.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2979 | TRANS-1 2-DICHLOROETHENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2980 | 1 2-DICHLOROETHANE | N | 0 | UG/L | 3.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2981 | 1 1 1-TRICHLOROETHANE | N | 0 | UG/L | 249.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | N | 0 | UG/L | 3.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2983 | 1 2-DICHLOROPROPANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2984 | TRICHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2985 | 1 1 2-TRICHLOROETHANE | N | 0 | UG/L | 5.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2989 | CHLOROBENZENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2990 | BENZENE | N | 0 | UG/L | 1.4999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2991 | TOLUENE | N | 0 | UG/L | 1499.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2992 | ETHYLBENZENE | N | 0 | UG/L | 749.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | VOC | 2996 | STYRENE | N | 0 | UG/L | 149.9999 | 2018-08-09 | AAA |  | 0.5499
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1005 | ARSENIC | N | 0.0002 | MG/L | 0.0104 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1010 | BARIUM | N | 0.002 | MG/L | 2.4999 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1015 | CADMIUM | N | 0 | MG/L | 0.0055 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1020 | CHROMIUM | N | 0.0007 | MG/L | 0.1499 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1024 | CYANIDE | N | 0 | MG/L | 0.2499 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1025 | FLUORIDE | N | 0.18 | MG/L | 4.0499 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1030 | LEAD | N | 0 | MG/L | 0.0154 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1035 | MERCURY | N | 0 | MG/L | 0.0024 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1036 | NICKEL | N | 0 | MG/L | 0.1499 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1045 | SELENIUM | N | 0 | MG/L | 0.0549 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1052 | SODIUM | N | 4.2 | MG/L | 160.4999 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1074 | ANTIMONY | N | 0 | MG/L | 0.0065 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1075 | BERYLLIUM | N | 0 | MG/L | 0.0045 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | INOR | 1085 | THALLIUM | N | 0 | MG/L | 0.0025 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1002 | ALUMINUM | N | 0 | MG/L | 0.2499 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1017 | CHLORIDE | N | 10 | MG/L | 250.4999 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1022 | COPPER | N | 0.0093 | MG/L | 1.4999 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1025 | FLUORIDE | N | 0.18 | MG/L | 2.0499 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | SEC | 1028 | IRON | N | 0 | MG/L | 0.3499 | 2018-08-09 | AAA
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2015 | METHOXYCLOR | N | 0 | UG/L | 44.9999 | 2018-08-09 | AAA |  | 0.1499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2020 | TOXAPHENE | N | 0 | UG/L | 3.4999 | 2018-08-09 | AAA |  | 1.4999
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2031 | DALAPON | N | 0 | UG/L | 249.9999 | 2018-08-09 | AAA |  | 1.4999
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2032 | DIQUAT | N | 0 | UG/L | 24.9999 | 2018-08-09 | AAA |  | 0.4499
6422679 | RAINBOW SPRINGS CC ESTATES | SOC | 2033 | ENDOTHALL | N | 0 | UG/L | 149.9999 | 2018-08-09 | AAA |  | 9.4999