3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2021-03-31 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-03-31 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-03-31 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-03-31 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.3 | MG/L | 0 | 2021-03-31 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-03-31 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-03-31 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2021-03-31 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-03-31 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-03-31 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2021-03-31 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-03-31 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-03-31 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.99 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.28 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.02 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.84 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2021-04-14 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2021-04-14 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-04-14 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2021-04-14 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-04-14 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-04-14 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2021-04-14 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-04-14 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-04-14 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-04-14 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2021-04-14 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-04-14 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2021-04-14 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-04-14 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-04-14 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2021-04-14 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2021-04-14 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-04-14 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2021-04-14 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-04-14 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-04-14 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-14 | WTP11 | 0.5 | 0.6499 | SW WP PHTHALATE (EXTRA)
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.4 | MG/L | 0 | 2021-04-28 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-04-28 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2021-04-28 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-04-28 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-04-28 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-04-28 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 45.3 | MG/L | 0 | 2021-04-28 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2021-04-28 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-04-28 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2021-04-28 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-04-28 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-04-28 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2021-04-28 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-04-28 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-04-28 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2021-04-28 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-04-28 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-04-28 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 31.9 | MG/L | 0 | 2021-04-28 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-04-28 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-04-28 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.79 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.49 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.05 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.62 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.63 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.98 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.71 | UG/L | 60.4999 | 2021-05-07 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 45.33 | UG/L | 80.4999 | 2021-05-07 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.3 | UG/L | 60.4999 | 2021-05-07 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 56.28 | UG/L | 80.4999 | 2021-05-07 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.07 | UG/L | 60.4999 | 2021-05-07 | L6 | 2 |  | 5512 BAYSIDE DR. (6/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 35.63 | UG/L | 80.4999 | 2021-05-07 | L6 | 0.12 |  | 5512 BAYSIDE DR. (6/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.99 | UG/L | 60.4999 | 2021-05-07 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 57.69 | UG/L | 80.4999 | 2021-05-07 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.11 | UG/L | 60.4999 | 2021-05-07 | L5 | 2 |  | LANDSTAR (BLVD.) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 65.71 | UG/L | 80.4999 | 2021-05-07 | L5 | 0.12 |  | LANDSTAR (BLVD.) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.16 | UG/L | 60.4999 | 2021-05-07 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 66.27 | UG/L | 80.4999 | 2021-05-07 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.9 | MG/L | 0 | 2021-05-12 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-05-12 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2021-05-12 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2021-05-12 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-12 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-05-12 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2021-05-12 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-05-12 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-05-12 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.4 | MG/L | 0 | 2021-05-12 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-05-12 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-05-12 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2021-05-12 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-12 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-05-12 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.6 | MG/L | 0 | 2021-05-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-05-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-05-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 31.6 | MG/L | 0 | 2021-05-12 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-05-12 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-05-12 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-05-26 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2021-05-26 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2021-05-26 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-05-26 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2021-05-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-05-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-05-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2021-05-26 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-26 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-05-26 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-05-26 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-26 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-05-26 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-05-26 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2021-05-26 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-05-26 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2021-05-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-05-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-05-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2021-05-26 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-26 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.28 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE SW POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.33 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.87 | UG/L | 60.4999 | 2021-06-07 | L7 |  |  | BROMATE HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.12 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.52 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.7 | MG/L | 0 | 2021-06-09 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-06-09 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-06-09 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2021-06-09 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-06-09 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-06-09 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2021-06-09 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-06-09 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-06-09 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2021-06-09 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-06-09 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-06-09 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2021-06-09 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-06-09 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-06-09 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-06-09 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2021-06-09 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-06-09 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.5 | MG/L | 0 | 2021-06-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-06-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-06-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.3 | MG/L | 0 | 2021-06-23 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-06-23 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-06-23 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2021-06-23 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-06-23 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2021-06-23 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2021-06-23 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-06-23 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-06-23 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.4 | MG/L | 0 | 2021-06-23 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-06-23 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2021-06-23 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.1 | MG/L | 0 | 2021-06-23 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-06-23 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-06-23 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-06-23 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2021-06-23 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-06-23 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2021-06-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-06-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-06-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.08 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.88 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 6.85 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.74 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.69 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.26 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-07-06 | WTP11 | 0.5 | 0.6499 | SW WP PHTHALATE (EXTRA) HLKD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.7 | MG/L | 0 | 2021-07-07 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-07 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-07-07 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.8 | MG/L | 0 | 2021-07-07 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-07-07 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-07-07 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2021-07-07 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-07-07 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-07-07 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 45.1 | MG/L | 0 | 2021-07-07 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-07-07 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-07-07 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2021-07-07 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-07-07 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-07-07 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2021-07-07 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-07 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-07-07 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 31.8 | MG/L | 0 | 2021-07-07 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-07-07 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-07-07 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.5 | MG/L | 0 | 2021-07-21 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-07-21 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-07-21 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2021-07-21 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-07-21 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-07-21 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2021-07-21 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-07-21 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-07-21 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 44 | MG/L | 0 | 2021-07-21 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-07-21 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-07-21 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2021-07-21 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-07-21 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-07-21 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-07-21 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-07-21 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-07-21 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 31.5 | MG/L | 0 | 2021-07-21 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2021-07-21 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-07-21 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.86 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | SW POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.24 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | KIRKMAN POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.69 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | PINE HILLS POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 7.68 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | HIGHLAND POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.27 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | NAVY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.71 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | CONWAY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.13 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | SKY LAKE POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.26 | UG/L | 60.4999 | 2021-08-02 | L1 |  |  | SMP PT 10 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 20.91 | UG/L | 80.4999 | 2021-08-02 | L1 |  |  | SMP PT 10 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.6 | UG/L | 60.4999 | 2021-08-02 | L2 |  |  | SMP PT 23 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 58.93 | UG/L | 80.4999 | 2021-08-02 | L2 |  |  | SMP PT 23 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.62 | UG/L | 60.4999 | 2021-08-02 | L3 |  |  | SMP PT 169 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 62.5 | UG/L | 80.4999 | 2021-08-02 | L3 |  |  | SMP PT 169 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.74 | UG/L | 60.4999 | 2021-08-02 | L4 |  |  | SMP PT SE5 LAKE NONA
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 67.51 | UG/L | 80.4999 | 2021-08-02 | L4 |  |  | SMP PT SE5 LAKE NONA
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.28 | UG/L | 60.4999 | 2021-08-02 | L5 |  |  | SMP PT 124 LANDSTAR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 66.19 | UG/L | 80.4999 | 2021-08-02 | L5 |  |  | SMP PT 124 LANDSTAR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.43 | UG/L | 60.4999 | 2021-08-02 | L6 |  |  | SMP PT 121 BAYSIDE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 38.98 | UG/L | 80.4999 | 2021-08-02 | L6 |  |  | SMP PT 121 BAYSIDE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2021-08-04 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2021-08-04 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-08-04 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-08-04 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-08-04 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-08-04 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-08-04 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-08-04 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-08-04 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.9 | MG/L | 0 | 2021-08-04 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-08-04 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-08-04 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34 | MG/L | 0 | 2021-08-04 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-08-04 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2021-08-04 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-08-04 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-08-04 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-08-04 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.7 | MG/L | 0 | 2021-08-04 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-08-04 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-08-04 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.3 | MG/L | 0 | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-08-18 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-08-18 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-08-18 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-08-18 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-08-18 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-08-18 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2021-08-18 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-08-18 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2021-08-18 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2021-08-18 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-08-18 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-08-18 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2021-08-18 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-08-18 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2021-08-18 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.9 | MG/L | 0 | 2021-09-01 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-09-01 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-09-01 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2021-09-01 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-09-01 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2021-09-01 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2021-09-01 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-09-01 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-09-01 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.6 | MG/L | 0 | 2021-09-01 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-09-01 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-09-01 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.6 | MG/L | 0 | 2021-09-01 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-09-01 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-09-01 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2021-09-01 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-09-01 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-09-01 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.8 | MG/L | 0 | 2021-09-01 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-09-01 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-09-01 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.01 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.03 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.16 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.14 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.68 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.18 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.1 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - SKY LAKE (HLKD) 9/21 BROMATE RAA ALREADY HLKD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2021-09-15 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-09-15 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-09-15 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2021-09-15 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-09-15 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-09-15 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2021-09-15 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2021-09-15 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-09-15 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2021-09-15 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-09-15 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2021-09-15 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2021-09-15 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-09-15 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-09-15 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-09-15 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-09-15 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-09-15 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.2 | MG/L | 0 | 2021-09-15 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2021-09-15 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-09-15 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.2 | MG/L | 0 | 2021-09-29 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-09-29 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-09-29 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-09-29 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2021-09-29 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-09-29 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2021-09-29 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-09-29 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-09-29 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-09-29 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-09-29 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-09-29 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 32.6 | MG/L | 0 | 2021-09-29 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-09-29 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2021-09-29 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-09-29 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-09-29 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-09-29 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.5 | MG/L | 0 | 2021-09-29 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-29 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-09-29 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.81 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - SW
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.68 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.12 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.03 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.8 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.98 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.09 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2021-10-13 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2021-10-13 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-10-13 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2021-10-13 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-10-13 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-10-13 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-10-13 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-10-13 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-10-13 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.8 | MG/L | 0 | 2021-10-13 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2021-10-13 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-10-13 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2021-10-13 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-10-13 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-10-13 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-10-13 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-13 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-10-13 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.9 | MG/L | 0 | 2021-10-13 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-10-13 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-10-13 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2021-10-27 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-10-27 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-10-27 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2021-10-27 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-10-27 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-10-27 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-10-27 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-10-27 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-10-27 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 45 | MG/L | 0 | 2021-10-27 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-10-27 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-10-27 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 33.9 | MG/L | 0 | 2021-10-27 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-10-27 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-10-27 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2021-10-27 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-10-27 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-10-27 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2021-10-27 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-10-27 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-10-27 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.75 | UG/L | 60.4999 | 2021-11-01 | L1 |  |  | 1642 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 19.72 | UG/L | 80.4999 | 2021-11-01 | L1 |  |  | 1642 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.63 | UG/L | 60.4999 | 2021-11-01 | L2 |  |  | 2714 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 58.43 | UG/L | 80.4999 | 2021-11-01 | L2 |  |  | 2714 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.64 | UG/L | 60.4999 | 2021-11-01 | L3 |  |  | 758 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 58.28 | UG/L | 80.4999 | 2021-11-01 | L3 |  |  | 758 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.56 | UG/L | 60.4999 | 2021-11-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 69.94 | UG/L | 80.4999 | 2021-11-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.95 | UG/L | 60.4999 | 2021-11-01 | L5 |  |  | 124 LANDSTAR RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 68.61 | UG/L | 80.4999 | 2021-11-01 | L5 |  |  | 124 LANDSTAR RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.31 | UG/L | 60.4999 | 2021-11-01 | L6 |  |  | 5512 BAY SIDE DR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 39.91 | UG/L | 80.4999 | 2021-11-01 | L6 |  |  | 5512 BAY SIDE DR
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.99 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | SOUTHWEST BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.36 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.61 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 8.21 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.7 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.07 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.64 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.2 | MG/L | 0 | 2021-11-10 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-11-10 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-11-10 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2021-11-10 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-11-10 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2021-11-10 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-11-10 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-11-10 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-11-10 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.8 | MG/L | 0 | 2021-11-10 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-11-10 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-11-10 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.8 | MG/L | 0 | 2021-11-10 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-11-10 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-11-10 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-11-10 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2021-11-10 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-11-10 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 31.4 | MG/L | 0 | 2021-11-10 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2021-11-10 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-11-10 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-11-23 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.658 | LN(10) |  | 2021-11-23 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-11-23 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2021-11-23 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-11-23 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-11-23 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-11-23 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-11-23 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-11-23 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 44.2 | MG/L | 0 | 2021-11-23 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-11-23 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2021-11-23 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2021-11-23 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-11-23 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-11-23 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-11-23 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-11-23 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-11-23 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 31 | MG/L | 0 | 2021-11-23 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2021-11-23 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-11-23 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.11 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | SW POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.43 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.35 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 10.1 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.67 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.77 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.51 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2021-12-08 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-12-08 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-12-08 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2021-12-08 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-12-08 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-12-08 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-12-08 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-12-08 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-12-08 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.5 | MG/L | 0 | 2021-12-08 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-12-08 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-12-08 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37 | MG/L | 0 | 2021-12-08 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-12-08 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-12-08 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2021-12-08 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-12-08 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-12-08 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30 | MG/L | 0 | 2021-12-08 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-12-08 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-12-08 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2021-12-22 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-12-22 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-12-22 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2021-12-22 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-12-22 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-12-22 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41 | MG/L | 0 | 2021-12-22 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-12-22 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-12-22 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.5 | MG/L | 0 | 2021-12-22 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-12-22 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-12-22 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.5 | MG/L | 0 | 2021-12-22 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-12-22 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-12-22 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-12-22 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-12-22 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-12-22 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2021-12-22 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-12-22 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-12-22 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.08 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.57 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.27 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 8.96 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.62 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.62 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.31 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-01-05 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-01-05 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-01-05 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2022-01-05 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-01-05 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-01-05 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2022-01-05 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2022-01-05 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-01-05 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2022-01-05 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-01-05 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-01-05 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-01-05 | WTP11 |  | 0.6499 | 1 AM POE SW WP [ JQ RESULTS ACCEPTED BASED ON QC_MFC]
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2022-01-05 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-01-05 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-01-05 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2022-01-05 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-01-05 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-01-05 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2022-01-05 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2022-01-05 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-01-05 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-01-19 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2022-01-19 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-01-19 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2022-01-19 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-01-19 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-01-19 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.9 | MG/L | 0 | 2022-01-19 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-01-19 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-01-19 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2022-01-19 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-01-19 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-01-19 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 33.1 | MG/L | 0 | 2022-01-19 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2022-01-19 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-01-19 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2022-01-19 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-01-19 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-01-19 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.3 | MG/L | 0 | 2022-01-19 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2022-01-19 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-01-19 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.49 | UG/L | 60.4999 | 2022-02-01 | L1 |  |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 41.75 | UG/L | 80.4999 | 2022-02-01 | L1 |  |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.03 | UG/L | 60.4999 | 2022-02-01 | L2 |  |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 52.37 | UG/L | 80.4999 | 2022-02-01 | L2 |  |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.58 | UG/L | 60.4999 | 2022-02-01 | L3 |  |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 62.95 | UG/L | 80.4999 | 2022-02-01 | L3 |  |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.43 | UG/L | 60.4999 | 2022-02-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 58.19 | UG/L | 80.4999 | 2022-02-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.76 | UG/L | 60.4999 | 2022-02-01 | L5 |  |  | 124 LANDSTAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 61.08 | UG/L | 80.4999 | 2022-02-01 | L5 |  |  | 124 LANDSTAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.36 | UG/L | 60.4999 | 2022-02-01 | L6 |  |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 32.37 | UG/L | 80.4999 | 2022-02-01 | L6 |  |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.3 | MG/L | 0 | 2022-02-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2022-02-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-02-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.7 | MG/L | 0 | 2022-02-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-02-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-02-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2022-02-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-02-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-02-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2022-02-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-02-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-02-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 32.2 | MG/L | 0 | 2022-02-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-02-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2022-02-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.2 | MG/L | 0 | 2022-02-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2022-02-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-02-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.2 | MG/L | 0 | 2022-02-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-02-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-02-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 9.59 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.34 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | NAVY PPOE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.57 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.33 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.9 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | SOUTHWEST POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.79 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.27 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2022-02-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-02-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-02-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 39.1 | MG/L | 0 | 2022-02-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-02-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-02-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.1 | MG/L | 0 | 2022-02-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-02-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-02-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2022-02-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2022-02-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2022-02-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 33.4 | MG/L | 0 | 2022-02-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-02-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-02-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2022-02-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2022-02-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 137 | MG/L |  | 2022-02-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.1 | MG/L | 0 | 2022-02-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-02-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-02-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-03-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1040 | NITRATE | 0.04 | MG/L | 10.4999 | 2022-03-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2022-03-01 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-03-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2022-03-01 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2022-03-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2022-03-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2022-03-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-03-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-03-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2022-03-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-03-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-03-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 45.2 | MG/L | 0 | 2022-03-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-03-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-03-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2022-03-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2022-03-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2022-03-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2022-03-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2022-03-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-03-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-03-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2022-03-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-03-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.4 | MG/L | 0 | 2022-03-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2022-03-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-03-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.64 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.06 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.6 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | PINE HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 8.74 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.78 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | NAVY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.57 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | CONWAY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.24 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | SKY LAKE POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2022-03-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-03-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-03-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2022-03-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2022-03-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-03-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2022-03-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-03-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-03-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2022-03-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2022-03-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-03-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-03-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2022-03-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-03-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.9 | MG/L | 0 | 2022-03-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2022-03-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-03-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 31.6 | MG/L | 0 | 2022-03-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-03-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-03-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 38.4 | MG/L | 0 | 2022-03-30 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-03-30 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-03-30 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2022-03-30 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-03-30 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-03-30 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 46.2 | MG/L | 0 | 2022-03-30 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-03-30 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-03-30 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2022-03-30 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-03-30 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-03-30 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2022-03-30 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-03-30 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2022-03-30 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2022-03-30 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-03-30 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-03-30 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 32.6 | MG/L | 0 | 2022-03-30 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-03-30 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-03-30 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.45 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | SOUTHWEST ENTRY PPOINT
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.2 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | KIRKMAN ENTRY POINT
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.99 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 8.01 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.25 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.39 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.71 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2022-04-13 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-04-13 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-04-13 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41 | MG/L | 0 | 2022-04-13 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-04-13 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-04-13 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2022-04-13 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-04-13 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-04-13 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2022-04-13 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2022-04-13 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-04-13 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-04-13 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2022-04-13 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-04-13 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2022-04-13 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-04-13 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-04-13 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.6 | MG/L | 0 | 2022-04-13 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-04-13 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-04-13 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2022-04-27 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-04-27 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-04-27 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2022-04-27 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-04-27 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-04-27 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-04-27 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-04-27 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-04-27 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2022-04-27 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-04-27 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-04-27 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-04-27 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-04-27 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-04-27 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2022-04-27 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2022-04-27 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-04-27 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.1 | MG/L | 0 | 2022-04-27 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-04-27 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-04-27 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.43 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.32 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.15 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 8.12 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.5 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.38 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.6 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.96 | UG/L | 60.4999 | 2022-05-02 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 16.73 | UG/L | 80.4999 | 2022-05-02 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.32 | UG/L | 60.4999 | 2022-05-02 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 53.3 | UG/L | 80.4999 | 2022-05-02 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.64 | UG/L | 60.4999 | 2022-05-02 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 53.2 | UG/L | 80.4999 | 2022-05-02 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.1 | UG/L | 60.4999 | 2022-05-02 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 60.54 | UG/L | 80.4999 | 2022-05-02 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.8 | UG/L | 60.4999 | 2022-05-02 | L5 | 2 |  | LANDSTAR BLVD. & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 61.41 | UG/L | 80.4999 | 2022-05-02 | L5 | 0.12 |  | LANDSTAR BLVD. & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.18 | UG/L | 60.4999 | 2022-05-02 | L6 | 2 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 32.97 | UG/L | 80.4999 | 2022-05-02 | L6 | 0.12 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2022-05-11 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-05-11 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-05-11 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2022-05-11 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2022-05-11 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-05-11 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-05-11 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-05-11 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-05-11 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2022-05-11 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2022-05-11 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-05-11 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-05-11 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-05-11 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-05-11 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2022-05-11 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-05-11 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-05-11 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.7 | MG/L | 0 | 2022-05-11 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-05-11 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-05-11 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2022-05-25 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-05-25 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-05-25 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2022-05-25 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-05-25 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-05-25 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 42.3 | MG/L | 0 | 2022-05-25 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-05-25 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-05-25 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2022-05-25 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2022-05-25 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-05-25 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2022-05-25 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-05-25 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-05-25 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2022-05-25 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2022-05-25 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-05-25 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.6 | MG/L | 0 | 2022-05-25 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-05-25 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-05-25 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.99 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.46 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.17 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 7.91 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.95 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.1 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.68 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2022-06-08 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-06-08 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2022-06-08 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2022-06-08 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-06-08 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-06-08 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2022-06-08 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2022-06-08 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-06-08 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-06-08 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2022-06-08 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2022-06-08 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 33.4 | MG/L | 0 | 2022-06-08 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-06-08 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-06-08 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2022-06-08 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-06-08 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-06-08 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 29.3 | MG/L | 0 | 2022-06-08 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-06-08 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-06-08 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-06-22 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-06-22 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-06-22 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2022-06-22 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-06-22 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2022-06-22 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-06-22 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-06-22 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-06-22 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 37.5 | MG/L | 0 | 2022-06-22 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2022-06-22 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-06-22 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 34.6 | MG/L | 0 | 2022-06-22 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-06-22 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-06-22 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2022-06-22 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-06-22 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-06-22 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1919 | HARDNESS - CALCIUM | 30.6 | MG/L | 0 | 2022-06-22 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-06-22 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-06-22 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.06 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.32 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.52 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 8.74 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.95 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.96 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.29 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - SKY LAKE (HLKD)
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.41 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.36 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.32 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 9.53 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.54 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.16 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.18 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - SKYLAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.04 | UG/L | 60.4999 | 2022-08-01 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 24.86 | UG/L | 80.4999 | 2022-08-01 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.04 | UG/L | 60.4999 | 2022-08-01 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 61.33 | UG/L | 80.4999 | 2022-08-01 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.84 | UG/L | 60.4999 | 2022-08-01 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 60.76 | UG/L | 80.4999 | 2022-08-01 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.98 | UG/L | 60.4999 | 2022-08-01 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 67.08 | UG/L | 80.4999 | 2022-08-01 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.84 | UG/L | 60.4999 | 2022-08-01 | L5 | 2 |  | LANDSTAR (BLVD) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 66.16 | UG/L | 80.4999 | 2022-08-01 | L5 | 0.12 |  | LANDSTAR (BLVD) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.71 | UG/L | 60.4999 | 2022-08-01 | L6 | 2 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 37.12 | UG/L | 80.4999 | 2022-08-01 | L6 | 0.12 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.83 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | SOUTHWEST POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.55 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | KIRKMAN POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.97 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | PINE HILLS POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 6.88 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | HIGHLAND POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.31 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.47 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | CONWAY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.78 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | SKY LAKE POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.84 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.4 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.97 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 9.22 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.12 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.74 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.6 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.27 | UG/L | 60.4999 | 2022-11-01 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 44.98 | UG/L | 80.4999 | 2022-11-01 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.32 | UG/L | 60.4999 | 2022-11-01 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 58.57 | UG/L | 80.4999 | 2022-11-01 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.09 | UG/L | 60.4999 | 2022-11-01 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 74.86 | UG/L | 80.4999 | 2022-11-01 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.24 | UG/L | 60.4999 | 2022-11-01 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 66.29 | UG/L | 80.4999 | 2022-11-01 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.06 | UG/L | 60.4999 | 2022-11-01 | L5 | 2 |  | LANDSTAR & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 68.94 | UG/L | 80.4999 | 2022-11-01 | L5 | 0.12 |  | LANDSTAR & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.12 | UG/L | 60.4999 | 2022-11-01 | L6 | 2 |  | 5512 BAYSIDE DR. (12/22 QTR DISINF BYP RPRT RCVD SEPARATELY) HLKD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 2950 | TOTAL THMS | 36.59 | UG/L | 80.4999 | 2022-11-01 | L6 | 0.12 |  | 5512 BAYSIDE DR. (12/22 QTR DISINF BYP RPRT RCVD SEPARATELY) HLKD
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.07 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - SW
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.65 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 0.63 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 8.55 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.49 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.48 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 5.63 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.19 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - SW
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 3.92 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.54 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 11.4 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 1.19 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 2.97 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION (7 WPS) | DBP | 1011 | BROMATE | 4.99 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - SKY LAKE
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.5 | UG/L | 60.4999 | 2018-09-12 | L1 |  |  | LOT #501 (LATE REPORTING, CAN CONTINUE ON TRIENNIAL, NES SAMPLE DUE 2021_VP) | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 36.4 | UG/L | 80.4999 | 2018-09-12 | L1 |  |  | LOT #501 (LATE REPORTING, CAN CONTINUE ON TRIENNIAL, NES SAMPLE DUE 2021_VP) | 2
3481016 | PINE ISLE MOBILE VILLA | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-10-22 | AAA |  |  | MISSING THE REST OF THE INORGANIC CONTAMINANTS. MKAE UP SAMPLES COLLCTED 4/1/19, ENTERED AS S SAMPLE ONCE THEY COME IN _VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-10-22 | AAA |  |  | MISSING THE REST OF THE INORGANIC CONTAMINANTS. MKAE UP SAMPLES COLLCTED 4/1/19, ENTERED AS S SAMPLE ONCE THEY COME IN _VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1025 | FLUORIDE | 0.253 | MG/L | 4.0499 | 2018-10-22 | AAA |  |  | MISSING THE REST OF THE INORGANIC CONTAMINANTS. MKAE UP SAMPLES COLLCTED 4/1/19, ENTERED AS S SAMPLE ONCE THEY COME IN _VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1025 | FLUORIDE | 0.253 | MG/L | 2.0499 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1028 | IRON | 0.0826 | MG/L | 0.3499 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1055 | SULFATE | 20.6 | MG/L | 250.4999 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.24 | LN(10) |  | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 284 | MG/L | 500.4999 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-10-22 | AAA |  | 0.5499
3481016 | PINE ISLE MOBILE VILLA | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-10-22 | AAA |  | 0.0149 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-10-22 | AAA |  | 0.0249 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-10-22 | AAA |  | 0.1499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-10-22 | AAA |  | 1.4999 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-10-22 | AAA |  | 1.4999 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-10-22 | AAA |  | 0.4499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-10-22 | AAA |  | 9.4999 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-10-22 | AAA |  | 6.4999 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-10-22 | AAA |  | 0.6499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-10-22 | AAA |  | 2.4999 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-10-22 | AAA |  | 0.0749 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-10-22 | AAA |  | 0.6499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-10-22 | AAA |  | 0.1499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-10-22 | AAA |  | 0.2499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-10-22 | AAA |  | 0.1499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-10-22 | AAA |  | 0.9499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-10-22 | AAA |  | 0.1499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-10-22 | AAA |  | 0.2499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-10-22 | AAA |  | 0.0449 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-10-22 | AAA |  | 0.0249 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-10-22 | AAA |  | 0.1499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-10-22 | AAA |  | 0.2499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-10-22 | AAA |  | 0.1499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-10-22 | AAA |  | 0.0249 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-10-22 | AAA |  | 0.0449 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-10-22 | AAA |  | 0.1499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-10-22 | AAA |  | 0.0249 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-10-22 | AAA |  | 0.0149 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-10-22 | AAA |  | 0.2499 | 1AM DALAPON (NEXT DUE 4Q19)
3481016 | PINE ISLE MOBILE VILLA | SEC | 1017 | CHLORIDE | 45.7 | MG/L | 250.4999 | 2018-10-22 | AAA |  |  | FLUORIDE. J QUALIFIER (46.7 MG/L) J AUALIFIER TYPO. PROVIDED QA DATA TO BACK UP AND NEW RESULT PAGE_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1010 | BARIUM | 0.0231 | MG/L | 2.4999 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1020 | CHROMIUM | 0.0036 | MG/L | 0.1499 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1052 | SODIUM | 32.7 | MG/L | 160.4999 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2019-03-15 | AAA |  |  | MAKE UP SAMPLES FOR MISSING 18 INORGANICS_VP
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.9 | UG/L | 60.4999 | 2019-09-18 | L1 |  |  | LOT #501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 32.2 | UG/L | 80.4999 | 2019-09-18 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-10-01 | AAA
3481016 | PINE ISLE MOBILE VILLA | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-10-01 | AAA
3481016 | PINE ISLE MOBILE VILLA | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2019-10-09 | AAA |  | 1.4999
3481016 | PINE ISLE MOBILE VILLA | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-08-12 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-08-12 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 67.3 | UG/L | 60.4999 | 2020-09-18 | L1 | 1 |  | LOT 501 TTHM AND HAA5> MCL. MOVE TO Q SAMPLING | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 127 | UG/L | 80.4999 | 2020-09-18 | L1 | 0.5 |  | LOT 501 TTHM AND HAA5> MCL. MOVE TO Q SAMPLING | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.1 | UG/L | 60.4999 | 2020-12-15 | L1 | 1 |  | LOT #501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 55.4 | UG/L | 80.4999 | 2020-12-15 | L1 | 0.5 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.75 | UG/L | 60.4999 | 2021-06-16 | L1 | 0.98 |  | 501 PINE ISLE DR. (PROBABLY LOT #501) NOTE: 3/21 T/H MISSED PER VIOL SCREEN | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 20.24 | UG/L | 80.4999 | 2021-06-16 | L1 | 1 |  | 501 PINE ISLE DR. (PROBABLY LOT #501) NOTE: 3/21 T/H MISSED PER VIOL SCREEN | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.44 | UG/L | 60.4999 | 2021-09-17 | L1 | 0.98 |  | LOT 501 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 25.74 | UG/L | 80.4999 | 2021-09-17 | L1 | 0.39 |  | LOT 501 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.44 | UG/L | 60.4999 | 2021-09-17 | L1 | 0.98 |  | LOT #501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 25.74 | UG/L | 80.4999 | 2021-09-17 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2450 | MONOCHLORACETIC ACID | 1.62 | UG/L |  | 2021-09-17 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2451 | DICHLOROACETIC ACID | 6.47 | UG/L |  | 2021-09-17 | L1 | 0.42 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2452 | TRICHLOROACETIC ACID | 10.06 | UG/L |  | 2021-09-17 | L1 | 0.94 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-09-17 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2454 | DIBROMOACETIC ACID | 1.29 | UG/L |  | 2021-09-17 | L1 | 0.74 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2941 | CHLOROFORM | 16.02 | UG/L | 100 | 2021-09-17 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-09-17 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2943 | BROMODICHLOROMETHANE | 9.72 | UG/L | 100 | 2021-09-17 | L1 | 0.14 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2944 | DIBROMOCHLOROMETHANE | 0 | UG/L | 100 | 2021-09-17 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22 | UG/L | 60.4999 | 2021-09-21 | L2 | 0.98 |  | LOT 607 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 29.06 | UG/L | 80.4999 | 2021-09-21 | L2 | 0.39 |  | LOT 607 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.75 | UG/L | 60.4999 | 2021-11-04 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 30.91 | UG/L | 80.4999 | 2021-11-04 | L2 |  |  | LOT 607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.65 | UG/L | 60.4999 | 2021-11-04 | L1 |  |  | LOT 501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 28.42 | UG/L | 80.4999 | 2021-11-04 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.75 | UG/L | 60.4999 | 2021-11-04 | L2 | 0.98 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 30.91 | UG/L | 80.4999 | 2021-11-04 | L2 | 0.39 |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2450 | MONOCHLORACETIC ACID | 0 | UG/L |  | 2021-11-04 | L2 |  |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2451 | DICHLOROACETIC ACID | 6.96 | UG/L |  | 2021-11-04 | L2 |  |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2452 | TRICHLOROACETIC ACID | 9.17 | UG/L |  | 2021-11-04 | L2 | 0.94 |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-11-04 | L2 |  |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2454 | DIBROMOACETIC ACID | 1.61 | UG/L |  | 2021-11-04 | L2 | 0.74 |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2941 | CHLOROFORM | 17.68 | UG/L | 100 | 2021-11-04 | L2 | 0.39 |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-11-04 | L2 |  |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2943 | BROMODICHLOROMETHANE | 8.56 | UG/L | 100 | 2021-11-04 | L2 | 0.14 |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2944 | DIBROMOCHLOROMETHANE | 4.66 | UG/L | 100 | 2021-11-04 | L2 | 0.32 |  | LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1010 | BARIUM | 0.021 | MG/L | 2.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1025 | FLUORIDE | 0.3 | MG/L | 4.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1052 | SODIUM | 40 | MG/L | 160.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1017 | CHLORIDE | 61 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1025 | FLUORIDE | 0.3 | MG/L | 2.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1055 | SULFATE | 18 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.07 | LN(10) |  | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 309 | MG/L | 500.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SEC | 2905 | FOAMING AGENTS | 0.06 |  | 0.5499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.3 | PCI/L | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-08 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | RAD | 4020 | RADIUM-226 | 1.4 | PCI/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-08 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-08 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.18 | UG/L | 60.4999 | 2021-12-16 | L1 |  |  | LOT 501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 24.02 | UG/L | 80.4999 | 2021-12-16 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.89 | UG/L | 60.4999 | 2021-12-16 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 30.63 | UG/L | 80.4999 | 2021-12-16 | L2 |  |  | LOT 607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.18 | UG/L | 60.4999 | 2021-12-16 | L1 | 0.98 |  | LOT #501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 24.02 | UG/L | 80.4999 | 2021-12-16 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2450 | MONOCHLORACETIC ACID | 2.18 | UG/L |  | 2021-12-16 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2451 | DICHLOROACETIC ACID | 6.9 | UG/L |  | 2021-12-16 | L1 | 0.42 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2452 | TRICHLOROACETIC ACID | 9.15 | UG/L |  | 2021-12-16 | L1 | 0.94 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-12-16 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2454 | DIBROMOACETIC ACID | 0.96 | UG/L |  | 2021-12-16 | L1 | 0.74 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2941 | CHLOROFORM | 12.58 | UG/L | 100 | 2021-12-16 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-12-16 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2943 | BROMODICHLOROMETHANE | 7.5 | UG/L | 100 | 2021-12-16 | L1 | 0.14 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2944 | DIBROMOCHLOROMETHANE | 3.93 | UG/L | 100 | 2021-12-16 | L1 | 0.32 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.91 | UG/L | 60.4999 | 2022-03-16 | L2 | 0.98
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 39.6 | UG/L | 80.4999 | 2022-03-16 | L2 | 0.44 |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2450 | MONOCHLORACETIC ACID | 0 | UG/L |  | 2022-03-16 | L2 |  |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2451 | DICHLOROACETIC ACID | 7.38 | UG/L |  | 2022-03-16 | L2 | 0.42 |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2452 | TRICHLOROACETIC ACID | 11.5 | UG/L |  | 2022-03-16 | L2 | 0.94 |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2022-03-16 | L2 |  |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2454 | DIBROMOACETIC ACID | 4.02 | UG/L |  | 2022-03-16 | L2 | 0.74 |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2941 | CHLOROFORM | 24.85 | UG/L | 100 | 2022-03-16 | L2 | 0.32 |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2022-03-16 | L2 |  |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2943 | BROMODICHLOROMETHANE | 10.18 | UG/L | 100 | 2022-03-16 | L2 | 0.42 |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2944 | DIBROMOCHLOROMETHANE | 39.6 | UG/L | 100 | 2022-03-16 | L2 | 0.44 |  |  | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.91 | UG/L | 60.4999 | 2022-03-16 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 39.6 | UG/L | 80.4999 | 2022-03-16 | L2 |  |  | LOT 607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.07 | UG/L | 60.4999 | 2022-03-16 | L1 |  |  | LOT 501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 38.84 | UG/L | 80.4999 | 2022-03-16 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.05 | UG/L | 60.4999 | 2022-06-17 | L2 | 0.98 |  | LOT #607 (HLKD) J QUALIFIER ON 2941 CHLOROFORM IN THE TTHMS-NO EXPLANATION PROVIDED. CHANGE SAMPLE TYPE FROM "S" TO "D" IF ACCEPTABLE.
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 58.25 | UG/L | 80.4999 | 2022-06-17 | L2 | 0.39 |  | LOT #607 (HLKD) J QUALIFIER ON 2941 CHLOROFORM IN THE TTHMS-NO EXPLANATION PROVIDED. CHANGE SAMPLE TYPE FROM "S" TO "D" IF ACCEPTABLE.
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.89 | UG/L | 60.4999 | 2022-06-17 | L1 | 0.98 |  | LOT #501 (NO J QUALIFIERS ON THIS SAMPLE - OK) | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 56.67 | UG/L | 80.4999 | 2022-06-17 | L1 | 0.39 |  | LOT #501 (NO J QUALIFIERS ON THIS SAMPLE - OK) | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.5 | UG/L | 60.4999 | 2022-06-17 | L2 | 0.98 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 58.25 | UG/L | 80.4999 | 2022-06-17 | L2 | 0.39 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2450 | MONOCHLORACETIC ACID | 1.08 | UG/L |  | 2022-06-17 | L2 | 0.98 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2451 | DICHLOROACETIC ACID | 10.84 | UG/L |  | 2022-06-17 | L2 | 0.42 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2452 | TRICHLOROACETIC ACID | 16.21 | UG/L |  | 2022-06-17 | L2 | 0.94 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2453 | MONOBROMACETIC ACID | 9.52 | UG/L |  | 2022-06-17 | L2 | 0.41 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2454 | DIBROMOACETIC ACID | 1.41 | UG/L |  | 2022-06-17 | L2 | 0.74 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2941 | CHLOROFORM | 36.47 | UG/L | 100 | 2022-06-17 | L2 | 0.39 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2022-06-17 | L2 |  |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2943 | BROMODICHLOROMETHANE | 5.98 | UG/L | 100 | 2022-06-17 | L2 | 0.32 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2944 | DIBROMOCHLOROMETHANE | 5.98 | UG/L | 100 | 2022-06-17 | L2 | 0.39 |  | A2205216001-LOT #607 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.89 | UG/L | 60.4999 | 2022-06-17 | L1 | 0.98 |  | A2205216002 - LOT #501 | 2
3481016 | PINE ISLE MOBILE VILLA | DBP | 2950 | TOTAL THMS | 56.67 | UG/L | 80.4999 | 2022-06-17 | L1 | 0.39 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2450 | MONOCHLORACETIC ACID | 2.07 | UG/L |  | 2022-06-17 | L1 | 0.98 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2451 | DICHLOROACETIC ACID | 10.73 | UG/L |  | 2022-06-17 | L1 | 0.42 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2452 | TRICHLOROACETIC ACID | 17.63 | UG/L |  | 2022-06-17 | L1 | 0.94 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2453 | MONOBROMACETIC ACID | 7.95 | UG/L |  | 2022-06-17 | L1 | 0.41 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2454 | DIBROMOACETIC ACID | 1.52 | UG/L |  | 2022-06-17 | L1 | 0.74 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2941 | CHLOROFORM | 35.67 | UG/L | 100 | 2022-06-17 | L1 | 0.39 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2022-06-17 | L1 |  |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2943 | BROMODICHLOROMETHANE | 15.02 | UG/L | 100 | 2022-06-17 | L1 | 0.14 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | DBP | 2944 | DIBROMOCHLOROMETHANE | 5.98 | UG/L | 100 | 2022-06-17 | L1 | 0.32 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-14 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | INOR | 1041 | NITRITE | 0.11 | MG/L | 1.4999 | 2022-10-14 | AAA | 0.0034 |  | POE
3481093 | ROCK SPRINGS MHP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-03-21 | AAA | 0.2
3481093 | ROCK SPRINGS MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-03-21 | AAA | 0.2
3481093 | ROCK SPRINGS MHP | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | INOR | 1010 | BARIUM | 0.0135 | MG/L | 2.4999 | 2018-03-21 | AAA | 0.002
3481093 | ROCK SPRINGS MHP | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | INOR | 1020 | CHROMIUM | 0.0011 | MG/L | 0.1499 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | INOR | 1024 | CYANIDE | 0.0059 | MG/L | 0.2499 | 2018-03-21 | AAA | 0.005
3481093 | ROCK SPRINGS MHP | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2018-03-21 | AAA | 0.2
3481093 | ROCK SPRINGS MHP | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-03-21 | AAA | 2e-05
3481093 | ROCK SPRINGS MHP | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-03-21 | AAA | 0.002
3481093 | ROCK SPRINGS MHP | INOR | 1052 | SODIUM | 15.2 | MG/L | 160.4999 | 2018-03-21 | AAA | 0.5
3481093 | ROCK SPRINGS MHP | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-03-21 | AAA | 0.0005
3481093 | ROCK SPRINGS MHP | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-03-21 | AAA | 0.02
3481093 | ROCK SPRINGS MHP | SEC | 1017 | CHLORIDE | 20.3 | MG/L | 250.4999 | 2018-03-21 | AAA | 0.4
3481093 | ROCK SPRINGS MHP | SEC | 1022 | COPPER | 0.0072 | MG/L | 1.4999 | 2018-03-21 | AAA | 0.001
3481093 | ROCK SPRINGS MHP | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2018-03-21 | AAA | 0.4
3481093 | ROCK SPRINGS MHP | SEC | 1028 | IRON | 0.0283 | MG/L | 0.3499 | 2018-03-21 | AAA | 0.01
3481093 | ROCK SPRINGS MHP | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-03-21 | AAA | 0.01
3481093 | ROCK SPRINGS MHP | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-03-21 | AAA | 0.0005
3481093 | ROCK SPRINGS MHP | SEC | 1055 | SULFATE | 13.6 | MG/L | 250.4999 | 2018-03-21 | AAA | 1
3481093 | ROCK SPRINGS MHP | SEC | 1095 | ZINC | 0.0271 | MG/L | 5.4999 | 2018-03-21 | AAA | 0.01
3481093 | ROCK SPRINGS MHP | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-03-21 | AAA | 5
3481093 | ROCK SPRINGS MHP | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-03-21 | AAA | 1
3481093 | ROCK SPRINGS MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.18 | LN(10) |  | 2018-03-21 | AAA | 0.01
3481093 | ROCK SPRINGS MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 188 | MG/L | 500.4999 | 2018-03-21 | AAA | 2.5
3481093 | ROCK SPRINGS MHP | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-03-21 | AAA | 0.2
3481093 | ROCK SPRINGS MHP | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-03-21 | AAA | 0.2 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-03-21 | AAA | 0.5 | 0.5499 | 3YR VOC & 2AM/ETHYLBENZENE (3AM/ETHYLBENZENE AND TOT XYLENE DUE 1Q 2019)
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36 | UG/L | 60.4999 | 2018-09-17 | L1 |  |  | 314 BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 36.1 | UG/L | 80.4999 | 2018-09-17 | L1 |  |  | 314 BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2018-11-14 | AAA
3481093 | ROCK SPRINGS MHP | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-11-14 | AAA |  | 1.4999
3481093 | ROCK SPRINGS MHP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2019-02-27 | AAA | 0.5 | 0.5499 | 3AM/XY+ETH (3 CONSEC. YEARS, NO DETECT TOT XY AND ETHY. TEST TRIANNUAL WITH OTHER VOCS. NEXT DUE 2021_VP)
3481093 | ROCK SPRINGS MHP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2019-02-27 | AAA | 0.5 | 0.5499 | 3AM/XY+ETH (3 CONSEC. YEARS, NO DETECT TOT XY AND ETHY. TEST TRIANNUAL WITH OTHER VOCS. NEXT DUE 2021_VP)
3481093 | ROCK SPRINGS MHP | INOR | 1040 | NITRATE | 0.364 | MG/L | 10.4999 | 2019-09-16 | AAA
3481093 | ROCK SPRINGS MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-09-16 | AAA
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.2 | UG/L | 60.4999 | 2019-11-22 | L1 | 1 |  |  | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 33.9 | UG/L | 80.4999 | 2019-11-22 | L1 | 0.5 |  |  | 3
3481093 | ROCK SPRINGS MHP | VOC | 2955 | TOT XYLENE | 0.91 | UG/L | 10499.9999 | 2020-03-25 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-03-25 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | INOR | 1040 | NITRATE | 0.414 | MG/L | 10.4999 | 2020-06-23 | AAA | 0.2 |  | POE NN
3481093 | ROCK SPRINGS MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-06-23 | AAA | 0.2 |  | POE NN
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2020-09-30 | L1 | 1 |  | 314 BAHIA MAR (XXX ALL RESULTS HAVE Q QUALIFIERS-ALL OVER HOLDING TIME-ENTERED FOR INFO. PURPOSES ONLY) HLKD-ENT'D WITH SAMPLE TYPE "S" (RECEIVED 10/29/20 - LATE) | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2020-09-30 | L1 | 0.5 |  | 314 BAHIA MAR (XXX ALL RESULTS HAVE Q QUALIFIERS-ALL OVER HOLDING TIME-ENTERED FOR INFO. PURPOSES ONLY) HLKD-ENT'D WITH SAMPLE TYPE "S" (RECEIVED 10/29/20 - LATE) | 3
3481093 | ROCK SPRINGS MHP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-06-07 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | INOR | 1040 | NITRATE | 0.361 | MG/L | 10.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1010 | BARIUM | 0.0143 | MG/L | 2.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1020 | CHROMIUM | 0.0011 | MG/L | 0.1499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1052 | SODIUM | 13.9 | MG/L | 160.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1017 | CHLORIDE | 20.2 | MG/L | 250.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1022 | COPPER | 0.0017 | MG/L | 1.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1028 | IRON | 0.0303 | MG/L | 0.3499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1055 | SULFATE | 19.1 | MG/L | 250.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1095 | ZINC | 0.002 | MG/L | 5.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.19 | LN(10) |  | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 238 | MG/L | 500.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-08-12 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-08-12 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-08-12 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-08-12 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-08-12 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-08-12 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-08-12 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-08-12 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-08-12 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-08-12 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-08-12 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-08-12 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-08-12 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-08-12 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-09-03 | L1 |  |  | BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-09-03 | L1 |  |  | BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-09-03 | L2 |  |  | SEWER PLANT | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-09-03 | L2 |  |  | SEWER PLANT | 3
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.3 | UG/L | 60.4999 | 2021-12-08 | L1 | 60 |  |  | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 30.9 | UG/L | 80.4999 | 2021-12-08 | L1 | 80 |  |  | 3
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.3 | UG/L | 60.4999 | 2021-12-08 | L1 | 60 |  |  | 3
3481093 | ROCK SPRINGS MHP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1040 | NITRATE | 0.339 | MG/L | 10.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-09-20 | L1 | 0.38 |  | 314 BAHIA MAR (HLKD) HAA5/E87052 | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2022-09-20 | L1 | 0.5 |  | 314 BAHIA MAR (HLKD) HAA5/E87052 | 3
3481093 | ROCK SPRINGS MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0.38 | UG/L | 60.4999 | 2022-09-20 | L2 |  |  | SEWER PLANT (HLKD) HAA5/E87052 | 3
3481093 | ROCK SPRINGS MHP | DBP | 2950 | TOTAL THMS | 0.5 | UG/L | 80.4999 | 2022-09-20 | L2 |  |  | SEWER PLANT (HLKD) HAA5/E87052 | 3
3481155 | SHADY OAKS TRAILER PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-03-05 | AAA | 0.051 |  | NN
3481155 | SHADY OAKS TRAILER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-03-05 | AAA | 0.053 |  | NN
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8.6 | PCI/L | 15.4999 | 2018-03-22 | AAA | 1.2 |  | RADS (HLK'D 5-18-18 TO ER+JF) **PER 6/15/18 7:17 AM EMAIL FROM DS TO ER&BB: "THE GUIDANCE (FOR RADS) IS TO KEEP THEM ON QTRLY UNTIL THEY ARE HOOKED UP WITH COUNTY. THEY DO HAVE A PERMIT TO HOOK UP."
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 4.6 | PCI/L | 3.4999 | 2018-03-22 | AAA | 0.4 | 1.4999 | RADS (HLK'D 5-18-18 TO ER+JF) **PER 6/15/18 7:17 AM EMAIL FROM DS TO ER&BB: "THE GUIDANCE (FOR RADS) IS TO KEEP THEM ON QTRLY UNTIL THEY ARE HOOKED UP WITH COUNTY. THEY DO HAVE A PERMIT TO HOOK UP."
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-03-22 | AAA | 0.7 | 1.4999 | RADS (HLK'D 5-18-18 TO ER+JF) **PER 6/15/18 7:17 AM EMAIL FROM DS TO ER&BB: "THE GUIDANCE (FOR RADS) IS TO KEEP THEM ON QTRLY UNTIL THEY ARE HOOKED UP WITH COUNTY. THEY DO HAVE A PERMIT TO HOOK UP."
3481155 | SHADY OAKS TRAILER PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-03-22 | AAA | 0.05 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-03-22 | AAA | 0.05 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-03-22 | AAA | 8e-05 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1010 | BARIUM | 0.017 | MG/L | 2.4999 | 2018-03-22 | AAA | 0.00083 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-03-22 | AAA | 0.00045 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-03-22 | AAA | 0.0016 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-03-22 | AAA | 0.0048 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1025 | FLUORIDE | 0.29 | MG/L | 4.0499 | 2018-03-22 | AAA | 0.05 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-03-22 | AAA | 0.00024 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-03-22 | AAA | 5e-05 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-03-22 | AAA | 0.006 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-03-22 | AAA | 0.00058 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1052 | SODIUM | 27 | MG/L | 160.4999 | 2018-03-22 | AAA | 0.34 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-03-22 | AAA | 0.00011 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-03-22 | AAA | 0.0004 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-03-22 | AAA | 6e-05 |  | E82535/NN,FL (ALL INORG OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-03-22 | AAA | 0.028 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1017 | CHLORIDE | 42 | MG/L | 250.4999 | 2018-03-22 | AAA | 0.5 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1022 | COPPER | 0.0051 | MG/L | 1.4999 | 2018-03-22 | AAA | 0.0032 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1025 | FLUORIDE | 0.29 | MG/L | 2.0499 | 2018-03-22 | AAA | 0.05 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-03-22 | AAA | 0.1 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-03-22 | AAA | 0.0019 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-03-22 | AAA | 0.0001 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1055 | SULFATE | 4.6 | MG/L | 250.4999 | 2018-03-22 | AAA | 0.5 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-03-22 | AAA | 0.033 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-03-22 | AAA | 5 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-03-22 | AAA | 1 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.79 | LN(10) |  | 2018-03-22 | AAA |  |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 250 | MG/L | 500.4999 | 2018-03-22 | AAA | 10 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-03-22 | AAA | 0.04 |  | E82535/CHL,FL,SULF; E53076/COL,OD,PH,TDS; E82001/F.AG (ALL OK)
3481155 | SHADY OAKS TRAILER PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-03-22 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-03-22 | AAA | 0.32 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-03-22 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-03-22 | AAA | 0.44 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-03-22 | AAA | 0.46 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-03-22 | AAA | 0.26 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-03-22 | AAA | 0.2 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-03-22 | AAA | 0.18 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-03-22 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-03-22 | AAA | 0.36 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-03-22 | AAA | 0.39 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-03-22 | AAA | 0.23 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-03-22 | AAA | 0.26 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-03-22 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-03-22 | AAA | 0.12 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-03-22 | AAA | 0.24 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-03-22 | AAA | 0.12 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-03-22 | AAA | 0.17 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-03-22 | AAA | 0.22 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-03-22 | AAA | 0.17 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-03-22 | AAA | 0.39 | 0.5499 | 3YR VOC (ALL OK) NOTE: SOCS NOT TESTED WITH THESE 3/22/18 TRIENNIAL CHEMS - BB
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 11.3 | PCI/L | 15.4999 | 2018-05-10 | AAA
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 4.8 | PCI/L | 3.4999 | 2018-05-10 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 1.4 | PCI/L | 2.4999 | 2018-05-10 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 12.2 | PCI/L | 15.4999 | 2018-05-17 | AAA
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 6.6 | PCI/L | 3.4999 | 2018-05-17 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0.6 | PCI/L | 2.4999 | 2018-05-17 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 17.2 | PCI/L | 15.4999 | 2018-07-25 | AAA |  |  | SUBCONTRACTED LAB E84025. GA INC. U = RAA= 10.64; RA228+RA226, RAA = 4.78, NO PN NEEDED. STAY ON Q DUE TO CONSENT ORDER. VP
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 4.3 | PCI/L | 3.4999 | 2018-07-25 | AAA |  | 1.4999 | SUBCONTRACTED LAB E84025. GA INC. U = RAA= 10.64; RA228+RA226, RAA = 4.78, NO PN NEEDED. STAY ON Q DUE TO CONSENT ORDER. VP
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-07-25 | AAA |  | 1.4999 | SUBCONTRACTED LAB E84025. GA INC. U = RAA= 10.64; RA228+RA226, RAA = 4.78, NO PN NEEDED. STAY ON Q DUE TO CONSENT ORDER. VP
3481155 | SHADY OAKS TRAILER PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.15 | UG/L | 60.4999 | 2018-08-08 | L1 |  |  | SITE#8 1761 SHADY OAKS *NO CHLORINE RESIDUAL ON REPORT* | 3
3481155 | SHADY OAKS TRAILER PARK | DBP | 2950 | TOTAL THMS | 12.71 | UG/L | 80.4999 | 2018-08-08 | L1 |  |  | SITE#8 1761 SHADY OAKS *NO CHLORINE RESIDUAL ON REPORT* | 3
3481155 | SHADY OAKS TRAILER PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.75 | UG/L | 60.4999 | 2018-08-09 | L1 |  |  | SITE#8 1761 SHADY OAKS | 3
3481155 | SHADY OAKS TRAILER PARK | DBP | 2950 | TOTAL THMS | 14.46 | UG/L | 80.4999 | 2018-08-09 | L1 |  |  | SITE#8 1761 SHADY OAKS | 3
3481155 | SHADY OAKS TRAILER PARK | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2018-08-29 | AAA |  | 0.667 | URANIUM. RCVD 8/21/19. NEEDED UNITS REVISED_VP
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 9.7 | PCI/L | 15.4999 | 2018-10-03 | AAA |  |  | GA INC. U = RAA= 12.6; RA228+RA226, RAA = 5.1, PN NEEDED FOR RA226+RA228 > MCL (5PCI/L). STAY ON Q DUE TO CONSENT ORDER. VP - SUBCONTRACT LAB E84025
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 5.1 | PCI/L | 3.4999 | 2018-10-03 | AAA |  | 1.4999 | GA INC. U = RAA= 12.6; RA228+RA226, RAA = 5.1, PN NEEDED FOR RA226+RA228 > MCL (5PCI/L). STAY ON Q DUE TO CONSENT ORDER. VP - SUBCONTRACT LAB E84025
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-10-03 | AAA |  | 1.4999 | GA INC. U = RAA= 12.6; RA228+RA226, RAA = 5.1, PN NEEDED FOR RA226+RA228 > MCL (5PCI/L). STAY ON Q DUE TO CONSENT ORDER. VP - SUBCONTRACT LAB E84025
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 11.1 | PCI/L | 15.4999 | 2019-02-07 | AAA |  |  | LATE REORTING_VP [ GA RAA=12.43, CONTINUE Q;
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 6.3 | PCI/L | 3.4999 | 2019-02-07 | AAA |  | 1.4999 | LATE REORTING_VP [ GA RAA=12.43, CONTINUE Q;
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2019-02-07 | AAA |  | 1.4999 | LATE REORTING_VP [ GA RAA=12.43, CONTINUE Q;
3481155 | SHADY OAKS TRAILER PARK | INOR | 1040 | NITRATE | 0.48 | MG/L | 10.4999 | 2019-05-15 | AAA
3481155 | SHADY OAKS TRAILER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-05-15 | AAA
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 5.1 | PCI/L | 3.4999 | 2019-05-15 | AAA |  | 1.4999 | RA228+RA226, RAA = 5.7, PN NEEDED FOR RA226+RA228 > MCL (5PCI/L). STAY ON Q DUE TO CONSENT ORDER. VP
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0.6 | PCI/L | 2.4999 | 2019-05-15 | AAA |  | 1.4999 | RA228+RA226, RAA = 5.7, PN NEEDED FOR RA226+RA228 > MCL (5PCI/L). STAY ON Q DUE TO CONSENT ORDER. VP
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5.7 | PCI/L | 15.4999 | 2019-07-24 | AAA |  |  | GALRAA=10.925 < MCL NO PN NEEDED, GA>5 NEED TO TEST FOR RA226 AG
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2019-07-24 | AAA |  | 1.4999 | GALRAA=10.925 < MCL NO PN NEEDED, GA>5 NEED TO TEST FOR RA226 AG
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 4.2 | PCI/L | 3.4999 | 2019-08-15 | AAA |  | 1.4999 | RA226+RA228=4.2 PN RECEIVED AG
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 7.6 | PCI/L | 15.4999 | 2019-10-28 | AAA
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 4.4 | PCI/L | 3.4999 | 2019-10-28 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2019-10-28 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8.6 | PCI/L | 15.4999 | 2020-01-29 | AAA | 1.2
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 6.5 | PCI/L | 3.4999 | 2020-01-29 | AAA | 0.5 | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0.6 | PCI/L | 2.4999 | 2020-01-29 | AAA | 0.6 | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5.5 | PCI/L | 15.4999 | 2020-04-14 | AAA | 0.5 |  | RA228+RA226, RAA = 4.85, PN NOT NEEDED FOR RA226+RA228 < MCL (5PCI/L). GA 4 CONSECUTIVE SAMPLES UNDER MCL. RAA=6.85, CAN MOVE TO SAMPLING GA EVERY 6 YEARS_VPU
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 4.3 | PCI/L | 3.4999 | 2020-04-14 | AAA | 0.2 | 1.4999 | RA228+RA226, RAA = 4.85, PN NOT NEEDED FOR RA226+RA228 < MCL (5PCI/L). GA 4 CONSECUTIVE SAMPLES UNDER MCL. RAA=6.85, CAN MOVE TO SAMPLING GA EVERY 6 YEARS_VPU
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-04-14 | AAA | 0.6 | 1.4999 | RA228+RA226, RAA = 4.85, PN NOT NEEDED FOR RA226+RA228 < MCL (5PCI/L). GA 4 CONSECUTIVE SAMPLES UNDER MCL. RAA=6.85, CAN MOVE TO SAMPLING GA EVERY 6 YEARS_VPU
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5.1 | PCI/L | 15.4999 | 2020-08-31 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 3.7 | PCI/L | 3.4999 | 2020-08-31 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-08-31 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | INOR | 1040 | NITRATE | 0.012 | MG/L | 10.4999 | 2020-09-15 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-09-15 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8 | PCI/L | 15.4999 | 2020-10-28 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 1.4 | PCI/L | 3.4999 | 2020-10-28 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-10-28 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 9.3 | PCI/L | 15.4999 | 2021-02-08 | AAA | 1.5 |  | 1Q2021
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 2.6 | PCI/L | 3.4999 | 2021-02-08 | AAA | 0.4 | 1.4999 | 1Q2021
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-02-08 | AAA | 0.7 | 1.4999 | 1Q2021
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-28 | AAA | 0.7 | 1.4999 | R228 VALUE CORRECTED (FROM 0.7 TO -0-) ON 10/25/22 FROM DUPLICATE REPORT-BB
3481155 | SHADY OAKS TRAILER PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.3 | UG/L | 60.4999 | 2021-08-26 | L1 |  |  |  | 3
3481155 | SHADY OAKS TRAILER PARK | DBP | 2950 | TOTAL THMS | 6.36 | UG/L | 80.4999 | 2021-08-26 | L1 |  |  |  | 3
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5.3 | PCI/L | 15.4999 | 2021-09-28 | AAA
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-09-28 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 1.7 | PCI/L | 3.4999 | 2021-09-28 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-06 | AAA |  | 0.0149 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 1.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-06 | AAA |  | 1.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-06 | AAA |  | 0.4499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 9.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-06 | AAA |  | 6.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-06 | AAA |  | 0.6499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-06 | AAA |  | 2.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-06 | AAA |  | 0.0749 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-06 | AAA |  | 0.6499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-06 | AAA |  | 0.9499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-06 | AAA |  | 0.0449 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.0449 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-06 | AAA |  | 0.0149 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 7 | PCI/L | 15.4999 | 2021-12-06 | AAA
3481155 | SHADY OAKS TRAILER PARK | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-06 | AAA |  | 0.667
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 3.8 | PCI/L | 3.4999 | 2021-12-06 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-06 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1025 | FLUORIDE | 0.27 | MG/L | 4.0499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1052 | SODIUM | 25 | MG/L | 160.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1017 | CHLORIDE | 36 | MG/L | 250.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1025 | FLUORIDE | 0.27 | MG/L | 2.0499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1028 | IRON | 0.0078 | MG/L | 0.3499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1055 | SULFATE | 4.5 | MG/L | 250.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.21 | LN(10) |  | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 231 | MG/L | 500.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | SEC | 2905 | FOAMING AGENTS | 0.07 |  | 0.5499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 3.8 | PCI/L | 3.4999 | 2022-03-15 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-03-15 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 4.9 | PCI/L | 3.4999 | 2022-06-07 | AAA | 0.5 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-06-07 | AAA | 0.7 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8.6 | PCI/L | 15.4999 | 2022-07-12 | AAA | 2.6 |  | RADS
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 2.5 | PCI/L | 3.4999 | 2022-07-12 | AAA | 0.4 | 1.4999 | RADS
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-07-12 | AAA | 0.6 | 1.4999 | RADS
3481155 | SHADY OAKS TRAILER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8.6 | PCI/L | 15.4999 | 2022-07-13 | AAA | 2.6 |  | DIST.
3481155 | SHADY OAKS TRAILER PARK | RAD | 4020 | RADIUM-226 | 2.5 | PCI/L | 3.4999 | 2022-07-13 | AAA | 0.4 | 1.4999 | DIST.
3481155 | SHADY OAKS TRAILER PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-07-13 | AAA |  | 1.4999 | DIST.
3481155 | SHADY OAKS TRAILER PARK | INOR | 1041 | NITRITE | 0.01 | MG/L | 1.4999 | 2022-10-17 | AAA | 34 |  | POE
3481155 | SHADY OAKS TRAILER PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-17 | AAA |  |  | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1017 | CHLORIDE | 21 | MG/L | 250.4999 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1025 | FLUORIDE | 0.18 | MG/L | 2.0499 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1032 | MANGANESE | 0.0025 | MG/L | 0.0549 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1055 | SULFATE | 16 | MG/L | 250.4999 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.02 | LN(10) |  | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 170 | MG/L | 500.4999 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-06-14 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0.17 | MG/L | 10.4999 | 2018-06-14 | WTP2 | 0.051 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-06-14 | WTP2 | 0.053 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1005 | ARSENIC | 0.0002 | MG/L | 0.0104 | 2018-06-14 | WTP2 | 8e-05 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1010 | BARIUM | 0.0083 | MG/L | 2.4999 | 2018-06-14 | WTP2 | 0.00083 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-06-14 | WTP2 | 0.00045 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-06-14 | WTP2 | 0.0016 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-06-14 | WTP2 | 0.0048 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2018-06-14 | WTP2 | 0.075 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-06-14 | WTP2 | 0.00024 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-06-14 | WTP2 | 5e-05 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-06-14 | WTP2 | 0.006 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-06-14 | WTP2 | 0.00058 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2018-06-14 | WTP2 | 0.34 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-06-14 | WTP2 | 0.00011 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-06-14 | WTP2 | 0.0004 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-06-14 | WTP2 | 6e-05 |  | WELL #4
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-06-14 | WTP2 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-06-14 | WTP2 | 0.32 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-06-14 | WTP2 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-06-14 | WTP2 | 0.44 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-06-14 | WTP2 | 0.46 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-06-14 | WTP2 | 0.26 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-06-14 | WTP2 | 0.2 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-06-14 | WTP2 | 0.18 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-06-14 | WTP2 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP2 | 0.36 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-06-14 | WTP2 | 0.39 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP2 | 0.23 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-06-14 | WTP2 | 0.26 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP2 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-06-14 | WTP2 | 0.12 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP2 | 0.24 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-06-14 | WTP2 | 0.12 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-06-14 | WTP2 | 0.17 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-06-14 | WTP2 | 0.22 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-06-14 | WTP2 | 0.17 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-06-14 | WTP2 | 0.39 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2018-06-14 | WTP3 | 0.051
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-06-14 | WTP3 | 0.053
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1005 | ARSENIC | 0.0002 | MG/L | 0.0104 | 2018-06-14 | WTP3 | 8e-05
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1010 | BARIUM | 0.0095 | MG/L | 2.4999 | 2018-06-14 | WTP3 | 0.00083
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-06-14 | WTP3 | 0.00045
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-06-14 | WTP3 | 0.0016
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-06-14 | WTP3 | 0.0048
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2018-06-14 | WTP3 | 0.075
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-06-14 | WTP3 | 0.00024
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-06-14 | WTP3 | 5e-05
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-06-14 | WTP3 | 0.006
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-06-14 | WTP3 | 0.00058
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1052 | SODIUM | 15 | MG/L | 160.4999 | 2018-06-14 | WTP3 | 0.34
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-06-14 | WTP3 | 0.00011
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-06-14 | WTP3 | 0.0004
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-06-14 | WTP3 | 6e-05
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-06-14 | WTP3 | 0.028
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1017 | CHLORIDE | 22 | MG/L | 250.4999 | 2018-06-14 | WTP3 | 0.78
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-06-14 | WTP3 | 0.0032
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1025 | FLUORIDE | 0.19 | MG/L | 2.0499 | 2018-06-14 | WTP3 | 0.075
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-06-14 | WTP3 | 0.1
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1032 | MANGANESE | 0.003 | MG/L | 0.0549 | 2018-06-14 | WTP3 | 0.0001
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1050 | SILVER | 0.0004 | MG/L | 0.1499 | 2018-06-14 | WTP3 | 0.0001
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1055 | SULFATE | 19 | MG/L | 250.4999 | 2018-06-14 | WTP3 | 0.52
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-06-14 | WTP3 | 0.033
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-06-14 | WTP3 | 5
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-06-14 | WTP3 | 1
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.05 | LN(10) |  | 2018-06-14 | WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 190 | MG/L | 500.4999 | 2018-06-14 | WTP3 | 10
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-06-14 | WTP3 | 0.04
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-06-14 | WTP3 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-06-14 | WTP3 | 0.32 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-06-14 | WTP3 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-06-14 | WTP3 | 0.44 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-06-14 | WTP3 | 0.46 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-06-14 | WTP3 | 0.26 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-06-14 | WTP3 | 0.2 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-06-14 | WTP3 | 0.18 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-06-14 | WTP3 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP3 | 0.36 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-06-14 | WTP3 | 0.39 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP3 | 0.23 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-06-14 | WTP3 | 0.26 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP3 | 0.28 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-06-14 | WTP3 | 0.12 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-06-14 | WTP3 | 0.24 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-06-14 | WTP3 | 0.12 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-06-14 | WTP3 | 0.17 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-06-14 | WTP3 | 0.22 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-06-14 | WTP3 | 0.17 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-06-14 | WTP3 | 0.39 | 0.5499
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.59 | UG/L | 60.4999 | 2018-08-09 | L1 | 0.91 |  |  | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 15.49 | UG/L | 80.4999 | 2018-08-09 | L1 | 0.39 |  |  | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.77 | UG/L | 60.4999 | 2018-08-17 | L2 | 0.91
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 21.58 | UG/L | 80.4999 | 2018-08-17 | L2 | 0.39
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 25.9 | UG/L | 80.4999 | 2019-08-19 | L2 |  |  | 7006 ALAMENA
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.4 | UG/L | 60.4999 | 2019-08-19 | L1 |  |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 0.39 | UG/L | 80.4999 | 2019-08-19 | L1 |  |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.61 | UG/L | 60.4999 | 2019-08-19 | L2 |  |  | 7006 ALAMENA
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-10-30 | WTP2 | 0.051 |  | WELL 4 POE
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-10-30 | WTP2 | 0.13 |  | WELL 4 POE
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-10-30 | WTP3 | 0.051 |  | WELL 5 POE
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-10-30 | WTP3 | 0.13 |  | WELL 5 POE
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 83.2 | UG/L | 60.4999 | 2020-08-27 | L1 | 1 |  | 7189 LINMAR (HAA5 > MCL, TRIGGERS QTRLY MONITORING)
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 15.3 | UG/L | 80.4999 | 2020-08-27 | L1 | 0.5 |  | 7189 LINMAR (HAA5 > MCL, TRIGGERS QTRLY MONITORING)
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 86.5 | UG/L | 60.4999 | 2020-08-27 | L2 | 1 |  | 7006 ALAMENA (HAA5 > MCL, TRIGGERS QTRLY MONITORING) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 15 | UG/L | 80.4999 | 2020-08-27 | L2 | 0.5 |  | 7006 ALAMENA (HAA5 > MCL, TRIGGERS QTRLY MONITORING)
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-02-01 | WTP2 |  |  | WELL 4 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-01 | WTP2 |  |  | WELL 4 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-02-01 | WTP3 |  |  | WELL 5 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-01 | WTP3 |  |  | WELL 5 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.77 | UG/L | 60.4999 | 2021-02-22 | L1 | 1 |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 0.81 | UG/L | 80.4999 | 2021-02-22 | L1 | 0.5 |  | 7189 LINMAR | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.79 | UG/L | 60.4999 | 2021-02-22 | L2 | 1 |  | 7006 ALAMENA | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 0.8 | UG/L | 80.4999 | 2021-02-22 | L2 | 0.5 |  | 7006 ALAMENA
3481199 | SILVER STAR VILLAGE (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.7 | PCI/L | 15.4999 | 2021-05-18 | WTP3 |  |  | POE-SSV
3481199 | SILVER STAR VILLAGE (2 WPS) | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-05-18 | WTP3 |  | 1.4999 | POE-SSV
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0.202 | MG/L | 10.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1010 | BARIUM | 0.0084 | MG/L | 2.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1030 | LEAD | 0.0046 | MG/L | 0.0154 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1052 | SODIUM | 12.8 | MG/L | 160.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1017 | CHLORIDE | 22.9 | MG/L | 250.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1022 | COPPER | 0.0317 | MG/L | 1.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1028 | IRON | 0.31 | MG/L | 0.3499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.0449 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-05-18 | WTP3 |  | 0.0149 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1055 | SULFATE | 20.1 | MG/L | 250.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1095 | ZINC | 0.0877 | MG/L | 5.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.04 | LN(10) |  | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 200 | MG/L | 500.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-05-18 | WTP3 |  | 0.0149 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 1.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-05-18 | WTP3 |  | 1.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-05-18 | WTP3 |  | 0.4499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 9.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-05-18 | WTP3 |  | 6.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-05-18 | WTP3 |  | 0.6499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-05-18 | WTP3 |  | 2.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-05-18 | WTP3 |  | 0.0749 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-05-18 | WTP3 |  | 0.6499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-05-18 | WTP3 |  | 0.9499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-05-18 | WTP3 |  | 0.0449 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.86 | UG/L | 60.4999 | 2021-05-24 | L1 | 1 |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 8.57 | UG/L | 80.4999 | 2021-05-24 | L1 | 0.5 |  | 7189 LINMAR | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.53 | UG/L | 60.4999 | 2021-05-24 | L2 | 1 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 7.26 | UG/L | 80.4999 | 2021-05-24 | L2 | 0.5 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.5 | PCI/L | 15.4999 | 2021-06-10 | WTP2 |  |  | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-10 | WTP2 |  | 1.4999 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1010 | BARIUM | 0.0093 | MG/L | 2.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1036 | NICKEL | 0.0016 | MG/L | 0.1499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1052 | SODIUM | 12.9 | MG/L | 160.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1017 | CHLORIDE | 22.3 | MG/L | 250.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1022 | COPPER | 0.003 | MG/L | 1.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1028 | IRON | 0.231 | MG/L | 0.3499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1032 | MANGANESE | 0.0113 | MG/L | 0.0549 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1055 | SULFATE | 18 | MG/L | 250.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1095 | ZINC | 0.259 | MG/L | 5.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.18 | LN(10) |  | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 226 | MG/L | 500.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-06-10 | WTP2 |  | 0.0149 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 1.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-06-10 | WTP2 |  | 1.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-06-10 | WTP2 |  | 0.4499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 9.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-06-10 | WTP2 |  | 6.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-06-10 | WTP2 |  | 0.6499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-06-10 | WTP2 |  | 2.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-06-10 | WTP2 |  | 0.0749 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-06-10 | WTP2 |  | 0.6499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-06-10 | WTP2 |  | 0.9499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-06-10 | WTP2 |  | 0.0449 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.0449 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-06-10 | WTP2 |  | 0.0149 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.4 | UG/L | 60.4999 | 2021-08-23 | L1
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 3.51 | UG/L | 80.4999 | 2021-08-23 | L1 |  |  |  | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.7 | UG/L | 60.4999 | 2021-08-23 | L2 |  |  | ALAMENA | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 3.43 | UG/L | 80.4999 | 2021-08-23 | L2 |  |  | ALAMENA
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-11-23 | L1 | 1 |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-11-23 | L1 | 0.5 |  | 7189 LINMAR | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-11-23 | L2 | 1 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-11-23 | L2 | 0.5 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-27 | WTP2 |  |  | WP4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-27 | WTP2 |  |  | WP4
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1040 | NITRATE | 0.042 | MG/L | 10.4999 | 2022-01-27 | WTP3 |  |  | WP5
3481199 | SILVER STAR VILLAGE (2 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-27 | WTP3 |  |  | WP5
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2950 | TOTAL THMS | 1.5 | UG/L | 80.4999 | 2022-06-09 | L1 |  |  | 7189 LINMAR- SAMPLED WRONG MONTH_AL | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.6 | UG/L | 60.4999 | 2022-11-22 | L2 | 60 |  | MAKEUP FROM Q3 2022 HAA5 J QUALIFIER | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28 | UG/L | 60.4999 | 2019-07-08 | L1 |  |  | 1315 DUSTY PINE DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 43.5 | UG/L | 80.4999 | 2019-07-08 | L1 |  |  | 1315 DUSTY PINE DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.3 | UG/L | 60.4999 | 2019-07-08 | L2 |  |  | 743 BIRCH HOLLOW DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 48.5 | UG/L | 80.4999 | 2019-07-08 | L2 |  |  | 743 BIRCH HOLLOW DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.5 | UG/L | 60.4999 | 2020-07-15 | L1 | 1 |  | 1315 DUSTY PINE DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 44.5 | UG/L | 80.4999 | 2020-07-15 | L1 | 0.5 |  | 1315 DUSTY PINE DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.7 | UG/L | 60.4999 | 2020-07-15 | L2 | 1 |  | 743 BIRCH HOLLOW DR. (NO RESULTS PAGE FOR THE L1 SITE SUBMITTED - HLKD 8/3/20) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 35.2 | UG/L | 80.4999 | 2020-07-15 | L2 | 0.5 |  | 743 BIRCH HOLLOW DR. (NO RESULTS PAGE FOR THE L1 SITE SUBMITTED - HLKD 8/3/20) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.7 | UG/L | 60.4999 | 2021-07-12 | L1 | 1 |  | 1315 DUSTY PINE DR. (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 36.7 | UG/L | 80.4999 | 2021-07-12 | L1 | 0.5 |  | 1315 DUSTY PINE DR. (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.9 | UG/L | 60.4999 | 2021-07-12 | L2 | 1 |  | 743 BIRCH HOLLOW (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 36.7 | UG/L | 80.4999 | 2021-07-12 | L2 | 0.5 |  | 743 BIRCH HOLLOW (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 69.3 | UG/L | 80.4999 | 2022-07-07 | L1 | 1 |  | 1315 DUSTY PINE (TOTAL HAA5 REPORT CORRECTED | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 31.81 | UG/L | 80.4999 | 2022-07-07 | L2 | 0.5 |  | 743 BIRCH HOLLOW (TOTAL HAA5 REPORT CORRECTED_AL | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.68 | UG/L | 60.4999 | 2022-07-07 | L2 | 1.5 |  | 743 BIRCH HOLLOW (TOTAL HAA5 REPORT CORRECTED_AL | 3
3484431 | OCOEE PINES (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.5 | UG/L | 60.4999 | 2022-07-07 | L1 | 1.5 |  | 1315 DUSTY PINE (TOTAL HAA5 REPORT CORRECTED | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.63 | UG/L | 60.4999 | 2020-08-17 | L1 | 0.56 |  | 13337 FLAMINGO CROSS BLVD. | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2950 | TOTAL THMS | 57.86 | UG/L | 80.4999 | 2020-08-17 | L1 | 0.84 |  | 13337 FLAMINGO CROSS BLVD. | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.67 | UG/L | 60.4999 | 2020-08-17 | L2 | 0.56 |  | 13335 FLAMINGO CROSS BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2950 | TOTAL THMS | 60.71 | UG/L | 80.4999 | 2020-08-17 | L2 | 0.84 |  | 13335 FLAMINGO CROSS BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.24 | UG/L | 60.4999 | 2021-08-16 | L1 |  |  | 13337 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2950 | TOTAL THMS | 30.54 | UG/L | 80.4999 | 2021-08-16 | L1 |  |  | 13337 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.29 | UG/L | 60.4999 | 2021-08-16 | L2 |  |  | 1335 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2950 | TOTAL THMS | 28.93 | UG/L | 80.4999 | 2021-08-16 | L2 |  |  | 1335 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.72 | UG/L | 60.4999 | 2022-08-16 | L2 | 1.42 |  | 13335 FLAMINGO CROSSING BLVD TTHM HAA5 | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2950 | TOTAL THMS | 40.79 | UG/L | 80.4999 | 2022-08-16 | L2 | 0.84 |  | 13335 FLAMINGO CROSSING BLVD TTHM HAA5 | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.41 | UG/L | 60.4999 | 2022-08-16 | L1 | 1.43 |  | 13337 FLAMINGO CROSSING BLVD TTHM HAA5 | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | DBP | 2950 | TOTAL THMS | 25.43 | UG/L | 80.4999 | 2022-08-16 | L1 | 0.84 |  | 13337 FLAMINGO CROSSING BLVD TTHM HAA5 | 3

## Osceola
OSCEOLA CHEMS 2018-2022
PWS ID | Mailing Name | Contam Group | Contam Code | Contam Desc | Results | UOM | MCL | Sample Date | Loc Code | MDL | RDL | Remark | Max Qtr
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-10 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-01-10 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-01-10 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-01-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-01-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.1 | UG/L | 60.4999 | 2018-01-30 | DBP-5 |  |  | 1721 BRASSIE CT., KISS. DIBROMAOACETIC ACID HAS A RESULT OF U, J
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 48.3 | UG/L | 80.4999 | 2018-01-30 | DBP-5 |  |  | 1721 BRASSIE CT., KISS. DIBROMAOACETIC ACID HAS A RESULT OF U, J
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.3 | UG/L | 60.4999 | 2018-01-30 | DBP-1 |  |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 52.3 | UG/L | 80.4999 | 2018-01-30 | DBP-1 |  |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.3 | UG/L | 60.4999 | 2018-01-30 | DBP-2 |  |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 57.6 | UG/L | 80.4999 | 2018-01-30 | DBP-2 |  |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.7 | UG/L | 60.4999 | 2018-01-30 | DBP-3 |  |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 36 | UG/L | 80.4999 | 2018-01-30 | DBP-3 |  |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.9 | UG/L | 60.4999 | 2018-01-30 | DBP-4 |  |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 35.7 | UG/L | 80.4999 | 2018-01-30 | DBP-4 |  |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.6 | UG/L | 60.4999 | 2018-01-30 | DBP-6 |  |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55.3 | UG/L | 80.4999 | 2018-01-30 | DBP-6 |  |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-02-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-02-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2018-02-09 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-26 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-26 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2018-02-26 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-03-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-03-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2018-03-09 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-03-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2018-03-23 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-03-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-04-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-04-09 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-04-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-04-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.6 | UG/L | 60.4999 | 2018-04-24 | DBP-5 | 0.48 |  | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 56.6 | UG/L | 80.4999 | 2018-04-24 | DBP-5 | 0.32 |  | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.1 | UG/L | 60.4999 | 2018-04-24 | DBP-1 | 0.48 |  | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 21 | UG/L | 80.4999 | 2018-04-24 | DBP-1 | 0.32 |  | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.4 | UG/L | 60.4999 | 2018-04-24 | DBP-2 | 0.48 |  | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 62.4 | UG/L | 80.4999 | 2018-04-24 | DBP-2 | 0.62 |  | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.3 | UG/L | 60.4999 | 2018-04-24 | DBP-3 | 0.48 |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 32.8 | UG/L | 80.4999 | 2018-04-24 | DBP-3 | 0.32 |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.3 | UG/L | 60.4999 | 2018-04-24 | DBP-4 | 0.48 |  | 145 E LAKESHORE BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 43.4 | UG/L | 80.4999 | 2018-04-24 | DBP-4 | 0.32 |  | 145 E LAKESHORE BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.8 | UG/L | 60.4999 | 2018-04-24 | DBP-6 | 0.48 |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 52.7 | UG/L | 80.4999 | 2018-04-24 | DBP-6 | 0.32 |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-10 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-05-10 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-05-10 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-24 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-05-24 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-05-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-06-08 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-06-08 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-06-25 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-06-25 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-25 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-09 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-07-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-09 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-25 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2018-07-25 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-25 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.2 | UG/L | 60.4999 | 2018-07-26 | DBP-2 | 0.48 |  | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 73 | UG/L | 80.4999 | 2018-07-26 | DBP-2 | 0.32 |  | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.7 | UG/L | 60.4999 | 2018-07-26 | DBP-3 | 0.48 |  | 120 SIMPSON
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 43.3 | UG/L | 80.4999 | 2018-07-26 | DBP-3 | 0.32 |  | 120 SIMPSON
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.3 | UG/L | 60.4999 | 2018-07-26 | DBP-4 | 0.48 |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 49.3 | UG/L | 80.4999 | 2018-07-26 | DBP-4 | 0.32 |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.5 | UG/L | 60.4999 | 2018-07-26 | DBP-6 | 0.48 |  | 2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 66.8 | UG/L | 80.4999 | 2018-07-26 | DBP-6 | 0.32 |  | 2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.6 | UG/L | 60.4999 | 2018-07-27 | DBP-5 | 0.48 |  | 1721 BRASSIE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 69.3 | UG/L | 80.4999 | 2018-07-27 | DBP-5 | 0.32 |  | 1721 BRASSIE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.8 | UG/L | 60.4999 | 2018-07-27 | DBP-1 | 0.48 |  | 3200 SERALAGO
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55.8 | UG/L | 80.4999 | 2018-07-27 | DBP-1 | 0.32 |  | 3200 SERALAGO
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-08-09 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2018-08-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-08-09 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-08-27 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-08-27 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-08-27 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-09-07 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-09-07 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-09-07 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-09-24 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-09-24 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-09-24 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-10-09 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-10-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-10-09 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.3 | UG/L | 60.4999 | 2018-10-23 | DBP-5 |  |  | 2950-1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55 | UG/L | 80.4999 | 2018-10-23 | DBP-5 |  |  | 2950-1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35 | UG/L | 60.4999 | 2018-10-23 | DBP-1 |  |  | 2950-3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 63.3 | UG/L | 80.4999 | 2018-10-23 | DBP-1 |  |  | 2950-3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.6 | UG/L | 60.4999 | 2018-10-23 | DBP-2 |  |  | 2950-1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 42.3 | UG/L | 80.4999 | 2018-10-23 | DBP-2 |  |  | 2950-1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.5 | UG/L | 60.4999 | 2018-10-23 | DBP-3 |  |  | 2950-120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 33.2 | UG/L | 80.4999 | 2018-10-23 | DBP-3 |  |  | 2950-120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.9 | UG/L | 60.4999 | 2018-10-23 | DBP-4 |  |  | 2950-145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 57.9 | UG/L | 80.4999 | 2018-10-23 | DBP-4 |  |  | 2950-145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.3 | UG/L | 60.4999 | 2018-10-23 | DBP-6 |  |  | 2950-2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 54.8 | UG/L | 80.4999 | 2018-10-23 | DBP-6 |  |  | 2950-2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-10-25 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-10-25 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-10-25 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-09 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-09 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-26 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-26 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-11-26 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-10 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-12-10 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-12-10 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-26 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2018-12-26 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-26 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-01-10 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-01-10 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-01-10 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-01-24 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-01-24 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-01-24 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.5 | UG/L | 60.4999 | 2019-01-28 | DBP-5 | 0.48 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 45.9 | UG/L | 80.4999 | 2019-01-28 | DBP-5 | 0.32 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.5 | UG/L | 60.4999 | 2019-01-28 | DBP-1 | 0.48 |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 15.3 | UG/L | 80.4999 | 2019-01-28 | DBP-1 | 0.32 |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.6 | UG/L | 60.4999 | 2019-01-28 | DBP-2 | 0.48 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55.8 | UG/L | 80.4999 | 2019-01-28 | DBP-2 | 0.32 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.9 | UG/L | 60.4999 | 2019-01-28 | DBP-3 | 0.48 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 34.3 | UG/L | 80.4999 | 2019-01-28 | DBP-3 | 0.32 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.1 | UG/L | 60.4999 | 2019-01-28 | DBP-4 | 0.48 |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 53.4 | UG/L | 80.4999 | 2019-01-28 | DBP-4 | 0.32 |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.7 | UG/L | 60.4999 | 2019-01-28 | DBP-6 | 0.48 |  | 2713 RISMEN CT., KISS. (HLKD) 1ST QTR 2019 DISINF BYP RPRT RCVD W/RSLTS
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 54 | UG/L | 80.4999 | 2019-01-28 | DBP-6 | 0.32 |  | 2713 RISMEN CT., KISS. (HLKD) 1ST QTR 2019 DISINF BYP RPRT RCVD W/RSLTS
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-08 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-02-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-11 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-02-26 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-26 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-02-26 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-03-09 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-03-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-03-11 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-03-23 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-03-25 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2019-03-29 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-04-09 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-04-09 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-04-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-04-24 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2019-04-24 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-04-24 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.7 | UG/L | 60.4999 | 2019-04-26 | DBP-5 |  |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 53.4 | UG/L | 80.4999 | 2019-04-26 | DBP-5 |  |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.1 | UG/L | 60.4999 | 2019-04-26 | DBP-1 |  |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 60.8 | UG/L | 80.4999 | 2019-04-26 | DBP-1 |  |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.1 | UG/L | 60.4999 | 2019-04-26 | DBP-2 |  |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 50.6 | UG/L | 80.4999 | 2019-04-26 | DBP-2 |  |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.5 | UG/L | 60.4999 | 2019-04-26 | DBP-3 |  |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 40.7 | UG/L | 80.4999 | 2019-04-26 | DBP-3 |  |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.6 | UG/L | 60.4999 | 2019-04-26 | DBP-4 |  |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 75.7 | UG/L | 80.4999 | 2019-04-26 | DBP-4 |  |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.2 | UG/L | 60.4999 | 2019-04-26 | DBP-6 |  |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 62.5 | UG/L | 80.4999 | 2019-04-26 | DBP-6 |  |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-10 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-10 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-05-10 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-24 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-24 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-05-24 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-06-08 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-06-08 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-06-08 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-06-25 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-06-25 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-06-25 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-07-02 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-07-05 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-07-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-07-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-07-18 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-07-22 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36 | UG/L | 60.4999 | 2019-07-24 | DBP-6 |  |  | 2713 RISMEN CT (DBP-6) (REPLACED 2750 RISMENT CT. ON 1-24-13, PRIOR DATA IS FROM 2720 RISMEN)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38 | UG/L | 60.4999 | 2019-07-24 | DBP-5 |  |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55.7 | UG/L | 80.4999 | 2019-07-24 | DBP-5 |  |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2019-07-24 | DBP-1 |  |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 44.2 | UG/L | 80.4999 | 2019-07-24 | DBP-1 |  |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.2 | UG/L | 60.4999 | 2019-07-24 | DBP-2 |  |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 72.8 | UG/L | 80.4999 | 2019-07-24 | DBP-2 |  |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2019-07-24 | DBP-3 |  |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 37 | UG/L | 80.4999 | 2019-07-24 | DBP-3 |  |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.1 | UG/L | 60.4999 | 2019-07-24 | DBP-4 |  |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 34.4 | UG/L | 80.4999 | 2019-07-24 | DBP-4 |  |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 60.6 | UG/L | 80.4999 | 2019-07-24 | DBP-6 |  |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2019-08-05 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-08-05 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-08-05 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-08-14 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-08-20 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2019-08-27 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-09-07 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-09-07 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-09 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2019-09-17 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-20 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2019-09-27 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-10-02 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-03 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-04 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-21 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-10-24 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.6 | UG/L | 60.4999 | 2019-10-24 | DBP-5 | 0.9 |  | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 56.4 | UG/L | 80.4999 | 2019-10-24 | DBP-5 | 0.32 |  | 1721 BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.1 | UG/L | 60.4999 | 2019-10-24 | DBP-1 | 0.9 |  | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 27.8 | UG/L | 80.4999 | 2019-10-24 | DBP-1 | 0.32 |  | 3200 SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.7 | UG/L | 60.4999 | 2019-10-24 | DBP-2 | 0.9 |  | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 56.5 | UG/L | 80.4999 | 2019-10-24 | DBP-2 | 0.32 |  | 1400 RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.3 | UG/L | 60.4999 | 2019-10-24 | DBP-3 | 0.9 |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 34.1 | UG/L | 80.4999 | 2019-10-24 | DBP-3 | 0.32 |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.9 | UG/L | 60.4999 | 2019-10-24 | DBP-4 | 0.9 |  | 145 E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 54.8 | UG/L | 80.4999 | 2019-10-24 | DBP-4 | 0.32 |  | 145 E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.9 | UG/L | 60.4999 | 2019-10-24 | DBP-6 | 0.9 |  | 2713 RISMEN CR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55.7 | UG/L | 80.4999 | 2019-10-24 | DBP-6 | 0.32 |  | 2713 RISMEN CR
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-11-01 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-08 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-09 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2019-11-15 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-21 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-26 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-12-03 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-12-07 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-12-12 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2019-12-23 | WTP5
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-12-23 | WTP1
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-12-27 | WTP3
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-03 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-01-04 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-14 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.9 | UG/L | 60.4999 | 2020-01-24 | DBP-5 | 0.9 |  | 1721 BRASSIE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 45.6 | UG/L | 80.4999 | 2020-01-24 | DBP-5 | 0.32 |  | 1721 BRASSIE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.8 | UG/L | 60.4999 | 2020-01-24 | DBP-1 | 0.9 |  | 3200 SERALAGO
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 36.3 | UG/L | 80.4999 | 2020-01-24 | DBP-1 | 0.32 |  | 3200 SERALAGO
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.1 | UG/L | 60.4999 | 2020-01-24 | DBP-2 | 0.9 |  | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 49.6 | UG/L | 80.4999 | 2020-01-24 | DBP-2 | 0.32 |  | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.9 | UG/L | 60.4999 | 2020-01-24 | DBP-3 | 0.9 |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 7.3 | UG/L | 80.4999 | 2020-01-24 | DBP-3 | 0.32 |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.3 | UG/L | 60.4999 | 2020-01-24 | DBP-6 | 0.9 |  | 2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 42.5 | UG/L | 80.4999 | 2020-01-24 | DBP-6 | 0.32 |  | 2713 RISMEN
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-24 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-25 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-01-25 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | WTP5 | 0.025
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | WTP5 | 0.025
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | WTP1 | 0.025
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | WTP3 | 0.025
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | WTP3 | 0.025
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 51.7 | UG/L | 60.4999 | 2020-01-28 | DBP-4 | 0.9 |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 58.8 | UG/L | 80.4999 | 2020-01-28 | DBP-4 | 0.32 |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-02-03 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-02-04 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-02-04 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-02-19 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-02-24 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP5 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-02-27 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-03-04 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-03-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-03-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2020-03-18 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-03-23 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-24 | WTP5 | 0.01 | 0.0149 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP5 | 0.01 | 0.0249 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-24 | WTP5 | 0.05 | 0.1499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-24 | WTP5 | 0.2 | 1.4999 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-24 | WTP5 | 0.6 | 0.6499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-24 | WTP5 | 0.03 | 0.0749 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-24 | WTP5 | 0.6 | 0.6499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-24 | WTP5 | 0.01 | 0.1499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-24 | WTP5 | 0.03 | 0.1499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-24 | WTP5 | 0.05 | 0.2499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-24 | WTP5 | 0.01 | 0.0449 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP5 | 0.02 | 0.0249 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-24 | WTP5 | 0.01 | 0.1499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP5 | 0.01 | 0.0249 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-24 | WTP5 | 0.1 | 0.1499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-24 | WTP5 | 0.01 | 0.2499 | CAMELOT WEST (482105/35539366001) 1Q 16 OF 29 SOCS. RESULTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-24 | WTP1 | 0.01 | 0.0149 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP1 | 0.01 | 0.0249 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-24 | WTP1 | 0.05 | 0.1499 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-24 | WTP1 | 0.6 | 0.6499 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-24 | WTP1 | 0.03 | 0.0749 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-24 | WTP1 | 0.6 | 0.6499 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-24 | WTP1 | 0.01 | 0.1499 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-24 | WTP1 | 0.03 | 0.1499 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-24 | WTP1 | 0.05 | 0.2499 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-24 | WTP1 | 0.01 | 0.0449 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP1 | 0.02 | 0.0249 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-24 | WTP1 | 0.01 | 0.1499 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP1 | 0.01 | 0.0249 | N. BERMUDA WP (482105/35539366002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-24 | WTP3 | 0.01 | 0.0149 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP3 | 0.01 | 0.0249 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-24 | WTP3 | 0.05 | 0.1499 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-24 | WTP3 | 0.6 | 0.6499 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-24 | WTP3 | 0.03 | 0.0749 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-24 | WTP3 | 0.6 | 0.6499 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.01 | UG/L | 54.9999 | 2020-03-24 | WTP3 | 0.01 | 0.1499 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-24 | WTP3 | 0.03 | 0.1499 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-24 | WTP3 | 0.05 | 0.2499 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-24 | WTP3 | 0.01 | 0.0449 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP3 | 0.02 | 0.0249 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-24 | WTP3 | 0.01 | 0.1499 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP3 | 0.01 | 0.0249 | PARKWAY WP (482105/35539366003) 1Q 13 OF 29 SOCS. RSLTS RCVD 3/24/21 (LATE) TO DEP. LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE. 2042 HEX... 0.01 < RDL OF 0.1 (J QUAL REMOVED)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-24 | WTP1 | 4.2 | 6.4999 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-24 | WTP1 | 0.44 | 2.4999 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-24 | WTP1 | 0.094 | 0.1499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-24 | WTP1 | 0.16 | 0.2499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-24 | WTP1 | 0.67 | 0.9499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-24 | WTP1 | 0.0032 | 0.0055 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-24 | WTP1 | 0.096 | 0.1499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-24 | WTP1 | 0.16 | 0.2499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-24 | WTP1 | 0.03 | 0.0449 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-24 | WTP1 | 0.077 | 0.1499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP1 | 0.0065 | 0.0249 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-24 | WTP1 | 0.0076 | 0.0149 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-24 | WTP1 | 0.046 | 0.2499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-24 | WTP3 | 0.59 | 1.4999 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-24 | WTP3 | 0.89 | 1.4999 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-24 | WTP3 | 0.16 | 0.4499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-24 | WTP3 | 3.3 | 9.4999 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-24 | WTP3 | 4.2 | 6.4999 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-24 | WTP3 | 0.44 | 2.4999 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-24 | WTP3 | 0.094 | 0.1499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-24 | WTP3 | 0.16 | 0.2499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-24 | WTP3 | 0.67 | 0.9499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-24 | WTP3 | 0.0042 | 0.0055 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-24 | WTP3 | 0.096 | 0.1499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-24 | WTP3 | 0.16 | 0.2499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-24 | WTP3 | 0.03 | 0.0449 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-24 | WTP3 | 0.077 | 0.1499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP3 | 0.0064 | 0.0249 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-24 | WTP3 | 0.0075 | 0.0149 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-24 | WTP3 | 0.045 | 0.2499 | PARKWAY WP (35539366003) 1Q 16 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT RQRD) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-24 | WTP5 | 0.89 | 1.4999 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-24 | WTP5 | 0.16 | 0.4499 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-24 | WTP5 | 3.3 | 9.4999 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-24 | WTP5 | 4.2 | 6.4999 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-24 | WTP5 | 0.44 | 2.4999 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-24 | WTP5 | 0.094 | 0.1499 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-24 | WTP5 | 0.16 | 0.2499 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-24 | WTP5 | 0.67 | 0.9499 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-24 | WTP5 | 0.004 | 0.0055 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-24 | WTP5 | 0.096 | 0.1499 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-24 | WTP5 | 0.16 | 0.2499 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-24 | WTP5 | 0.03 | 0.0449 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-24 | WTP5 | 0.0066 | 0.0249 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-24 | WTP5 | 0.0077 | 0.0149 | CAMELOT WEST (35539366001) 1Q 13 OF 29 SOCS PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 (LATE) TO DEP. LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-24 | WTP1 | 0.59 | 1.4999 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-24 | WTP1 | 0.89 | 1.4999 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-24 | WTP1 | 0.16 | 0.4499 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-24 | WTP1 | 3.3 | 9.4999 | N. BERMUDA WP (35539366002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 1ST WEEK OF MAY 2020 PER LAB SIGNATURE DATE.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-03-25 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-04-01 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-04-04 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-04-04 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-04-15 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-04-20 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-04-25 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.7 | UG/L | 60.4999 | 2020-04-28 | DBP-5 | 0.9 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 50.9 | UG/L | 80.4999 | 2020-04-28 | DBP-5 | 0.32 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.9 | UG/L | 60.4999 | 2020-04-28 | DBP-2 | 0.9 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 50.6 | UG/L | 80.4999 | 2020-04-28 | DBP-2 | 0.32 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.5 | UG/L | 60.4999 | 2020-04-28 | DBP-1 | 0.9 |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 17.1 | UG/L | 80.4999 | 2020-04-28 | DBP-1 | 0.32 |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.4 | UG/L | 60.4999 | 2020-04-28 | DBP-3 | 0.9 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2020-04-28 | DBP-3 | 0.32 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.8 | UG/L | 60.4999 | 2020-04-28 | DBP-4 | 0.9 |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 84.7 | UG/L | 80.4999 | 2020-04-28 | DBP-4 | 0.32 |  | 145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.1 | UG/L | 60.4999 | 2020-04-28 | DBP-6 | 0.9 |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 69 | UG/L | 80.4999 | 2020-04-28 | DBP-6 | 0.32 |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1025 | FLUORIDE | 0.19 | MG/L | 2.0499 | 2020-04-30 | WTP3 | 0.015 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-04-30 | WTP3 | 0.016 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-04-30 | WTP3 | 0.0012 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.0015 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1055 | SULFATE | 17 | MG/L | 250.4999 | 2020-04-30 | WTP3 | 2.5 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2020-04-30 | WTP3 | 0.0076 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP3 | 5 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.1 | LN(10) |  | 2020-04-30 | WTP3 | 0.1 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 167 | MG/L | 500.4999 | 2020-04-30 | WTP3 | 5 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP3 | 0.099 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-04-30 | WTP1 | 0.025 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-04-30 | WTP1 | 0.025 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-04-30 | WTP1 | 0.005 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2020-04-30 | WTP1 | 0.0023 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP1 | 0.00024 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.00081 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP1 | 0.00492 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1025 | FLUORIDE | 0.68 | MG/L | 4.0499 | 2020-04-30 | WTP1 | 0.015 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP1 | 0.00064 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP1 | 0.0001 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.002 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-04-30 | WTP1 | 0.00083 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1052 | SODIUM | 10.6 | MG/L | 160.4999 | 2020-04-30 | WTP1 | 0.59 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-04-30 | WTP1 | 0.0005 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP1 | 0.00021 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP1 | 0.0005 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP1 | 0.2 |  | N BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP1 | 0.0072 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1017 | CHLORIDE | 11.1 | MG/L | 250.4999 | 2020-04-30 | WTP1 | 2.5 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1022 | COPPER | 0.0041 | MG/L | 1.4999 | 2020-04-30 | WTP1 | 0.0093 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1025 | FLUORIDE | 0.68 | MG/L | 2.0499 | 2020-04-30 | WTP1 | 0.015 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-04-30 | WTP1 | 0.016 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-04-30 | WTP1 | 0.0015 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.0015 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1055 | SULFATE | 9.1 | MG/L | 250.4999 | 2020-04-30 | WTP1 | 2.5 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP1 | 5 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2020-04-30 | WTP1 | 0.1 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 128 | MG/L | 500.4999 | 2020-04-30 | WTP1 | 5 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP1 | 0.099 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-04-30 | WTP5 | 0.025 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2020-04-30 | WTP5 | 0.0023 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP5 | 0.00024 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP5 | 0.00081 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP5 | 0.00492 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1025 | FLUORIDE | 0.6 | MG/L | 4.0499 | 2020-04-30 | WTP5 | 0.015 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP5 | 0.00064 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP5 | 0.0001 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP5 | 0.002 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-04-30 | WTP5 | 0.00083 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1052 | SODIUM | 6.2 | MG/L | 160.4999 | 2020-04-30 | WTP5 | 0.59 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-04-30 | WTP5 | 0.0005 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP5 | 0.00021 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP5 | 0.0005 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP5 | 0.2 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP5 | 0.0072 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1017 | CHLORIDE | 9.5 | MG/L | 250.4999 | 2020-04-30 | WTP5 | 2.5 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2020-04-30 | WTP5 | 0.00093 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1025 | FLUORIDE | 0.6 | MG/L | 2.0499 | 2020-04-30 | WTP5 | 0.015 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-04-30 | WTP5 | 0.016 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP5 | 0.0015 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1055 | SULFATE | 10.2 | MG/L | 250.4999 | 2020-04-30 | WTP5 | 2.5 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2020-04-30 | WTP5 | 0.0076 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP5 | 5 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2020-04-30 | WTP5 | 0.1 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 145 | MG/L | 500.4999 | 2020-04-30 | WTP5 | 5 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP5 | 0.099 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-04-30 | WTP3 | 0.025 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-04-30 | WTP3 | 0.025 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-04-30 | WTP3 | 0.005 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2020-04-30 | WTP3 | 0.0023 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP3 | 0.00024 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.00081 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP3 | 0.00492 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2020-04-30 | WTP3 | 0.015 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP3 | 0.00064 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP3 | 0.0001 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.002 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-04-30 | WTP3 | 0.00083 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1052 | SODIUM | 12 | MG/L | 160.4999 | 2020-04-30 | WTP3 | 0.59 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-04-30 | WTP3 | 0.0005 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP3 | 0.00021 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP3 | 0.0005 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP3 | 0.2 |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP3 | 0.0072 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1017 | CHLORIDE | 13.9 | MG/L | 250.4999 | 2020-04-30 | WTP3 | 2.5 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2020-04-30 | WTP3 | 0.00093 |  | PARKWAY. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1095 | ZINC | 0.012 | MG/L | 5.4999 | 2020-04-30 | WTP1 | 0.0076 |  | NORTH BERMUDA. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1032 | MANGANESE | 0.0013 | MG/L | 0.0549 | 2020-04-30 | WTP5 | 0.0012 |  | CAMELOT WEST. ODOR Q QUALIEFIED, NOT ACCEPTED._VPU
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0.047 | MG/L | 1.4999 | 2020-04-30 | WTP5 | 0.025 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1005 | ARSENIC | 0.0006 | MG/L | 0.0104 | 2020-04-30 | WTP5 | 0.0005 |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-05-02 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-05-04 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2020-05-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-05-20 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-05-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-05-28 | WTP1 |  |  | NORTH BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP1 |  | 1.4999 | NORTH BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-05-28 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP5 |  | 1.4999 | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-05-28 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP3 |  | 1.4999 | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-05-28 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-06-01 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-06-02 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-06-07 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-06-15 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-06-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-06-24 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-07-03 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-07-04 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-07-11 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-07-23 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-07-23 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-07-24 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.1 | UG/L | 60.4999 | 2020-07-27 | DBP-5 | 0.9 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 62.1 | UG/L | 80.4999 | 2020-07-27 | DBP-5 | 0.47 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7 | UG/L | 60.4999 | 2020-07-27 | DBP-1 | 0.9 |  | 3200 SERALAGO BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 26.3 | UG/L | 80.4999 | 2020-07-27 | DBP-1 | 0.47 |  | 3200 SERALAGO BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.7 | UG/L | 60.4999 | 2020-07-27 | DBP-2 | 0.9 |  | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 72.2 | UG/L | 80.4999 | 2020-07-27 | DBP-2 | 0.47 |  | 1400 RIVIERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.8 | UG/L | 60.4999 | 2020-07-27 | DBP-3 | 0.9 |  | 120 SIMPSON RD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2020-07-27 | DBP-3 | 0.47 |  | 120 SIMPSON RD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 52.6 | UG/L | 60.4999 | 2020-07-27 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 74.5 | UG/L | 80.4999 | 2020-07-27 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.1 | UG/L | 60.4999 | 2020-07-27 | DBP-6 | 0.9 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 73.3 | UG/L | 80.4999 | 2020-07-27 | DBP-6 | 0.47 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-08-04 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-08-06 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-08-13 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-08-20 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-08-21 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-08-23 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1920 | ODOR THRESHOLD | 4 |  | 3.4999 | 2020-08-26 | WTP1 | 1 |  | N. BERMUDA WP - ODOR 4.0 (RCVD 4/14/21)
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2020-08-26 | WTP5 | 1 |  | CAMELOT WEST WP - ODOR -0- (RCVD 4/14/21)
3490751 | TOHO WATER AUTHORITY EASTERN | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2020-08-26 | WTP3 | 1 |  | PARKWAY WP - ODOR 1.0 (RCVD 4/14/21)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP5 | 0.68 | 1.4999 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP5 | 0.89 | 1.4999 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP5 | 0.16 | 0.4499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP5 | 3.3 | 9.4999 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP5 | 4.2 | 6.4999 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP5 | 0.44 | 2.4999 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP5 | 0.094 | 0.1499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP5 | 0.16 | 0.2499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP5 | 0.67 | 0.9499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP5 | 0.00071 | 0.0055 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP5 | 0.096 | 0.1499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP5 | 0.16 | 0.2499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP5 | 0.03 | 0.0449 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-27 | WTP5 | 0.044 | 0.1499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP5 | 0.0066 | 0.0249 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP5 | 0.0077 | 0.0149 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP5 | 0.035 | 0.2499 | CAMELOT WEST WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906006 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP1 | 0.69 | 1.4999 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP1 | 0.89 | 1.4999 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP1 | 0.16 | 0.4499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP1 | 3.3 | 9.4999 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP1 | 4.2 | 6.4999 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP1 | 0.44 | 2.4999 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP1 | 0.094 | 0.1499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP1 | 0.16 | 0.2499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP1 | 0.67 | 0.9499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP1 | 0.00093 | 0.0055 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP1 | 0.096 | 0.1499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP1 | 0.16 | 0.2499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP1 | 0.03 | 0.0449 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-27 | WTP1 | 0.045 | 0.1499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP1 | 0.0065 | 0.0249 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP1 | 0.0076 | 0.0149 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP1 | 0.035 | 0.2499 | N. BERMUDA WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH FOR ALL WPS) SMP 35573906007 (RCVD LATE 12/16/20+REVISED 12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-08-27 | WTP3 | 0.0054 | 0.0149 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP3 | 0.0065 | 0.0249 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-08-27 | WTP3 | 0.023 | 0.1499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP3 | 0.69 | 1.4999 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP3 | 0.89 | 1.4999 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP3 | 0.16 | 0.4499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP3 | 3.3 | 9.4999 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP3 | 4.2 | 6.4999 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-08-27 | WTP3 | 0.35 | 0.6499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP3 | 0.44 | 2.4999 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-08-27 | WTP3 | 0.039 | 0.0749 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-08-27 | WTP3 | 0.46 | 0.6499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP3 | 0.094 | 0.1499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP3 | 0.16 | 0.2499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-08-27 | WTP3 | 0.024 | 0.1499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP3 | 0.67 | 0.9499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP3 | 0.014 | 0.1499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-08-27 | WTP3 | 0.029 | 0.2499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP3 | 0.0007 | 0.0055 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-08-27 | WTP3 | 0.013 | 0.0449 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP3 | 0.003 | 0.0249 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP3 | 0.096 | 0.1499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP3 | 0.16 | 0.2499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-08-27 | WTP3 | 0.014 | 0.1499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP3 | 0.019 | 0.0249 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP3 | 0.03 | 0.0449 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-27 | WTP3 | 0.045 | 0.1499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP3 | 0.0065 | 0.0249 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP3 | 0.0076 | 0.0149 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP3 | 0.036 | 0.2499 | PARKWAY WP-2Q 29 OF 29 SOCS(PLUS EX.DIOX-NOT RQRD)J QUAL-ALL LCS BIASED HIGH: ENDOTHALL 145%,ALACHLOR 135%,ATRAZINE 132%(ENTD ALL 3 SINCE BIASED HIGH)SMP 35573906009(RCVD LATE12/16/20+REVISED12/23/20)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-09-03 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-09-05 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-09-08 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-09-21 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-09-23 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-09-24 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-10-05 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-10-12 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-10-21 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-10-21 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-10-22 | WTP5 | 0.0055 | 0.0149 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP5 | 0.0067 | 0.0249 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-10-22 | WTP5 | 0.024 | 0.1499 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-10-22 | WTP5 | 0.36 | 0.6499 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-10-22 | WTP5 | 0.04 | 0.0749 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-10-22 | WTP5 | 0.47 | 0.6499 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-10-22 | WTP5 | 0.025 | 0.1499 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-10-22 | WTP5 | 0.015 | 0.1499 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-10-22 | WTP5 | 0.029 | 0.2499 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-10-22 | WTP5 | 0.014 | 0.0449 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP5 | 0.003 | 0.0249 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-10-22 | WTP5 | 0.015 | 0.1499 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP5 | 0.02 | 0.0249 | CAMELOT WEST WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.5 | UG/L | 60.4999 | 2020-10-26 | DBP-5 | 0.9 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55.8 | UG/L | 80.4999 | 2020-10-26 | DBP-5 | 0.47 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.3 | UG/L | 60.4999 | 2020-10-26 | DBP-1 | 0.9 |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 23 | UG/L | 80.4999 | 2020-10-26 | DBP-1 | 0.47 |  | 3200 SERALAGO BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.4 | UG/L | 60.4999 | 2020-10-26 | DBP-2 | 0.9 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55.6 | UG/L | 80.4999 | 2020-10-26 | DBP-2 | 0.47 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22 | UG/L | 60.4999 | 2020-10-26 | DBP-3 | 0.9 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 35.8 | UG/L | 80.4999 | 2020-10-26 | DBP-3 | 0.47 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 59.5 | UG/L | 60.4999 | 2020-10-26 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 75.6 | UG/L | 80.4999 | 2020-10-26 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.6 | UG/L | 60.4999 | 2020-10-26 | DBP-6 | 0.9 |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 64.7 | UG/L | 80.4999 | 2020-10-26 | DBP-6 | 0.47 |  | 2713 RISMEN CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-10-27 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-10-31 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-11-03 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-11-05 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-11-09 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-11-19 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-11-22 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-11-23 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-12-02 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-12-03 | DIST | 0.2 |  | TUPPERWARE HYDRANT
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-12-03 | WTP1 | 0.0056 | 0.0149 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP1 | 0.0068 | 0.0249 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-12-03 | WTP1 | 0.024 | 0.1499 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-12-03 | WTP1 | 0.37 | 0.6499 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-12-03 | WTP1 | 0.041 | 0.0749 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-12-03 | WTP1 | 0.48 | 0.6499 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-12-03 | WTP1 | 0.025 | 0.1499 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-12-03 | WTP1 | 0.015 | 0.1499 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-12-03 | WTP1 | 0.03 | 0.2499 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-12-03 | WTP1 | 0.014 | 0.0449 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP1 | 0.0031 | 0.0249 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-12-03 | WTP1 | 0.015 | 0.1499 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP1 | 0.02 | 0.0249 | N. BERMUDA WP-2Q 13 OF 29 (1ST RCVD 12/16/20, REVISION RCVD 12/23/20) 1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-12-03 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-12-06 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-12-15 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-12-24 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-12-28 | WTP5 |  |  | CAMELOT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-01-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-14 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-20 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.6 | UG/L | 60.4999 | 2021-01-26 | DBP-5 | 0.9 |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 58.9 | UG/L | 80.4999 | 2021-01-26 | DBP-5 | 0.47 |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.7 | UG/L | 60.4999 | 2021-01-26 | DBP-1 | 0.9 |  | SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 70.4 | UG/L | 80.4999 | 2021-01-26 | DBP-1 | 0.47 |  | SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.8 | UG/L | 60.4999 | 2021-01-26 | DBP-2 | 0.9 |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 71.9 | UG/L | 80.4999 | 2021-01-26 | DBP-2 | 0.47 |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.4 | UG/L | 60.4999 | 2021-01-26 | DBP-3 | 0.9 |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 45.9 | UG/L | 80.4999 | 2021-01-26 | DBP-3 | 0.47 |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.9 | UG/L | 60.4999 | 2021-01-26 | DBP-4 | 0.9 |  | EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 70.9 | UG/L | 80.4999 | 2021-01-26 | DBP-4 | 0.47 |  | EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.8 | UG/L | 60.4999 | 2021-01-26 | DBP-6 | 0.9 |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 70.1 | UG/L | 80.4999 | 2021-01-26 | DBP-6 | 0.47 |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP1 |  |  | POE NORTH BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP1 |  |  | POE NORTH BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP3 |  |  | POE PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP3 |  |  | POE PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP5 |  |  | POE CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP5 |  |  | POE CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-02-09 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-02-11 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-11 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-19 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-02-20 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-27 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-05 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-03-08 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-09 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-03-20 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-03-24 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-26 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-06 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-08 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-13 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.3 | UG/L | 60.4999 | 2021-04-22 | DBP-5 | 0.9 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 47 | UG/L | 80.4999 | 2021-04-22 | DBP-5 | 0.47 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.7 | UG/L | 60.4999 | 2021-04-22 | DBP-1 | 0.9 |  | 3200 SERALAGO BLVD. [2Q TTHM LRAA=51.775]
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 87.4 | UG/L | 80.4999 | 2021-04-22 | DBP-1 | 0.47 |  | 3200 SERALAGO BLVD. [2Q TTHM LRAA=51.775]
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.3 | UG/L | 60.4999 | 2021-04-22 | DBP-2 | 0.9 |  | 1400 RIVERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 78.5 | UG/L | 80.4999 | 2021-04-22 | DBP-2 | 0.47 |  | 1400 RIVERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.4 | UG/L | 60.4999 | 2021-04-22 | DBP-3 | 0.9 |  | 120 SIMPSON RD. [2Q TTHM LRAA=55.42]
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 96.9 | UG/L | 80.4999 | 2021-04-22 | DBP-3 | 0.47 |  | 120 SIMPSON RD. [2Q TTHM LRAA=55.42]
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.6 | UG/L | 60.4999 | 2021-04-22 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 78.4 | UG/L | 80.4999 | 2021-04-22 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.3 | UG/L | 60.4999 | 2021-04-22 | DBP-6 | 0.9 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 69.8 | UG/L | 80.4999 | 2021-04-22 | DBP-6 | 0.47 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-23 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-01 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-10 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-05-15 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-24 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-05-27 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-06-02 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-08 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-08 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-22 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-25 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-25 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-07 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-07-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-21 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-07-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.1 | UG/L | 60.4999 | 2021-07-23 | DBP-1 | 0.9 |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 51.1 | UG/L | 80.4999 | 2021-07-23 | DBP-1 | 0.47 |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.3 | UG/L | 60.4999 | 2021-07-23 | DBP-5 |  |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 67.8 | UG/L | 80.4999 | 2021-07-23 | DBP-5 |  |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.6 | UG/L | 60.4999 | 2021-07-23 | DBP-2 |  |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 63.1 | UG/L | 80.4999 | 2021-07-23 | DBP-2 |  |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.8 | UG/L | 60.4999 | 2021-07-23 | DBP-3 |  |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 41.1 | UG/L | 80.4999 | 2021-07-23 | DBP-3 |  |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.6 | UG/L | 60.4999 | 2021-07-23 | DBP-4 |  |  | E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 59.9 | UG/L | 80.4999 | 2021-07-23 | DBP-4 |  |  | E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.6 | UG/L | 60.4999 | 2021-07-23 | DBP-6 |  |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 72.6 | UG/L | 80.4999 | 2021-07-23 | DBP-6 |  |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-08-04 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-11 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-08-11 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-18 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-08-24 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-08-27 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-01 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-04 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-06 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-19 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-21 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-09-22 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.2 | UG/L | 60.4999 | 2021-09-28 | DBP-7 |  |  | 2722 MATERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 49.3 | UG/L | 80.4999 | 2021-09-28 | DBP-7 |  |  | 2722 MATERA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.7 | UG/L | 60.4999 | 2021-09-28 | DBP-8 |  |  | 5690 BARLETTA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 50.6 | UG/L | 80.4999 | 2021-09-28 | DBP-8 |  |  | 5690 BARLETTA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-10-06 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-10-06 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-11 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-20 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.3 | UG/L | 60.4999 | 2021-10-25 | DBP-5 | 0.9 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 59 | UG/L | 80.4999 | 2021-10-25 | DBP-5 | 0.47 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.4 | UG/L | 60.4999 | 2021-10-25 | DBP-1 | 0.9 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 34.5 | UG/L | 80.4999 | 2021-10-25 | DBP-1 | 0.47 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.1 | UG/L | 60.4999 | 2021-10-25 | DBP-2 | 0.9 |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 55 | UG/L | 80.4999 | 2021-10-25 | DBP-2 | 0.47 |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.4 | UG/L | 60.4999 | 2021-10-25 | DBP-3 | 0.9 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 41.4 | UG/L | 80.4999 | 2021-10-25 | DBP-3 | 0.47 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.4 | UG/L | 60.4999 | 2021-10-25 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 64.9 | UG/L | 80.4999 | 2021-10-25 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.3 | UG/L | 60.4999 | 2021-10-25 | DBP-6 | 0.9 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 66.1 | UG/L | 80.4999 | 2021-10-25 | DBP-6 | 0.47 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-10-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-10-27 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-11-03 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-11-03 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-11-17 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-11-17 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-24 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-12-02 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-08 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-12-13 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-22 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.3 | UG/L | 60.4999 | 2021-12-22 | DBP-7 | 0.9 |  | 2722 MATERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 79.9 | UG/L | 80.4999 | 2021-12-22 | DBP-7 | 0.47 |  | 2722 MATERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 46.6 | UG/L | 60.4999 | 2021-12-22 | DBP-8 | 0.9 |  | 5690 BARLETTA DR
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 85 | UG/L | 80.4999 | 2021-12-22 | DBP-8 | 0.47 |  | 5690 BARLETTA DR
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-12-23 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-29 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-01-04 | WTP5 |  |  | WTP 5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-06 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-12 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-17 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-01-19 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-21 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.5 | UG/L | 60.4999 | 2022-01-26 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 49.5 | UG/L | 80.4999 | 2022-01-26 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28 | UG/L | 60.4999 | 2022-01-26 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 37.2 | UG/L | 80.4999 | 2022-01-26 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.9 | UG/L | 60.4999 | 2022-01-26 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 41.3 | UG/L | 80.4999 | 2022-01-26 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.9 | UG/L | 60.4999 | 2022-01-26 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 35 | UG/L | 80.4999 | 2022-01-26 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.4 | UG/L | 60.4999 | 2022-01-26 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 52.8 | UG/L | 80.4999 | 2022-01-26 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.9 | UG/L | 60.4999 | 2022-01-26 | DBP-6 |  |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 46.4 | UG/L | 80.4999 | 2022-01-26 | DBP-6 |  |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-02-02 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-02-08 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-02-15 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-17 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP5 | 0.025 |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP5 | 0.025 |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP1 | 0.025 |  | N. BERMUDA WP (NITRATE OK-ENT'D, NITRITE J QUALIFIER-NOT ENT'D PENDING EVALUATION)
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP3 | 0.025 |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP3 | 0.025 |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-22 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-02-24 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-03-04 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-07 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-03-08 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-14 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-22 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-03-22 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-03-24 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-04-05 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-07 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-12 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-18 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-04-20 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30 | UG/L | 60.4999 | 2022-04-22 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 46.9 | UG/L | 80.4999 | 2022-04-22 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.1 | UG/L | 60.4999 | 2022-04-22 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 40.8 | UG/L | 80.4999 | 2022-04-22 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.8 | UG/L | 60.4999 | 2022-04-22 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 52.7 | UG/L | 80.4999 | 2022-04-22 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.8 | UG/L | 60.4999 | 2022-04-22 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 26.2 | UG/L | 80.4999 | 2022-04-22 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.7 | UG/L | 60.4999 | 2022-04-22 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 61.9 | UG/L | 80.4999 | 2022-04-22 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33 | UG/L | 60.4999 | 2022-04-22 | DBP-6 |  |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 53.8 | UG/L | 80.4999 | 2022-04-22 | DBP-6 |  |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-23 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-10 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-10 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-12 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-18 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-24 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-25 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-07 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-07 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-09 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-14 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-27 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-28 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.1 | UG/L | 60.4999 | 2022-07-25 | DBP-5 | 0.9 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 62.7 | UG/L | 80.4999 | 2022-07-25 | DBP-5 | 0.47 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.5 | UG/L | 60.4999 | 2022-07-25 | DBP-1 | 0.9 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 45 | UG/L | 80.4999 | 2022-07-25 | DBP-1 | 0.47 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.6 | UG/L | 60.4999 | 2022-07-25 | DBP-2 | 0.9 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 52.3 | UG/L | 80.4999 | 2022-07-25 | DBP-2 | 0.47 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.1 | UG/L | 60.4999 | 2022-07-25 | DBP-3 | 0.9 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 39.7 | UG/L | 80.4999 | 2022-07-25 | DBP-3 | 0.47 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.3 | UG/L | 60.4999 | 2022-07-25 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 52.9 | UG/L | 80.4999 | 2022-07-25 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.3 | UG/L | 60.4999 | 2022-07-25 | DBP-6 | 0.9 |  | 2713 RISMEN CT., KISS. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 71 | UG/L | 80.4999 | 2022-07-25 | DBP-6 | 0.47 |  | 2713 RISMEN CT., KISS. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.4 | UG/L | 60.4999 | 2022-10-26 | DBP-5 |  |  | 1721 BRASSIE CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 51.3 | UG/L | 80.4999 | 2022-10-26 | DBP-5 |  |  | 1721 BRASSIE CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.4 | UG/L | 60.4999 | 2022-10-26 | DBP-1 |  |  | 3250 OWASSA CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 44.9 | UG/L | 80.4999 | 2022-10-26 | DBP-1 |  |  | 3250 OWASSA CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.2 | UG/L | 60.4999 | 2022-10-26 | DBP-2 |  |  | 1400 RIVIERA DR TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 53.6 | UG/L | 80.4999 | 2022-10-26 | DBP-2 |  |  | 1400 RIVIERA DR TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.5 | UG/L | 60.4999 | 2022-10-26 | DBP-3 |  |  | 120 SIMPSON RD TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 13.1 | UG/L | 80.4999 | 2022-10-26 | DBP-3 |  |  | 120 SIMPSON RD TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.9 | UG/L | 60.4999 | 2022-10-26 | DBP-4 |  |  | 145 E LAKESHORE TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 24.4 | UG/L | 80.4999 | 2022-10-26 | DBP-4 |  |  | 145 E LAKESHORE TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.6 | UG/L | 60.4999 | 2022-10-26 | DBP-6 |  |  | 2713 RISEMEN CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | DBP | 2950 | TOTAL THMS | 32.9 | UG/L | 80.4999 | 2022-10-26 | DBP-6 |  |  | 2713 RISEMEN CT TTHM HAA5
3490766 | LAKE MARIAN RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-05-02 | AAA
3490766 | LAKE MARIAN RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-02 | AAA
3490766 | LAKE MARIAN RESORT | INOR | 1040 | NITRATE | 0.45 | MG/L | 10.4999 | 2019-10-09 | AAA
3490766 | LAKE MARIAN RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-10-09 | AAA
3490766 | LAKE MARIAN RESORT | INOR | 1040 | NITRATE | 0.058 | MG/L | 10.4999 | 2020-10-14 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-10-14 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1017 | CHLORIDE | 58 | MG/L | 250.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1025 | FLUORIDE | 2 | MG/L | 2.0499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1055 | SULFATE | 7.6 | MG/L | 250.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1905 | COLOR | 7.7 | COLOR UNITS | 15.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.01 | LN(10) |  | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 300 | MG/L | 500.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | INOR | 1040 | NITRATE | 0.011 | MG/L | 10.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1025 | FLUORIDE | 2 | MG/L | 4.0499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1052 | SODIUM | 36 | MG/L | 160.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-02-22 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-22 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-22 | AAA |  | 0.4499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 9.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-22 | AAA |  | 6.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-02-22 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-22 | AAA |  | 2.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-02-22 | AAA |  | 0.0749 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-02-22 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-22 | AAA |  | 0.9499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-02-22 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-22 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.6 | PCI/L | 15.4999 | 2021-03-01 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | RAD | 4020 | RADIUM-226 | 3.2 | PCI/L | 3.4999 | 2021-03-01 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-03-01 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | INOR | 1025 | FLUORIDE | 1.9 | MG/L | 4.0499 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | INOR | 1030 | LEAD | 0.0011 | MG/L | 0.0154 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | INOR | 1052 | SODIUM | 38.1 | MG/L | 160.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | SEC | 1017 | CHLORIDE | 60.7 | MG/L | 250.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | SEC | 1022 | COPPER | 0.025 | MG/L | 1.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | SEC | 1025 | FLUORIDE | 1.9 | MG/L | 2.0499 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | SEC | 1055 | SULFATE | 9 | MG/L | 250.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | SEC | 1095 | ZINC | 0.049 | MG/L | 5.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 305 | MG/L | 500.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-03-23 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-03-23 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-08-09 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-08-09 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-08-09 | AAA |  | 0.4499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 9.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-08-09 | AAA |  | 6.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-08-09 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-08-09 | AAA |  | 2.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-08-09 | AAA |  | 0.0749 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-08-09 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-08-09 | AAA |  | 0.9499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-08-09 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-08-09 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.5 | PCI/L | 15.4999 | 2021-08-09 | AAA |  |  | POE (REVISED SMP DATE FROM 8/11/21 TO 8/9/21-BB)
3490766 | LAKE MARIAN RESORT | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2021-08-09 | AAA |  | 1.4999 | POE (REVISED SMP DATE FROM 8/11/21 TO 8/9/21-BB)
3490766 | LAKE MARIAN RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-08-09 | AAA |  | 1.4999 | POE (REVISED SMP DATE FROM 8/11/21 TO 8/9/21-BB)
3490766 | LAKE MARIAN RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-09-01 | AAA | 1.2 |  | RCVD SAMPLER CERT 11/18/21
3490766 | LAKE MARIAN RESORT | RAD | 4020 | RADIUM-226 | 1.4 | PCI/L | 3.4999 | 2021-09-01 | AAA | 0.2 | 1.4999 | RCVD SAMPLER CERT 11/18/21
3490766 | LAKE MARIAN RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-09-01 | AAA | 0.7 | 1.4999 | RCVD SAMPLER CERT 11/18/21
3490766 | LAKE MARIAN RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-09-01 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-09-01 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-09-01 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-09-01 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-09-01 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-09-01 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-09-01 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-09-01 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-09-01 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-09-01 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-09-01 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-09-07 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-09-07 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-03 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-03 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-03 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-03 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-03 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-03 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-03 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-03 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-03 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.3 | PCI/L | 15.4999 | 2021-11-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-11-03 | AAA | 1.5 | 3.4999 | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-11-03 | AAA | 1.5 |  | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-11-03 | AAA | 0.4 | 0.667 | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-11-03 | AAA | 0.6 | 1.4999 | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1010 | BARIUM | 0.0131 | MG/L | 2.4999 | 2021-11-03 | AAA | 0.002 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1020 | CHROMIUM | 0.0013 | MG/L | 0.1499 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-11-03 | AAA | 0.005 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1025 | FLUORIDE | 2.05 | MG/L | 4.0499 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-11-03 | AAA | 0.0001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-11-03 | AAA | 0.002 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1052 | SODIUM | 41 | MG/L | 160.4999 | 2021-11-03 | AAA | 0.5 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-11-03 | AAA | 0.0005 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1017 | CHLORIDE | 73.8 | MG/L | 250.4999 | 2021-11-03 | AAA | 0.4 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1022 | COPPER | 0.0029 | MG/L | 1.4999 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1025 | FLUORIDE | 2.05 | MG/L | 2.0499 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1028 | IRON | 0.0601 | MG/L | 0.3499 | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1050 | SILVER | 0.0005 | MG/L | 0.1499 | 2021-11-03 | AAA | 0.0005 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1055 | SULFATE | 8.8 | MG/L | 250.4999 | 2021-11-03 | AAA | 1 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1095 | ZINC | 0.0373 | MG/L | 5.4999 | 2021-11-03 | AAA | 0.002 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-11-03 | AAA | 5 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-11-03 | AAA | 1 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.97 | LN(10) |  | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 374 | MG/L | 500.4999 | 2021-11-03 | AAA | 2.5 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-03 | AAA | 0.01 | 0.0149 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.01 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-03 | AAA | 0.05 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 1.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-03 | AAA | 0.1 | 1.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-03 | AAA | 0.4 | 0.4499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 9 | 9.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA | 6 | 6.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-03 | AAA | 0.6 | 0.6499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-03 | AAA | 2 | 2.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-03 | AAA | 0.07 | 0.0749 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-03 | AAA | 0.6 | 0.6499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-03 | AAA | 0.2 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-03 | AAA | 0.9 | 0.9499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-03 | AAA | 0.2 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-03 | AAA | 0.01 | 0.0449 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.01 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-03 | AAA | 0.2 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.02 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.04 | 0.0449 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.02 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-03 | AAA | 0.01 | 0.0149 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-03 | AAA | 0.01 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-11-09 | AAA |  | 0.0055 | DIOXIN - NOT REQUIRED
3490766 | LAKE MARIAN RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19 | UG/L | 60.4999 | 2021-11-13 | L1 | 1 |  | LOT 134
3490766 | LAKE MARIAN RESORT | DBP | 2950 | TOTAL THMS | 69.6 | UG/L | 80.4999 | 2021-11-13 | L1 | 0.5 |  | LOT 134
3490766 | LAKE MARIAN RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.8 | UG/L | 60.4999 | 2021-11-13 | L2 | 1 |  | LOT 107 TTHM MCL_NMS
3490766 | LAKE MARIAN RESORT | DBP | 2950 | TOTAL THMS | 82.1 | UG/L | 80.4999 | 2021-11-13 | L2 | 0.5 |  | LOT 107 TTHM MCL_NMS
3490766 | LAKE MARIAN RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0.5 | UG/L | 74.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0.5 | UG/L | 74.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2955 | TOT XYLENE | 0.5 | UG/L | 10499.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2964 | DICHLOROMETHANE | 0.5 | UG/L | 5.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0.5 | UG/L | 649.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0.5 | UG/L | 75.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2976 | VINYL CHLORIDE | 0.5 | UG/L | 1.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0.5 | UG/L | 7.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0.5 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0.5 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0.5 | UG/L | 249.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0.5 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0.5 | UG/L | 5.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0.5 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0.5 | UG/L | 5.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0.5 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2989 | CHLOROBENZENE | 0.5 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2990 | BENZENE | 0.5 | UG/L | 1.4999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2991 | TOLUENE | 0.5 | UG/L | 1499.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2992 | ETHYLBENZENE | 0.5 | UG/L | 749.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | VOC | 2996 | STYRENE | 0.5 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2005 | ENDRIN | 0.01 | UG/L | 2.4999 | 2022-01-26 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2010 | LINDANE | 0.01 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2015 | METHOXYCLOR | 0.05 | UG/L | 44.9999 | 2022-01-26 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2020 | TOXAPHENE | 0.5 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2031 | DALAPON | 0.1 | UG/L | 249.9999 | 2022-01-26 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2032 | DIQUAT | 0.4 | UG/L | 24.9999 | 2022-01-26 | AAA |  | 0.4499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2033 | ENDOTHALL | 9 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 9.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2034 | GLYPHOSATE | 6 | UG/L | 749.9999 | 2022-01-26 | AAA |  | 6.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0.6 | UG/L | 449.9999 | 2022-01-26 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2036 | OXAMYL (VYDATE) | 2 | UG/L | 249.9999 | 2022-01-26 | AAA |  | 2.4999 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2037 | SIMAZINE | 0.07 | UG/L | 4.4999 | 2022-01-26 | AAA |  | 0.0749 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0.6 | UG/L | 6.4999 | 2022-01-26 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2040 | PICLORAM | 0.1 | UG/L | 549.9999 | 2022-01-26 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.1 | UG/L | 54.9999 | 2022-01-26 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2046 | CARBOFURAN | 0.9 | UG/L | 44.9999 | 2022-01-26 | AAA |  | 0.9499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2050 | ATRAZINE | 0.1 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0.2 | UG/L | 2.4999 | 2022-01-26 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2065 | HEPTACHLOR | 0.01 | UG/L | 0.4499 | 2022-01-26 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0.01 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2105 | 2,4-D | 0.1 | UG/L | 74.9999 | 2022-01-26 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0.2 | UG/L | 54.9999 | 2022-01-26 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0.1 | UG/L | 1.4999 | 2022-01-26 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2306 | BENZO(A)PYRENE | 0.02 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0.1 | UG/L | 0.5499 | 2022-01-26 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0.02 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0.01 | UG/L | 0.0249 | 2022-01-26 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | SOC | 2959 | CHLORDANE | 0.01 | UG/L | 2.4999 | 2022-01-26 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.3 | PCI/L | 15.4999 | 2022-01-26 | AAA |  |  | 1ST QRTR (SAMPLE DATE REVISED FROM 2/1/22 TO 1/26/22 3/16/22, R228 REVISED FROM 0.5 TO -0- 3/16/22)
3490766 | LAKE MARIAN RESORT | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2022-01-26 | AAA |  | 1.4999 | 1ST QRTR (SAMPLE DATE REVISED FROM 2/1/22 TO 1/26/22 3/16/22, R228 REVISED FROM 0.5 TO -0- 3/16/22)
3490766 | LAKE MARIAN RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-01-26 | AAA |  | 1.4999 | 1ST QRTR (SAMPLE DATE REVISED FROM 2/1/22 TO 1/26/22 3/16/22, R228 REVISED FROM 0.5 TO -0- 3/16/22)
3490766 | LAKE MARIAN RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.6 | UG/L | 60.4999 | 2022-02-28 | L2 | 1 |  | LOT 107
3490766 | LAKE MARIAN RESORT | DBP | 2950 | TOTAL THMS | 47.3 | UG/L | 80.4999 | 2022-02-28 | L2 | 0.5 |  | LOT 107
3490766 | LAKE MARIAN RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.7 | UG/L | 60.4999 | 2022-02-28 | L1 | 1 |  | LOT 134 (HLKD)
3490766 | LAKE MARIAN RESORT | DBP | 2950 | TOTAL THMS | 25.9 | UG/L | 80.4999 | 2022-02-28 | L1 | 0.5 |  | LOT 134 (HLKD)
3490766 | LAKE MARIAN RESORT | INOR | 1025 | FLUORIDE | 2.05 | MG/L | 4.0499 | 2022-05-31 | AAA | 0.2 |  | FLUORIDE 2.05 MG/L
3490766 | LAKE MARIAN RESORT | SEC | 1025 | FLUORIDE | 2.05 | MG/L | 2.0499 | 2022-05-31 | AAA | 0.2 |  | FLUORIDE 2.05 MG/L (HLKD). SYSTEM UNDER DRAFT CO. NEW WELL IS BEING DRILLED/PERMITTED AT THIS TIME_VPU
3490766 | LAKE MARIAN RESORT | INOR | 1025 | FLUORIDE | 1.9 | MG/L | 4.0499 | 2022-08-09 | AAA | 0.05 |  | (FL 1.9 MG/L) PAGE 2 OF LAB REPORT NOT SIGNED BY LAB REPRESENTATIVE TO VERIFY RESULTS (HLKD)
3490766 | LAKE MARIAN RESORT | SEC | 1025 | FLUORIDE | 1.9 | MG/L | 2.0499 | 2022-08-09 | AAA | 0.05 |  | (FL 1.9 MG/L) PAGE 2 OF LAB REPORT NOT SIGNED BY LAB REPRESENTATIVE TO VERIFY RESULTS (HLKD)
3490766 | LAKE MARIAN RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20 | UG/L | 60.4999 | 2022-08-10 | L1 |  |  | LOT 134
3490766 | LAKE MARIAN RESORT | DBP | 2950 | TOTAL THMS | 0.5 | UG/L | 80.4999 | 2022-08-10 | L1 |  |  | LOT 134
3490766 | LAKE MARIAN RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20 | UG/L | 60.4999 | 2022-08-10 | L2 |  |  | LOT 107
3490766 | LAKE MARIAN RESORT | DBP | 2950 | TOTAL THMS | 0.5 | UG/L | 80.4999 | 2022-08-10 | L2 |  |  | LOT 107
3490766 | LAKE MARIAN RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-17 | AAA | 0.01 | 0.0449 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-17 | AAA | 0.01 | 0.0249 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-17 | AAA | 0.18 | 0.1499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-17 | AAA | 0.35 | 0.2499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-17 | AAA | 0.1 | 0.1499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-17 | AAA | 0.02 | 0.0249 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-17 | AAA | 0.07 | 0.0449 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-17 | AAA | 0.1 | 0.1499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-17 | AAA | 0.02 | 0.0249 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-17 | AAA | 0.01 | 0.0149 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-17 | AAA | 0.01 | 0.2499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | RAD | 4020 | RADIUM-226 | 1.12 | PCI/L | 3.4999 | 2022-08-17 | AAA | 0.328 | 1.4999 | 4002 GA LAB MDL, 4.32, EXCEEDS THE RDL OF 3(MDL MUST BE
3490986 | PLEASANT HILL VILLAGE | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.1499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.0449 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2019-02-14 | AAA |  | 0.1499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2019-02-14 | AAA |  | 0.0149 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.0149 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.1499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 1.4999 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 1.4999 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2019-02-14 | AAA |  | 0.4499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2019-02-14 | AAA |  | 9.4999 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2019-02-14 | AAA |  | 6.4999 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2019-02-14 | AAA |  | 0.6499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 2.4999 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2019-02-14 | AAA |  | 0.0749 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2019-02-14 | AAA |  | 0.6499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2019-02-14 | AAA |  | 0.1499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2019-02-14 | AAA |  | 0.2499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2019-02-14 | AAA |  | 0.1499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.9499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 0.1499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2019-02-14 | AAA |  | 0.0449 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2019-02-14 | AAA |  | 0.1499 | MAKEUP 2018 SAMPLES. REC'D 03/07/19
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2019-02-14 | AAA |  | 0.5499 | 1QM TOT XYLENE (2QM DUE 4-6/19)_VP. MISSING Q2, INPUT Q3 11/4/19. NEED DX WHEN Q2 REC GC
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2019-08-27 | AAA | 0.25 | 0.5499 | 1QM (2QM DUE 10-12/2019) ; QM/XY (RCVD 10-30-19)._VP [10-12/2019 3QM MISSED, RESTART Q SAMPLING_VPU]
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-08-27 | AAA
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-08-27 | AAA
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.6 | UG/L | 60.4999 | 2019-11-19 | L1 | 0.9 |  | MAKUP SAMPLES. MISSED 3Q19, RETURN TO ROUTINE, 2 LOCATIONS ANNUALLY_VPU | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | 21.5 | UG/L | 80.4999 | 2019-11-19 | L1 | 0.32 |  | MAKUP SAMPLES. MISSED 3Q19, RETURN TO ROUTINE, 2 LOCATIONS ANNUALLY_VPU | 3
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-01-31 | AAA | 0.25 | 0.5499 | 1QM TOT XYLENE (RES-START DUE TO MISSED Q, 2QM NEXT DUE 4-6/20_VPU)
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-04-27 | AAA |  | 0.5499 | 2QM BIB AT WASTEWATER PLANT
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-07-14 | AAA | 0.11 | 0.5499 | 3QM BIB WW PLANT
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-07-14 | AAA | 0.025 |  | POE PLANT TAP NN
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-14 | AAA | 0.025 |  | POE PLANT TAP NN
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.1 | UG/L | 60.4999 | 2020-08-11 | L1 | 0.9 |  | BIBB @ WWTP | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | 30.6 | UG/L | 80.4999 | 2020-08-11 | L1 | 0.47 |  | BIBB @ WWTP | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.5 | UG/L | 60.4999 | 2020-08-11 | L2 | 0.9 |  | MH 100 | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | 33.9 | UG/L | 80.4999 | 2020-08-11 | L2 | 0.47 |  | MH 100 | 3
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-10-09 | AAA |  | 0.5499 | 4QM TOT XYLENE. MOVE TO ANNUAL 1Q. NEXT DUE 1Q2021
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-01-06 | AAA |  | 0.5499 | 1AM - TOTAL XYLENE. 2AM DUE 1Q2022_VPU
3490986 | PLEASANT HILL VILLAGE | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-04-09 | AAA | 0.042
3490986 | PLEASANT HILL VILLAGE | SEC | 1017 | CHLORIDE | 14.3 | MG/L | 250.4999 | 2021-04-09 | AAA | 2.5
3490986 | PLEASANT HILL VILLAGE | SEC | 1022 | COPPER | 0.0028 | MG/L | 1.4999 | 2021-04-09 | AAA | 0.0026
3490986 | PLEASANT HILL VILLAGE | SEC | 1025 | FLUORIDE | 0.25 | MG/L | 2.0499 | 2021-04-09 | AAA | 0.015
3490986 | PLEASANT HILL VILLAGE | SEC | 1028 | IRON | 0.035 | MG/L | 0.3499 | 2021-04-09 | AAA | 0.016
3490986 | PLEASANT HILL VILLAGE | SEC | 1032 | MANGANESE | 0.0037 | MG/L | 0.0549 | 2021-04-09 | AAA | 0.0012
3490986 | PLEASANT HILL VILLAGE | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-04-09 | AAA | 0.0015
3490986 | PLEASANT HILL VILLAGE | SEC | 1055 | SULFATE | 32.6 | MG/L | 250.4999 | 2021-04-09 | AAA | 2.5
3490986 | PLEASANT HILL VILLAGE | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-04-09 | AAA | 0.0076
3490986 | PLEASANT HILL VILLAGE | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-04-09 | AAA | 5
3490986 | PLEASANT HILL VILLAGE | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-04-09 | AAA | 1
3490986 | PLEASANT HILL VILLAGE | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.1 | LN(10) |  | 2021-04-09 | AAA | 0.1
3490986 | PLEASANT HILL VILLAGE | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 246 | MG/L | 500.4999 | 2021-04-09 | AAA | 5
3490986 | PLEASANT HILL VILLAGE | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-04-09 | AAA | 0.099
3490986 | PLEASANT HILL VILLAGE | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-04-09 | AAA | 2.86
3490986 | PLEASANT HILL VILLAGE | RAD | 4020 | RADIUM-226 | 1.12 | PCI/L | 3.4999 | 2021-04-09 | AAA | 0.44 | 1.4999
3490986 | PLEASANT HILL VILLAGE | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-09 | AAA | 0.83 | 1.4999
3490986 | PLEASANT HILL VILLAGE | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-09 | AAA | 0.0054 | 0.0149 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.0065 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-09 | AAA | 0.023 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.67 | 1.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2031 | DALAPON | 0.32 | UG/L | 249.9999 | 2021-04-09 | AAA | 0.23 | 1.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-04-09 | AAA | 0.16 | 0.4499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 3.3 | 9.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA | 4.2 | 6.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-04-09 | AAA | 0.36 | 0.6499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-04-09 | AAA | 0.46 | 2.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-09 | AAA | 0.039 | 0.0749 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-09 | AAA | 0.46 | 0.6499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-04-09 | AAA | 0.04 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-04-09 | AAA | 0.16 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-09 | AAA | 0.024 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-04-09 | AAA | 0.59 | 0.9499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.014 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-09 | AAA | 0.029 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-09 | AAA | 0.013 | 0.0449 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.003 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-04-09 | AAA | 0.096 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-04-09 | AAA | 0.053 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.014 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.019 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.014 | 0.0449 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-04-09 | AAA | 0.043 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.0065 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-04-09 | AAA | 0.0076 | 0.0149 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-04-09 | AAA | 0.035 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-04-09 | AAA | 0.025
3490986 | PLEASANT HILL VILLAGE | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-09 | AAA | 0.025
3490986 | PLEASANT HILL VILLAGE | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-04-09 | AAA | 0.0005
3490986 | PLEASANT HILL VILLAGE | INOR | 1010 | BARIUM | 0.026 | MG/L | 2.4999 | 2021-04-09 | AAA | 0.0023
3490986 | PLEASANT HILL VILLAGE | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-04-09 | AAA | 0.00024
3490986 | PLEASANT HILL VILLAGE | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-04-09 | AAA | 0.00081
3490986 | PLEASANT HILL VILLAGE | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-04-09 | AAA | 0.005
3490986 | PLEASANT HILL VILLAGE | INOR | 1025 | FLUORIDE | 0.25 | MG/L | 4.0499 | 2021-04-09 | AAA | 0.015
3490986 | PLEASANT HILL VILLAGE | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-04-09 | AAA | 0.00022
3490986 | PLEASANT HILL VILLAGE | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-04-09 | AAA | 9e-05
3490986 | PLEASANT HILL VILLAGE | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-04-09 | AAA | 0.002
3490986 | PLEASANT HILL VILLAGE | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-04-09 | AAA | 0.00083
3490986 | PLEASANT HILL VILLAGE | INOR | 1052 | SODIUM | 12.6 | MG/L | 160.4999 | 2021-04-09 | AAA | 0.59
3490986 | PLEASANT HILL VILLAGE | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-04-09 | AAA | 0.00021
3490986 | PLEASANT HILL VILLAGE | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-04-09 | AAA | 0.00021
3490986 | PLEASANT HILL VILLAGE | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-04-09 | AAA | 0.0005
3490986 | PLEASANT HILL VILLAGE | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA | 0.35 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA | 0.33 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-09 | AAA | 0.11 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA | 0.44 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-09 | AAA | 0.3 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.12 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-09 | AAA | 0.29 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 0.27 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.3 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-09 | AAA | 0.27 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.28 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA | 0.44 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA | 0.28 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.4 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-09 | AAA | 0.28 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA | 0.23 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 0.2 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.4 | UG/L | 60.4999 | 2021-08-20 | L1 | 0.9 |  | HOSEBIBB @ WWTP (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | 24.9 | UG/L | 80.4999 | 2021-08-20 | L1 | 0.47 |  | HOSEBIBB @ WWTP (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21 | UG/L | 60.4999 | 2021-08-20 | L2 | 0.9 |  | MOB. HOME 100 (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2021-08-20 | L2 | 0.47 |  | MOB. HOME 100 (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490986 | PLEASANT HILL VILLAGE | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-03-30 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.2 | UG/L | 60.4999 | 2022-08-19 | L2 | 0.9 |  | MH 100 TTHM HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | 29.5 | UG/L | 80.4999 | 2022-08-19 | L2 | 0.47 |  | MH 100 TTHM HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2022-08-19 | L1 | 0.9 |  | BIBB @ WWTP TTHM HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | DBP | 2950 | TOTAL THMS | 22.6 | UG/L | 80.4999 | 2022-08-19 | L1 | 0.47 |  | BIBB @ WWTP TTHM HAA5 | 3
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-02-09 | AAA |  | 0.6499 | START OF QTRLY SAMPLING FOR ADIPATE- 2018
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-06-19 | AAA | 0.6 | 0.6499
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-06-19 | AAA | 0.6 | 0.6499
3491002 | KISSIMMEE RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28 | UG/L | 60.4999 | 2018-09-17 | L1 |  |  | WWTF HOSE BIB | 3
3491002 | KISSIMMEE RV PARK | DBP | 2950 | TOTAL THMS | 17.8 | UG/L | 80.4999 | 2018-09-17 | L1 |  |  | WWTF HOSE BIB | 3
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-09-21 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | SEC | 1017 | CHLORIDE | 21.1 | MG/L | 250.4999 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1017 | CHLORIDE | 21.1 | MG/L | 250.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1028 | IRON | 0.0385 | MG/L | 0.3499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1055 | SULFATE | 3.2 | MG/L | 250.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.17 | LN(10) |  | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 176 | MG/L | 500.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 0.5499 | 1AMSAMPLE 3 ANNUAL 2018, 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-10-29 | AAA |  | 0.0149 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-10-29 | AAA |  | 0.1499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 1.4999 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 1.4999 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-10-29 | AAA |  | 0.4499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-10-29 | AAA |  | 9.4999 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-10-29 | AAA |  | 6.4999 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-10-29 | AAA |  | 0.6499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-10-29 | AAA |  | 2.4999 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-10-29 | AAA |  | 0.0749 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-10-29 | AAA |  | 0.6499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-10-29 | AAA |  | 0.1499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-10-29 | AAA |  | 0.2499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-10-29 | AAA |  | 0.1499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-10-29 | AAA |  | 0.9499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-10-29 | AAA |  | 0.1499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-10-29 | AAA |  | 0.2499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-10-29 | AAA |  | 0.0449 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-10-29 | AAA |  | 0.1499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-10-29 | AAA |  | 0.2499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.1499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-10-29 | AAA |  | 0.0449 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-10-29 | AAA |  | 0.1499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-10-29 | AAA |  | 0.0249 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-10-29 | AAA |  | 0.0149 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-10-29 | AAA |  | 0.2499 | 1ST AM FOR PHTALATE, SAMPLE 4TH Q 2019, 2020
3491002 | KISSIMMEE RV PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.17 | LN(10) |  | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 176 | MG/L | 500.4999 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1010 | BARIUM | 0.0144 | MG/L | 2.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1020 | CHROMIUM | 0.0011 | MG/L | 0.1499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1052 | SODIUM | 14.7 | MG/L | 160.4999 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-10-29 | AAA
3491002 | KISSIMMEE RV PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1028 | IRON | 0.0385 | MG/L | 0.3499 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1055 | SULFATE | 3.2 | MG/L | 250.4999 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-10-29 | AAA |  |  | J QUALIFIER REVISED FOR CHLORIDE 12/04/2018 FROM VICTORIA HAGEN_KK
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-04-01 | AAA
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-04-01 | AAA
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2019-09-24 | AAA |  | 0.5499 | 2AM. (3AM DUE 2020)
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2019-09-24 | AAA |  | 0.6499
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2019-10-21 | AAA | 0.6 | 0.6499 | 2AM/2039 PHTHALATE
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-06-08 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-06-08 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-08-05 | AAA |  | 0.6499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-10-26 | AAA |  | 0.5499 | POE
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-10-26 | AAA |  | 0.6499 | POE
3491002 | KISSIMMEE RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.9 | UG/L | 60.4999 | 2021-12-23 | L1 | 1 |  | COLLECTED DURING WRONG TIMEFRAME. MAKEUP SAMPLES | 3
3491002 | KISSIMMEE RV PARK | DBP | 2950 | TOTAL THMS | 27.8 | UG/L | 80.4999 | 2021-12-23 | L1 | 1 |  | COLLECTED DURING WRONG TIMEFRAME. MAKEUP SAMPLES | 3
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | SEC | 1002 | ALUMINUM | 0.0339 | MG/L | 0.2499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1017 | CHLORIDE | 13.6 | MG/L | 250.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1022 | COPPER | 0.0079 | MG/L | 1.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1028 | IRON | 0.0974 | MG/L | 0.3499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1055 | SULFATE | 3.16 | MG/L | 250.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1095 | ZINC | 0.0151 | MG/L | 5.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.23 | LN(10) |  | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 128 | MG/L | 500.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-23 | AAA |  | 0.0149 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-23 | AAA |  | 0.4499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 9.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-23 | AAA |  | 6.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-23 | AAA |  | 0.6499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-23 | AAA |  | 2.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-23 | AAA |  | 0.0749 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-23 | AAA |  | 0.6499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-23 | AAA |  | 0.9499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-23 | AAA |  | 0.0449 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.0449 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-23 | AAA |  | 0.0149 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 1.4 | PCI/L | 15.4999 | 2021-12-23 | AAA |  | 3.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.4 | PCI/L | 15.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-23 | AAA |  | 0.667 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | RAD | 4020 | RADIUM-226 | 0.5 | PCI/L | 3.4999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.8 | UG/L | 60.4999 | 2022-11-30 | L1 | 1.2 |  | WASTEWATER SINK (NO DISINFECTANT RESIDUAL REPORTED) HLKD (THIS REPORT RECEIVED & ENT'D 1/26/23) | 3
3491002 | KISSIMMEE RV PARK | DBP | 2950 | TOTAL THMS | 1.8 | UG/L | 80.4999 | 2022-11-30 | L1 | 0.5 |  | WASTEWATER SINK (NO DISINFECTANT RESIDUAL REPORTED) HLKD (THIS REPORT RECEIVED & ENT'D 1/26/23) | 3
3491002 | KISSIMMEE RV PARK | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2022-12-29 | AAA | 0.2 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-01-05 | L5 |  |  | 1/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-02-02 | L5 |  |  | 2/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0.87 | MG/L | 10.4999 | 2018-02-28 | WTP1 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP1 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | WTP3 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP3 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-03-02 | L5 |  |  | 3/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-04-06 | L5 |  |  | 4/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.8 | UG/L | 60.4999 | 2018-04-23 | L1 | 0.48 |  | 2600 EMERALD ISLAND
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 22.5 | UG/L | 80.4999 | 2018-04-23 | L1 | 0.32 |  | 2600 EMERALD ISLAND
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-05-04 | L5 |  |  | 5/18 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-06-01 | L5 |  |  | 6/18 BROMATE - SW WP (6/18 BROMATE RAA RCVD & HLKD TO SB - BB)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-07-06 | L5 |  |  | 07/2018 BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.6 | UG/L | 60.4999 | 2018-07-26 | L2 |  |  |  | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 36.3 | UG/L | 80.4999 | 2018-07-26 | L2 |  |  |  | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-08-03 | L5 |  |  | 08/2018 BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-09-07 | L5
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-10-05 | L5 | 3.2 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2018-11-02 | L5 |  |  | 11/2018 BROMATE - SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0.92 | UG/L | 10.4999 | 2018-12-07 | L5 | 0.64 |  | BROMATE (12/18 BROMATE RAA RCVD & HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-01-04 | L5 | 0.64 |  | 1/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-02-01 | L5 | 0.64 |  | 2/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0.56 | MG/L | 10.4999 | 2019-02-28 | WTP1
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP1
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | WTP3
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-03-01 | L5 | 0.64 |  | 3/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-04-05 | L5 |  |  | 2019-04 BROMATE - SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.6 | UG/L | 60.4999 | 2019-04-26 | L1 |  |  | 2600 EMERALD ISLAND(TEST T/H 4/23/15) | 2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 29.3 | UG/L | 80.4999 | 2019-04-26 | L1 |  |  | 2600 EMERALD ISLAND(TEST T/H 4/23/15) | 2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-05-03 | L5 |  |  | 2019-05 SOUTHWEST POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-06-07 | L5 | 0.64 |  | 6/19 BROMATE - SW WP (HLKD) 6/19 BROMATE RAA RCVD (HLKD SEP)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 5.1 | UG/L | 10.4999 | 2019-07-05 | L5 |  |  | 07/2019 BROMATE - SOUTHWEST POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.4 | UG/L | 60.4999 | 2019-07-25 | L2 |  |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 36 | UG/L | 80.4999 | 2019-07-25 | L2 |  |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-08-02 | L5 |  |  | 2019-08 BROMATE / SOUTHWEST POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-09-06 | L5 |  |  | 2019 09 - BROMATE / SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-10-04 | L5 | 0.64 |  | BROMATE - SW POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-11-01 | L5 | 0.64 |  | 11/19 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2019-12-06 | L5 | 0.64 |  | BROMATE LRAA = 0.05
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-01-03 | L5 | 0.64 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0.062 | MG/L | 10.4999 | 2020-01-28 | WTP1 | 0.025 |  | POE NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | WTP1 | 0.025 |  | POE NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | WTP3 | 0.025 |  | POE SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | WTP3 | 0.025 |  | POE SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-02-07 | L5 | 0.64 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-03-06 | L5 | 0.64 |  | 3/20 BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-25 | WTP1 | 0.58 | 1.4999 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-25 | WTP1 | 0.89 | 1.4999 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-25 | WTP1 | 0.16 | 0.4499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-25 | WTP1 | 3.3 | 9.4999 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-25 | WTP1 | 0.44 | 2.4999 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-25 | WTP1 | 0.094 | 0.1499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-25 | WTP1 | 0.16 | 0.2499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-25 | WTP1 | 0.67 | 0.9499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-25 | WTP1 | 0.00064 | 0.0055 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-25 | WTP1 | 0.096 | 0.1499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-25 | WTP1 | 0.16 | 0.2499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-25 | WTP1 | 0.03 | 0.0449 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-25 | WTP1 | 0.076 | 0.1499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP1 | 0.0064 | 0.0249 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-25 | WTP1 | 0.0076 | 0.0149 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-25 | WTP1 | 0.045 | 0.2499 | NW WP(35539636001)1Q 15 OF 29 SOC PLUS DIOXIN(DIOX NOT NDD)GLYPHOSATE 4.2 U W/J QUALIFIER,NOT ENTD,NO EXPLANATION. RSLTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RSLTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-25 | WTP3 | 0.58 | 1.4999 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-25 | WTP3 | 0.89 | 1.4999 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-25 | WTP3 | 0.16 | 0.4499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-25 | WTP3 | 3.3 | 9.4999 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-25 | WTP3 | 4.2 | 6.4999 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-25 | WTP3 | 0.44 | 2.4999 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-25 | WTP3 | 0.094 | 0.1499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-25 | WTP3 | 0.16 | 0.2499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-25 | WTP3 | 0.67 | 0.9499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-25 | WTP3 | 0.00077 | 0.0055 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-25 | WTP3 | 0.096 | 0.1499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-25 | WTP3 | 0.16 | 0.2499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-25 | WTP3 | 0.03 | 0.0449 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-25 | WTP3 | 0.076 | 0.1499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP3 | 0.0066 | 0.0249 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-25 | WTP3 | 0.0077 | 0.0149 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-25 | WTP3 | 0.045 | 0.2499 | SW WP (35539636002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/22/20 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-25 | WTP1 | 0.01 | 0.0149 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP1 | 0.01 | 0.0249 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-25 | WTP1 | 0.05 | 0.1499 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-25 | WTP1 | 0.6 | 0.6499 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-25 | WTP1 | 0.03 | 0.0749 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-25 | WTP1 | 0.6 | 0.6499 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-25 | WTP1 | 0.01 | 0.1499 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-25 | WTP1 | 0.03 | 0.1499 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-25 | WTP1 | 0.05 | 0.2499 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-25 | WTP1 | 0.01 | 0.0449 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP1 | 0.02 | 0.0249 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-25 | WTP1 | 0.01 | 0.1499 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP1 | 0.01 | 0.0249 | NW WP(482080/35539636001)1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-25 | WTP3 | 0.01 | 0.0149 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP3 | 0.01 | 0.0249 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-25 | WTP3 | 0.05 | 0.1499 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-25 | WTP3 | 0.6 | 0.6499 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-25 | WTP3 | 0.03 | 0.0749 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-25 | WTP3 | 0.6 | 0.6499 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-25 | WTP3 | 0.01 | 0.1499 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-25 | WTP3 | 0.03 | 0.1499 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-25 | WTP3 | 0.05 | 0.2499 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-25 | WTP3 | 0.01 | 0.0449 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP3 | 0.02 | 0.0249 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-25 | WTP3 | 0.01 | 0.1499 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-25 | WTP3 | 0.01 | 0.0249 | SW WP (482080/35539636002) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/16/21 PER LAB SIGNATURE DATE.
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-04-03 | L5 | 0.64 |  | 4/20 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.9 | UG/L | 60.4999 | 2020-04-28 | L1 | 0.9 |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 40.2 | UG/L | 80.4999 | 2020-04-28 | L1 | 0.32 |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-04-30 | WTP1 | 0.025 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-04-30 | WTP1 | 0.0005 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2020-04-30 | WTP1 | 0.0023 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP1 | 0.00024 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.00081 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP1 | 0.00492 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1025 | FLUORIDE | 0.56 | MG/L | 4.0499 | 2020-04-30 | WTP1 | 0.015 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP1 | 0.00064 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP1 | 0.0001 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.002 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-04-30 | WTP1 | 0.00083 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1052 | SODIUM | 9.1 | MG/L | 160.4999 | 2020-04-30 | WTP1 | 0.59 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-04-30 | WTP1 | 0.0005 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP1 | 0.00021 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP1 | 0.0005 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP1 | 0.2 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP1 | 0.0072 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1017 | CHLORIDE | 13.5 | MG/L | 250.4999 | 2020-04-30 | WTP1 | 2.5 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1022 | COPPER | 0.0025 | MG/L | 1.4999 | 2020-04-30 | WTP1 | 0.00093 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1025 | FLUORIDE | 0.56 | MG/L | 2.0499 | 2020-04-30 | WTP1 | 0.015 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1028 | IRON | 0.084 | MG/L | 0.3499 | 2020-04-30 | WTP1 | 0.016 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.0015 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1055 | SULFATE | 25 | MG/L | 250.4999 | 2020-04-30 | WTP1 | 2.5 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2020-04-30 | WTP1 | 0.0076 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP1 | 5 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2020-04-30 | WTP1 | 0.1 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 233 | MG/L | 500.4999 | 2020-04-30 | WTP1 | 5 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP1 | 0.099 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-04-30 | WTP3 | 0.025 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-04-30 | WTP3 | 0.025 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-04-30 | WTP3 | 0.0005 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1010 | BARIUM | 0.027 | MG/L | 2.4999 | 2020-04-30 | WTP3 | 0.0023 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP3 | 0.00024 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.00081 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP3 | 0.00492 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2020-04-30 | WTP3 | 0.015 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP3 | 0.00064 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP3 | 0.0001 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.002 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-04-30 | WTP3 | 0.00083 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1052 | SODIUM | 7.9 | MG/L | 160.4999 | 2020-04-30 | WTP3 | 0.59 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-04-30 | WTP3 | 0.0005 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP3 | 0.00021 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP3 | 0.0005 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP3 | 0.2 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP3 | 0.0072 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1017 | CHLORIDE | 9.5 | MG/L | 250.4999 | 2020-04-30 | WTP3 | 2.5 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1022 | COPPER | 0.0032 | MG/L | 1.4999 | 2020-04-30 | WTP3 | 0.00093 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2020-04-30 | WTP3 | 0.015 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-04-30 | WTP3 | 0.016 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.0015 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1055 | SULFATE | 50.6 | MG/L | 250.4999 | 2020-04-30 | WTP3 | 2.5 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2020-04-30 | WTP3 | 0.0076 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP3 | 5 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2020-04-30 | WTP3 | 0.1 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 197 | MG/L | 500.4999 | 2020-04-30 | WTP3 | 5 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP3 | 0.099 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1032 | MANGANESE | 0.0038 | MG/L | 0.0549 | 2020-04-30 | WTP1 | 0.0012 |  | NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1032 | MANGANESE | 0.0027 | MG/L | 0.0549 | 2020-04-30 | WTP3 | 0.0012 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-05-01 | L5 | 0.64 |  | 5/20 BROMATE - SW WP (HLKD 5-22-20)
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.69 | PCI/L | 15.4999 | 2020-05-28 | WTP1
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP1 |  | 1.4999
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-05-28 | WTP3
3491011 | TOHO WATER AUTHORITY WESTERN | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP3 |  | 1.4999
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-06-05 | L5 | 0.64 |  | 6/20 BROMATE - SW WP (HLKD) 6/20 QTR BROMATE RAA RCVD & HLKD
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-07-02 | L5 | 0.64 |  | 7/20 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.6 | UG/L | 60.4999 | 2020-07-27 | L2 | 0.9 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 31.9 | UG/L | 80.4999 | 2020-07-27 | L2 | 0.47 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-08-07 | L5 | 0.64 |  | 8/20 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1920 | ODOR THRESHOLD | 2 |  | 3.4999 | 2020-08-26 | WTP1 | 1 |  | NORTHWEST WP - ODOR 2.0 (RCVD 4/14/21)
3491011 | TOHO WATER AUTHORITY WESTERN | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2020-08-26 | WTP3 | 1 |  | SOUTHWEST WP - ODOR 1.0 (RCVD 4/14/21)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP1 | 0.7 | 1.4999 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP1 | 0.89 | 1.4999 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP1 | 0.16 | 0.4499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP1 | 3.3 | 9.4999 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP1 | 4.2 | 6.4999 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP1 | 0.44 | 2.4999 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP1 | 0.094 | 0.1499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP1 | 0.16 | 0.2499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP1 | 0.67 | 0.9499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP1 | 0.0006 | 0.0055 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP1 | 0.096 | 0.1499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP1 | 0.16 | 0.2499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP1 | 0.03 | 0.0449 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-27 | WTP1 | 0.045 | 0.1499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP1 | 0.0066 | 0.0249 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP1 | 0.0077 | 0.0149 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP1 | 0.036 | 0.2499 | NW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906005 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP3 | 0.68 | 1.4999 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP3 | 0.89 | 1.4999 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP3 | 0.16 | 0.4499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP3 | 3.3 | 9.4999 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP3 | 4.2 | 6.4999 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP3 | 0.44 | 2.4999 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP3 | 0.094 | 0.1499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP3 | 0.16 | 0.2499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP3 | 0.67 | 0.9499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP3 | 0.0008 | 0.0055 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP3 | 0.096 | 0.1499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP3 | 0.16 | 0.2499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP3 | 0.03 | 0.0449 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-27 | WTP3 | 0.044 | 0.1499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP3 | 0.0067 | 0.0249 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP3 | 0.0078 | 0.0149 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP3 | 0.035 | 0.2499 | SW WP-2Q 16 OF 29 SOCS(PLUS EX. DIOX-NOT RQRD)ENDOTHALL, J QUAL BIASED HIGH, 145% LCS (ENTD ENDOTHALL SINCE LCS BIASED HIGH) SMP 35573906004 (RSLTS DUE 10/10/20, RCVD LATE 12/16/20+REVISED 12/23/20)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-09-04 | L5 | 0.64 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-10-02 | L5 | 0.64 |  | 10/20 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-10-22 | WTP3 | 0.0055 | 0.0149 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP3 | 0.0067 | 0.0249 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-10-22 | WTP3 | 0.024 | 0.1499 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-10-22 | WTP3 | 0.37 | 0.6499 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-10-22 | WTP3 | 0.041 | 0.0749 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-10-22 | WTP3 | 0.48 | 0.6499 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-10-22 | WTP3 | 0.025 | 0.1499 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-10-22 | WTP3 | 0.015 | 0.1499 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-10-22 | WTP3 | 0.03 | 0.2499 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-10-22 | WTP3 | 0.014 | 0.0449 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP3 | 0.0031 | 0.0249 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-10-22 | WTP3 | 0.015 | 0.1499 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP3 | 0.02 | 0.0249 | SW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923004 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-10-22 | WTP1 | 0.0055 | 0.0149 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP1 | 0.0066 | 0.0249 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-10-22 | WTP1 | 0.023 | 0.1499 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-10-22 | WTP1 | 0.36 | 0.6499 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-10-22 | WTP1 | 0.04 | 0.0749 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-10-22 | WTP1 | 0.47 | 0.6499 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-10-22 | WTP1 | 0.024 | 0.1499 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-10-22 | WTP1 | 0.015 | 0.1499 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-10-22 | WTP1 | 0.029 | 0.2499 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-10-22 | WTP1 | 0.014 | 0.0449 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP1 | 0.003 | 0.0249 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-10-22 | WTP1 | 0.015 | 0.1499 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP1 | 0.02 | 0.0249 | NW WP 2Q 13 OF 29 SOC (1ST RCVD 12/16/20,REVISION RCVD 12/23/20,LAB SIGNED RSLTS 10/30/20) SMP 35586923005 (1Q SOCS 1ST RCVD 12/23/20 (LATE) & THE SUBCONTRACTED TESTS STILL NEED REVISION AS OF 2/3/21.
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-11-06 | L5 | 0.64 |  | 11/20 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-12-03 | DIST | 0.2 |  | 8530 W 192
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2020-12-04 | L5 | 0.64 |  | 12/20 BROMATE - SW WP (HLKD) 12/20 BROMATE RAA RCVD (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-01-08 | L5 | 0.64 |  | 1/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0.61 | MG/L | 10.4999 | 2021-01-27 | WTP1 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP1 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-02-05 | L5 |  |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-03-12 | L5 | 0.64 |  | 3/21 BROMATE - SW WP (HLKD) 3/21 BROMATE RAA RCVD SEPARATELY (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-04-02 | L5 | 0.64 |  | 4/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.9 | UG/L | 60.4999 | 2021-04-22 | L1 | 0.9 |  | 2600 EMERALD ISLAND BLVD. (HLKD) | 2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 31.3 | UG/L | 80.4999 | 2021-04-22 | L1 | 0.47 |  | 2600 EMERALD ISLAND BLVD. (HLKD) | 2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 1.4 | UG/L | 10.4999 | 2021-05-07 | L5 | 0.22 |  | 5/21 BROMATE - SW WP (HLKD) (6/21 QTR BROMATE RAA RCVD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-07-02 | L5 | 0.22 |  | 7/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.1 | UG/L | 60.4999 | 2021-07-23 | L2 | 0.9 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 28 | UG/L | 80.4999 | 2021-07-23 | L2 | 0.47 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-08-06 | L5 | 0.22 |  | 8/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-09-03 | L5 | 0.22 |  | 9/21 BROMATE - SW WP (HLKD) JQ RESULT ACCEPTED_MFC
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-10-01 | L5 | 0.22 |  | 10/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-12-03 | L5 | 0.22 |  | 12/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-01-07 | L5 |  |  | SW POE BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0.94 | UG/L | 10.4999 | 2022-02-04 | L5 | 0.22 |  | 2/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP3 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP3 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1040 | NITRATE | 0.033 | MG/L | 10.4999 | 2022-02-21 | WTP1 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP1 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0.72 | UG/L | 10.4999 | 2022-03-04 | L5 | 0.22 |  | 3/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 2 | UG/L | 10.4999 | 2022-04-01 | L5 | 0.22 |  | 4/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.5 | UG/L | 60.4999 | 2022-04-22 | L1 |  |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 27.7 | UG/L | 80.4999 | 2022-04-22 | L1 |  |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-05-20 | L5 | 0.22 |  | 5/22 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-06-03 | L5 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-06-03 | L5 |  |  | 6/3/22 BROMATE - SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-07-01 | L5 |  |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.1 | UG/L | 60.4999 | 2022-07-25 | L2 | 0.9 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 2950 | TOTAL THMS | 26.9 | UG/L | 80.4999 | 2022-07-25 | L2 | 0.47 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-08-05 | L5 | 0.22 |  | 8/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-09-02 | L5 | 0.22 |  | 9/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-10-07 | L5 | 0.22 |  | 10/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-11-09 | L5 | 0.22 |  | 11/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-12-02 | L5 |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.51 | UG/L | 60.4999 | 2018-02-21 | L2 |  |  | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 65.35 | UG/L | 80.4999 | 2018-02-21 | L2 |  |  | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | 0.18 | MG/L | 10.4999 | 2018-02-21 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-21 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.26 | UG/L | 60.4999 | 2018-05-23 | L2 |  |  | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 88.06 | UG/L | 80.4999 | 2018-05-23 | L2 |  |  | MANAGER'S HOUSE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 50.8 | UG/L | 80.4999 | 2018-08-10 | L2 |  |  |  | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.02 | UG/L | 60.4999 | 2018-08-10 | L2 |  |  |  | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.43 | UG/L | 60.4999 | 2018-11-12 | L2 |  |  | 2950-MANAGER'S HOUSE | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 27.46 | UG/L | 80.4999 | 2018-11-12 | L2 |  |  | 2950-MANAGER'S HOUSE | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | 0.24 | MG/L | 10.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1025 | FLUORIDE | 0.24 | MG/L | 4.0499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1035 | MERCURY | 0.0001 | MG/L | 0.0024 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1052 | SODIUM | 35 | MG/L | 160.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1017 | CHLORIDE | 36 | MG/L | 250.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1022 | COPPER | 0.0051 | MG/L | 1.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1025 | FLUORIDE | 0.24 | MG/L | 2.0499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1055 | SULFATE | 5 | MG/L | 250.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1095 | ZINC | 0.1 | MG/L | 5.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.93 | LN(10) |  | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 360 | MG/L | 500.4999 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 2905 | FOAMING AGENTS | 0.056 |  | 0.5499 | 2018-11-27 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.28 | UG/L | 60.4999 | 2019-02-13 | L2 | 0.91 |  | MANAGER'S HOUSE (HLKD TO KC,JF-BB) | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 36.42 | UG/L | 80.4999 | 2019-02-13 | L2 | 0.39 |  | MANAGER'S HOUSE (HLKD TO KC,JF-BB) | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | 0.51 | MG/L | 10.4999 | 2019-04-22 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-04-22 | AAA
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.53 | UG/L | 60.4999 | 2019-05-10 | L2 |  |  | MANAGER'S HOUSE | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 66.22 | UG/L | 80.4999 | 2019-05-10 | L2 |  |  | MANAGER'S HOUSE | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.71 | UG/L | 60.4999 | 2019-08-12 | L2 |  |  | MANAGERS HOUSE [LRAA TTHM=48.655, HAA5=19.74] | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 64.52 | UG/L | 80.4999 | 2019-08-12 | L2 |  |  | MANAGERS HOUSE [LRAA TTHM=48.655, HAA5=19.74] | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.15 | UG/L | 60.4999 | 2019-11-14 | L2 |  |  | MANAGERS HOUSE [LRAA TTHM=55.45; HAA5= 19.17] TEST BOTH ANNUALLY 2Q_VP | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 54.64 | UG/L | 80.4999 | 2019-11-14 | L2 |  |  | MANAGERS HOUSE [LRAA TTHM=55.45; HAA5= 19.17] TEST BOTH ANNUALLY 2Q_VP | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2020-04-07 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 490 | MG/L | 0 | 2020-04-07 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 75 | MG/L | 0 | 2020-04-07 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2020-04-07 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-04-07 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.2 |  |  | 2020-04-07 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2020-04-07 | DIST |  |  | LOT #23
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 490 | MG/L | 0 | 2020-04-07 | DIST |  |  | LOT #23
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 75 | MG/L | 0 | 2020-04-07 | DIST |  |  | LOT #23
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2020-04-07 | DIST |  |  | LOT #23
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-04-07 | DIST |  |  | LOT #23
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.2 |  |  | 2020-04-07 | DIST |  |  | LOT #23
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.64 | UG/L | 60.4999 | 2020-05-06 | L2 | 0.91 |  |  | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 27.03 | UG/L | 80.4999 | 2020-05-06 | L2 | 0.56 |  |  | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.46 | MG/L |  | 2020-05-13 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 520 | MG/L | 0 | 2020-05-13 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 73 | MG/L | 0 | 2020-05-13 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2020-05-13 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-05-13 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.4 |  |  | 2020-05-13 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.41 | MG/L |  | 2020-05-13 | DIST |  |  | LOT #23 (HLKD 7/6/20)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 230 | MG/L | 0 | 2020-05-13 | DIST |  |  | LOT #23 (HLKD 7/6/20)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 72 | MG/L | 0 | 2020-05-13 | DIST |  |  | LOT #23 (HLKD 7/6/20)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2020-05-13 | DIST |  |  | LOT #23 (HLKD 7/6/20)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-05-13 | DIST |  |  | LOT #23 (HLKD 7/6/20)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.4 |  |  | 2020-05-13 | DIST |  |  | LOT #23 (HLKD 7/6/20)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2020-06-23 | AAA |  |  | POE (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 500 | MG/L | 0 | 2020-06-23 | AAA |  |  | POE (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 68 | MG/L | 0 | 2020-06-23 | AAA |  |  | POE (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2020-06-23 | AAA |  |  | POE (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-06-23 | AAA |  |  | POE (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.1 |  |  | 2020-06-23 | AAA |  |  | POE (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2020-06-23 | DIST |  |  | LOT #23 (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 500 | MG/L | 0 | 2020-06-23 | DIST |  |  | LOT #23 (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 69 | MG/L | 0 | 2020-06-23 | DIST |  |  | LOT #23 (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2020-06-23 | DIST |  |  | LOT #23 (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-06-23 | DIST |  |  | LOT #23 (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.3 |  |  | 2020-06-23 | DIST |  |  | LOT #23 (1 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2020-07-01 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-01 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2020-07-27 | DIST |  |  | LOT 23 (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 530 | MG/L | 0 | 2020-07-27 | DIST |  |  | LOT 23 (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 73 | MG/L | 0 | 2020-07-27 | DIST |  |  | LOT 23 (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-07-27 | DIST |  |  | LOT 23 (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.1 |  |  | 2020-07-27 | DIST |  |  | LOT 23 (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.2 |  |  | 2020-07-27 | AAA |  |  | POE (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2020-07-27 | AAA |  |  | POE (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2020-07-27 | DIST |  |  | LOT 23 (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2020-07-27 | AAA | 0.19 |  | POE (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 520 | MG/L | 0 | 2020-07-27 | AAA | 2 |  | POE (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 72 | MG/L | 0 | 2020-07-27 | AAA | 0.2 |  | POE (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2020-07-27 | AAA | 5 |  | POE (2 OF 4 CONSEC. QUARTERS FOLLOWING ALE)
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2020-12-16 | AAA | 0.023 |  | LOT 235 (3 OF 4 CONSEC. QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 460 | MG/L | 0 | 2020-12-16 | AAA | 2 |  | LOT 235 (3 OF 4 CONSEC. QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 63 | MG/L | 0 | 2020-12-16 | AAA | 0.2 |  | LOT 235 (3 OF 4 CONSEC. QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2020-12-16 | AAA | 5 |  | LOT 235 (3 OF 4 CONSEC. QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2020-12-16 | AAA | 0.023 |  | POE ( 3 OF 4 CONSEC QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 460 | MG/L | 0 | 2020-12-16 | AAA | 2 |  | POE ( 3 OF 4 CONSEC QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 63 | MG/L | 0 | 2020-12-16 | AAA | 0.2 |  | POE ( 3 OF 4 CONSEC QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2020-12-16 | AAA | 5 |  | POE ( 3 OF 4 CONSEC QUARTERS FOLLOWING ALE)_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1022 | COPPER | 0.0062 | MG/L | 1.4999 | 2020-12-22 | AAA | 0.005 |  | ENTRY POINT COPPER AFTER 7-12/19 PB ALE_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-12-22 | AAA |  |  | ENTRY POINT LEAD AFTER 7-12/19 PB ALE_NMS
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.03 | MG/L |  | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 2.2 | MG/L | 0 | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 24 | MG/L | 0 | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 85 | MG/L |  | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.04 | MG/L |  | 2021-02-23 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 2.2 | MG/L | 0 | 2021-02-23 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 24 | MG/L | 0 | 2021-02-23 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-02-23 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 86 | MG/L |  | 2021-02-23 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2021-04-21 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 500 | MG/L | 0 | 2021-04-21 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 70 | MG/L | 0 | 2021-04-21 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2021-04-21 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2021-04-21 | AAA |  |  | LOT 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1064 | CONDUCTIVITY | 510 | MG/L | 0 | 2021-04-21 | AAA |  |  | LOT 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1919 | HARDNESS - CALCIUM | 69 | MG/L | 0 | 2021-04-21 | AAA |  |  | LOT 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2021-04-21 | AAA |  |  | LOT 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1927 | TOTAL ALKALINITY | 240 | MG/L |  | 2021-04-21 | AAA |  |  | LOT 235
3491077 | BOGGY CREEK RESORT AND RV PARK | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-04-21 | AAA |  |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-11 | L2 |  |  |  | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-11 | L2 |  |  |  | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1052 | SODIUM | 32 | MG/L | 160.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1017 | CHLORIDE | 42 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1028 | IRON | 0.025 | MG/L | 0.3499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1032 | MANGANESE | 0.0079 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1055 | SULFATE | 5 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.06 | LN(10) |  | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 278 | MG/L | 500.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 2905 | FOAMING AGENTS | 0.1 |  | 0.5499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-08 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | RAD | 4020 | RADIUM-226 | 0.7 | PCI/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-08 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-08 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.47 | UG/L | 60.4999 | 2022-05-09 | L2 | 0.98 |  | MANAGER'S RESIDENCE (HLKD) (LRAA: TTHM:38.78, HAA5-15.31) | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | DBP | 2950 | TOTAL THMS | 73.44 | UG/L | 80.4999 | 2022-05-09 | L2 | 0.39 |  | MANAGER'S RESIDENCE (HLKD) (LRAA: TTHM:38.78, HAA5-15.31) | 2
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2022-10-31 | AAA | 0.024 |  | POE
3491077 | BOGGY CREEK RESORT AND RV PARK | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-31 | AAA | 0.0034 |  | POE
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | 0.14 | MG/L | 10.4999 | 2018-02-20 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-20 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1010 | BARIUM | 0.0048 | MG/L | 2.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1025 | FLUORIDE | 0.28 | MG/L | 4.0499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1052 | SODIUM | 21 | MG/L | 160.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1017 | CHLORIDE | 27 | MG/L | 250.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1025 | FLUORIDE | 0.28 | MG/L | 2.0499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1028 | IRON | 0.13 | MG/L | 0.3499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1032 | MANGANESE | 0.0044 | MG/L | 0.0549 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1055 | SULFATE | 3.1 | MG/L | 250.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.12 | LN(10) |  | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 270 | MG/L | 500.4999 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | SEC | 2905 | FOAMING AGENTS | 0.064 |  | 0.5499 | 2018-04-03 | AAA
3491298 | SHELTER COVE RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-04-03 | AAA |  | 0.5499
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 53.75 | UG/L | 60.4999 | 2018-08-14 | L1 | 0.91 |  | RETURN TO ROUTINE, ANNUAL MONITORING DURING 3RD Q_JMF
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 72.04 | UG/L | 80.4999 | 2018-08-14 | L1 | 0.39 |  | RETURN TO ROUTINE, ANNUAL MONITORING DURING 3RD Q_JMF
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | 0.46 | MG/L | 10.4999 | 2019-04-23 | AAA
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-04-23 | AAA
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.77 | UG/L | 60.4999 | 2019-08-22 | L1 |  |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 157.87 | UG/L | 80.4999 | 2019-08-22 | L1 |  |  | 805 PARKWAY EAST EXCEEDANCE PLACE ON QUARTERLY_JB
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.5 | UG/L | 60.4999 | 2019-11-20 | L1 | 0.91 |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 12.99 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.39 |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.37 | UG/L | 60.4999 | 2019-11-20 | L2 | 0.91 |  | 392 PINE ISLAND
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 67.83 | UG/L | 80.4999 | 2019-11-20 | L2 | 0.39 |  | 392 PINE ISLAND
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2020-02-18 | L1 | 0.91 |  | 805 PARKWAY EAST (HLKD)
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 24.72 | UG/L | 80.4999 | 2020-02-18 | L1 | 0.39 |  | 805 PARKWAY EAST (HLKD)
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2020-05-14 | L2 | 0.91 |  | PINE ISLAND [SAMPLED OUTSIDE APPROVED TIMEFRAME (MAY 15-21), PN REQUESTED]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2020-05-14 | L2 | 0.39 |  | PINE ISLAND [SAMPLED OUTSIDE APPROVED TIMEFRAME (MAY 15-21), PN REQUESTED]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.11 | UG/L | 60.4999 | 2020-05-19 | L1 | 0.91 |  | 805 PARKWAY EAST (MARKED REVISED) HLKD
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 76.83 | UG/L | 80.4999 | 2020-05-19 | L1 | 0.39 |  | 805 PARKWAY EAST (MARKED REVISED) HLKD
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.94 | UG/L | 60.4999 | 2020-05-19 | L2 | 0.91 |  | 392 PINE ISLAND (MARKED REVISED) HLKD
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 55.47 | UG/L | 80.4999 | 2020-05-19 | L2 | 0.39 |  | 392 PINE ISLAND (MARKED REVISED) HLKD
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-07-15 | AAA |  |  | POE
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-15 | AAA |  |  | POE
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.11 | UG/L | 60.4999 | 2020-08-18 | L1 | 0.98 |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 67.08 | UG/L | 80.4999 | 2020-08-18 | L1 | 0.39 |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.54 | UG/L | 60.4999 | 2020-08-18 | L3 | 0.98 |  | 1315 PINE ISLAND [NEW SITE, L2 SAMPLING SITE NO LONGER AVAILABLE]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 70.67 | UG/L | 80.4999 | 2020-08-18 | L3 | 0.39 |  | 1315 PINE ISLAND [NEW SITE, L2 SAMPLING SITE NO LONGER AVAILABLE]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 58.36 | UG/L | 60.4999 | 2020-11-18 | L1 | 0.98 |  | 805 PARKWAY E [LRAA TTHM = 78.2475; OE= 108.1575; HAA5=32.895] NEED OE REPORT
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 144.36 | UG/L | 80.4999 | 2020-11-18 | L1 | 0.39 |  | 805 PARKWAY E [LRAA TTHM = 78.2475; OE= 108.1575; HAA5=32.895] NEED OE REPORT
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.97 | UG/L | 60.4999 | 2020-11-18 | L3 | 0.98 |  | 1315 PINE ISLAND [NEW SITE, L2 SAMPLING SITE NO LONGER AVAILABLE, NO LRAA YET, ONLY 2 SAMPLING EVENTS DONE]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 142.83 | UG/L | 80.4999 | 2020-11-18 | L3 | 0.39 |  | 1315 PINE ISLAND [NEW SITE, L2 SAMPLING SITE NO LONGER AVAILABLE, NO LRAA YET, ONLY 2 SAMPLING EVENTS DONE]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.87 | UG/L | 60.4999 | 2021-02-17 | L1 | 0.98 |  | 805 PARKWAY EAST (HLKD) [LRAA TTHM = 93.37., OEL= 95.48; HAA5=43.11]. TTHM MCL VIO, NEED PN AND OE REPORT_VPU
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 85.23 | UG/L | 80.4999 | 2021-02-17 | L1 | 0.39 |  | 805 PARKWAY EAST (HLKD) [LRAA TTHM = 93.37., OEL= 95.48; HAA5=43.11]. TTHM MCL VIO, NEED PN AND OE REPORT_VPU
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.83 | UG/L | 60.4999 | 2021-02-17 | L3 | 0.98 |  | 1315 PINE ISLAND (HLKD) [3 CONSEC QUARTERS AT THIS LOCATION, NO LRAA YET]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 82.13 | UG/L | 80.4999 | 2021-02-17 | L3 | 0.39 |  | 1315 PINE ISLAND (HLKD) [3 CONSEC QUARTERS AT THIS LOCATION, NO LRAA YET]_VPU
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-17 | L1 | 0.39 |  | 805 PARKWAY EAST (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN)
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-17 | L3 | 0.39 |  | 1315 PINE ISLAND DR. (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN)
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-17 | L3 | 0.98 |  | 1315 PINE ISLAND DR. (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN)
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-17 | L1 | 0.98 |  | 805 PARKWAY EAST (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN)
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.3 | UG/L | 60.4999 | 2021-08-20 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 43.15 | UG/L | 80.4999 | 2021-08-20 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.99 | UG/L | 60.4999 | 2021-08-20 | L1 |  |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 67.41 | UG/L | 80.4999 | 2021-08-20 | L1 |  |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | 0.12 | MG/L | 10.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1010 | BARIUM | 0.0043 | MG/L | 2.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1025 | FLUORIDE | 0.26 | MG/L | 4.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1052 | SODIUM | 18 | MG/L | 160.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1017 | CHLORIDE | 18 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1025 | FLUORIDE | 0.26 | MG/L | 2.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1028 | IRON | 0.14 | MG/L | 0.3499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1055 | SULFATE | 2.2 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1905 | COLOR | 13 | COLOR UNITS | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 5.3 | LN(10) |  | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 304 | MG/L | 500.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-10-25 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-25 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-25 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.09 | UG/L | 60.4999 | 2021-11-17 | L1 |  |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 52.58 | UG/L | 80.4999 | 2021-11-17 | L1 |  |  | 805 PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.57 | UG/L | 60.4999 | 2021-11-17 | L3 |  |  | 1315 PINE ISLAND (LRAA, HAA5=21.43; TTHMS=43.83 -KAOB)
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 50.03 | UG/L | 80.4999 | 2021-11-17 | L3 |  |  | 1315 PINE ISLAND (LRAA, HAA5=21.43; TTHMS=43.83 -KAOB)
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.28 | UG/L | 60.4999 | 2022-02-16 | L1 |  |  | PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 79.67 | UG/L | 80.4999 | 2022-02-16 | L1 |  |  | PARKWAY EAST
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.79 | UG/L | 60.4999 | 2022-02-16 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 78.17 | UG/L | 80.4999 | 2022-02-16 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.1 | UG/L | 60.4999 | 2022-05-18 | L1 |  |  | 805 PARKWAY EAST TTHM LRAA 70.905
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 84.06 | UG/L | 80.4999 | 2022-05-18 | L1 |  |  | 805 PARKWAY EAST TTHM LRAA 70.905
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-05-18 | L3 |  |  | 1315 PINE ISLAND TTHM: 64.14
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 85.21 | UG/L | 80.4999 | 2022-05-18 | L3 |  |  | 1315 PINE ISLAND TTHM: 64.14
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 63.37 | UG/L | 60.4999 | 2022-08-16 | L1 | 0.98 |  | 805 PARKWAY EAST (**TTHM LRAA MCL VIOL**) HLKD
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 140.8 | UG/L | 80.4999 | 2022-08-16 | L1 | 0.39 |  | 805 PARKWAY EAST (**TTHM LRAA MCL VIOL**) HLKD
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 81.6 | UG/L | 60.4999 | 2022-08-16 | L3 | 0.98 |  | 1315 PINE ISLAND DR. (HLKD) **HIGH RESULTS** (**TTHM LRAA MCL VIOL**)
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 143.95 | UG/L | 80.4999 | 2022-08-16 | L3 | 0.39 |  | 1315 PINE ISLAND DR. (HLKD) **HIGH RESULTS** (**TTHM LRAA MCL VIOL**)
3491298 | SHELTER COVE RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3491298 | SHELTER COVE RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.46 | UG/L | 60.4999 | 2022-11-16 | L1 | 0.98
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 65.38 | UG/L | 80.4999 | 2022-11-16 | L1 | 0.39
3491298 | SHELTER COVE RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.15 | UG/L | 60.4999 | 2022-11-16 | L3 | 0.98
3491298 | SHELTER COVE RESORT | DBP | 2950 | TOTAL THMS | 76.32 | UG/L | 80.4999 | 2022-11-16 | L3 | 0.39
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-01-01 | WTP4 |  | 0.6499 | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-01-01 | WTP4 |  | 0.6499 | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.33 | UG/L | 60.4999 | 2018-02-19 | L1 |  |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 28.1 | UG/L | 80.4999 | 2018-02-19 | L1 |  |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.4 | UG/L | 60.4999 | 2018-02-19 | L2 |  |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 31.2 | UG/L | 80.4999 | 2018-02-19 | L2 |  |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.1 | UG/L | 60.4999 | 2018-02-19 | L3 |  |  | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 45.2 | UG/L | 80.4999 | 2018-02-19 | L3 |  |  | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2018-02-19 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 29.9 | UG/L | 80.4999 | 2018-02-19 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.7 | UG/L | 60.4999 | 2018-05-15 | L1 |  |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 28.3 | UG/L | 80.4999 | 2018-05-15 | L1 |  |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.9 | UG/L | 60.4999 | 2018-05-15 | L2 |  |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 55.9 | UG/L | 80.4999 | 2018-05-15 | L2 |  |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.6 | UG/L | 60.4999 | 2018-05-15 | L3 |  |  | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 25.7 | UG/L | 80.4999 | 2018-05-15 | L3 |  |  | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.2 | UG/L | 60.4999 | 2018-05-15 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 29 | UG/L | 80.4999 | 2018-05-15 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.5 | UG/L | 60.4999 | 2018-08-15 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 13.9 | UG/L | 80.4999 | 2018-08-15 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.8 | UG/L | 60.4999 | 2018-08-15 | L2 | 0.5 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 34.5 | UG/L | 80.4999 | 2018-08-15 | L2 | 0.5 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.7 | UG/L | 60.4999 | 2018-08-15 | L3 | 0.5 |  | 3600 CANOE CREEK
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 32.1 | UG/L | 80.4999 | 2018-08-15 | L3 | 0.5 |  | 3600 CANOE CREEK
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21 | UG/L | 60.4999 | 2018-08-15 | L4 | 0.5 |  | 803 MASSACHUSSETTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 25.2 | UG/L | 80.4999 | 2018-08-15 | L4 | 0.5 |  | 803 MASSACHUSSETTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.6 | UG/L | 60.4999 | 2018-11-15 | L1 |  |  | 2950-5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 28.2 | UG/L | 80.4999 | 2018-11-15 | L1 |  |  | 2950-5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.6 | UG/L | 60.4999 | 2018-11-15 | L2 |  |  | 2950-4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 29.5 | UG/L | 80.4999 | 2018-11-15 | L2 |  |  | 2950-4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22 | UG/L | 60.4999 | 2018-11-15 | L3 |  |  | 2950-3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 36.1 | UG/L | 80.4999 | 2018-11-15 | L3 |  |  | 2950-3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.2 | UG/L | 60.4999 | 2018-11-15 | L4 |  |  | 2950-803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 43.4 | UG/L | 80.4999 | 2018-11-15 | L4 |  |  | 2950-803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-01-17 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-01-17 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-01-17 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-01-17 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-01-17 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-01-17 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-01-17 | WTP1 |  |  | MISSED SAMPLING. RCVD 01/28/19_KAC
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-01-17 | WTP1 |  |  | MISSED SAMPLING. RCVD 01/28/19_KAC
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-01-17 | WTP2 |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19_KAC
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-01-17 | WTP2 |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19_KAC
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-01-17 | WTP4 |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-01-17 | WTP4 |  |  | MISSED 2018 SAMPLE. RCVD 01/28/19
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-12 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-12 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-12 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-12 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-12 | WTP4 | 0.2 |  | WP4 (RCVD 2/19 WP4 NN ON 6/28/19--BB, OTHER 2 WP'S 2/19 NN RCVD EARLIER)
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-12 | WTP4 | 0.2 |  | WP4 (RCVD 2/19 WP4 NN ON 6/28/19--BB, OTHER 2 WP'S 2/19 NN RCVD EARLIER)
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34 | UG/L | 60.4999 | 2019-02-20 | L1 | 1 |  | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 35.7 | UG/L | 80.4999 | 2019-02-20 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.2 | UG/L | 60.4999 | 2019-02-20 | L2 | 1 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 38.7 | UG/L | 80.4999 | 2019-02-20 | L2 | 0.5 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.4 | UG/L | 60.4999 | 2019-02-20 | L3 | 1 |  | 3600 CANOE CREEK
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 35 | UG/L | 80.4999 | 2019-02-20 | L3 | 0.5 |  | 3600 CANOE CREEK
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.6 | UG/L | 60.4999 | 2019-02-20 | L4 | 1 |  | 803 MASS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 37 | UG/L | 80.4999 | 2019-02-20 | L4 | 0.5 |  | 803 MASS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 67.5 | UG/L | 60.4999 | 2019-05-21 | L1 |  |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 81.1 | UG/L | 80.4999 | 2019-05-21 | L1 |  |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 50.3 | UG/L | 60.4999 | 2019-05-21 | L2 |  |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 68.4 | UG/L | 80.4999 | 2019-05-21 | L2 |  |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 46.7 | UG/L | 60.4999 | 2019-05-21 | L3 |  |  | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 54 | UG/L | 80.4999 | 2019-05-21 | L3 |  |  | 3600 CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.4 | UG/L | 60.4999 | 2019-05-21 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 63.1 | UG/L | 80.4999 | 2019-05-21 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.1 | UG/L | 60.4999 | 2019-08-15 | L1 |  |  | 5371 MAJESTIC ISLAND CIR. H LRAA = 43.3 T LRAA = 50.65
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 57.6 | UG/L | 80.4999 | 2019-08-15 | L1 |  |  | 5371 MAJESTIC ISLAND CIR. H LRAA = 43.3 T LRAA = 50.65
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 81.1 | UG/L | 60.4999 | 2019-08-15 | L2 |  |  | 4805 DOC DR. H LRAA = 42.6 T LRAA = 52.8
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 74.7 | UG/L | 80.4999 | 2019-08-15 | L2 |  |  | 4805 DOC DR. H LRAA = 42.6 T LRAA = 52.8
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 84.5 | UG/L | 60.4999 | 2019-08-15 | L3 |  |  | 3600 CANOE CREEK RD. H LRAA = 46.4 T LRAA = 49.6
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 73.2 | UG/L | 80.4999 | 2019-08-15 | L3 |  |  | 3600 CANOE CREEK RD. H LRAA = 46.4 T LRAA = 49.6
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 83.8 | UG/L | 60.4999 | 2019-08-15 | L4 |  |  | 803 MASSACHUSETTS AVE. H LRAA = 47.8 T LRAA = 55.1
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 76.9 | UG/L | 80.4999 | 2019-08-15 | L4 |  |  | 803 MASSACHUSETTS AVE. H LRAA = 47.8 T LRAA = 55.1
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.6 | UG/L | 60.4999 | 2019-11-20 | L1 | 1 |  | 5371 MAJESTIC ISLAND [LRAA TTHM=62.15; HAA5=49.55]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 74.2 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND [LRAA TTHM=62.15; HAA5=49.55]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37 | UG/L | 60.4999 | 2019-11-20 | L2 | 1 |  | 4805 DOC DR [LRAA TTHM=74.7 ; HAA5=48.9]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 117 | UG/L | 80.4999 | 2019-11-20 | L2 | 0.5 |  | 4805 DOC DR [LRAA TTHM=74.7 ; HAA5=48.9]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.9 | UG/L | 60.4999 | 2019-11-20 | L3 | 1 |  | 3600 CANOE CREEK [LRAA TTHM=53.28; HAA5=50.13]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 50.9 | UG/L | 80.4999 | 2019-11-20 | L3 | 0.5 |  | 3600 CANOE CREEK [LRAA TTHM=53.28; HAA5=50.13]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.4 | UG/L | 60.4999 | 2019-11-20 | L4 | 1 |  | 803 MASSACHUSETTS [LRAA TTHM= 60.75; HAA5=49.55]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 66 | UG/L | 80.4999 | 2019-11-20 | L4 | 0.5 |  | 803 MASSACHUSETTS [LRAA TTHM= 60.75; HAA5=49.55]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.9 | UG/L | 60.4999 | 2020-02-19 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 59.7 | UG/L | 80.4999 | 2020-02-19 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.73 | UG/L | 60.4999 | 2020-02-19 | L2 | 1 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 49.9 | UG/L | 80.4999 | 2020-02-19 | L2 | 0.5 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.9 | UG/L | 60.4999 | 2020-02-19 | L3 | 1 |  | 3600 CANOE CREEK
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 53.2 | UG/L | 80.4999 | 2020-02-19 | L3 | 0.5 |  | 3600 CANOE CREEK
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.9 | UG/L | 60.4999 | 2020-02-19 | L4 | 1 |  | 803 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 41.6 | UG/L | 80.4999 | 2020-02-19 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31 | UG/L | 60.4999 | 2020-05-18 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 73.7 | UG/L | 80.4999 | 2020-05-18 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.7 | UG/L | 60.4999 | 2020-05-18 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 47.2 | UG/L | 80.4999 | 2020-05-18 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.8 | UG/L | 60.4999 | 2020-05-18 | L3 | 1 |  | 3600 CANOE CREEK RD. [TTHM/LRAA= 67.63]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 93.2 | UG/L | 80.4999 | 2020-05-18 | L3 | 0.5 |  | 3600 CANOE CREEK RD. [TTHM/LRAA= 67.63]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.8 | UG/L | 60.4999 | 2020-05-18 | L4 | 1 |  | 803 MASSACHUSSETS AVE. (6/20 DISINF BYP RPRT RCVD S/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 36.9 | UG/L | 80.4999 | 2020-05-18 | L4 | 0.5 |  | 803 MASSACHUSSETS AVE. (6/20 DISINF BYP RPRT RCVD S/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-07-09 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 147 | MG/L |  | 2020-07-09 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-07-09 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 90 | MG/L |  | 2020-07-09 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-07-09 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2020-07-09 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0.221 | MG/L | 10.4999 | 2020-07-09 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-09 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2020-07-09 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-09 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0.276 | MG/L | 10.4999 | 2020-07-09 | WTP1 |  |  | WTP #1 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-09 | WTP1 |  |  | WTP #1 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-07-23 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 150 | MG/L |  | 2020-07-23 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-07-23 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2020-07-23 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-07-23 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2020-07-23 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0.348 | MG/L | 10.4999 | 2020-07-30 | WTP1 | 0.2 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-30 | WTP1 | 0.2 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1010 | BARIUM | 0.0192 | MG/L | 2.4999 | 2020-07-30 | WTP1 | 0.002 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-07-30 | WTP1 | 0.005 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | 0.431 | MG/L | 4.0499 | 2020-07-30 | WTP1 | 0.2 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-07-30 | WTP1 | 2e-05 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-07-30 | WTP1 | 0.002 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1052 | SODIUM | 47.1 | MG/L | 160.4999 | 2020-07-30 | WTP1 | 0.5 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-07-30 | WTP1 | 0.0005 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (RESULTS RECEIVED 1/7/21) ALL 3 WPS' 7/30/20 TRIENNIAL RESULTS RECEIVED 1/7/21
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-07-30 | WTP1 | 0.01 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1022 | COPPER | 0.002 | MG/L | 1.4999 | 2020-07-30 | WTP1 | 0.001 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | 0.431 | MG/L | 2.0499 | 2020-07-30 | WTP1 | 0.2 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1028 | IRON | 0.0277 | MG/L | 0.3499 | 2020-07-30 | WTP1 | 0.01 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-07-30 | WTP1 | 0.01 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1095 | ZINC | 0.0049 | MG/L | 5.4999 | 2020-07-30 | WTP1 | 0.002 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-07-30 | WTP1 | 5 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2020-07-30 | WTP1 | 1 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.09 | LN(10) |  | 2020-07-30 | WTP1 | 0.01 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 402 | MG/L | 500.4999 | 2020-07-30 | WTP1 | 2.5 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-07-30 | WTP1 | 0.2 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-07-30 | WTP1 | 0.2 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP1 | 0.5 | 0.5499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-07-30 | WTP1 | 0.01 | 0.0149 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP1 | 0.01 | 0.0249 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-07-30 | WTP1 | 0.05 | 0.1499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP1 | 0.5 | 1.4999 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-07-30 | WTP1 | 0.1 | 1.4999 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-07-30 | WTP1 | 0.4 | 0.4499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-07-30 | WTP1 | 9 | 9.4999 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-07-30 | WTP1 | 6 | 6.4999 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-07-30 | WTP1 | 0.6 | 0.6499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-07-30 | WTP1 | 2 | 2.4999 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-07-30 | WTP1 | 0.07 | 0.0749 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-07-30 | WTP1 | 0.6 | 0.6499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-07-30 | WTP1 | 0.1 | 0.1499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-07-30 | WTP1 | 0.2 | 0.2499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-07-30 | WTP1 | 0.1 | 0.1499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-07-30 | WTP1 | 0.9 | 0.9499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP1 | 0.1 | 0.1499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-07-30 | WTP1 | 0.2 | 0.2499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-07-30 | WTP1 | 0.01 | 0.0449 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP1 | 0.01 | 0.0249 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-07-30 | WTP1 | 0.1 | 0.1499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-07-30 | WTP1 | 0.2 | 0.2499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP1 | 0.1 | 0.1499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP1 | 0.02 | 0.0249 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-07-30 | WTP1 | 0.04 | 0.0449 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-07-30 | WTP1 | 0.1 | 0.1499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP1 | 0.02 | 0.0249 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-07-30 | WTP1 | 0.01 | 0.0149 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-07-30 | WTP1 | 0.01 | 0.2499 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.7 | PCI/L | 15.4999 | 2020-07-30 | WTP1 | 1.3 |  | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | 1.5 | PCI/L | 3.4999 | 2020-07-30 | WTP1 | 0.4 | 1.4999 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-07-30 | WTP1 | 0.8 | 1.4999 | WP1 (RESULTS RECEIVED 1/7/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0.205 | MG/L | 10.4999 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | 0.453 | MG/L | 4.0499 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1052 | SODIUM | 25.2 | MG/L | 160.4999 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-07-30 | WTP4 |  |  | WTP #4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | 44.8 | MG/L | 250.4999 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | 0.453 | MG/L | 2.0499 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1055 | SULFATE | 5.32 | MG/L | 250.4999 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.02 | LN(10) |  | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 236 | MG/L | 500.4999 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-07-30 | WTP4 |  |  | WTP#4 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP4 |  | 0.5499 | WTP # 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-07-30 | WTP4 |  | 0.0149 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP4 |  | 0.0249 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-07-30 | WTP4 |  | 0.1499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP4 |  | 1.4999 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-07-30 | WTP4 |  | 1.4999 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-07-30 | WTP4 |  | 0.4499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-07-30 | WTP4 |  | 9.4999 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-07-30 | WTP4 |  | 6.4999 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-07-30 | WTP4 |  | 0.6499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-07-30 | WTP4 |  | 2.4999 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-07-30 | WTP4 |  | 0.0749 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-07-30 | WTP4 |  | 0.6499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-07-30 | WTP4 |  | 0.1499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-07-30 | WTP4 |  | 0.2499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-07-30 | WTP4 |  | 0.1499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-07-30 | WTP4 |  | 0.9499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP4 |  | 0.1499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-07-30 | WTP4 |  | 0.2499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-07-30 | WTP4 |  | 0.0449 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP4 |  | 0.0249 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-07-30 | WTP4 |  | 0.1499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-07-30 | WTP4 |  | 0.2499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP4 |  | 0.1499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP4 |  | 0.0249 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-07-30 | WTP4 |  | 0.0449 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-07-30 | WTP4 |  | 0.1499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP4 |  | 0.0249 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-07-30 | WTP4 |  | 0.0149 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-07-30 | WTP4 |  | 0.2499 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-07-30 | WTP4 |  |  | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | 0.5 | PCI/L | 3.4999 | 2020-07-30 | WTP4 |  | 1.4999 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-07-30 | WTP4 |  | 1.4999 | WTP #4
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0.21 | MG/L | 10.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1010 | BARIUM | 0.0138 | MG/L | 2.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1025 | FLUORIDE | 0.52 | MG/L | 4.0499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1052 | SODIUM | 26.3 | MG/L | 160.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | 50.5 | MG/L | 250.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1022 | COPPER | 0.0011 | MG/L | 1.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1025 | FLUORIDE | 0.52 | MG/L | 2.0499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1028 | IRON | 0.0149 | MG/L | 0.3499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1055 | SULFATE | 6.51 | MG/L | 250.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1095 | ZINC | 0.0049 | MG/L | 5.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.05 | LN(10) |  | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 250 | MG/L | 500.4999 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-07-30 | WTP2 |  |  | WTP #2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-07-30 | WTP2 |  | 0.0149 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP2 |  | 0.0249 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-07-30 | WTP2 |  | 0.1499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP2 |  | 1.4999 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-07-30 | WTP2 |  | 1.4999 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-07-30 | WTP2 |  | 0.4499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-07-30 | WTP2 |  | 9.4999 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-07-30 | WTP2 |  | 6.4999 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-07-30 | WTP2 |  | 0.6499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-07-30 | WTP2 |  | 2.4999 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-07-30 | WTP2 |  | 0.0749 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-07-30 | WTP2 |  | 0.6499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-07-30 | WTP2 |  | 0.1499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-07-30 | WTP2 |  | 0.2499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-07-30 | WTP2 |  | 0.1499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-07-30 | WTP2 |  | 0.9499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP2 |  | 0.1499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-07-30 | WTP2 |  | 0.2499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-07-30 | WTP2 |  | 0.0449 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP2 |  | 0.0249 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-07-30 | WTP2 |  | 0.1499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-07-30 | WTP2 |  | 0.2499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP2 |  | 0.1499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP2 |  | 0.0249 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-07-30 | WTP2 |  | 0.0449 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-07-30 | WTP2 |  | 0.1499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-07-30 | WTP2 |  | 0.0249 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-07-30 | WTP2 |  | 0.0149 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-07-30 | WTP2 |  | 0.2499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-07-30 | WTP2 |  | 0.5499 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1017 | CHLORIDE | 82.4 | MG/L | 250.4999 | 2020-07-30 | WTP1 | 0.4 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1050 | SILVER | 0.0006 | MG/L | 0.1499 | 2020-07-30 | WTP1 | 0.0005 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SEC | 1055 | SULFATE | 44.5 | MG/L | 250.4999 | 2020-07-30 | WTP1 | 1 |  | WP1 (J QUALIFIER: CHLORIDE, SILVER, & SULFATE, NO EXPLANATION, THESE NOT ENTERED IN PWS) RESULTS RCVD 1/7/21. JQ RESULTS ACCEPTED. REPEAT SAMPLES FOR CHLORIDE AND SULFATES REQUESTED. MS/MSD LOW%_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-08-06 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 144 | MG/L |  | 2020-08-06 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-08-06 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2020-08-06 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-08-07 | WTP2 |  |  | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4020 | RADIUM-226 | 0.5 | PCI/L | 3.4999 | 2020-08-07 | WTP2 |  | 1.4999 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-08-07 | WTP2 |  | 1.4999 | WTP#2 POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-08-16 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2020-08-16 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.3 | UG/L | 60.4999 | 2020-08-19 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 54.1 | UG/L | 80.4999 | 2020-08-19 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.7 | UG/L | 60.4999 | 2020-08-19 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 46.7 | UG/L | 80.4999 | 2020-08-19 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.4 | UG/L | 60.4999 | 2020-08-19 | L3 | 1 |  | 3600 CANOE CREEK RD. [TTHM/LRAA=58.45]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 36.5 | UG/L | 80.4999 | 2020-08-19 | L3 | 0.5 |  | 3600 CANOE CREEK RD. [TTHM/LRAA=58.45]
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.7 | UG/L | 60.4999 | 2020-08-19 | L4 | 1 |  | 803 MASSACHUSETTS AVE. (9/20 DISINF BYP RPRT RCVD W/RSLTS) FOUND THESE 8/10 T/H RESULTS, RCVD 10/10/20, IN BP CHEM FOLDER ON 10/27/20-RSLTS ENTD 10/27/20-BB
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 30.1 | UG/L | 80.4999 | 2020-08-19 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. (9/20 DISINF BYP RPRT RCVD W/RSLTS) FOUND THESE 8/10 T/H RESULTS, RCVD 10/10/20, IN BP CHEM FOLDER ON 10/27/20-RSLTS ENTD 10/27/20-BB
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-08-20 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2020-08-20 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-08-20 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2020-08-20 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-08-20 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2020-08-20 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-09-03 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2020-09-03 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-09-03 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2020-09-03 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-09-03 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2020-09-03 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-09-17 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2020-09-17 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-09-17 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2020-09-17 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-09-17 | WTP4 |  |  | 7/20 TO 12/20 DIST WQPS FOR PH & ALK SUBMITTED WITH THESE POE WQPS-IN OCULUS (7 SITES TESTED APPROX. EV. 14 DAYS)
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2020-09-17 | WTP4 |  |  | 7/20 TO 12/20 DIST WQPS FOR PH & ALK SUBMITTED WITH THESE POE WQPS-IN OCULUS (7 SITES TESTED APPROX. EV. 14 DAYS)
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-10-01 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2020-10-01 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-10-01 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2020-10-01 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-10-01 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2020-10-01 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-10-15 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2020-10-15 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-10-15 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2020-10-15 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-10-15 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2020-10-15 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-10-29 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2020-10-29 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-10-29 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2020-10-29 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-10-29 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2020-10-29 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-11-12 | WTP1 | 0.01 | 0.0149 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP1 | 0.01 | 0.0249 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-11-12 | WTP1 | 0.05 | 0.1499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-11-12 | WTP1 | 0.5 | 1.4999 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-11-12 | WTP1 | 0.1 | 1.4999 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-11-12 | WTP1 | 0.4 | 0.4499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-11-12 | WTP1 | 9 | 9.4999 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-11-12 | WTP1 | 6 | 6.4999 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-11-12 | WTP1 | 0.6 | 0.6499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-11-12 | WTP1 | 2 | 2.4999 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-11-12 | WTP1 | 0.07 | 0.0749 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-11-12 | WTP1 | 0.6 | 0.6499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-11-12 | WTP1 | 0.1 | 0.1499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-11-12 | WTP1 | 0.2 | 0.2499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-11-12 | WTP1 | 0.1 | 0.1499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-11-12 | WTP1 | 0.9 | 0.9499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-11-12 | WTP1 | 0.1 | 0.1499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-11-12 | WTP1 | 0.2 | 0.2499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-11-12 | WTP1 | 0.01 | 0.0449 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP1 | 0.01 | 0.0249 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-11-12 | WTP1 | 0.1 | 0.1499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-11-12 | WTP1 | 0.2 | 0.2499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-11-12 | WTP1 | 0.1 | 0.1499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-11-12 | WTP1 | 0.04 | 0.0449 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-11-12 | WTP1 | 0.1 | 0.1499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP1 | 0.02 | 0.0249 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-11-12 | WTP1 | 0.01 | 0.0149 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-11-12 | WTP1 | 0.01 | 0.2499 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-11-12 | WTP2 | 0.01 | 0.0149 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP2 | 0.01 | 0.0249 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-11-12 | WTP2 | 0.05 | 0.1499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-11-12 | WTP2 | 0.5 | 1.4999 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-11-12 | WTP2 | 0.1 | 1.4999 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-11-12 | WTP2 | 0.4 | 0.4499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-11-12 | WTP2 | 9 | 9.4999 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-11-12 | WTP2 | 6 | 6.4999 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-11-12 | WTP2 | 0.6 | 0.6499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-11-12 | WTP2 | 2 | 2.4999 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-11-12 | WTP2 | 0.07 | 0.0749 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-11-12 | WTP2 | 0.6 | 0.6499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-11-12 | WTP2 | 0.1 | 0.1499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-11-12 | WTP2 | 0.2 | 0.2499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-11-12 | WTP2 | 0.1 | 0.1499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-11-12 | WTP2 | 0.9 | 0.9499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-11-12 | WTP2 | 0.1 | 0.1499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-11-12 | WTP2 | 0.2 | 0.2499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-11-12 | WTP2 | 0.01 | 0.0449 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP2 | 0.01 | 0.0249 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-11-12 | WTP2 | 0.1 | 0.1499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-11-12 | WTP2 | 0.2 | 0.2499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-11-12 | WTP2 | 0.1 | 0.1499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP2 | 0.02 | 0.0249 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-11-12 | WTP2 | 0.04 | 0.0449 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-11-12 | WTP2 | 0.1 | 0.1499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP2 | 0.02 | 0.0249 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-11-12 | WTP2 | 0.01 | 0.0149 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-11-12 | WTP2 | 0.01 | 0.2499 | WP2 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-11-12 | WTP4 | 0.01 | 0.0149 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP4 | 0.01 | 0.0249 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-11-12 | WTP4 | 0.05 | 0.1499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-11-12 | WTP4 | 0.5 | 1.4999 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-11-12 | WTP4 | 0.1 | 1.4999 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-11-12 | WTP4 | 0.4 | 0.4499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-11-12 | WTP4 | 9 | 9.4999 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-11-12 | WTP4 | 6 | 6.4999 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-11-12 | WTP4 | 0.6 | 0.6499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-11-12 | WTP4 | 2 | 2.4999 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-11-12 | WTP4 | 0.07 | 0.0749 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-11-12 | WTP4 | 0.6 | 0.6499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-11-12 | WTP4 | 0.1 | 0.1499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-11-12 | WTP4 | 0.2 | 0.2499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-11-12 | WTP4 | 0.1 | 0.1499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-11-12 | WTP4 | 0.9 | 0.9499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-11-12 | WTP4 | 0.1 | 0.1499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-11-12 | WTP4 | 0.2 | 0.2499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-11-12 | WTP4 | 0.01 | 0.0449 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP4 | 0.01 | 0.0249 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-11-12 | WTP4 | 0.1 | 0.1499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-11-12 | WTP4 | 0.2 | 0.2499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-11-12 | WTP4 | 0.1 | 0.1499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP4 | 0.02 | 0.0249 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-11-12 | WTP4 | 0.04 | 0.0449 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-11-12 | WTP4 | 0.1 | 0.1499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP4 | 0.02 | 0.0249 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-11-12 | WTP4 | 0.01 | 0.0149 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-11-12 | WTP4 | 0.01 | 0.2499 | WP4 (ALL OK)
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-11-12 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2020-11-12 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-11-12 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2020-11-12 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-11-12 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2020-11-12 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-11-12 | WTP1 | 0.02 | 0.0249 | WP1 (BENZO(A)PYRENE HAS J QUALIFIER, NO EXPLANATION, NOT ENTD) HLKD. 2/9/21 ACCEPTED [MS/MSD-97/86%,70-130%]_MFC
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20 | UG/L | 60.4999 | 2020-11-17 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 51 | UG/L | 80.4999 | 2020-11-17 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26 | UG/L | 60.4999 | 2020-11-17 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 39.7 | UG/L | 80.4999 | 2020-11-17 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.8 | UG/L | 60.4999 | 2020-11-17 | L3 | 1 |  | LS 67 FRIAR'S COVE & OLD CANOE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 27.1 | UG/L | 80.4999 | 2020-11-17 | L3 | 0.5 |  | LS 67 FRIAR'S COVE & OLD CANOE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.1 | UG/L | 60.4999 | 2020-11-17 | L4 | 1 |  | 803 MASSACHUSETTS AVE. (12/20 DISINF BYP RPRT RCVD W/RSLTS) FOUND REPORT ON FTP WEBSITE 1/28/21, RCVD 1/7/21. BB
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 51.1 | UG/L | 80.4999 | 2020-11-17 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. (12/20 DISINF BYP RPRT RCVD W/RSLTS) FOUND REPORT ON FTP WEBSITE 1/28/21, RCVD 1/7/21. BB
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-11-26 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 142 | MG/L |  | 2020-11-26 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-11-26 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 150 | MG/L |  | 2020-11-26 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-11-26 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2020-11-26 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-12-10 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2020-12-10 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-12-10 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2020-12-10 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-12-10 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2020-12-10 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-12-14 | DIST | 0.2 |  | VERMONT AND 5TH STREET
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-12-24 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 138 | MG/L |  | 2020-12-24 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2020-12-24 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2020-12-24 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-12-24 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2020-12-24 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-01-07 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-01-07 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-01-07 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-01-07 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-01-07 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-01-07 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-01-21 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-01-21 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-01-22 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 139 | MG/L |  | 2021-01-22 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-01-22 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-01-22 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2021-02-04 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-02-04 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-02-04 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-02-04 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-02-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-02-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.3 | UG/L | 60.4999 | 2021-02-14 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 43.5 | UG/L | 80.4999 | 2021-02-14 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.4 | UG/L | 60.4999 | 2021-02-14 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 33.4 | UG/L | 80.4999 | 2021-02-14 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.5 | UG/L | 60.4999 | 2021-02-14 | L3 | 1 |  | LS 67 (FRIAR'S AND CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 32.1 | UG/L | 80.4999 | 2021-02-14 | L3 | 0.5 |  | LS 67 (FRIAR'S AND CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.6 | UG/L | 60.4999 | 2021-02-14 | L4 | 1 |  | 803 MASSACHUSSETTS AVE. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS-PGS 2 & 3 W/T RAA & H RAA DID NOT COPY) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 28.9 | UG/L | 80.4999 | 2021-02-14 | L4 | 0.5 |  | 803 MASSACHUSSETTS AVE. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS-PGS 2 & 3 W/T RAA & H RAA DID NOT COPY) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-02-18 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 137 | MG/L |  | 2021-02-18 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-02-18 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 145 | MG/L |  | 2021-02-18 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-02-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-02-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-03-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-03-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-03-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-03-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-03-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-03-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-03-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-25 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-03-25 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-03-25 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-03-25 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-01 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-04-01 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-01 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-04-01 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-04-01 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-04-01 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-04-15 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-04-15 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-04-15 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-04-15 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-04-15 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2021-04-15 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-04-29 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-04-29 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2021-04-29 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-04-29 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-04-29 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-04-29 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-13 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-05-13 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-13 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-05-13 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-05-13 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-05-13 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2021-05-18 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIRCLE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 36 | UG/L | 80.4999 | 2021-05-18 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIRCLE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.4 | UG/L | 60.4999 | 2021-05-18 | L2 | 1 |  | 4805 DOC DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 27.2 | UG/L | 80.4999 | 2021-05-18 | L2 | 0.5 |  | 4805 DOC DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.3 | UG/L | 60.4999 | 2021-05-18 | L3 | 1 |  | L.S. 67 FRIARS LN & (OLD) CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 24.3 | UG/L | 80.4999 | 2021-05-18 | L3 | 0.5 |  | L.S. 67 FRIARS LN & (OLD) CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.3 | UG/L | 60.4999 | 2021-05-18 | L4 | 1 |  | 803 MASSACHUSETTS AVE. (6/21 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 26.4 | UG/L | 80.4999 | 2021-05-18 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. (6/21 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-05-27 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-05-27 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-27 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-05-27 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-27 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2021-05-27 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-10 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-06-10 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-06-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-06-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-06-24 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-06-24 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-24 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2021-06-24 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-06-27 | WTP4 |  |  | 1/21 TO 6/21 DIST WQPS ALSO RCVD, TESTED APPROX. EV. 2 WEEKS AT 7 SITES (RCVD WITH THESE 1/21-6/21 POE WQPS BUT NOT ENTERED AT TIME OF RECEIPT ON 7/8/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-06-27 | WTP4 |  |  | 1/21 TO 6/21 DIST WQPS ALSO RCVD, TESTED APPROX. EV. 2 WEEKS AT 7 SITES (RCVD WITH THESE 1/21-6/21 POE WQPS BUT NOT ENTERED AT TIME OF RECEIPT ON 7/8/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-08 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 137 | MG/L |  | 2021-07-08 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-08 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2021-07-08 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-07-08 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-07-08 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-07-22 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-07-22 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-22 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-07-22 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-22 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-07-22 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-05 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-08-05 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-08-05 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-08-05 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-08-05 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-08-05 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 63.1 | UG/L | 60.4999 | 2021-08-18 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIRCLE (SINGLE SAMPLE HAA5 EXCEEDANCE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 79 | UG/L | 80.4999 | 2021-08-18 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIRCLE (SINGLE SAMPLE HAA5 EXCEEDANCE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.5 | UG/L | 60.4999 | 2021-08-18 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 53.1 | UG/L | 80.4999 | 2021-08-18 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 57 | UG/L | 60.4999 | 2021-08-18 | L3 | 1 |  | LS 67 (FRIAR'S & OLD CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 33.8 | UG/L | 80.4999 | 2021-08-18 | L3 | 0.5 |  | LS 67 (FRIAR'S & OLD CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.7 | UG/L | 60.4999 | 2021-08-18 | L4 | 1 |  | 803 MASSACHUSETTS AVE. (9/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 43.8 | UG/L | 80.4999 | 2021-08-18 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. (9/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-19 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-08-19 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-19 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2021-08-19 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-08-19 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-08-19 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-02 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-09-02 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-09-02 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-09-02 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-09-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-09-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-09-16 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2021-09-16 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-09-16 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-09-16 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-18 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-09-18 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-30 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-09-30 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-30 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-09-30 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-09-30 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-09-30 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-14 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-10-14 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-14 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-10-14 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-14 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-10-14 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-28 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-10-28 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-10-28 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-10-28 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-10-28 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2021-10-28 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-11-11 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-11-11 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-11-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-11-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-11-11 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-11-11 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.9 | UG/L | 60.4999 | 2021-11-15 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 48 | UG/L | 80.4999 | 2021-11-15 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13 | UG/L | 60.4999 | 2021-11-15 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 36.6 | UG/L | 80.4999 | 2021-11-15 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.5 | UG/L | 60.4999 | 2021-11-15 | L3 | 1 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 25.9 | UG/L | 80.4999 | 2021-11-15 | L3 | 0.5 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.5 | UG/L | 60.4999 | 2021-11-15 | L4 | 1 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 28.1 | UG/L | 80.4999 | 2021-11-15 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-11-25 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-11-25 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-11-25 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-11-25 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-11-25 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-11-25 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-09 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-12-09 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-09 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-12-09 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-12-09 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-12-09 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-12-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-12-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-12-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-12-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-12-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.1 | UG/L | 60.4999 | 2022-02-21 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 56.1 | UG/L | 80.4999 | 2022-02-21 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.5 | UG/L | 60.4999 | 2022-02-21 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 35.6 | UG/L | 80.4999 | 2022-02-21 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.4 | UG/L | 60.4999 | 2022-02-21 | L3 |  |  | LS 67
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 28.2 | UG/L | 80.4999 | 2022-02-21 | L3 |  |  | LS 67
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.7 | UG/L | 60.4999 | 2022-02-21 | L4 |  |  | 803 MASSACHUSETTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 27.5 | UG/L | 80.4999 | 2022-02-21 | L4 |  |  | 803 MASSACHUSETTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-13 | WTP4 |  |  | WTP 4 POE NN
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-13 | WTP4 |  |  | WTP 4 POE NN
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-13 | WTP1 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-13 | WTP1 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-13 | WTP2 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-13 | WTP2 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.5 | UG/L | 60.4999 | 2022-05-18 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 83.7 | UG/L | 80.4999 | 2022-05-18 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.4 | UG/L | 60.4999 | 2022-05-18 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 54.8 | UG/L | 80.4999 | 2022-05-18 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.8 | UG/L | 60.4999 | 2022-05-18 | L3 |  |  | FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 50.6 | UG/L | 80.4999 | 2022-05-18 | L3 |  |  | FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.8 | UG/L | 60.4999 | 2022-05-18 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 50.7 | UG/L | 80.4999 | 2022-05-18 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 66.6 | UG/L | 80.4999 | 2022-08-17 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR. J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 46.2 | UG/L | 80.4999 | 2022-08-17 | L2 | 0.5 |  | 4805 DOC DR. J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 45.37 | UG/L | 80.4999 | 2022-08-17 | L3 | 0.5 |  | LS 67 (FRIAR'S & OLD CANOE) J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 44.54 | UG/L | 80.4999 | 2022-08-17 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.3 | UG/L | 60.4999 | 2022-11-18 | L3 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 49.8 | UG/L | 80.4999 | 2022-11-18 | L3 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.7 | UG/L | 60.4999 | 2022-11-18 | L1 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 91 | UG/L | 80.4999 | 2022-11-18 | L1 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.5 | UG/L | 60.4999 | 2022-11-18 | L2 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 46.7 | UG/L | 80.4999 | 2022-11-18 | L2 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.9 | UG/L | 60.4999 | 2022-11-18 | L4 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | DBP | 2950 | TOTAL THMS | 56.7 | UG/L | 80.4999 | 2022-11-18 | L4 |  |  | LATE DATA ENTRY_SMD
3491702 | FLORIDIAN RV RESORT | INOR | 1040 | NITRATE | 0.282 | MG/L | 10.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1010 | BARIUM | 0.0095 | MG/L | 2.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1020 | CHROMIUM | 0.0029 | MG/L | 0.1499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1052 | SODIUM | 43.6 | MG/L | 160.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1017 | CHLORIDE | 68.7 | MG/L | 250.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1022 | COPPER | 0.0197 | MG/L | 1.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1028 | IRON | 2.06 | MG/L | 0.3499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1055 | SULFATE | 75.6 | MG/L | 250.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1095 | ZINC | 0.0945 | MG/L | 5.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.61 | LN(10) |  | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 408 | MG/L | 500.4999 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-05-15 | AAA
3491702 | FLORIDIAN RV RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-05-15 | AAA |  | 0.5499
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 53.4 | UG/L | 60.4999 | 2018-08-09 | L1 | 0.5 |  | BOAT RAMP (T>60, H>45, RETURN TO ROUTINE, ANNUAL, DBP TESTING) HLKD TO SB
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 61.3 | UG/L | 80.4999 | 2018-08-09 | L1 | 0.5 |  | BOAT RAMP (T>60, H>45, RETURN TO ROUTINE, ANNUAL, DBP TESTING) HLKD TO SB
3491702 | FLORIDIAN RV RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.65 | PCI/L | 15.4999 | 2018-12-26 | AAA |  |  | DUE 2024
3491702 | FLORIDIAN RV RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-12-26 | AAA |  | 1.4999 | DUE 2024
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.1 | UG/L | 60.4999 | 2019-08-27 | L1 | 0.9 |  | BOAT RAMP (RCVD 11/7/19) HLKD (*****TTHMS > MCL*****) QTRLY TESTING NEEDED FOR BOTH T/H
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 84.3 | UG/L | 80.4999 | 2019-08-27 | L1 | 0.32 |  | BOAT RAMP (RCVD 11/7/19) HLKD (*****TTHMS > MCL*****) QTRLY TESTING NEEDED FOR BOTH T/H
3491702 | FLORIDIAN RV RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-08-27 | AAA
3491702 | FLORIDIAN RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-08-27 | AAA
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.7 | UG/L | 60.4999 | 2019-12-30 | L1 |  |  | BOAT RAMP. START Q TESTING 1Q20. SAMPLES RCVD LATE, 1Q20 MISSED. PENDING CORRECTED SAMPLING PLAN FOR APPROVAL_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 99.6 | UG/L | 80.4999 | 2019-12-30 | L1 |  |  | BOAT RAMP. START Q TESTING 1Q20. SAMPLES RCVD LATE, 1Q20 MISSED. PENDING CORRECTED SAMPLING PLAN FOR APPROVAL_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.9 | UG/L | 60.4999 | 2020-05-13 | L1 | 0.9 |  | BOAT RAMP MAKEUP SAMPLES | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 46.3 | UG/L | 80.4999 | 2020-05-13 | L1 | 0.32 |  | BOAT RAMP MAKEUP SAMPLES | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.3 | UG/L | 60.4999 | 2020-05-13 | L2 | 0.9 |  | A-15 MAKUP SAMPLES
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 45.2 | UG/L | 80.4999 | 2020-05-13 | L2 | 0.32 |  | A-15 MAKUP SAMPLES
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 46.8 | UG/L | 60.4999 | 2020-05-21 | L1 | 0.9 |  | BOAT RAMP | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 86.4 | UG/L | 80.4999 | 2020-05-21 | L1 | 0.32 |  | BOAT RAMP
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 50.5 | UG/L | 60.4999 | 2020-05-21 | L2 | 0.9 |  | A-15 [2 QUARTERS, CAN'T CALCULATE LRAA YET]_VPU
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 89.8 | UG/L | 80.4999 | 2020-05-21 | L2 | 0.32 |  | A-15 [2 QUARTERS, CAN'T CALCULATE LRAA YET]_VPU
3491702 | FLORIDIAN RV RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-08-17 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-08-17 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.7 | UG/L | 60.4999 | 2020-08-17 | L1 | 1 |  | BOAT RAMP [TTHM LRAA=88.57 ; HAA5 =36.76]_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 79.7 | UG/L | 80.4999 | 2020-08-17 | L1 | 0.5 |  | BOAT RAMP [TTHM LRAA=88.57 ; HAA5 =36.76]_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.3 | UG/L | 60.4999 | 2020-08-17 | L2 | 1 |  | A-15 [ONLY 2 SAMPLING EVENTS, CAN'T CALCULATE LRAA YET]_VPU
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 80.9 | UG/L | 80.4999 | 2020-08-17 | L2 | 0.5 |  | A-15 [ONLY 2 SAMPLING EVENTS, CAN'T CALCULATE LRAA YET]_VPU
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 57.8 | UG/L | 60.4999 | 2020-11-15 | L1 | 1 |  | BOAT RAMP [TTHM LRAA=91.03, OE=95.025 ; HAA5 =49.1]MCL VIOLATION, NEED PN AND OE REPORT_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 107 | UG/L | 80.4999 | 2020-11-15 | L1 | 0.5 |  | BOAT RAMP [TTHM LRAA=91.03, OE=95.025 ; HAA5 =49.1]MCL VIOLATION, NEED PN AND OE REPORT_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 55.5 | UG/L | 60.4999 | 2020-11-15 | L2 | 1 |  | A-15 [TTHM LRAA=90.9, OE= 93.68 ; HAA5 =51.43] MCL VIOLATION, NEED PN AND OE REPORT_VPU
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 102 | UG/L | 80.4999 | 2020-11-15 | L2 | 0.5 |  | A-15 [TTHM LRAA=90.9, OE= 93.68 ; HAA5 =51.43] MCL VIOLATION, NEED PN AND OE REPORT_VPU
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 83.6 | UG/L | 60.4999 | 2021-02-16 | L1 | 1 |  | BOAT RAMP [LRAA TTHM=106.28 ; HAA5=57.73 ]_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 152 | UG/L | 80.4999 | 2021-02-16 | L1 | 0.5 |  | BOAT RAMP [LRAA TTHM=106.28 ; HAA5=57.73 ]_VPU | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 91.5 | UG/L | 60.4999 | 2021-02-16 | L2 | 1 |  | A-15 (HLKD) [LRAA TTHM=107.43 ; HAA5=61.45]
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 157 | UG/L | 80.4999 | 2021-02-16 | L2 | 0.5 |  | A-15 (HLKD) [LRAA TTHM=107.43 ; HAA5=61.45]
3491702 | FLORIDIAN RV RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1010 | BARIUM | 0.0085 | MG/L | 2.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1052 | SODIUM | 40.9 | MG/L | 160.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1017 | CHLORIDE | 68.9 | MG/L | 250.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1028 | IRON | 0.118 | MG/L | 0.3499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1055 | SULFATE | 73.8 | MG/L | 250.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1095 | ZINC | 0.0026 | MG/L | 5.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.05 | LN(10) |  | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 442 | MG/L | 500.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-03-16 | AAA |  | 0.0149 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 1.4999 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-03-16 | AAA |  | 1.4999 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-03-16 | AAA |  | 0.4499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 9.4999 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-03-16 | AAA |  | 6.4999 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-03-16 | AAA |  | 0.6499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-03-16 | AAA |  | 2.4999 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-03-16 | AAA |  | 0.0749 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-03-16 | AAA |  | 0.6499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-03-16 | AAA |  | 0.9499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-03-16 | AAA |  | 0.0449 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.0449 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-03-16 | AAA |  | 0.0149 | POE
3491702 | FLORIDIAN RV RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.6 | UG/L | 60.4999 | 2021-05-18 | L1 | 1 |  | BOAT RAMP LRAA TTHM=92.175 HAA5=49.925 (OEL: TTHM=79.75 HAA5=43.15)_NMS | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 30 | UG/L | 80.4999 | 2021-05-18 | L1 | 0.5 |  | BOAT RAMP LRAA TTHM=92.175 HAA5=49.925 (OEL: TTHM=79.75 HAA5=43.15)_NMS | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.87 | UG/L | 60.4999 | 2021-05-18 | L2 | 1 |  | A-15 LRAA TTHM=92.5 HAA5=50.5425 (OEL: TTHM = 79.8 HAA5=40.185)_NMS
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 30.1 | UG/L | 80.4999 | 2021-05-18 | L2 | 0.5 |  | A-15 LRAA TTHM=92.5 HAA5=50.5425 (OEL: TTHM = 79.8 HAA5=40.185)_NMS
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 56.3 | UG/L | 60.4999 | 2021-08-19 | L1 |  |  | BOAT RAMP. L1 TTHM LRAA = 96.15 AND OEL = 93.3. L1 HAA5 LRAA = 53.33 AND OEL = 52.95_AMF | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 95.6 | UG/L | 80.4999 | 2021-08-19 | L1 |  |  | BOAT RAMP. L1 TTHM LRAA = 96.15 AND OEL = 93.3. L1 HAA5 LRAA = 53.33 AND OEL = 52.95_AMF | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-08-19 | L2 |  |  | A-15. L2 TTHM LRAA = 96.68 AND OEL = 95.58. L2 HAA5 LRAA = 38.48 AND OEL = 24.59_AMF | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 97.6 | UG/L | 80.4999 | 2021-08-19 | L2 |  |  | A-15. L2 TTHM LRAA = 96.68 AND OEL = 95.58. L2 HAA5 LRAA = 38.48 AND OEL = 24.59_AMF | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.2 | UG/L | 60.4999 | 2021-11-15 | L1 | 1 |  | BOAT RAMP; L1 HAA5 LRAA = 39.93 AND OEL = 20.08; L1 TTHM LRAA = 70.74 AND OEL = 34.07_AMF | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 5.34 | UG/L | 80.4999 | 2021-11-15 | L1 | 0.5 |  | BOAT RAMP; L1 HAA5 LRAA = 39.93 AND OEL = 20.08; L1 TTHM LRAA = 70.74 AND OEL = 34.07_AMF | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.02 | UG/L | 60.4999 | 2021-11-15 | L2 | 1 |  | A-15; L2 HAA5 LRAA = 20.1 AND OEL = 4.73; L2 TTHM LRAA = 72.36 AND OEL = 34.3_AMF | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 4.75 | UG/L | 80.4999 | 2021-11-15 | L2 | 0.5 |  | A-15; L2 HAA5 LRAA = 20.1 AND OEL = 4.73; L2 TTHM LRAA = 72.36 AND OEL = 34.3_AMF | 3
3491702 | FLORIDIAN RV RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | SEC | 1022 | COPPER | 0.0014 | MG/L | 1.4999 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.1 | UG/L | 60.4999 | 2022-05-17 | L1 |  |  | BOAT RAMP | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 2.98 | UG/L | 80.4999 | 2022-05-17 | L1 |  |  | BOAT RAMP
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.9 | UG/L | 60.4999 | 2022-05-17 | L2 |  |  | A-15
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 2.9 | UG/L | 80.4999 | 2022-05-17 | L2 |  |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2950 | TOTAL THMS | 4.18 | UG/L | 80.4999 | 2022-08-15 | L2 | 0.39 |  | LOT A-15 OUTSIDE BIB | 3
3491702 | FLORIDIAN RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.41 | UG/L | 60.4999 | 2022-08-15 | L1 | 0.98 |  | BOAT RAMP SINK BIB (HLKD) | 3
3491702 | FLORIDIAN RV RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 6.79 | LN(10) |  | 2022-11-08 | AAA |  |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1002 | ALUMINUM | 0.027 | MG/L | 0.2499 | 2022-11-08 | AAA | 0.024 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1017 | CHLORIDE | 66 | MG/L | 250.4999 | 2022-11-08 | AAA | 0.039 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2022-11-08 | AAA | 0.005 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2022-11-08 | AAA | 0.0099 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1028 | IRON | 0.05 | MG/L | 0.3499 | 2022-11-08 | AAA | 0.038 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-11-08 | AAA | 0.005 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-11-08 | AAA | 0.008 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1055 | SULFATE | 82 | MG/L | 250.4999 | 2022-11-08 | AAA | 0.034 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-11-08 | AAA | 0.05 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1905 | COLOR | 50 | COLOR UNITS | 15.4999 | 2022-11-08 | AAA | 5 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2022-11-08 | AAA | 1 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 450 | MG/L | 500.4999 | 2022-11-08 | AAA | 5 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-11-08 | AAA | 0.04 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0.14 | MG/L | 10.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | 0.22 | MG/L | 4.0499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1052 | SODIUM | 25 | MG/L | 160.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | 29 | MG/L | 250.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1022 | COPPER | 0.0038 | MG/L | 1.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | 0.22 | MG/L | 2.0499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | 0.003 | MG/L | 0.0549 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1055 | SULFATE | 2.9 | MG/L | 250.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1095 | ZINC | 0.04 | MG/L | 5.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.68 | LN(10) |  | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 340 | MG/L | 500.4999 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | 0.068 |  | 0.5499 | 2018-02-12 | AAA
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-02-12 | AAA |  | 0.5499
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2018-02-20 | AAA |  |  | RESULTS ACCEPTED WITH J4 QUALIFER- QAQC ACCEPTABLE_SLB
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-20 | AAA |  |  | RESULTS ACCEPTED WITH J4 QUALIFER- QAQC ACCEPTABLE_SLB
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.54 | UG/L | 60.4999 | 2018-08-07 | L1 | 0.91 |  |  | 3
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | 49.3 | UG/L | 80.4999 | 2018-08-07 | L1 | 0.39 |  |  | 3
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0.46 | MG/L | 10.4999 | 2019-04-17 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-04-17 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-07-15 | AAA
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-15 | AAA
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.04 | UG/L | 60.4999 | 2021-08-31 | L1 | 0.98 |  | LOT #47 (HLKD) | 3
3491726 | SHARP'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | 28.37 | UG/L | 80.4999 | 2021-08-31 | L1 | 0.39 |  | LOT #47 (HLKD) | 3
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0.095 | MG/L | 10.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1010 | BARIUM | 0.0091 | MG/L | 2.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1052 | SODIUM | 30 | MG/L | 160.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | 32 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1055 | SULFATE | 1.7 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.01 | LN(10) |  | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 376 | MG/L | 500.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-10-25 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2031 | DALAPON | 2.3 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-25 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-25 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.2 | PCI/L | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2031 | DALAPON | 0.99 | UG/L | 249.9999 | 2022-02-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2031 | DALAPON | 1.4 | UG/L | 249.9999 | 2022-06-23 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008, ROUTINE COMP W/ 62-550
3491726 | SHARP'S MOBILE HOME PARK | SOC | 2031 | DALAPON | 1.5 | UG/L | 249.9999 | 2022-08-31 | AAA | 0.9 | 1.4999 | DALAPON 1.50 UG/L (HLKD 9/20/22)
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3491726 | SHARP'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-03-05 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-03-05 | AAA
3491904 | KING'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.78 | UG/L | 60.4999 | 2018-08-08 | L1 | 0.91 |  |  | 3
3491904 | KING'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | 3.13 | UG/L | 80.4999 | 2018-08-08 | L1 | 0.39 |  |  | 3
3491904 | KING'S MOBILE HOME PARK | SEC | 1028 | IRON | 0.033 | MG/L | 0.3499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | 0.0023 | MG/L | 0.0549 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1055 | SULFATE | 10 | MG/L | 250.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1095 | ZINC | 0.033 | MG/L | 5.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 | LN(10) |  | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 170 | MG/L | 500.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-11-27 | AAA |  | 0.5499
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0.19 | MG/L | 10.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | 17 | MG/L | 250.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1022 | COPPER | 0.0055 | MG/L | 1.4999 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2018-11-27 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0.46 | MG/L | 10.4999 | 2019-04-23 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-04-23 | AAA
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2020-07-02 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-02 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.47 | UG/L | 60.4999 | 2021-08-17 | L1 |  |  |  | 3
3491904 | KING'S MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | 8.18 | UG/L | 80.4999 | 2021-08-17 | L1 |  |  |  | 3
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1025 | FLUORIDE | 0.1 | MG/L | 4.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1052 | SODIUM | 9.8 | MG/L | 160.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1017 | CHLORIDE | 14 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1025 | FLUORIDE | 0.1 | MG/L | 2.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1055 | SULFATE | 9 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.81 | LN(10) |  | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 222 | MG/L | 500.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | 0.06 |  | 0.5499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-02 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-02 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-02 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-04 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-04 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-11-14 | AAA
3491909 | LAKE TOHO RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-11-14 | AAA
3491909 | LAKE TOHO RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-09-23 | AAA
3491909 | LAKE TOHO RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-09-23 | AAA
3491909 | LAKE TOHO RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-08-10 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-08-10 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-07-05 | AAA | 0.2 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-05 | AAA | 0.2 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1010 | BARIUM | 0.0114 | MG/L | 2.4999 | 2021-07-05 | AAA | 0.002 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-07-05 | AAA | 0.2 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1030 | LEAD | 0.0036 | MG/L | 0.0154 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-07-05 | AAA | 2e-05 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-07-05 | AAA | 0.002 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1052 | SODIUM | 28.5 | MG/L | 160.4999 | 2021-07-05 | AAA | 0.5 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-07-05 | AAA | 0.0005 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | SEC | 1017 | CHLORIDE | 36 | MG/L | 250.4999 | 2021-07-05 | AAA | 0.4 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1022 | COPPER | 0.02 | MG/L | 1.4999 | 2021-07-05 | AAA | 0.001 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-07-05 | AAA | 0.2 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1028 | IRON | 0.493 | MG/L | 0.3499 | 2021-07-05 | AAA | 0.01 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-07-05 | AAA | 0.001 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-07-05 | AAA | 0.0005 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1055 | SULFATE | 1.84 | MG/L | 250.4999 | 2021-07-05 | AAA | 1 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1095 | ZINC | 0.0072 | MG/L | 5.4999 | 2021-07-05 | AAA | 0.002 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-07-05 | AAA | 5 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.05 | LN(10) |  | 2021-07-05 | AAA | 0.01 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 176 | MG/L | 500.4999 | 2021-07-05 | AAA | 2.5 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-07-05 | AAA | 0.2 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-07-05 | AAA | 0.01 | 0.0149 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.01 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-07-05 | AAA | 0.05 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 1.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-07-05 | AAA | 0.1 | 1.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-07-05 | AAA | 0.4 | 0.4499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 9 | 9.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-07-05 | AAA | 6 | 6.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-07-05 | AAA | 0.6 | 0.6499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-07-05 | AAA | 2 | 2.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-07-05 | AAA | 0.07 | 0.0749 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-07-05 | AAA | 0.6 | 0.6499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-07-05 | AAA | 0.2 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-07-05 | AAA | 0.9 | 0.9499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-07-05 | AAA | 0.2 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-07-05 | AAA | 0.01 | 0.0449 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.01 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-07-05 | AAA | 0.2 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.02 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.04 | 0.0449 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.02 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-07-05 | AAA | 0.01 | 0.0149 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-07-05 | AAA | 0.01 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-09-30 | AAA | 0.01 | 0.0149 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.01 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-09-30 | AAA | 0.05 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 1.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-09-30 | AAA | 0.1 | 1.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-09-30 | AAA | 0.4 | 0.4499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 9 | 9.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-09-30 | AAA | 6 | 6.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-09-30 | AAA | 0.6 | 0.6499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-09-30 | AAA | 2 | 2.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-09-30 | AAA | 0.07 | 0.0749 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 2.08 | UG/L | 6.4999 | 2021-09-30 | AAA | 0.6 | 0.6499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-09-30 | AAA | 0.2 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-09-30 | AAA | 0.9 | 0.9499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-09-30 | AAA | 0.2 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-09-30 | AAA | 0.01 | 0.0449 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.01 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-09-30 | AAA | 0.2 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.02 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.04 | 0.0449 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.02 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-09-30 | AAA | 0.01 | 0.0149 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-09-30 | AAA | 0.01 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2022-07-12 | AAA | 1.2 |  | RADS
3491909 | LAKE TOHO RESORT | RAD | 4020 | RADIUM-226 | 0.7 | PCI/L | 3.4999 | 2022-07-12 | AAA | 0.3 | 1.4999 | RADS
3491909 | LAKE TOHO RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-07-12 | AAA | 0.7 | 1.4999 | RADS
3491909 | LAKE TOHO RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-07-29 | AAA | 0.44 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-07-29 | AAA | 0.27 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-07-29 | AAA | 0.44 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-07-29 | AAA | 0.44 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-07-29 | AAA | 0.39 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-07-29 | AAA | 0.33 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.29 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-07-29 | AAA | 0.22 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 0.21 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.24 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-07-29 | AAA | 0.29 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.25 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-07-29 | AAA | 0.26 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.14 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-07-29 | AAA | 0.27 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.42 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 0.36 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.26 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-07-29 | AAA | 0.33 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-07-29 | AAA | 0.31 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 0.25 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-07-29 | AAA | 0.0069 | 0.0149 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.0071 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-07-29 | AAA | 0.0068 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.12 | 1.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-07-29 | AAA | 0.37 | 0.4499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 6 | 9.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-07-29 | AAA | 5.9 | 6.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-07-29 | AAA | 0.5 | 0.6499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-07-29 | AAA | 1.8 | 2.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-07-29 | AAA | 0.06 | 0.0749 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-07-29 | AAA | 0.5 | 0.6499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-07-29 | AAA | 0.09 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-07-29 | AAA | 0.18 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-07-29 | AAA | 0.019 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-07-29 | AAA | 0.51 | 0.9499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.09 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-07-29 | AAA | 0.15 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-07-29 | AAA | 0.006 | 0.0449 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.0056 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-07-29 | AAA | 0.095 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-07-29 | AAA | 0.09 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.0063 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.015 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.038 | 0.0449 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-07-29 | AAA | 0.093 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.0058 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-07-29 | AAA | 0.0049 | 0.0149 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-07-29 | AAA | 0.053 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.69 | UG/L | 60.4999 | 2022-08-04 | L1 |  |  | LOT 19 AL
3491909 | LAKE TOHO RESORT | DBP | 2950 | TOTAL THMS | 41.29 | UG/L | 80.4999 | 2022-08-04 | L1 |  |  | LOT 19 AL
3491909 | LAKE TOHO RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 56.6 | UG/L | 60.4999 | 2022-08-17 | L2 |  |  | LOT 64 AL
3491909 | LAKE TOHO RESORT | DBP | 2950 | TOTAL THMS | 111.52 | UG/L | 80.4999 | 2022-08-17 | L2 |  |  | LOT 64 AL
3491909 | LAKE TOHO RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-30 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-05 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-05 | AAA | 0.0034 |  | POE
3491909 | LAKE TOHO RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-05 | AAA |  | 0.4499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-05 | AAA |  | 9.4999 | POE
3491909 | LAKE TOHO RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-05 | AAA |  | 6.4999 | POE
3491909 | LAKE TOHO RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-05 | AAA |  | 2.4999 | POE
3491909 | LAKE TOHO RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-05 | AAA |  | 0.0749 | POE
3491909 | LAKE TOHO RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-05 | AAA |  | 0.9499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-10-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2022-10-07 | AAA | 0.6 |  | POE
3491909 | LAKE TOHO RESORT | RAD | 4020 | RADIUM-226 | 1.2 | PCI/L | 3.4999 | 2022-10-07 | AAA | 0.4 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-10-07 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 55.54 | UG/L | 60.4999 | 2022-11-17 | L1 | 0.98 |  | TTHM EXCEEDANCE
3491909 | LAKE TOHO RESORT | DBP | 2950 | TOTAL THMS | 96.53 | UG/L | 80.4999 | 2022-11-17 | L1 | 0.39 |  | TTHM EXCEEDANCE
3491909 | LAKE TOHO RESORT | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-12-15 | AAA | 0.024 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-15 | AAA | 0.0034 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-12-15 | AAA | 0.00025 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2022-12-15 | AAA | 0.003 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-12-15 | AAA | 0.00025 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-12-15 | AAA | 0.1 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-12-15 | AAA | 0.004 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2022-12-15 | AAA | 0.0099 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-12-15 | AAA | 0.0005 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-12-15 | AAA | 3e-05 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-12-15 | AAA | 0.008 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-12-15 | AAA | 0.0012 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1052 | SODIUM | 17 | MG/L | 160.4999 | 2022-12-15 | AAA | 0.8 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-12-15 | AAA | 0.001 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-12-15 | AAA | 0.002 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-12-15 | AAA | 0.00025 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-12-15 | AAA | 0.0024 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1017 | CHLORIDE | 23 | MG/L | 250.4999 | 2022-12-15 | AAA | 0.0039 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2022-12-15 | AAA | 0.005 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1025 | FLUORIDE | 0.17 | MG/L | 2.0499 | 2022-12-15 | AAA | 0.0099 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-12-15 | AAA | 0.038 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1032 | MANGANESE | 0.0071 | MG/L | 0.0549 | 2022-12-15 | AAA | 0.005 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-12-15 | AAA | 0.0005 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-12-15 | AAA | 0.05 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1905 | COLOR | 28 | COLOR UNITS | 15.4999 | 2022-12-15 | AAA | 5 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-12-15 | AAA | 1 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 200 | MG/L | 500.4999 | 2022-12-15 | AAA | 5 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | SEC | 2905 | FOAMING AGENTS | 0.059 |  | 0.5499 | 2022-12-15 | AAA | 0.04 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.2 | UG/L | 60.4999 | 2018-07-24 | L1 |  |  | 2950 - 3203 WHISPERWIND DR. | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 97.1 | UG/L | 80.4999 | 2018-07-24 | L1 |  |  | 2950 - 3203 WHISPERWIND DR. | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.2 | UG/L | 60.4999 | 2018-10-24 | L1 |  |  | 2950-3203 WHISPERWIND DR. | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2018-10-24 | L1 |  |  | 2950-3203 WHISPERWIND DR. | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.5 | UG/L | 60.4999 | 2019-01-29 | L1 |  |  | SAMPLED OUTSIDE TIMEFRAME (1/22 - 1/28) ON PLAN. SURROGATE RECOVERY OUTSIDE RANGE. RESAMPLE REQUIRED_JMF | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 67.5 | UG/L | 80.4999 | 2019-01-29 | L1 |  |  | SAMPLED OUTSIDE TIMEFRAME (1/22 - 1/28) ON PLAN. SURROGATE RECOVERY OUTSIDE RANGE. RESAMPLE REQUIRED_JMF | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.1 | UG/L | 60.4999 | 2019-02-22 | L1 |  |  | RESAMPLE FROM JANUARY TESTS WITH QUALIFIERS_JMF | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 77.2 | UG/L | 80.4999 | 2019-02-22 | L1 |  |  | RESAMPLE FROM JANUARY TESTS WITH QUALIFIERS_JMF | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.6 | UG/L | 60.4999 | 2019-04-26 | L1 |  |  | 3203 WHISPERWIND DR. | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 72 | UG/L | 80.4999 | 2019-04-26 | L1 |  |  | 3203 WHISPERWIND DR. | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 127 | UG/L | 80.4999 | 2019-07-26 | L1 |  |  | 3203 WHISPERWIND DR. TTHMS LRAA = 79.8 HAA5 LRAA = 31.4 (1QM OVER LRAA) [1/19 SAMPLES QUALIFIED, DO NOT COUNT TOWARDS CALCULATION]_VP | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 62.9 | UG/L | 60.4999 | 2019-07-26 | L1 |  |  | 3203 WHISPERWIND DR. TTHMS LRAA = 79.8 HAA5 LRAA = 31.4 (1QM OVER LRAA) [1/19 SAMPLES QUALIFIED, DO NOT COUNT TOWARDS CALCULATION]_VP | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.2 | UG/L | 60.4999 | 2019-10-26 | L1 |  |  | 3203 WHISPERWIND DR. [LRAA TTHM=93.1; HAA5=37.95]. (2QM OVER LRAA) CONTINUE Q SAMPLING_VP | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 96.2 | UG/L | 80.4999 | 2019-10-26 | L1 |  |  | 3203 WHISPERWIND DR. [LRAA TTHM=93.1; HAA5=37.95]. (2QM OVER LRAA) CONTINUE Q SAMPLING_VP | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.7 | UG/L | 60.4999 | 2020-01-24 | L1 | 0.9 |  | 3203 WHISPERWIND DR [TTHM LRAA=86.95; HAA5=39.85 ] (3QM TTHM OVER LRAA)_VPU | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 52.6 | UG/L | 80.4999 | 2020-01-24 | L1 | 0.32 |  | 3203 WHISPERWIND DR [TTHM LRAA=86.95; HAA5=39.85 ] (3QM TTHM OVER LRAA)_VPU | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.3 | UG/L | 60.4999 | 2020-04-29 | L1 | 0.9 |  | 3203 WHISPERWIND DR. [TTHM LRAA = 83.05 ; HAA5=36.03]_VPU | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 56.4 | UG/L | 80.4999 | 2020-04-29 | L1 | 0.32 |  | 3203 WHISPERWIND DR. [TTHM LRAA = 83.05 ; HAA5=36.03]_VPU | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.3 | UG/L | 60.4999 | 2020-07-28 | L1 | 0.9 |  | 3203 WHISPERWIND DR. (HLKD) [LRAA TTHM= 70.15; HAA5=20.63]_VPU | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 75.4 | UG/L | 80.4999 | 2020-07-28 | L1 | 0.47 |  | 3203 WHISPERWIND DR. (HLKD) [LRAA TTHM= 70.15; HAA5=20.63]_VPU | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.1 | UG/L | 60.4999 | 2020-10-26 | L1 | 0.9 |  | 3203 WHISPERWIND DR. [TTHM LRAA =60.325 ; HAA5 = 20.1 ] | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 56.9 | UG/L | 80.4999 | 2020-10-26 | L1 | 0.47 |  | 3203 WHISPERWIND DR. [TTHM LRAA =60.325 ; HAA5 = 20.1 ] | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13 | UG/L | 60.4999 | 2021-01-26 | L1 | 0.9 |  | WHISPERWIND [LRAA TTHM=59.75; HAA5=16.68] | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 50.3 | UG/L | 80.4999 | 2021-01-26 | L1 | 0.47 |  | WHISPERWIND [LRAA TTHM=59.75; HAA5=16.68] | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.9 | UG/L | 60.4999 | 2021-07-23 | L1 |  |  |  | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 54.2 | UG/L | 80.4999 | 2021-07-23 | L1 |  |  |  | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.8 | UG/L | 60.4999 | 2022-07-26 | L1 | 0.9 |  | 3203 WHISPERWIND DR. (HLKD) | 3
3491956 | LAKE AJAY VILLAGE S/D (CONSEC.) | DBP | 2950 | TOTAL THMS | 75.1 | UG/L | 80.4999 | 2022-07-26 | L1 | 0.47 |  | 3203 WHISPERWIND DR. (HLKD) | 3
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-21 | AAA
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-21 | AAA
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-06-25 | AAA | 0.051 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | 0.24 | MG/L | 1.4999 | 2018-06-25 | AAA | 0.053 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-06-25 | AAA | 8e-05 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1010 | BARIUM | 0.021 | MG/L | 2.4999 | 2018-06-25 | AAA | 0.00083 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-06-25 | AAA | 0.00045 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-06-25 | AAA | 0.0016 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-06-25 | AAA | 0.0048 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1025 | FLUORIDE | 0.24 | MG/L | 4.0499 | 2018-06-25 | AAA | 0.075 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-06-25 | AAA | 0.00024 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-06-25 | AAA | 5e-05 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-06-25 | AAA | 0.006 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-06-25 | AAA | 0.00058 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1052 | SODIUM | 6.8 | MG/L | 160.4999 | 2018-06-25 | AAA | 0.34 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-06-25 | AAA | 0.00011 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-06-25 | AAA | 0.0004 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-06-25 | AAA | 6e-05 |  | E53076/NN,FL, E84589/CY,HG
3494313 | WHISPERING PINES MHP | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-06-25 | AAA | 0.028 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1017 | CHLORIDE | 10 | MG/L | 250.4999 | 2018-06-25 | AAA | 0.78 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-06-25 | AAA | 0.0032 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1025 | FLUORIDE | 0.24 | MG/L | 2.0499 | 2018-06-25 | AAA | 0.075 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-06-25 | AAA | 0.1 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1032 | MANGANESE | 0.0025 | MG/L | 0.0549 | 2018-06-25 | AAA | 0.0019 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-06-25 | AAA | 0.0001 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1055 | SULFATE | 44 | MG/L | 250.4999 | 2018-06-25 | AAA | 0.52 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-06-25 | AAA | 0.033 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-06-25 | AAA | 5 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-06-25 | AAA | 1 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.32 | LN(10) |  | 2018-06-25 | AAA |  |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 170 | MG/L | 500.4999 | 2018-06-25 | AAA | 10 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-06-25 | AAA | 0.04 |  | 53076/CHL,FL,SULF,COL,OD,PH,TDS, E82001/F.AGENTS
3494313 | WHISPERING PINES MHP | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-06-25 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-06-25 | AAA | 0.32 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-06-25 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-06-25 | AAA | 0.44 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-06-25 | AAA | 0.46 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-06-25 | AAA | 0.26 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-06-25 | AAA | 0.2 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-06-25 | AAA | 0.18 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-06-25 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.36 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-06-25 | AAA | 0.39 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.23 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-06-25 | AAA | 0.26 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.28 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-06-25 | AAA | 0.12 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-06-25 | AAA | 0.24 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-06-25 | AAA | 0.12 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-06-25 | AAA | 0.17 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-06-25 | AAA | 0.22 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-06-25 | AAA | 0.17 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-06-25 | AAA | 0.39 | 0.5499 | 3YR VOC (ALL OK)
3494313 | WHISPERING PINES MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.57 | UG/L | 60.4999 | 2018-08-08 | L1 | 0.91 |  |  | 3
3494313 | WHISPERING PINES MHP | DBP | 2950 | TOTAL THMS | 23.48 | UG/L | 80.4999 | 2018-08-08 | L1 | 0.39 |  |  | 3
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-11-27 | AAA |  | 1.4999 | 1AM
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-04-16 | AAA
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-04-16 | AAA
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2019-11-19 | AAA |  | 1.4999 | 2AM
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-08-03 | AAA | 0.051 |  | NITRITIE J QUAL. ACPETED_VPU
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-08-03 | AAA | 0.13 |  | NITRITIE J QUAL. ACPETED_VPU
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-10-02 | AAA | 0.9 | 1.4999 | 3AM DALAPON (HLKD 11/12/20). 3 CONSEC. YEARS W/O DETECT. TEST EVERY 3 YEARS WITH OTHER SOCS _VPU
3494313 | WHISPERING PINES MHP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.36 | UG/L | 60.4999 | 2021-08-16 | L1 |  |  | 1729 GRAND CYPRESS | 3
3494313 | WHISPERING PINES MHP | DBP | 2950 | TOTAL THMS | 14.46 | UG/L | 80.4999 | 2021-08-16 | L1 |  |  | 1729 GRAND CYPRESS | 3
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1052 | SODIUM | 8.3 | MG/L | 160.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1017 | CHLORIDE | 8 | MG/L | 250.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1028 | IRON | 0.059 | MG/L | 0.3499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1055 | SULFATE | 46 | MG/L | 250.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.77 | LN(10) |  | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 192 | MG/L | 500.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SEC | 2905 | FOAMING AGENTS | 0.05 |  | 0.5499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-22 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-22 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-22 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-22 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-22 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-22 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-22 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-22 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-22 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-22 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.6 | PCI/L | 15.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-05 | AAA |  |  | POE
3494313 | WHISPERING PINES MHP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-05 | AAA |  |  | POE
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1025 | FLUORIDE | 0.13 | MG/L | 4.0499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1017 | CHLORIDE | 12.6 | MG/L | 250.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1025 | FLUORIDE | 0.13 | MG/L | 2.0499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1028 | IRON | 0.13 | MG/L | 0.3499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1032 | MANGANESE | 0.0029 | MG/L | 0.0549 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1055 | SULFATE | 3.2 | MG/L | 250.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 107 | MG/L | 500.4999 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-02-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-02-27 | AAA |  | 0.5499
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-03-27 | AAA |  | 9.4999 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-03-27 | AAA |  | 0.0149 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2018-03-27 | AAA |  |  | DUE 2024_JMF
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-03-27 | AAA |  | 1.4999 | DUE 2024_JMF
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.0149 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.1499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 1.4999 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 1.4999 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-03-27 | AAA |  | 0.4499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-03-27 | AAA |  | 6.4999 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-03-27 | AAA |  | 0.6499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 2.4999 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-03-27 | AAA |  | 0.0749 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-03-27 | AAA |  | 0.6499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-03-27 | AAA |  | 0.1499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-03-27 | AAA |  | 0.2499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.1499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.9499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 0.1499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-03-27 | AAA |  | 0.0449 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-03-27 | AAA |  | 0.1499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.2499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.1499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.0449 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-03-27 | AAA |  | 0.1499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 | 1QM[2QM 4-6/18] ETHOXYCLOR,ENDOTHALL,SIMAZINE,CARBOFURAN,DIBROMOCHLOROPROPANE,ETHYLENE DIBROMIDE HAVE RESULTS OF U,J, BUT ACCEPTABLE QAQC. ENDOTHALL AND EDB HAVE BEEN RESAMPLED AND ARE ACCEPTABLE. SLB
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.0149 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-05-22 | AAA |  | 0.1499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-05-22 | AAA |  | 1.4999 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-05-22 | AAA |  | 1.4999 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-05-22 | AAA |  | 0.4499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-05-22 | AAA |  | 9.4999 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-05-22 | AAA |  | 6.4999 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-05-22 | AAA |  | 0.6499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-05-22 | AAA |  | 0.0749 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-05-22 | AAA |  | 0.6499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-05-22 | AAA |  | 0.1499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-05-22 | AAA |  | 0.2499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-05-22 | AAA |  | 0.1499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-05-22 | AAA |  | 0.1499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.2499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-05-22 | AAA |  | 0.0449 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-05-22 | AAA |  | 0.1499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-05-22 | AAA |  | 0.2499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-05-22 | AAA |  | 0.1499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-05-22 | AAA |  | 0.0249 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-05-22 | AAA |  | 0.0449 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-05-22 | AAA |  | 0.1499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-05-22 | AAA |  | 0.2499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-05-22 | AAA |  | 2.4999 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-05-22 | AAA |  | 0.9499 | 2QM RCVD 8/8/19. EDB AND 2931 J QUAL , ACCEPTED_VP. SUBCONTRACT LAB E87610
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-09-25 | AAA |  | 0.0149 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-09-25 | AAA |  | 0.1499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-09-25 | AAA |  | 1.4999 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-09-25 | AAA |  | 1.4999 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-09-25 | AAA |  | 0.4499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-09-25 | AAA |  | 9.4999 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-09-25 | AAA |  | 6.4999 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-09-25 | AAA |  | 0.6499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-09-25 | AAA |  | 2.4999 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-09-25 | AAA |  | 0.0749 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-09-25 | AAA |  | 0.6499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-09-25 | AAA |  | 0.1499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-09-25 | AAA |  | 0.2499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-09-25 | AAA |  | 0.1499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-09-25 | AAA |  | 0.9499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-09-25 | AAA |  | 0.1499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-09-25 | AAA |  | 0.2499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-09-25 | AAA |  | 0.0449 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-09-25 | AAA |  | 0.1499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-09-25 | AAA |  | 0.2499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-09-25 | AAA |  | 0.1499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-09-25 | AAA |  | 0.0449 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-09-25 | AAA |  | 0.1499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-09-25 | AAA |  | 0.0249 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-09-25 | AAA |  | 0.0149 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-09-25 | AAA |  | 0.2499 | 3QM [4QM DUE 10-12/18]
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.9 | UG/L | 60.4999 | 2018-09-25 | L1 |  |  | RECV'D 02/14/19_KAC | 3
3494316 | BERMUDA MOBILE HOME PARK | DBP | 2950 | TOTAL THMS | 8.2 | UG/L | 80.4999 | 2018-09-25 | L1 |  |  | RECV'D 02/14/19_KAC | 3
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-12-26 | AAA |  | 0.6499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-12-26 | AAA |  | 2.4999 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-12-26 | AAA |  | 0.0749 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-12-26 | AAA |  | 0.6499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-12-26 | AAA |  | 0.1499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-12-26 | AAA |  | 0.2499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-12-26 | AAA |  | 0.1499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-12-26 | AAA |  | 0.9499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-12-26 | AAA |  | 0.1499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-12-26 | AAA |  | 0.2499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-12-26 | AAA |  | 0.0449 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-12-26 | AAA |  | 0.1499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-12-26 | AAA |  | 0.2499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-12-26 | AAA |  | 0.1499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-12-26 | AAA |  | 0.0449 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-12-26 | AAA |  | 0.1499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-12-26 | AAA |  | 0.0149 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-12-26 | AAA |  | 0.2499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-12-26 | AAA |  | 0.0149 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-12-26 | AAA |  | 0.0249 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-12-26 | AAA |  | 0.1499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-12-26 | AAA |  | 1.4999 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-12-26 | AAA |  | 1.4999 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-12-26 | AAA |  | 0.4499 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-12-26 | AAA |  | 9.4999 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-12-26 | AAA |  | 6.4999 | 4QM [CAN MOVE TO "T", MISISNG 2Q18SAMPLES RCVD 8/8/19, NEXT SOCS DUE 2021_VP]
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.0149 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.1499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 1.4999 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 1.4999 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2019-02-14 | AAA |  | 0.4499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2019-02-14 | AAA |  | 9.4999 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2019-02-14 | AAA |  | 6.4999 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2019-02-14 | AAA |  | 0.6499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2019-02-14 | AAA |  | 0.0749 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2019-02-14 | AAA |  | 0.6499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2019-02-14 | AAA |  | 0.1499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2019-02-14 | AAA |  | 0.2499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2019-02-14 | AAA |  | 0.1499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2019-02-14 | AAA |  | 0.9499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2019-02-14 | AAA |  | 0.1499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2019-02-14 | AAA |  | 0.0449 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2019-02-14 | AAA |  | 0.1499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2019-02-14 | AAA |  | 0.2499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.1499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2019-02-14 | AAA |  | 0.0449 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2019-02-14 | AAA |  | 0.1499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2019-02-14 | AAA |  | 0.0249 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2019-02-14 | AAA |  | 0.0149 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2019-02-14 | AAA |  | 0.2499 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2019-02-14 | AAA |  | 2.4999 | EXTRA SET. OXAMYL 2036 UNDETECTED J QUAL.BIASED HIGH. ACCEPTED_VP
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-08-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-08-27 | AAA
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-06-16 | AAA | 0.025 |  | POE BI - NN
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-06-16 | AAA | 0.025 |  | POE BI - NN
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-06-16 | AAA | 0.07 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-06-16 | AAA | 0.14 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-06-16 | AAA | 0.11 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-06-16 | AAA | 0.44 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-06-16 | AAA | 0.093 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-06-16 | AAA | 0.09 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-06-16 | AAA | 0.12 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-06-16 | AAA | 0.11 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-06-16 | AAA | 0.1 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-06-16 | AAA | 0.11 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-06-16 | AAA | 0.11 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-06-16 | AAA | 0.082 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-06-16 | AAA | 0.13 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-06-16 | AAA | 0.11 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-06-16 | AAA | 0.03 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-06-16 | AAA | 0.072 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-06-16 | AAA | 0.03 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-06-16 | AAA | 0.11 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-06-16 | AAA | 0.28 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-06-16 | AAA | 0.039 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-06-16 | AAA | 0.038 | 0.5499 | POE PLANT TAP
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1030 | LEAD | 0.0003 | MG/L | 0.0154 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1052 | SODIUM | 11.2 | MG/L | 160.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1017 | CHLORIDE | 12.5 | MG/L | 250.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1022 | COPPER | 0.0033 | MG/L | 1.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1028 | IRON | 0.069 | MG/L | 0.3499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1032 | MANGANESE | 0.0024 | MG/L | 0.0549 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1055 | SULFATE | 3.9 | MG/L | 250.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1095 | ZINC | 0.01 | MG/L | 5.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.2 | LN(10) |  | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 128 | MG/L | 500.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-04-09 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-09 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-04-09 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-04-09 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-04-09 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-09 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-09 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-04-09 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-09 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-04-09 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2018-03-15 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3.3 |  |  | 2018-03-15 | AAA |  |  | TOC AFTER FILTER AT ENTRY POINT FOR INFORMATIONAL PURPOSES
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | 0.18 | MG/L | 10.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.6 | MG/L | 4.0499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1005 | ARSENIC | 0.0015 | MG/L | 0.0104 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1010 | BARIUM | 0.026 | MG/L | 2.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1030 | LEAD | 0.0002 | MG/L | 0.0154 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1052 | SODIUM | 21 | MG/L | 160.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1074 | ANTIMONY | 0.0004 | MG/L | 0.0065 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1022 | COPPER | 0.0049 | MG/L | 1.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1017 | CHLORIDE | 39 | MG/L | 250.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.6 | MG/L | 2.0499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1055 | SULFATE | 3.7 | MG/L | 250.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.73 | LN(10) |  | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 310 | MG/L | 500.4999 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-05-24 | AAA
3494318 | LAKE MARIAN SHORES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.2 | PCI/L | 15.4999 | 2018-05-24 | AAA |  |  | DUE 2024
3494318 | LAKE MARIAN SHORES | RAD | 4030 | RADIUM-228 | 0.7 | PCI/L | 2.4999 | 2018-05-24 | AAA |  | 1.4999 | DUE 2024
3494318 | LAKE MARIAN SHORES | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-05-24 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2018-07-23 | AAA | 0.075 |  | FLUORIDE 2.5 MG/L
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2018-07-23 | AAA | 0.075 |  | FLUORIDE 2.5 MG/L
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 142.3 | UG/L | 60.4999 | 2018-08-10 | L1 |  |  | 2950-LOT 64, BREEZEWAY COURT HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 152.28 | UG/L | 80.4999 | 2018-08-10 | L1 |  |  | 2950-LOT 64, BREEZEWAY COURT HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.7 | MG/L | 4.0499 | 2018-10-25 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.7 | MG/L | 2.0499 | 2018-10-25 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3.4 |  |  | 2018-10-25 | AAA
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-10-25 | AAA |  | 0.5499 | SUBCONTRACT LAB E84589
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.88 | UG/L | 60.4999 | 2018-11-20 | L1 | 0.91 |  | LOT 64, BREEZEWAY CT. OST (HLKD 12/28/18)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 64.39 | UG/L | 80.4999 | 2018-11-20 | L1 | 0.56 |  | LOT 64, BREEZEWAY CT. OST (HLKD 12/28/18)
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3.9 |  |  | 2018-12-04 | AAA |  |  | FLOURIDE CONTINUE TO ISSUE ANNUAL PN. SLB
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.6 | MG/L | 2.0499 | 2018-12-04 | AAA |  |  | FLOURIDE CONTINUE TO ISSUE ANNUAL PN. SLB
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.6 | MG/L | 4.0499 | 2019-01-02 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2019-01-02 | AAA
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.6 | MG/L | 4.0499 | 2019-02-05 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.6 | MG/L | 2.0499 | 2019-02-05 | AAA
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 74.77 | UG/L | 60.4999 | 2019-02-19 | L1 | 0.91 |  | LOT 64,BREEZEWAY CT [HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)]_JMF
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 104.66 | UG/L | 80.4999 | 2019-02-19 | L1 | 0.39 |  | LOT 64,BREEZEWAY CT [HAA5 RAA = 66.74 (>MCL OF 60); TTHM RAA = 80.3 (< MCL OF 80.499)]_JMF
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2019-03-08 | AAA |  |  | 1Q REAULTS AVERAGE - 2.53 (
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2019-03-08 | AAA |  |  | 1Q AVERAGE 2.53 > 4 MCL. CONTINUE COLELCTING QUARTELRY. NEED PN ONCE PER YEAR_VPU
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2019-04-04 | AAA
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2019-04-04 | AAA |  |  | RESULT > 2 MCL. CONTINUE COLELCTING QUARTELRY. NEED PN ONCE PER YEAR_VPU
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3.6 |  |  | 2019-04-19 | AAA |  |  | TOC AFTER FILTER AT ENTRY POINT FOR INFORMATIONAL PURPOSES
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 4.2 |  |  | 2019-05-09 | AAA |  |  | TOC AFTER FILTER AT ENTRY POINT FOR INFORMATIONAL PURPOSES
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.8 | UG/L | 60.4999 | 2019-05-20 | L1 |  |  | LOT 64, BREEZEWAY COURT [HAA5 LRAA = 74.69 (>MCL) OE=47.06; TTHM LRAA =91.37(>MCL); OEL=64.34 NEED PN, OER NOT NEEDED ]_VP
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 44.16 | UG/L | 80.4999 | 2019-05-20 | L1 |  |  | LOT 64, BREEZEWAY COURT [HAA5 LRAA = 74.69 (>MCL) OE=47.06; TTHM LRAA =91.37(>MCL); OEL=64.34 NEED PN, OER NOT NEEDED ]_VP
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.6 | MG/L | 2.0499 | 2019-07-22 | AAA |  |  | 7/22/2019 SECONDARY RESULTS FOR FLOURIDE_AG [RCVD IN CORRECT FORMAT ON 5/29/20_VPU]
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.99 | UG/L | 60.4999 | 2019-08-20 | L1 |  |  | LOT 64, BREEZEWAY COURT [LRAA TTHM= 59.12 OEL=38.29; HAA5= 41.11 ]_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 23.3 | UG/L | 80.4999 | 2019-08-20 | L1 |  |  | LOT 64, BREEZEWAY COURT [LRAA TTHM= 59.12 OEL=38.29; HAA5= 41.11 ]_VPU
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | 0.46 | MG/L | 10.4999 | 2019-10-09 | AAA | 0.1
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-10-09 | AAA | 0.25
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.8 | MG/L | 4.0499 | 2019-10-09 | AAA | 0.15
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.8 | MG/L | 2.0499 | 2019-10-09 | AAA | 0.15 |  | RESULT > 2 MCL. CONTINUE COLELCTING QUARTELRY. NEED PN ONCE PER YEAR_VPU
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2019-10-09 | AAA | 0.28 | 0.5499 | XYLENES
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.25 | UG/L | 60.4999 | 2019-11-20 | L1 | 0.91 |  | LOT 64, BREEZEWAY COURT [LRAA TTHM= 46.19, OEL=20.10; HAA5= 31.45]_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 12.64 | UG/L | 80.4999 | 2019-11-20 | L1 | 0.39 |  | LOT 64, BREEZEWAY COURT [LRAA TTHM= 46.19, OEL=20.10; HAA5= 31.45]_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 53.25 | UG/L | 60.4999 | 2020-02-18 | L1 | 0.91 |  | LOT 64, BREEZEWAY CT. [LRAA TTHM= 45.20, OEL=69.83 ; HAA5=26.07 ] NO PN OR OER REQUIRED_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 121.69 | UG/L | 80.4999 | 2020-02-18 | L1 | 0.39 |  | LOT 64, BREEZEWAY CT. [LRAA TTHM= 45.20, OEL=69.83 ; HAA5=26.07 ] NO PN OR OER REQUIRED_VPU
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.6 | MG/L | 2.0499 | 2020-04-27 | AAA | 0.075 |  | RESULT > 2 MCL. CONTINUE COLLECTING QUARTELRY. NEED PN ONCE PER YEAR_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.86 | UG/L | 60.4999 | 2020-05-18 | L1 | 0.91 |  | LOT 64 [LRAA TTHM=61.18 , OEL=77.13; HAA5= 27.34] NO PN OR OER REQUIRED_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 87.1 | UG/L | 80.4999 | 2020-05-18 | L1 | 0.39 |  | LOT 64 [LRAA TTHM=61.18 , OEL=77.13; HAA5= 27.34] NO PN OR OER REQUIRED_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.15 | UG/L | 60.4999 | 2020-05-20 | L2 | 0.91 |  | LOT 46
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 81.25 | UG/L | 80.4999 | 2020-05-20 | L2 | 0.39 |  | LOT 46
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.7 | MG/L | 4.0499 | 2020-07-20 | AAA | 0.075 |  | FLUORIDE 2.7 (HLKD) TOC 2.7 MG/L
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.7 | MG/L | 2.0499 | 2020-07-20 | AAA | 0.075 |  | FLUORIDE 2.7 (HLKD) TOC 2.7 MG/L. NEED ANNUAL PN. FLUORIDE >2 MCL_VPU
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2.7 |  |  | 2020-07-20 | AAA | 0.5 |  | FLUORIDE 2.7 (HLKD) TOC 2.7 MG/L. NEED ANNUAL PN. FLUORIDE >2 MCL_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.61 | UG/L | 60.4999 | 2020-08-20 | L1 | 0.98 |  | LOT 64, BREEZEWAY COURT [LRAA TTHM = 74.96 OEL=91.41 ; HAA5=35.74]
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 78.42 | UG/L | 80.4999 | 2020-08-20 | L1 | 0.39 |  | LOT 64, BREEZEWAY COURT [LRAA TTHM = 74.96 OEL=91.41 ; HAA5=35.74]
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.35 | UG/L | 60.4999 | 2020-08-20 | L2 | 0.98 |  | LOT 46 [NO LRAA YET, ONLY 2 QUARTERS SAMPLED SO FAR]_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 79.29 | UG/L | 80.4999 | 2020-08-20 | L2 | 0.39 |  | LOT 46 [NO LRAA YET, ONLY 2 QUARTERS SAMPLED SO FAR]_VPU
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | 0.029 | MG/L | 10.4999 | 2020-10-07 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-10-07 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3.8 |  |  | 2020-10-15 | AAA | 0.5 |  | FLUORIDE 2.6 (HLKD) TOC 3.8 MG/L. NEED ANNUAL PN. FLUORIDE >2 MCL_VPU
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | 0.026 | MG/L | 10.4999 | 2020-10-15 | AAA | 0.0075
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-10-15 | AAA | 0.048
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.6 | MG/L | 4.0499 | 2020-10-15 | AAA | 0.065
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.6 | MG/L | 2.0499 | 2020-10-15 | AAA | 0.0065 |  | FLUORIDE 2.6 (HLKD) TOC 3.8 MG/L. NEED ANNUAL PN. FLUORIDE >2 MCL_VPU
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-10-15 | AAA | 0.28 | 0.5499
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.78 | UG/L | 60.4999 | 2020-11-16 | L2 | 0.98 |  | LOT 46 [NO LRAA YET, ONLY 3 QUARTERS SAMPLED SO FAR]_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 76.9 | UG/L | 80.4999 | 2020-11-16 | L2 | 0.39 |  | LOT 46 [NO LRAA YET, ONLY 3 QUARTERS SAMPLED SO FAR]_VPU
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.24 | UG/L | 60.4999 | 2020-11-16 | L1 | 0.98 |  | LOT 64, BREEZEWAY COURT [LRAA TTHM = 91.7875 OEL=81.35 ; HAA5=42.99] NEED PN AND OE REPORT _VPU
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 79.94 | UG/L | 80.4999 | 2020-11-16 | L1 | 0.39 |  | LOT 64, BREEZEWAY COURT [LRAA TTHM = 91.7875 OEL=81.35 ; HAA5=42.99] NEED PN AND OE REPORT _VPU
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-06 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-06 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2021-01-13 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2021-01-13 | AAA |  |  | POE...FLUORIDE MCL
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.24 | UG/L | 60.4999 | 2021-02-17 | L1 |  |  | BREEZEWAY
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 13.72 | UG/L | 80.4999 | 2021-02-17 | L1 |  |  | BREEZEWAY
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.4 | UG/L | 60.4999 | 2021-02-17 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 13.74 | UG/L | 80.4999 | 2021-02-17 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 1.7 |  |  | 2021-03-01 | AAA | 0.5 |  | TOC
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2 |  |  | 2021-04-01 | AAA | 0.5 |  | POE TOC 2.0 MG/L (PRIOR TO FILTER 2.3 MG/L) SPECIAL MONITORING TO CHECK TOC LEVEL FOR DBPS
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2021-04-22 | AAA | 0.0065 |  | FLUORIDE 2.5 MG/L
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2021-04-22 | AAA | 0.0065 |  | FLUORIDE 2.5 MG/L (OVER THE SECONDARY MCL OF 2.0 MG/L)
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.19 | UG/L | 60.4999 | 2021-05-19 | L1 |  |  | LOT 64, LRAA TTHM= 45.185 HAA5=22.1325_NMS
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-19 | L1 |  |  | LOT 64, LRAA TTHM= 45.185 HAA5=22.1325_NMS
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-19 | L2 |  |  | LOT 46, LRAA TTHM=42.4825 HAA5=21.1325_NMS
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-19 | L2 |  |  | LOT 46, LRAA TTHM=42.4825 HAA5=21.1325_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2021-07-15 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2021-07-15 | AAA |  |  | POE...FLUORIDE MCL
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2021-08-23 | AAA | 0.0065 |  | FLUORIDE 2.4
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2021-08-23 | AAA | 0.0065 |  | FLUORIDE 2.4 (OVER THE SECONDARY MCL OF 2.0 MG/L) HLKD
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2.2 |  |  | 2021-08-23 | AAA | 0.5 |  | POST FILTER TOC 2.2 MG/L (PRE FILTER 2.2 MG/L) SPECIAL MONITORING TO CHECK TOC LEVEL FOR DBPS
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.71 | UG/L | 60.4999 | 2021-08-25 | L2 | 0.98 |  | (BREEZEWAY CT.) LOT 46 (HLKD)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 13.22 | UG/L | 80.4999 | 2021-08-25 | L2 | 0.39 |  | (BREEZEWAY CT.) LOT 46 (HLKD)
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.83 | UG/L | 60.4999 | 2021-08-25 | L1 | 0.98 |  | (BREEZEWAY COURT) LOT 64 (HLKD)
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 9.75 | UG/L | 80.4999 | 2021-08-25 | L1 | 0.39 |  | (BREEZEWAY COURT) LOT 64 (HLKD)
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1052 | SODIUM | 24 | MG/L | 160.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1017 | CHLORIDE | 34 | MG/L | 250.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1055 | SULFATE | 2.9 | MG/L | 250.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.92 | LN(10) |  | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 259 | MG/L | 500.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-10-26 | AAA |  | 0.667
3494318 | LAKE MARIAN SHORES | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.0149
3494318 | LAKE MARIAN SHORES | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-26 | AAA |  | 0.4499
3494318 | LAKE MARIAN SHORES | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 9.4999
3494318 | LAKE MARIAN SHORES | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-26 | AAA |  | 6.4999
3494318 | LAKE MARIAN SHORES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-26 | AAA |  | 0.6499
3494318 | LAKE MARIAN SHORES | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 2.4999
3494318 | LAKE MARIAN SHORES | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-26 | AAA |  | 0.0749
3494318 | LAKE MARIAN SHORES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-26 | AAA |  | 0.6499
3494318 | LAKE MARIAN SHORES | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-26 | AAA |  | 0.9499
3494318 | LAKE MARIAN SHORES | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-26 | AAA |  | 0.0449
3494318 | LAKE MARIAN SHORES | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.0449
3494318 | LAKE MARIAN SHORES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-26 | AAA |  | 0.0149
3494318 | LAKE MARIAN SHORES | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5.4 | PCI/L | 15.4999 | 2021-10-26 | AAA
3494318 | LAKE MARIAN SHORES | RAD | 4020 | RADIUM-226 | 2.6 | PCI/L | 3.4999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2022-02-09 | AAA |  |  | ENTERED LATE_AL
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2022-02-09 | AAA |  |  | ENTERED LATE
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.3 | MG/L | 2.0499 | 2022-06-23 | AAA |  |  | RECIEVED LATE_AL
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2 |  |  | 2022-06-23 | AAA | 0.5 |  | POE TOC 2.0 MG/L
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.3 | MG/L | 4.0499 | 2022-06-23 | AAA |  |  | FLUORIDE 2.30 MG/L (NEED FLUORIDE REPORTED FOR SECONDARIES)
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2022-08-02 | AAA | 0.0099 |  | RECIEVED CORRECTED REPORT_AL
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2022-08-02 | AAA | 0.0099 |  | FLUORIDE 2.50 MG/L (NEED LAB REPORT DATED NEXT TO LAB MANAGER'S SIGNATURE ON EACH PAGE 2 IN SUBMITTAL, DATE WILL BE 9/8/22 OR EARLIER MOST LIKELY GOING BY OTHER REPORTS)
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3 |  |  | 2022-08-02 | AAA | 0.5 |  | PRE-FILTER TOCS 3 MG/L (NEED LAB REPORT DATED NEXT TO LAB MANAGER'S SIGNATURE ON EACH PAGE 2 IN SUBMITTAL, DATE WILL BE 9/8/22 OR EARLIER MOST LIKELY GOING BY OTHER REPORTS)
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2 |  |  | 2022-08-02 | AAA | 0.5 |  | RECIEVED CORRECTED REPORT_AL
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.64 | UG/L | 60.4999 | 2022-08-16 | L1 |  |  | LOT 64
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 146.03 | UG/L | 80.4999 | 2022-08-16 | L1 |  |  | LOT 64
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 55.54 | UG/L | 60.4999 | 2022-08-16 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 191.62 | UG/L | 80.4999 | 2022-08-16 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2022-10-26 | AAA | 0.024 |  | SAMPLE TYPE- ENTRY POINT - POE AND DISTRIBUTION
3494318 | LAKE MARIAN SHORES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | SAMPLE TYPE- ENTRY POINT - POE AND DISTRIBUTION
3494318 | LAKE MARIAN SHORES | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2022-11-07 | AAA | 0.0099 |  | FLUORIDE 2.50 MG/L (RCVD 1-23-23)
3494318 | LAKE MARIAN SHORES | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2022-11-07 | AAA | 0.0099 |  | FLUORIDE 2.50 MG/L (RCVD 1-23-23)
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3 |  |  | 2022-11-07 | AAA | 0.5 |  | PRE-FILTER TOCS 3 MG/L
3494318 | LAKE MARIAN SHORES | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 1.8 |  |  | 2022-11-07 | AAA | 0.5 |  | POST FILTER TOCS 1.80 MG/L
3494318 | LAKE MARIAN SHORES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-11-08 | AAA |  | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.24 | UG/L | 60.4999 | 2022-11-16 | L1 |  |  | Q422 TTHM HAA5 LOT 64, BREEZEWAY COURT
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 64.77 | UG/L | 80.4999 | 2022-11-16 | L1 |  |  | Q422 TTHM HAA5 LOT 64, BREEZEWAY COURT
3494318 | LAKE MARIAN SHORES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.44 | UG/L | 60.4999 | 2022-11-16 | L2 |  |  | 4Q22 TTHM HAA5 LOT46
3494318 | LAKE MARIAN SHORES | DBP | 2950 | TOTAL THMS | 58.22 | UG/L | 80.4999 | 2022-11-16 | L2 |  |  | 4Q22 TTHM HAA5 LOT46
3494320 | 21 PALMS RV RESORT | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2018-12-28 | AAA
3494320 | 21 PALMS RV RESORT | INOR | 1041 | NITRITE | 0.053 | MG/L | 1.4999 | 2018-12-28 | AAA
3494320 | 21 PALMS RV RESORT | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2019-12-31 | AAA
3494320 | 21 PALMS RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-12-31 | AAA
3494320 | 21 PALMS RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-03-27 | AAA | 0.13 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-03-27 | AAA | 8e-05 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2020-03-27 | AAA | 0.003 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-03-27 | AAA | 0.005 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-03-27 | AAA | 0.005 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-03-27 | AAA | 0.0048 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1025 | FLUORIDE | 0.13 | MG/L | 4.0499 | 2020-03-27 | AAA | 0.075 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1030 | LEAD | 0.0037 | MG/L | 0.0154 | 2020-03-27 | AAA | 0.00024 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-03-27 | AAA | 5e-05 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-03-27 | AAA | 0.01 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-03-27 | AAA | 0.00058 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1052 | SODIUM | 3.3 | MG/L | 160.4999 | 2020-03-27 | AAA | 0.8 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-03-27 | AAA | 0.00011 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-03-27 | AAA | 0.002 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-03-27 | AAA | 6e-05 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-03-27 | AAA | 0.2 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-03-27 | AAA | 0.02 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1017 | CHLORIDE | 16 | MG/L | 250.4999 | 2020-03-27 | AAA | 0.31 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1022 | COPPER | 0.091 | MG/L | 1.4999 | 2020-03-27 | AAA | 0.01 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1025 | FLUORIDE | 0.13 | MG/L | 2.0499 | 2020-03-27 | AAA | 0.075 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-03-27 | AAA | 0.2 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1032 | MANGANESE | 0.007 | MG/L | 0.0549 | 2020-03-27 | AAA | 0.005 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-03-27 | AAA | 7e-05 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1095 | ZINC | 0.11 | MG/L | 5.4999 | 2020-03-27 | AAA | 0.05 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1905 | COLOR | 24 | COLOR UNITS | 15.4999 | 2020-03-27 | AAA | 5 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2020-03-27 | AAA | 1 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.82 | LN(10) |  | 2020-03-27 | AAA |  |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 190 | MG/L | 500.4999 | 2020-03-27 | AAA | 5 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-03-27 | AAA | 0.28 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-03-27 | AAA | 0.32 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-03-27 | AAA | 0.28 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-03-27 | AAA | 0.44 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-03-27 | AAA | 0.46 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-03-27 | AAA | 0.26 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-03-27 | AAA | 0.2 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-03-27 | AAA | 0.18 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-03-27 | AAA | 0.28 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-03-27 | AAA | 0.36 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-03-27 | AAA | 0.39 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-03-27 | AAA | 0.23 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-03-27 | AAA | 0.26 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-03-27 | AAA | 0.28 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-03-27 | AAA | 0.12 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-03-27 | AAA | 0.24 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-03-27 | AAA | 0.12 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-03-27 | AAA | 0.17 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-03-27 | AAA | 0.22 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-03-27 | AAA | 0.17 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-03-27 | AAA | 0.39 | 0.5499 | 1QM INITIAL (2QM DUE 4-6/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-27 | AAA | 0.069 | 0.0149 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-27 | AAA | 0.0071 | 0.0249 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-27 | AAA | 0.0068 | 0.1499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-27 | AAA | 0.12 | 1.4999 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-27 | AAA | 0.9 | 1.4999 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-27 | AAA | 0.37 | 0.4499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-27 | AAA | 1.8 | 9.4999 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-27 | AAA | 5.5 | 6.4999 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-27 | AAA | 0.5 | 0.6499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-27 | AAA | 0.57 | 2.4999 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-27 | AAA | 0.06 | 0.0749 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-27 | AAA | 0.5 | 0.6499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-27 | AAA | 0.09 | 0.1499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-27 | AAA | 0.18 | 0.2499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-27 | AAA | 0.019 | 0.1499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-27 | AAA | 0.28 | 0.9499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-27 | AAA | 0.09 | 0.1499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-27 | AAA | 0.15 | 0.2499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-27 | AAA | 0.006 | 0.0449 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-27 | AAA | 0.0052 | 0.0249 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-27 | AAA | 0.095 | 0.1499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-27 | AAA | 0.09 | 0.2499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-27 | AAA | 0.0063 | 0.1499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-27 | AAA | 0.015 | 0.0249 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-27 | AAA | 0.038 | 0.0449 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-27 | AAA | 0.093 | 0.1499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-27 | AAA | 0.006 | 0.0249 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-27 | AAA | 0.0062 | 0.0149 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-27 | AAA | 0.053 | 0.2499 | 1QM INITIAL (2QM DUE 4-6/20)VPU
3494320 | 21 PALMS RV RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.2 | PCI/L | 15.4999 | 2020-03-27 | AAA | 0.8
3494320 | 21 PALMS RV RESORT | RAD | 4020 | RADIUM-226 | 1.2 | PCI/L | 3.4999 | 2020-03-27 | AAA | 0.4 | 1.4999
3494320 | 21 PALMS RV RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-03-27 | AAA | 0.6 | 1.4999
3494320 | 21 PALMS RV RESORT | INOR | 1040 | NITRATE | 0.23 | MG/L | 10.4999 | 2020-03-27 | AAA | 0.051 |  | 1040 J QUAL, ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 1055 | SULFATE | 5.5 | MG/L | 250.4999 | 2020-03-27 | AAA | 0.52 |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | SEC | 2905 | FOAMING AGENTS | 0.048 |  | 0.5499 | 2020-03-27 | AAA |  |  | 1055 J QUAL. ACCEPTED_VPU
3494320 | 21 PALMS RV RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-06-29 | AAA |  | 0.0149 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-06-29 | AAA |  | 0.0249 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-06-29 | AAA |  | 0.1499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-06-29 | AAA |  | 1.4999 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-06-29 | AAA |  | 1.4999 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-06-29 | AAA |  | 0.4499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-06-29 | AAA |  | 9.4999 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-06-29 | AAA |  | 6.4999 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-06-29 | AAA |  | 0.6499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-06-29 | AAA |  | 2.4999 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-06-29 | AAA |  | 0.0749 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-06-29 | AAA |  | 0.6499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-06-29 | AAA |  | 0.1499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-06-29 | AAA |  | 0.2499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-06-29 | AAA |  | 0.1499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-06-29 | AAA |  | 0.9499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-06-29 | AAA |  | 0.1499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-06-29 | AAA |  | 0.2499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-06-29 | AAA |  | 0.0449 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-06-29 | AAA |  | 0.0249 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-06-29 | AAA |  | 0.1499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-06-29 | AAA |  | 0.2499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-06-29 | AAA |  | 0.1499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-06-29 | AAA |  | 0.0249 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-06-29 | AAA |  | 0.0449 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-06-29 | AAA |  | 0.1499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-06-29 | AAA |  | 0.2499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-06-29 | AAA |  | 0.0249 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-06-29 | AAA |  | 0.0149 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-06-29 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | RAD | 4020 | RADIUM-226 | 0.9 | PCI/L | 3.4999 | 2020-06-29 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | RAD | 4030 | RADIUM-228 | 0.6 | PCI/L | 2.4999 | 2020-06-29 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-06-29 | AAA |  | 0.5499 | 2QM INITIAL (3QM DUE 7-9/20) POE
3494320 | 21 PALMS RV RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-08-31 | AAA | 0.28 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-08-31 | AAA | 0.32 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-08-31 | AAA | 0.28 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-08-31 | AAA | 0.44 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-08-31 | AAA | 0.46 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-08-31 | AAA | 0.26 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-08-31 | AAA | 0.2 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-08-31 | AAA | 0.18 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-08-31 | AAA | 0.28 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-08-31 | AAA | 0.36 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-08-31 | AAA | 0.39 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-08-31 | AAA | 0.23 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-08-31 | AAA | 0.26 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-08-31 | AAA | 0.28 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-08-31 | AAA | 0.12 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-08-31 | AAA | 0.24 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-08-31 | AAA | 0.12 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-08-31 | AAA | 0.17 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-08-31 | AAA | 0.22 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-08-31 | AAA | 0.17 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-08-31 | AAA | 0.39 | 0.5499 | 3Q VOC (INITIAL) RECEIVED 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.4 | PCI/L | 15.4999 | 2020-08-31 | AAA | 1 |  | 3Q RADS (INITIAL) RCVD 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2020-08-31 | AAA | 0.4 | 1.4999 | 3Q RADS (INITIAL) RCVD 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-08-31 | AAA | 0.6 | 1.4999 | 3Q RADS (INITIAL) RCVD 12/1/20 (LATE)
3494320 | 21 PALMS RV RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-08-31 | AAA | 0.0072 | 0.0149 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-08-31 | AAA | 0.0074 | 0.0249 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-08-31 | AAA | 0.0071 | 0.1499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-31 | AAA | 0.13 | 1.4999 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 3.2 | UG/L | 249.9999 | 2020-08-31 | AAA | 0.9 | 1.4999 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-31 | AAA | 0.37 | 0.4499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-31 | AAA | 1.8 | 9.4999 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-31 | AAA | 5.5 | 6.4999 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-08-31 | AAA | 0.5 | 0.6499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-31 | AAA | 0.57 | 2.4999 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-08-31 | AAA | 0.06 | 0.0749 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-08-31 | AAA | 0.5 | 0.6499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-31 | AAA | 0.09 | 0.1499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-31 | AAA | 0.18 | 0.2499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-08-31 | AAA | 0.02 | 0.1499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-31 | AAA | 0.28 | 0.9499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-08-31 | AAA | 0.09 | 0.1499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-08-31 | AAA | 0.15 | 0.2499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-08-31 | AAA | 0.0063 | 0.0449 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-08-31 | AAA | 0.0054 | 0.0249 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-31 | AAA | 0.095 | 0.1499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-31 | AAA | 0.09 | 0.2499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-08-31 | AAA | 0.0066 | 0.1499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-08-31 | AAA | 0.015 | 0.0249 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-31 | AAA | 0.038 | 0.0449 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-31 | AAA | 0.097 | 0.1499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-31 | AAA | 0.0058 | 0.0249 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-31 | AAA | 0.0049 | 0.0149 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-31 | AAA | 0.055 | 0.2499 | 3Q SOC (INITIAL) RECEIVED 12/1/20 (LATE) **DALAPON 3.2 UG/L (EXCEEDS RDL OF 1 UG/L, TRIGGERS QTRLY TESTING) HLKD
3494320 | 21 PALMS RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.81 | UG/L | 60.4999 | 2020-08-31 | L1 | 0.98 |  | LOT 20 (HLKD) RECEIVED 12/1/20 (LATE) | 3
3494320 | 21 PALMS RV RESORT | DBP | 2950 | TOTAL THMS | 11.51 | UG/L | 80.4999 | 2020-08-31 | L1 | 0.39 |  | LOT 20 (HLKD) RECEIVED 12/1/20 (LATE) | 3
3494320 | 21 PALMS RV RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-12-31 | AAA | 0.18 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-12-31 | AAA | 0.28 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-12-31 | AAA | 0.36 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-12-31 | AAA | 0.39 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-12-31 | AAA | 0.23 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-12-31 | AAA | 0.26 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-12-31 | AAA | 0.28 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-12-31 | AAA | 0.12 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-12-31 | AAA | 0.24 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-12-31 | AAA | 0.12 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-12-31 | AAA | 0.17 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-12-31 | AAA | 0.22 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-12-31 | AAA | 0.17 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-12-31 | AAA | 0.39 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-12-31 | AAA | 0.0069 | 0.0149 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-12-31 | AAA | 0.0071 | 0.0249 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-12-31 | AAA | 0.0068 | 0.1499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-12-31 | AAA | 0.12 | 1.4999 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 2.4 | UG/L | 249.9999 | 2020-12-31 | AAA | 0.9 | 1.4999 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-12-31 | AAA | 0.37 | 0.4499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-12-31 | AAA | 6 | 9.4999 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-12-31 | AAA | 5.9 | 6.4999 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-12-31 | AAA | 0.5 | 0.6499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-12-31 | AAA | 1.8 | 2.4999 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-12-31 | AAA | 0.06 | 0.0749 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-12-31 | AAA | 0.5 | 0.6499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-12-31 | AAA | 0.09 | 0.1499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-12-31 | AAA | 0.18 | 0.2499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-12-31 | AAA | 0.019 | 0.1499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-12-31 | AAA | 0.51 | 0.9499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-12-31 | AAA | 0.09 | 0.1499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-12-31 | AAA | 0.15 | 0.2499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-12-31 | AAA | 0.006 | 0.0449 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-12-31 | AAA | 0.0052 | 0.0249 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-12-31 | AAA | 0.095 | 0.1499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-12-31 | AAA | 0.09 | 0.2499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-12-31 | AAA | 0.0063 | 0.1499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-12-31 | AAA | 0.015 | 0.0249 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-12-31 | AAA | 0.038 | 0.0449 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-12-31 | AAA | 0.093 | 0.1499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-12-31 | AAA | 0.0056 | 0.0249 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-12-31 | AAA | 0.0047 | 0.0149 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-12-31 | AAA | 0.053 | 0.2499 | 4Q SOC (DALAPON 2.4). CONTINUE ON Q FOR DALAPON. ALL TOHER SOCS TEST IN 2021-VPU
3494320 | 21 PALMS RV RESORT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.3 | PCI/L | 15.4999 | 2020-12-31 | AAA | 0.7 |  | 4Q RADS. INITAL RADS DONE, TEST IN 6 YEARS. NEXT DUE 2024 PER SMF_VPU
3494320 | 21 PALMS RV RESORT | RAD | 4020 | RADIUM-226 | 1.2 | PCI/L | 3.4999 | 2020-12-31 | AAA | 0.4 | 1.4999 | 4Q RADS. INITAL RADS DONE, TEST IN 6 YEARS. NEXT DUE 2024 PER SMF_VPU
3494320 | 21 PALMS RV RESORT | RAD | 4030 | RADIUM-228 | 0.8 | PCI/L | 2.4999 | 2020-12-31 | AAA | 0.7 | 1.4999 | 4Q RADS. INITAL RADS DONE, TEST IN 6 YEARS. NEXT DUE 2024 PER SMF_VPU
3494320 | 21 PALMS RV RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-12-31 | AAA | 0.28 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-12-31 | AAA | 0.32 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-12-31 | AAA | 0.28 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-12-31 | AAA | 0.44 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-12-31 | AAA | 0.46 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-12-31 | AAA | 0.26 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-12-31 | AAA | 0.2 | 0.5499 | 4Q VOC. MOVE TO ANNUIAL FOR 3 CONSEC YEARS. NEXT DUE 2021, 2022 AND 2023
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-07-31 | AAA |  | 1.4999 | 1Q RESTART DUE TO MISSED SAMPLING. - NEED 4Q 2021 & 1Q, 2Q, 3Q 2022 - MISSED 1Q & 2Q 2021_NMS
3494320 | 21 PALMS RV RESORT | INOR | 1040 | NITRATE | 0.095 | MG/L | 10.4999 | 2021-11-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494320 | 21 PALMS RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-22 | AAA |  | 1.4999 | 2Q RESTART DUE TO MISSED SAMPLING DALAPON - NEED 1Q, 2Q, 3Q 2022 - MISSED 1Q & 2Q 2021_NMS
3494320 | 21 PALMS RV RESORT | INOR | 1040 | NITRATE | 0.47 | MG/L | 10.4999 | 2022-03-09 | AAA |  |  | 2022 ANNUAL N/N
3494320 | 21 PALMS RV RESORT | INOR | 1041 | NITRITE | 0.018 | MG/L | 1.4999 | 2022-03-09 | AAA |  |  | 2022 ANNUAL N/N
3494320 | 21 PALMS RV RESORT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0.089 | UG/L | 74.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0.079 | UG/L | 74.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2955 | TOT XYLENE | 0.16 | UG/L | 10499.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2964 | DICHLOROMETHANE | 0.15 | UG/L | 5.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0.065 | UG/L | 649.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2969 | P-DICHLOROBENZENE | 0.071 | UG/L | 75.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2976 | VINYL CHLORIDE | 0.12 | UG/L | 1.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2977 | 1,1-DICHLOROETHENE | 0.13 | UG/L | 7.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0.26 | UG/L | 149.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2980 | 1,2-DICHLOROETHANE | 0.12 | UG/L | 3.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0.091 | UG/L | 249.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2982 | CARBON TETRACHLORIDE | 0.16 | UG/L | 3.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0.21 | UG/L | 5.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2984 | TRICHLOROETHYLENE | 0.1 | UG/L | 3.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0.23 | UG/L | 5.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2987 | TETRACHLOROETHYLENE | 0.14 | UG/L | 3.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2989 | CHLOROBENZENE | 0.12 | UG/L | 149.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2990 | BENZENE | 0.066 | UG/L | 1.4999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2991 | TOLUENE | 0.11 | UG/L | 1499.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2992 | ETHYLBENZENE | 0.067 | UG/L | 749.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | VOC | 2996 | STYRENE | 0.049 | UG/L | 149.9999 | 2022-03-09 | AAA |  | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | INOR | 1040 | NITRATE | 0.47 | MG/L | 10.4999 | 2022-03-09 | AAA | 0.03 |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1010 | BARIUM | 0.0131 | MG/L | 2.4999 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1025 | FLUORIDE | 0.09 | MG/L | 4.0499 | 2022-03-09 | AAA | 0.034 |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1036 | NICKEL | 0.0014 | MG/L | 0.1499 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1052 | SODIUM | 8.79 | MG/L | 160.4999 | 2022-03-09 | AAA | 0.4 |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1017 | CHLORIDE | 15 | MG/L | 250.4999 | 2022-03-09 | AAA | 0.047 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1022 | COPPER | 0.0016 | MG/L | 1.4999 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1025 | FLUORIDE | 0.09 | MG/L | 2.0499 | 2022-03-09 | AAA | 0.034 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1028 | IRON | 0.0952 | MG/L | 0.3499 | 2022-03-09 | AAA | 0.022 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1032 | MANGANESE | 0.0058 | MG/L | 0.0549 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1055 | SULFATE | 1.3 | MG/L | 250.4999 | 2022-03-09 | AAA | 0.08 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1095 | ZINC | 0.0032 | MG/L | 5.4999 | 2022-03-09 | AAA | 0.0011 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2022-03-09 | AAA | 5 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2022-03-09 | AAA | 1 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 200 | MG/L | 500.4999 | 2022-03-09 | AAA | 10 |  | POE
3494320 | 21 PALMS RV RESORT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-03-09 | AAA |  | 0.0149 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-03-09 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-03-09 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-03-09 | AAA |  | 0.4499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-03-09 | AAA |  | 9.4999 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-03-09 | AAA |  | 6.4999 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-03-09 | AAA |  | 0.6499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-03-09 | AAA |  | 2.4999 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-03-09 | AAA |  | 0.0749 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-03-09 | AAA |  | 0.6499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-03-09 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-03-09 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-03-09 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-03-09 | AAA |  | 0.9499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-03-09 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-03-09 | AAA |  | 0.0449 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-03-09 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-03-09 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-03-09 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-03-09 | AAA |  | 0.0449 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-03-09 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-03-09 | AAA |  | 0.0149 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-03-09 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-03-09 | AAA | 0.9 | 1.4999
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-01 | AAA | 0.31 | 1.4999 | DALAPON
3494320 | 21 PALMS RV RESORT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2022-08-01 | L1 | 2 |  | ADDRESS GIVEN AS 6951 OSCEOLA POLK LINE RD., WHICH IS ADDRESS OF 21 PALMS RV RESORT (STAGE 2 SITE IS LOT 20 - ?) PG1 NOT SIGNED&SMP TYPE MISSING(PARTIAL REVISION RCVD 9/19/22 BUT LOT 20 STILL MISSING) | 3
3494320 | 21 PALMS RV RESORT | DBP | 2950 | TOTAL THMS | 46.2 | UG/L | 80.4999 | 2022-08-01 | L1 | 1 |  | ADDRESS GIVEN AS 6951 OSCEOLA POLK LINE RD., WHICH IS ADDRESS OF 21 PALMS RV RESORT (STAGE 2 SITE IS LOT 20 - ?) PG1 NOT SIGNED&SMP TYPE MISSING(PARTIAL REVISION RCVD 9/19/22 BUT LOT 20 STILL MISSING) | 3
3494320 | 21 PALMS RV RESORT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-18 | AAA |  | 1.4999 | POE-LOCATION CODE SET BY PWS - 03/10/2008 - DIST
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.3 | UG/L | 60.4999 | 2018-09-21 | L1 | 0.5 |  | RED HOUSE (T>60, MUST TEST ROUTINE - ANNUALLY - IN 2019, HLKD TO SB) | 3
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | 72.9 | UG/L | 80.4999 | 2018-09-21 | L1 | 0.5 |  | RED HOUSE (T>60, MUST TEST ROUTINE - ANNUALLY - IN 2019, HLKD TO SB) | 3
3494359 | HYATT FARMS | SEC | 1002 | ALUMINUM | 0.027 | MG/L | 0.2499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1017 | CHLORIDE | 119 | MG/L | 250.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1022 | COPPER | 0.025 | MG/L | 1.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1025 | FLUORIDE | 0.855 | MG/L | 2.0499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1032 | MANGANESE | 0.001 | MG/L | 0.0549 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1055 | SULFATE | 17.4 | MG/L | 250.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1095 | ZINC | 0.076 | MG/L | 5.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1920 | ODOR THRESHOLD | 2 |  | 3.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.83 | LN(10) |  | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 408 | MG/L | 500.4999 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-11-30 | AAA
3494359 | HYATT FARMS | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-11-30 | AAA |  | 0.0249
3494359 | HYATT FARMS | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-11-30 | AAA |  | 0.0749
3494359 | HYATT FARMS | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-11-30 | AAA |  | 0.9499
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | 0.048 | MG/L | 10.4999 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1010 | BARIUM | 0.047 | MG/L | 2.4999 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1025 | FLUORIDE | 0.855 | MG/L | 4.0499 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1030 | LEAD | 0.001 | MG/L | 0.0154 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1052 | SODIUM | 49.5 | MG/L | 160.4999 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | 0.01 | MG/L | 0.0065 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-11-30 | AAA |  |  | ANTIMONY OVER MCL, BEGIN QM_JMF
3494359 | HYATT FARMS | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | 1.64 | UG/L | 1499.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 0.5499 | 3 YR VOC OK. TOLUENE DETECT, BEGIN QM. SYSTEM MISSED 1ST Q 2019, BEGIN QM 2ND Q 2019_JMF
3494359 | HYATT FARMS | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-11-30 | AAA |  | 0.0149
3494359 | HYATT FARMS | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-11-30 | AAA |  | 0.0249
3494359 | HYATT FARMS | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 1.4999
3494359 | HYATT FARMS | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-11-30 | AAA |  | 1.4999
3494359 | HYATT FARMS | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-11-30 | AAA |  | 0.4499
3494359 | HYATT FARMS | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-11-30 | AAA |  | 9.4999
3494359 | HYATT FARMS | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-11-30 | AAA |  | 6.4999
3494359 | HYATT FARMS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-11-30 | AAA |  | 0.6499
3494359 | HYATT FARMS | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-11-30 | AAA |  | 2.4999
3494359 | HYATT FARMS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-11-30 | AAA |  | 0.6499
3494359 | HYATT FARMS | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-11-30 | AAA |  | 0.2499
3494359 | HYATT FARMS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-11-30 | AAA |  | 0.2499
3494359 | HYATT FARMS | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-11-30 | AAA |  | 0.0449
3494359 | HYATT FARMS | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-11-30 | AAA |  | 0.2499
3494359 | HYATT FARMS | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-11-30 | AAA |  | 0.1499
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2019-02-13 | AAA |  |  | 1ST QUARTER ANTIMONY_KAC
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-26 | AAA |  |  | 2019 NN SAMPLES_KAC
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-26 | AAA |  |  | 2019 NN SAMPLES_KAC
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2019-05-01 | AAA |  |  | 2QM (3QM DUE 7-9/19)
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2019-05-15 | AAA |  | 0.5499 | 1QM
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2019-08-28 | AAA |  |  | 3QM (4QM DUE 10-12/19)
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2019-08-28 | AAA |  | 0.5499 | 2QM (3QM DUE 10-12/19)
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.5 | UG/L | 60.4999 | 2019-09-04 | L1 |  |  | L-1 RED HOUSE | 3
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | 43.6 | UG/L | 80.4999 | 2019-09-04 | L1 |  |  | L-1 RED HOUSE | 3
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2019-11-11 | AAA |  |  | 4QM. 4 CONSEC. QUARTERS UNDETECTED. TEST WITH OTHER INORGANICS IN 2021_VP
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2019-11-11 | AAA |  | 0.5499 | 3 QM (4QM DUE 1-3/20)
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-05 | AAA |  | 0.5499 | 4 QM (TEST ANNUAL DURING 4Q)_VP
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | 0.018 | MG/L | 10.4999 | 2020-06-24 | AAA | 0.004 |  | POE NN
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-06-24 | AAA | 0.003 |  | POE NN
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.7 | UG/L | 60.4999 | 2020-09-23 | L1 | 0.5 |  | RED HOUSE | 3
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | 66.3 | UG/L | 80.4999 | 2020-09-23 | L1 | 0.5 |  | RED HOUSE | 3
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-08-18 | L1 |  |  |  | 3
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-08-18 | L1 |  |  |  | 3
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | 0.027 | MG/L | 10.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1005 | ARSENIC | 0.0007 | MG/L | 0.0104 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1010 | BARIUM | 0.048 | MG/L | 2.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1015 | CADMIUM | 0.001 | MG/L | 0.0055 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1025 | FLUORIDE | 0.881 | MG/L | 4.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1052 | SODIUM | 60.3 | MG/L | 160.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1075 | BERYLLIUM | 0.001 | MG/L | 0.0045 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1002 | ALUMINUM | 0.026 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1017 | CHLORIDE | 126 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1022 | COPPER | 0.019 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1025 | FLUORIDE | 0.881 | MG/L | 2.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1032 | MANGANESE | 0.001 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1055 | SULFATE | 13.4 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1095 | ZINC | 0.009 | MG/L | 5.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1905 | COLOR | 2.5 | COLOR UNITS | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.81 | LN(10) |  | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 412 | MG/L | 500.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SEC | 2905 | FOAMING AGENTS | 0.034 |  | 0.5499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.3 | PCI/L | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-02 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | RAD | 4020 | RADIUM-226 | 1.8 | PCI/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-02 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-02 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E83079, E83033, E84567
3494359 | HYATT FARMS | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494359 | HYATT FARMS | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494359 | HYATT FARMS | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-19 | AAA |  | 0.5499 | POE
3494359 | HYATT FARMS | DBP | 2950 | TOTAL THMS | 2.56 | UG/L | 80.4999 | 2022-11-02 | L1 |  |  | MAKEUP SAMPLES FOR MISSED DBP Q3 2022_DJ | 3
3494359 | HYATT FARMS | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-11-02 | L1 |  |  | MAKEUP SAMPLES FOR MISSED DBP Q3 2022_DJ | 3
3494399 | DEER PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-07-16 | AAA | 0.1 | 1.4999 | 3YR SOC
3494399 | DEER PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-07-16 | AAA | 0.4 | 0.4499 | 3YR SOC
3494399 | DEER PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 9 | 9.4999 | 3YR SOC
3494399 | DEER PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-07-16 | AAA | 6 | 6.4999 | 3YR SOC
3494399 | DEER PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-07-16 | AAA | 0.6 | 0.6499 | 3YR SOC
3494399 | DEER PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-07-16 | AAA | 2 | 2.4999 | 3YR SOC
3494399 | DEER PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-07-16 | AAA | 0.07 | 0.0749 | 3YR SOC
3494399 | DEER PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-07-16 | AAA | 0.6 | 0.6499 | 3YR SOC
3494399 | DEER PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-07-16 | AAA | 0.1 | 0.1499 | 3YR SOC
3494399 | DEER PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-07-16 | AAA | 0.2 | 0.2499 | 3YR SOC
3494399 | DEER PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-07-16 | AAA | 0.1 | 0.1499 | 3YR SOC
3494399 | DEER PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-07-16 | AAA | 0.9 | 0.9499 | 3YR SOC
3494399 | DEER PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.1 | 0.1499 | 3YR SOC
3494399 | DEER PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-07-16 | AAA | 0.2 | 0.2499 | 3YR SOC
3494399 | DEER PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-07-16 | AAA | 0.01 | 0.0449 | 3YR SOC
3494399 | DEER PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.01 | 0.0249 | 3YR SOC
3494399 | DEER PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-07-16 | AAA | 0.1 | 0.1499 | 3YR SOC
3494399 | DEER PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-07-16 | AAA | 0.2 | 0.2499 | 3YR SOC
3494399 | DEER PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.1 | 0.1499 | 3YR SOC
3494399 | DEER PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.02 | 0.0249 | 3YR SOC
3494399 | DEER PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.04 | 0.0449 | 3YR SOC
3494399 | DEER PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-07-16 | AAA | 0.1 | 0.1499 | 3YR SOC
3494399 | DEER PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.02 | 0.0249 | 3YR SOC
3494399 | DEER PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-07-16 | AAA | 0.01 | 0.0149 | 3YR SOC
3494399 | DEER PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-07-16 | AAA | 0.01 | 0.2499 | 3YR SOC
3494399 | DEER PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-07-16 | AAA | 0.2 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-07-16 | AAA | 0.2 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-07-16 | AAA | 0.001 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1010 | BARIUM | 0.0429 | MG/L | 2.4999 | 2018-07-16 | AAA | 0.002 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-07-16 | AAA | 0.001 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-07-16 | AAA | 0.001 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-07-16 | AAA | 0.005 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2018-07-16 | AAA | 0.2 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-07-16 | AAA | 0.001 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-07-16 | AAA | 2e-05 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-07-16 | AAA | 0.001 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-07-16 | AAA | 0.002 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1052 | SODIUM | 42.8 | MG/L | 160.4999 | 2018-07-16 | AAA | 0.5 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-07-16 | AAA | 0.001 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-07-16 | AAA | 0.0005 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-07-16 | AAA | 0.001 |  | (RADS NOT REPORTED) REPORT HAS 1038 TOTAL NN ON PRIM INORG PG - 1038 NN SHOULD BE MOVED TO "OTHER CONTAMINANTS" PAGE. IF YOU WANT TO ACCEPT REPORT AS IS, CHANGE SMP TYPE "S" TO "N." TOT NN NOT RQRD
3494399 | DEER PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-07-16 | AAA | 0.02 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1017 | CHLORIDE | 80.7 | MG/L | 250.4999 | 2018-07-16 | AAA | 0.4 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1022 | COPPER | 0.0069 | MG/L | 1.4999 | 2018-07-16 | AAA | 0.001 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2018-07-16 | AAA | 0.2 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1028 | IRON | 0.102 | MG/L | 0.3499 | 2018-07-16 | AAA | 0.01 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1032 | MANGANESE | 0.0206 | MG/L | 0.0549 | 2018-07-16 | AAA | 0.01 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-07-16 | AAA | 0.0005 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1055 | SULFATE | 8.28 | MG/L | 250.4999 | 2018-07-16 | AAA | 1 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1095 | ZINC | 0.0195 | MG/L | 5.4999 | 2018-07-16 | AAA | 0.01 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-07-16 | AAA | 5 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2018-07-16 | AAA | 1 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.81 | LN(10) |  | 2018-07-16 | AAA | 0.01 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 506 | MG/L | 500.4999 | 2018-07-16 | AAA | 2.5 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-07-16 | AAA | 0.2 |  | TDS 506 (>MCL OF 500)
3494399 | DEER PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-07-16 | AAA | 0.2 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-07-16 | AAA | 0.5 | 0.5499 | 3YR VOC
3494399 | DEER PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-07-16 | AAA | 0.01 | 0.0149 | 3YR SOC
3494399 | DEER PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-07-16 | AAA | 0.01 | 0.0249 | 3YR SOC
3494399 | DEER PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-07-16 | AAA | 0.05 | 0.1499 | 3YR SOC
3494399 | DEER PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-07-16 | AAA | 0.5 | 1.4999 | 3YR SOC
3494399 | DEER PARK | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.1 | PCI/L | 15.4999 | 2018-07-16 | AAA |  |  | RADS DUE 2024
3494399 | DEER PARK | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2018-07-16 | AAA |  | 1.4999 | RADS DUE 2024
3494399 | DEER PARK | RAD | 4030 | RADIUM-228 | 0.9 | PCI/L | 2.4999 | 2018-07-16 | AAA |  | 1.4999 | RADS DUE 2024
3494399 | DEER PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.7 | UG/L | 60.4999 | 2018-09-25 | L1 |  |  |  | 3
3494399 | DEER PARK | DBP | 2950 | TOTAL THMS | 31.7 | UG/L | 80.4999 | 2018-09-25 | L1 |  |  |  | 3
3494399 | DEER PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-12-12 | AAA | 0.2
3494399 | DEER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-12-12 | AAA | 0.2
3494399 | DEER PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-07-20 | AAA | 0.2 |  | POE NN DEER PARK
3494399 | DEER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-07-20 | AAA | 0.2 |  | POE NN DEER PARK
3494399 | DEER PARK | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.4 | UG/L | 60.4999 | 2021-09-23 | L1 | 1 |  | 13245 FAWN LANE | 3
3494399 | DEER PARK | DBP | 2950 | TOTAL THMS | 50.3 | UG/L | 80.4999 | 2021-09-23 | L1 | 0.5 |  | 13245 FAWN LANE | 3
3494399 | DEER PARK | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1010 | BARIUM | 0.0406 | MG/L | 2.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1020 | CHROMIUM | 0.0013 | MG/L | 0.1499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1052 | SODIUM | 43.3 | MG/L | 160.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1017 | CHLORIDE | 85.6 | MG/L | 250.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1022 | COPPER | 0.0042 | MG/L | 1.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1028 | IRON | 0.121 | MG/L | 0.3499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1032 | MANGANESE | 0.0243 | MG/L | 0.0549 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1055 | SULFATE | 6.85 | MG/L | 250.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1095 | ZINC | 0.0545 | MG/L | 5.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1905 | COLOR | 15 | COLOR UNITS | 15.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.88 | LN(10) |  | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 484 | MG/L | 500.4999 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-10-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-29 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-29 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-29 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-29 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-29 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-29 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-29 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-29 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-29 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-29 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-29 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-29 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-29 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-29 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-29 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-29 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-29 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-29 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-29 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-29 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-29 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-29 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-29 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-29 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-29 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-29 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-29 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-29 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-29 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494399 | DEER PARK | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-29 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.35 | UG/L | 60.4999 | 2018-02-02 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL). LRAA FOR TTHMS = 89.375. PWS DID NOT GENERATE VIO. MANUALLY ENTERED 10/19/18. SYSTEM UNDER LFCO AND 3RD Q RESULTS ARE BELOW MCL. JMF
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 103.22 | UG/L | 80.4999 | 2018-02-02 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL). LRAA FOR TTHMS = 89.375. PWS DID NOT GENERATE VIO. MANUALLY ENTERED 10/19/18. SYSTEM UNDER LFCO AND 3RD Q RESULTS ARE BELOW MCL. JMF
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 54.39 | UG/L | 60.4999 | 2018-02-21 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 84.31 | UG/L | 80.4999 | 2018-02-21 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2018-02-21 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-21 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.57 | UG/L | 60.4999 | 2018-05-23 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 50.38 | UG/L | 60.4999 | 2018-05-23 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 138.5 | UG/L | 80.4999 | 2018-05-23 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 38.76 | UG/L | 80.4999 | 2018-05-23 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2018-05-23 | AAA | 0.051
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-23 | AAA | 0.053
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2018-05-23 | AAA | 8e-05
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1010 | BARIUM | 0.0077 | MG/L | 2.4999 | 2018-05-23 | AAA | 0.00083
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-05-23 | AAA | 0.00045
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-05-23 | AAA | 0.0016
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-05-23 | AAA | 0.0048
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1025 | FLUORIDE | 0.26 | MG/L | 4.0499 | 2018-05-23 | AAA | 0.075
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-05-23 | AAA | 0.00024
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-05-23 | AAA | 5e-05
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-05-23 | AAA | 0.006
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-05-23 | AAA | 0.00058
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1052 | SODIUM | 30 | MG/L | 160.4999 | 2018-05-23 | AAA | 0.34
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-05-23 | AAA | 0.00011
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-05-23 | AAA | 0.0004
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-05-23 | AAA | 6e-05
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-05-23 | AAA | 0.028
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1017 | CHLORIDE | 40 | MG/L | 250.4999 | 2018-05-23 | AAA | 0.78
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-05-23 | AAA | 0.0032
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1025 | FLUORIDE | 0.26 | MG/L | 2.0499 | 2018-05-23 | AAA | 0.075
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2018-05-23 | AAA | 0.1
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1032 | MANGANESE | 0.0022 | MG/L | 0.0549 | 2018-05-23 | AAA | 0.0019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-05-23 | AAA | 0.0001
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1055 | SULFATE | 9.3 | MG/L | 250.4999 | 2018-05-23 | AAA | 0.52
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-05-23 | AAA | 0.033
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1905 | COLOR | 15 | COLOR UNITS | 15.4999 | 2018-05-23 | AAA | 5
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2018-05-23 | AAA | 1
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.87 | LN(10) |  | 2018-05-23 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 240 | MG/L | 500.4999 | 2018-05-23 | AAA | 10
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-05-23 | AAA | 0.04
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-05-23 | AAA | 0.32 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-05-23 | AAA | 0.44 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-05-23 | AAA | 0.46 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-05-23 | AAA | 0.26 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-05-23 | AAA | 0.2 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-05-23 | AAA | 0.18 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.36 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-05-23 | AAA | 0.39 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.23 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-05-23 | AAA | 0.26 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.28 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-05-23 | AAA | 0.12 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-05-23 | AAA | 0.24 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-05-23 | AAA | 0.12 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-05-23 | AAA | 0.17 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-05-23 | AAA | 0.22 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-05-23 | AAA | 0.17 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-05-23 | AAA | 0.39 | 0.5499
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.69 | UG/L | 60.4999 | 2018-07-24 | L1 | 0.91 |  | 5221 HAMMOCK POINTE CT. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 35.76 | UG/L | 80.4999 | 2018-07-24 | L1 | 0.14 |  | 5221 HAMMOCK POINTE CT. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.03 | UG/L | 60.4999 | 2018-07-24 | L2 | 0.91 |  | 2801 DEERFIELD ST. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 63.4 | UG/L | 80.4999 | 2018-07-24 | L2 | 0.14 |  | 2801 DEERFIELD ST. (E84589/HAA5)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 77.55 | UG/L | 60.4999 | 2018-10-24 | L2 |  |  | 2950-2801 DEERFIELD ST. (PHASE 3 EOL) / SUBCONTRACT LAB E84589 (HAA5 OEL = 63.3775; LRAA = 48.89. TTHM OEL = 132.48; LRAA = 117.28)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 164 | UG/L | 80.4999 | 2018-10-24 | L2 |  |  | 2950-2801 DEERFIELD ST. (PHASE 3 EOL) / SUBCONTRACT LAB E84589 (HAA5 OEL = 63.3775; LRAA = 48.89. TTHM OEL = 132.48; LRAA = 117.28)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 84.75 | UG/L | 60.4999 | 2018-10-24 | L1 |  |  | 2950-5221 HAMMOCK POINTE CT. / SUBCONTRACT LAB E84589 (HAA5 LRAA = 47.085 UG/L; TTHM LRAA = 49.205)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 37.99 | UG/L | 80.4999 | 2018-10-24 | L1 |  |  | 2950-5221 HAMMOCK POINTE CT. / SUBCONTRACT LAB E84589 (HAA5 LRAA = 47.085 UG/L; TTHM LRAA = 49.205)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.12 | UG/L | 60.4999 | 2019-01-23 | L2 |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 80.84 | UG/L | 80.4999 | 2019-01-23 | L2 |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.34 | UG/L | 60.4999 | 2019-01-23 | L1 |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 95.73 | UG/L | 80.4999 | 2019-01-23 | L1 |  |  | 1ST QUARTER 2019
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 52.54 | UG/L | 60.4999 | 2019-04-22 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL) TTHM LRAA = 99.1; H5 = 54.6
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 88.14 | UG/L | 80.4999 | 2019-04-22 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL) TTHM LRAA = 99.1; H5 = 54.6
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.16 | UG/L | 60.4999 | 2019-04-22 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 178.62 | UG/L | 80.4999 | 2019-04-22 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | 0.26 | MG/L | 10.4999 | 2019-04-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-04-22 | AAA
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.81 | UG/L | 60.4999 | 2019-07-24 | L1 |  |  | 5221 HAMMOCK POINTE CT. [LRAA TTHM = 97.65; LRAA HAA5 = 46.52 (
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 78.26 | UG/L | 80.4999 | 2019-07-24 | L1 |  |  | 5221 HAMMOCK POINTE CT. [LRAA TTHM = 97.65; LRAA HAA5 = 46.52 (
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.21 | UG/L | 60.4999 | 2019-07-24 | L2 | 0.91 |  | 2801 DEERFIELD [TTHM LRAA = 103.5; HAA5 LRAA = 52.105 (
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 81.09 | UG/L | 80.4999 | 2019-07-24 | L2 | 0.39 |  | 2801 DEERFIELD [TTHM LRAA = 103.5; HAA5 LRAA = 52.105 (
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.5 | UG/L | 60.4999 | 2019-10-23 | L2 | 0.91 |  | 2801 DEERFIELD ST TTHM LRAA = 63.59 UG/L
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 4.29 | UG/L | 80.4999 | 2019-10-23 | L2 | 0.39 |  | 2801 DEERFIELD ST TTHM LRAA = 63.59 UG/L
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.8 | UG/L | 60.4999 | 2019-10-23 | L1 | 0.91 |  | 5221 HAMMOCK POINTE LRAA TTHM=41.6225 HAA5=23.58
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 2.85 | UG/L | 80.4999 | 2019-10-23 | L1 | 0.39 |  | 5221 HAMMOCK POINTE LRAA TTHM=41.6225 HAA5=23.58
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.78 | UG/L | 60.4999 | 2020-01-21 | L2 |  |  | L2 - 2801 DEERFIELD (TTHM LRAA = 44.78; HAA5 LRAA = 34.51)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 5.59 | UG/L | 80.4999 | 2020-01-21 | L2 |  |  | L2 - 2801 DEERFIELD (TTHM LRAA = 44.78; HAA5 LRAA = 34.51)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.4 | UG/L | 60.4999 | 2020-01-21 | L1 |  |  | L1 - 5221 HAMMOCK PT (TTHM LRAA = 83.95; HAA5 LRAA = 26.29)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 76.05 | UG/L | 80.4999 | 2020-01-21 | L1 |  |  | L1 - 5221 HAMMOCK PT (TTHM LRAA = 83.95; HAA5 LRAA = 26.29)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.83 | UG/L | 60.4999 | 2020-04-22 | L1 |  |  | 5221 HAMMOCK POINTE CT. [LRAA TTHM = 52.11 ; HAA5=26.21 ]_VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 51.26 | UG/L | 80.4999 | 2020-04-22 | L1 |  |  | 5221 HAMMOCK POINTE CT. [LRAA TTHM = 52.11 ; HAA5=26.21 ]_VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.29 | UG/L | 60.4999 | 2020-04-22 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL) [LRAA TTHM =37.47 ; HAA5=26.95] _VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 58.9 | UG/L | 80.4999 | 2020-04-22 | L2 |  |  | 2801 DEERFIELD ST. (PHASE 3 EOL) [LRAA TTHM =37.47 ; HAA5=26.95] _VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.39 | UG/L | 60.4999 | 2020-07-22 | L1 | 0.98 |  | HAMMOCK POINTE [LRAA TTHM = 34.28; HAA5=15.86]. CONTINUE ON Q SAMPLNG PER CO SENT 8/19/20_VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 6.96 | UG/L | 80.4999 | 2020-07-22 | L1 | 0.39 |  | HAMMOCK POINTE [LRAA TTHM = 34.28; HAA5=15.86]. CONTINUE ON Q SAMPLNG PER CO SENT 8/19/20_VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.07 | UG/L | 60.4999 | 2020-07-22 | L2 | 0.98 |  | DEERFIELD [LRAA TTHM = 19.00; HAA5=17.41]. CONTINUE ON Q SAMPLNG PER CO SENT 8/19/20_VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 7.21 | UG/L | 80.4999 | 2020-07-22 | L2 | 0.39 |  | DEERFIELD [LRAA TTHM = 19.00; HAA5=17.41]. CONTINUE ON Q SAMPLNG PER CO SENT 8/19/20_VPU
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-08-04 | AAA | 0.051 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-08-04 | AAA | 0.13 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2020-10-26 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.[LRAA TTHM = 33.56; HAA5= 15.15]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2020-10-26 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.[LRAA TTHM = 33.56; HAA5= 15.15]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2020-10-26 | L2 | 0.98 |  | 2801 DEERFIELD ST. PHASE 3 EOL (TTHM/HAA5 -0-,-0-) UNDER CONSENT ORDER (C.R. .3 ON PAGE 1, .2 ON PAGE 3)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2020-10-26 | L2 | 0.39 |  | 2801 DEERFIELD ST. PHASE 3 EOL (TTHM/HAA5 -0-,-0-) UNDER CONSENT ORDER (C.R. .3 ON PAGE 1, .2 ON PAGE 3)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-01-26 | L2 |  |  | DEERFIELD ST [LRAA TTHM=16.53; HAA5=6.34]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-01-26 | L2 |  |  | DEERFIELD ST [LRAA TTHM=16.53; HAA5=6.34]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-01-26 | L1 |  |  | HAMMOCK POINTE [LRAA TTHM=14.55 ; HAA5=6.31] CONTINUE SAMPLING Q. NEED 4 CONSEC QUARTERS DUE TO AMENDED CO EXECUTED 8/2020
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-01-26 | L1 |  |  | HAMMOCK POINTE [LRAA TTHM=14.55 ; HAA5=6.31] CONTINUE SAMPLING Q. NEED 4 CONSEC QUARTERS DUE TO AMENDED CO EXECUTED 8/2020
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-04-22 | L2 |  |  | 2801 DEERFIELD LRAA - TTHMA=7.21 HAA5=3.07_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-04-22 | L2 |  |  | 2801 DEERFIELD LRAA - TTHMA=7.21 HAA5=3.07_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-04-22 | L1 |  |  | 5221 HAMMOCK POINT CT LRAA TTHMS= 6.96 HAA5 3.39_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-04-22 | L1 |  |  | 5221 HAMMOCK POINT CT LRAA TTHMS= 6.96 HAA5 3.39_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.28 | UG/L | 60.4999 | 2021-07-26 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 103.33 | UG/L | 80.4999 | 2021-07-26 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.81 | UG/L | 60.4999 | 2021-07-26 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 110.89 | UG/L | 80.4999 | 2021-07-26 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.48 | UG/L | 60.4999 | 2021-10-22 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 22.69 | UG/L | 80.4999 | 2021-10-22 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.59 | UG/L | 60.4999 | 2021-10-22 | L2 |  |  | 2801 DEERFIELD ST.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 23.29 | UG/L | 80.4999 | 2021-10-22 | L2 |  |  | 2801 DEERFIELD ST.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1010 | BARIUM | 0.0064 | MG/L | 2.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1052 | SODIUM | 27 | MG/L | 160.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1017 | CHLORIDE | 41 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1055 | SULFATE | 6 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.03 | LN(10) |  | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 75 | MG/L | 500.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SEC | 2905 | FOAMING AGENTS | 0.09 |  | 0.5499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-02 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-02 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-02 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.31 | UG/L | 60.4999 | 2022-01-27 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 69.31 | UG/L | 80.4999 | 2022-01-27 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.1 | UG/L | 60.4999 | 2022-01-27 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 45.08 | UG/L | 80.4999 | 2022-01-27 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 68.54 | UG/L | 60.4999 | 2022-07-20 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 116.05 | UG/L | 80.4999 | 2022-07-20 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 70.47 | UG/L | 60.4999 | 2022-07-20 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 114.52 | UG/L | 80.4999 | 2022-07-20 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.88 | UG/L | 60.4999 | 2022-10-11 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 101.77 | UG/L | 80.4999 | 2022-10-11 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-10-11 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | DBP | 2950 | TOTAL THMS | 6.69 | UG/L | 80.4999 | 2022-10-11 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2022-10-26 | AAA | 0.024 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-26 | AAA | 0.0034 |  | POE
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3494416 | HIDDEN GLEN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.0149 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.1499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 1.4999 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 1.4999 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-03-27 | AAA |  | 0.4499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-03-27 | AAA |  | 9.4999 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-03-27 | AAA |  | 6.4999 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-03-27 | AAA |  | 0.6499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 2.4999 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-03-27 | AAA |  | 0.0749 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-03-27 | AAA |  | 0.6499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-03-27 | AAA |  | 0.1499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-03-27 | AAA |  | 0.2499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.1499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.9499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 0.1499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2018-03-27 | AAA |  | 0.0055 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-03-27 | AAA |  | 0.0449 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-03-27 | AAA |  | 0.1499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.2499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.1499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.0449 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-03-27 | AAA |  | 0.1499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-03-27 | AAA |  | 0.0149 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 | ACCEPTED J QUALIFERS FOR CARBOFURAN, ENDRIN, METHOXYCHLOR AND SIMAZINE.
3494416 | HIDDEN GLEN | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1005 | ARSENIC | 0.0006 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1025 | FLUORIDE | 0.087 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1052 | SODIUM | 6.4 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  | NITRITE HAS A J DATA QUALIFIER. OK PER EMAIL FROM SALLY 6-21-18. ASBESTOS RESULTS DOH LAB ID#87975
3494416 | HIDDEN GLEN | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1017 | CHLORIDE | 8.6 | MG/L | 250.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1022 | COPPER | 0.0034 | MG/L | 1.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1025 | FLUORIDE | 0.087 | MG/L | 2.0499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1028 | IRON | 0.089 | MG/L | 0.3499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1032 | MANGANESE | 0.0036 | MG/L | 0.0549 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1095 | ZINC | 0.095 | MG/L | 5.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1920 | ODOR THRESHOLD | 2 |  | 3.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 162 | MG/L | 500.4999 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-05-24 | AAA
3494416 | HIDDEN GLEN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.1 | UG/L | 60.4999 | 2018-07-24 | L1 | 0.48 |  | T | 3
3494416 | HIDDEN GLEN | DBP | 2950 | TOTAL THMS | 55.9 | UG/L | 80.4999 | 2018-07-24 | L1 | 0.32 |  | T | 3
3494416 | HIDDEN GLEN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA |  |  | DUE 2024
3494416 | HIDDEN GLEN | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999 | DUE 2024
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | AAA
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, ACCEPTED)_VPU
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, ACCEPTED)_VPU
3494416 | HIDDEN GLEN | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA |  | 1.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 1.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-25 | AAA |  | 0.4499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-25 | AAA |  | 9.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-25 | AAA |  | 6.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 2.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-25 | AAA |  | 0.1499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-25 | AAA |  | 0.2499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-25 | AAA |  | 0.9499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-02-25 | AAA |  | 0.0055 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-25 | AAA |  | 0.1499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-25 | AAA |  | 0.2499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-25 | AAA |  | 0.0449 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-25 | AAA |  | 0.1499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-25 | AAA |  | 0.0149 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.2499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-03-19 | AAA |  | 0.0149 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-03-19 | AAA |  | 0.0249 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-03-19 | AAA |  | 0.6499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-03-19 | AAA |  | 0.0749 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-03-19 | AAA |  | 0.6499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-03-19 | AAA |  | 0.2499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-03-19 | AAA |  | 0.0449 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-03-19 | AAA |  | 0.0249 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-03-19 | AAA |  | 0.0249 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-27 | AAA | 0.025
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.025
3494416 | HIDDEN GLEN | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-27 | AAA | 0.0005
3494416 | HIDDEN GLEN | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2021-05-27 | AAA | 0.0062
3494416 | HIDDEN GLEN | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-27 | AAA | 0.00067
3494416 | HIDDEN GLEN | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0026
3494416 | HIDDEN GLEN | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.005
3494416 | HIDDEN GLEN | INOR | 1025 | FLUORIDE | 0.076 | MG/L | 4.0499 | 2021-05-27 | AAA | 0.015
3494416 | HIDDEN GLEN | INOR | 1030 | LEAD | 0.0012 | MG/L | 0.0154 | 2021-05-27 | AAA | 0.00022
3494416 | HIDDEN GLEN | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-27 | AAA | 9e-05
3494416 | HIDDEN GLEN | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.002
3494416 | HIDDEN GLEN | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.00083
3494416 | HIDDEN GLEN | INOR | 1052 | SODIUM | 5.8 | MG/L | 160.4999 | 2021-05-27 | AAA | 0.59
3494416 | HIDDEN GLEN | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-27 | AAA | 0.00021
3494416 | HIDDEN GLEN | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-27 | AAA | 0.00058
3494416 | HIDDEN GLEN | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-27 | AAA | 0.0005
3494416 | HIDDEN GLEN | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2021-05-27 | AAA | 0.2 |  | POE/D ASBESTOS (NOT TESTED OUT IN THE DISTRIBUTION SYSTEM)
3494416 | HIDDEN GLEN | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.0072
3494416 | HIDDEN GLEN | SEC | 1017 | CHLORIDE | 8.2 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5
3494416 | HIDDEN GLEN | SEC | 1022 | COPPER | 0.0071 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.00093
3494416 | HIDDEN GLEN | SEC | 1025 | FLUORIDE | 0.076 | MG/L | 2.0499 | 2021-05-27 | AAA | 0.015
3494416 | HIDDEN GLEN | SEC | 1028 | IRON | 0.083 | MG/L | 0.3499 | 2021-05-27 | AAA | 0.016
3494416 | HIDDEN GLEN | SEC | 1032 | MANGANESE | 0.0039 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.0027
3494416 | HIDDEN GLEN | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0033
3494416 | HIDDEN GLEN | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5
3494416 | HIDDEN GLEN | SEC | 1095 | ZINC | 0.022 | MG/L | 5.4999 | 2021-05-27 | AAA | 0.0076
3494416 | HIDDEN GLEN | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-05-27 | AAA | 5
3494416 | HIDDEN GLEN | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-05-27 | AAA | 1
3494416 | HIDDEN GLEN | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.7 | LN(10) |  | 2021-05-27 | AAA | 0.1
3494416 | HIDDEN GLEN | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 145 | MG/L | 500.4999 | 2021-05-27 | AAA | 5
3494416 | HIDDEN GLEN | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-27 | AAA | 0.099
3494416 | HIDDEN GLEN | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-06-28 | AAA |  |  | HIDDEN GLENN
3494416 | HIDDEN GLEN | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-28 | AAA |  | 1.4999 | HIDDEN GLENN
3494416 | HIDDEN GLEN | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | AAA | 0.025
3494416 | HIDDEN GLEN | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | AAA | 0.025
3494416 | HIDDEN GLEN | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.4 | UG/L | 60.4999 | 2022-07-25 | L1 | 0.9 |  | 6624 IVY MIST LN (HLKD) | 3
3494416 | HIDDEN GLEN | DBP | 2950 | TOTAL THMS | 28.1 | UG/L | 80.4999 | 2022-07-25 | L1 | 0.47 |  | 6624 IVY MIST LN (HLKD) | 3
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 1.4 | UG/L | 249.9999 | 2018-03-23 | AAA |  | 1.4999
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.0149 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.1499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 1.4999 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 2.3 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 1.4999 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-03-27 | AAA |  | 0.4499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-03-27 | AAA |  | 9.4999 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-03-27 | AAA |  | 6.4999 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-03-27 | AAA |  | 0.6499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-03-27 | AAA |  | 2.4999 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-03-27 | AAA |  | 0.0749 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-03-27 | AAA |  | 0.6499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-03-27 | AAA |  | 0.1499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-03-27 | AAA |  | 0.2499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.1499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-03-27 | AAA |  | 0.9499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-03-27 | AAA |  | 0.1499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2018-03-27 | AAA |  | 0.0055 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-03-27 | AAA |  | 0.0449 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-03-27 | AAA |  | 0.1499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-03-27 | AAA |  | 0.2499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.1499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-03-27 | AAA |  | 0.0449 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-03-27 | AAA |  | 0.1499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-03-27 | AAA |  | 0.0249 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-03-27 | AAA |  | 0.0149 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-03-27 | AAA |  | 0.2499 | ABLE TO ACCEPT J QUALIFERS AND I QUALIFERS FOR ENDRIN, METHOXYCHLOR, SIMAZINE, HECACHLOROCYCLOPENTADINENE, AND CARBOFUNRAN.
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1005 | ARSENIC | 0.0006 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1010 | BARIUM | 0.017 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1025 | FLUORIDE | 0.44 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1052 | SODIUM | 12.2 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1002 | ALUMINUM | 0.0064 | MG/L | 0.2499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1017 | CHLORIDE | 13.7 | MG/L | 250.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1022 | COPPER | 0.0011 | MG/L | 1.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1025 | FLUORIDE | 0.44 | MG/L | 2.0499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1028 | IRON | 0.021 | MG/L | 0.3499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1055 | SULFATE | 10.3 | MG/L | 250.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 157 | MG/L | 500.4999 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-05-24 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.3 | UG/L | 60.4999 | 2018-09-07 | L2 |  |  | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 58.5 | UG/L | 80.4999 | 2018-09-07 | L2 |  |  | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.4 | UG/L | 60.4999 | 2018-09-07 | L1 |  |  | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 57.7 | UG/L | 80.4999 | 2018-09-07 | L1 |  |  | RECEIVED 2/21/19
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 2.5 | UG/L | 249.9999 | 2019-06-21 | AAA |  | 1.4999 | MAKE-UP FOR MISSING 1ST Q ANNUAL DALAPON. CONTINUE SAMPLING ANNUALLY DURING THE 1ST Q_JMF
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 66.5 | UG/L | 60.4999 | 2019-09-05 | L2 | 0.9 |  | 1QM. 3645 LATE MORNING CIRCLE; QUARTERLY MONITORING TRIGGERED 09/05/19 - Q MONITORING SHOULD START IN DECEMBER_JB
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 111 | UG/L | 80.4999 | 2019-09-05 | L2 | 0.32 |  | 1QM. 3645 LATE MORNING CIRCLE; QUARTERLY MONITORING TRIGGERED 09/05/19 - Q MONITORING SHOULD START IN DECEMBER_JB
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.2 | UG/L | 60.4999 | 2019-09-05 | L1 | 0.9 |  | 1QM. 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 68.7 | UG/L | 80.4999 | 2019-09-05 | L1 | 0.32 |  | 1QM. 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.9 | UG/L | 60.4999 | 2019-12-23 | L2 | 0.9 |  | 2QM. 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 55.2 | UG/L | 80.4999 | 2019-12-23 | L2 | 0.32 |  | 2QM. 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.1 | UG/L | 60.4999 | 2019-12-23 | L1 | 0.9 |  | 2QM. 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 63.4 | UG/L | 80.4999 | 2019-12-23 | L1 | 0.32 |  | 2QM. 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-01-03 | AAA |  | 1.4999 | CONTINUE SAMPLING ANNUALLY DURING THE 1ST Q_VPU
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | AAA
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.2 | UG/L | 60.4999 | 2020-03-26 | L1 | 0.9 |  | 3QM 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 66.6 | UG/L | 80.4999 | 2020-03-26 | L1 | 0.32 |  | 3QM 3854 WOOD THRUSH DR.
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.9 | UG/L | 60.4999 | 2020-03-26 | L2 | 0.9 |  | 3QM 3645 LATE MORNING CIR. (HLKD)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 47.5 | UG/L | 80.4999 | 2020-03-26 | L2 | 0.32 |  | 3QM 3645 LATE MORNING CIR. (HLKD)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.7 | UG/L | 60.4999 | 2020-06-26 | L1 | 0.9 |  | 3854 WOOD THRUSH DR. [LRAA TTHM=65.23 ;HAA5=34.3]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 62.2 | UG/L | 80.4999 | 2020-06-26 | L1 | 0.3 |  | 3854 WOOD THRUSH DR. [LRAA TTHM=65.23 ;HAA5=34.3]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.7 | UG/L | 60.4999 | 2020-06-26 | L2 | 0.9 |  | 3645 LATE MORNING CIR. [LRAA TTHM=70.13;HAA5=40.75]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 66.8 | UG/L | 80.4999 | 2020-06-26 | L2 | 0.3 |  | 3645 LATE MORNING CIR. [LRAA TTHM=70.13;HAA5=40.75]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.1 | UG/L | 60.4999 | 2020-09-28 | L2 | 0.9 |  | LATE MORNING CIRCLE [LRAA TTHM=60.7; HAA5=34.65]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 73.3 | UG/L | 80.4999 | 2020-09-28 | L2 | 0.47 |  | LATE MORNING CIRCLE [LRAA TTHM=60.7; HAA5=34.65]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.4 | UG/L | 60.4999 | 2020-09-28 | L1 | 0.9 |  | WOOD THRUSH [LRAA TTHM=67.73; HAA5=34.35]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 78.7 | UG/L | 80.4999 | 2020-09-28 | L1 | 0.47 |  | WOOD THRUSH [LRAA TTHM=67.73; HAA5=34.35]_VPU
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.4 | UG/L | 60.4999 | 2020-12-23 | L1 | 0.9 |  | 3854 WOOD THRUSH DR. [LRAA TTHM=67.6; HAA5= 36.43]
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 62.9 | UG/L | 80.4999 | 2020-12-23 | L1 | 0.47 |  | 3854 WOOD THRUSH DR. [LRAA TTHM=67.6; HAA5= 36.43]
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.6 | UG/L | 60.4999 | 2020-12-23 | L2 | 0.9 |  | 3645 LATE MORNING CIR. (HLKD) [LRAA TTHM=65.13; HAA5=38.08]
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 72.9 | UG/L | 80.4999 | 2020-12-23 | L2 | 0.47 |  | 3645 LATE MORNING CIR. (HLKD) [LRAA TTHM=65.13; HAA5=38.08]
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 1 | UG/L | 249.9999 | 2021-01-08 | AAA | 0.89 | 1.4999 | CONTINUE SAMPLING ANNUALLY DURING THE 1ST Q_VPU
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, ACCEPTED)_VPU
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, ACCEPTED)_VPU
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA |  | 1.4999 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 0.79 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 1.4999 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-25 | AAA |  | 0.4499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-25 | AAA |  | 9.4999 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-25 | AAA |  | 6.4999 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 2.4999 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-25 | AAA |  | 0.1499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-25 | AAA |  | 0.2499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-25 | AAA |  | 0.9499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-02-25 | AAA |  | 0.0055 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-25 | AAA |  | 0.1499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-25 | AAA |  | 0.2499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-25 | AAA |  | 0.0449 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-25 | AAA |  | 0.1499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-25 | AAA |  | 0.0149 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.2499 | SLV- POE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35 | UG/L | 60.4999 | 2021-03-23 | L2 | 0.9 |  | 3645 LATE MORNING CIR. LRAA - TTHM=70 HAA5=38.6_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 67 | UG/L | 80.4999 | 2021-03-23 | L2 | 0.47 |  | 3645 LATE MORNING CIR. LRAA - TTHM=70 HAA5=38.6_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.3 | UG/L | 60.4999 | 2021-03-23 | L1 | 0.9 |  | 3854 WOOD THRUSH DR. (HLKD) LRAA - TTHM=67.625 HAA5=36.7_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 66.7 | UG/L | 80.4999 | 2021-03-23 | L1 | 0.47 |  | 3854 WOOD THRUSH DR. (HLKD) LRAA - TTHM=67.625 HAA5=36.7_NMS
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-23 | AAA |  | 0.0149 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-23 | AAA |  | 0.0249 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-23 | AAA |  | 0.1499 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-04-23 | AAA |  | 0.6499 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-23 | AAA |  | 0.0749 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-23 | AAA |  | 0.6499 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-23 | AAA |  | 0.1499 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-23 | AAA |  | 0.1499 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-23 | AAA |  | 0.2499 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-23 | AAA |  | 0.0449 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-23 | AAA |  | 0.0249 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-23 | AAA |  | 0.1499 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-04-23 | AAA |  | 0.0249 | SLV-POE
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-27 | AAA | 0.025 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.025 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-27 | AAA | 0.0005 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2021-05-27 | AAA | 0.0062 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-27 | AAA | 0.00067 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0026 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.005 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2021-05-27 | AAA | 0.015 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-05-27 | AAA | 0.00022 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-27 | AAA | 9e-05 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.002 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.00083 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1052 | SODIUM | 15.3 | MG/L | 160.4999 | 2021-05-27 | AAA | 0.59 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-27 | AAA | 0.00021 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-27 | AAA | 0.00058 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-27 | AAA | 0.0005 |  | POE ASBESTOS ENTERED SEP WITH SAMPLE TYPE "S" SINCE IT'S NOT A COMPLIANCE TEST FROM OUT IN THE DISTRIBUTION SYSTEM.
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2021-05-27 | AAA | 0.2 |  | POE/D ASBESTOS (ENT'D WITH SMP TYPE "S" SINCE NOT FROM THE DISTRIBUTION SYSTEM)
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1002 | ALUMINUM | 0.0114 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.0072
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1017 | CHLORIDE | 15.8 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1022 | COPPER | 0.0023 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.00093
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1025 | FLUORIDE | 0.19 | MG/L | 2.0499 | 2021-05-27 | AAA | 0.015
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1028 | IRON | 0.091 | MG/L | 0.3499 | 2021-05-27 | AAA | 0.016
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.0027
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0033
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1055 | SULFATE | 8.7 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-05-27 | AAA | 0.0076
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-05-27 | AAA | 5
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-05-27 | AAA | 1
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2021-05-27 | AAA | 0.1
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 184 | MG/L | 500.4999 | 2021-05-27 | AAA | 5
3494418 | SPRINGLAKE VILLAGE WTP | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-27 | AAA | 0.099
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.3 | UG/L | 60.4999 | 2021-06-24 | L1 |  |  | 3854 WOOD THRUSH DR, LRAA- TTHM = 66.075 HAA5=37.6_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 56 | UG/L | 80.4999 | 2021-06-24 | L1 |  |  | 3854 WOOD THRUSH DR, LRAA- TTHM = 66.075 HAA5=37.6_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45 | UG/L | 60.4999 | 2021-06-24 | L2 |  |  | 3645 LATE MORNING CIRCLE, LRAA- TTHM=71 HAA5=41.425_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 70.8 | UG/L | 80.4999 | 2021-06-24 | L2 |  |  | 3645 LATE MORNING CIRCLE, LRAA- TTHM=71 HAA5=41.425_NMS
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-06-28 | AAA |  |  | SPRINGLAKE VILLAGE
3494418 | SPRINGLAKE VILLAGE WTP | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-28 | AAA |  | 1.4999 | SPRINGLAKE VILLAGE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.6 | UG/L | 60.4999 | 2021-09-23 | L2 | 0.9 |  | 3645 LATE MORNING CIRCLE (J QUALIFIERS BIASED HIGH ON 2451 DIC ACID & 2453 MONOBROMO. ACID-MS/MSD 134/136 % & 132/133 % RECOVERIES, RESPECTIVELY. SINCE BIASED HIGH & < MCL, ENT'D RSLTS) BB
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 105 | UG/L | 80.4999 | 2021-09-23 | L2 | 0.47 |  | 3645 LATE MORNING CIRCLE (J QUALIFIERS BIASED HIGH ON 2451 DIC ACID & 2453 MONOBROMO. ACID-MS/MSD 134/136 % & 132/133 % RECOVERIES, RESPECTIVELY. SINCE BIASED HIGH & < MCL, ENT'D RSLTS) BB
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39 | UG/L | 60.4999 | 2021-09-23 | L1 | 0.9 |  | 3854 WOOD THRUSH DR. (NO QUALIFIERS ON THIS SAMPLE)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 84.7 | UG/L | 80.4999 | 2021-09-23 | L1 | 0.47 |  | 3854 WOOD THRUSH DR. (NO QUALIFIERS ON THIS SAMPLE)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.9 | UG/L | 60.4999 | 2021-12-22 | L2 |  |  | LATE MORNING CIRCLE TTHM LRAA 79.4
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 74.8 | UG/L | 80.4999 | 2021-12-22 | L2 |  |  | LATE MORNING CIRCLE TTHM LRAA 79.4
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42 | UG/L | 60.4999 | 2021-12-22 | L1 |  |  | WOOD THRUSH DR (LRAA, HAA5=38.4; TTHMS=71.5 -KAOB)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 78.6 | UG/L | 80.4999 | 2021-12-22 | L1 |  |  | WOOD THRUSH DR (LRAA, HAA5=38.4; TTHMS=71.5 -KAOB)
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 0.67 | UG/L | 249.9999 | 2022-01-03 | AAA | 0.49 | 1.4999 | SPRINGLAKE VILLAGE DALAPON
3494418 | SPRINGLAKE VILLAGE WTP | SOC | 2031 | DALAPON | 1 | UG/L | 249.9999 | 2022-01-07 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1040 | NITRATE | 0.025 | MG/L | 10.4999 | 2022-02-21 | AAA | 0.025
3494418 | SPRINGLAKE VILLAGE WTP | INOR | 1041 | NITRITE | 0.025 | MG/L | 1.4999 | 2022-02-21 | AAA | 0.0025
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.7 | UG/L | 60.4999 | 2022-03-25 | L2 |  |  | 3645 LATE MORNING CIR...LRAA TTHM MCL 83.875, HAA5=46.55_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 84.9 | UG/L | 80.4999 | 2022-03-25 | L2 |  |  | 3645 LATE MORNING CIR...LRAA TTHM MCL 83.875, HAA5=46.55_NMS
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.5 | UG/L | 60.4999 | 2022-03-25 | L1 |  |  | 3854 WOOD THRUSH DR. LRAA: TTHM=72, HAA5=38.7
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 68.8 | UG/L | 80.4999 | 2022-03-25 | L1 |  |  | 3854 WOOD THRUSH DR. LRAA: TTHM=72, HAA5=38.7
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.1 | UG/L | 60.4999 | 2022-06-24 | L2 | 0.9 |  | 3645 LATE MORNING CIR. TTHM LRAA- 80.925
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 59 | UG/L | 80.4999 | 2022-06-24 | L2 | 0.47 |  | 3645 LATE MORNING CIR. TTHM LRAA- 80.925
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.4 | UG/L | 60.4999 | 2022-06-24 | L1 | 0.9 |  | 3854 WOOD THRUSH DR. (HLKD 7/7/22)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 49.3 | UG/L | 80.4999 | 2022-06-24 | L1 | 0.47 |  | 3854 WOOD THRUSH DR. (HLKD 7/7/22)
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.4 | UG/L | 60.4999 | 2022-09-23 | L2 |  |  | 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 76.9 | UG/L | 80.4999 | 2022-09-23 | L2 |  |  | 3645 LATE MORNING CIRCLE
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.7 | UG/L | 60.4999 | 2022-09-23 | L1 |  |  | 3854 WOOD THRUSH DR
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 62.1 | UG/L | 80.4999 | 2022-09-23 | L1 |  |  | 3854 WOOD THRUSH DR
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35 | UG/L | 60.4999 | 2022-12-22 | L1 |  |  | 3854 WOOD THURSH DR TTHM HAA5 4Q22
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 68.9 | UG/L | 80.4999 | 2022-12-22 | L1 |  |  | 3854 WOOD THURSH DR TTHM HAA5 4Q22
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.4 | UG/L | 60.4999 | 2022-12-22 | L2 |  |  | 3645 LATE MORNING CIRCLE TTHM HAA5 4Q22
3494418 | SPRINGLAKE VILLAGE WTP | DBP | 2950 | TOTAL THMS | 75 | UG/L | 80.4999 | 2022-12-22 | L2 |  |  | 3645 LATE MORNING CIRCLE TTHM HAA5 4Q22
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | AAA |  |  | J QUAL ACCEPTED FOR NITRITE
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | AAA |  |  | J QUAL ACCEPTED FOR NITRITE
3490090 | BAY LAKE ESTATES | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 1.4999
3490090 | BAY LAKE ESTATES | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-03-26 | AAA |  | 0.4499
3490090 | BAY LAKE ESTATES | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-03-26 | AAA |  | 6.4999
3490090 | BAY LAKE ESTATES | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 2.4999
3490090 | BAY LAKE ESTATES | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-03-26 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-03-26 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-03-26 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-03-26 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-03-26 | AAA |  | 0.0449
3490090 | BAY LAKE ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-03-26 | AAA |  | 0.0149
3490090 | BAY LAKE ESTATES | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-04-20 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-04-20 | AAA |  | 1.4999
3490090 | BAY LAKE ESTATES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-04-20 | AAA |  | 0.6499
3490090 | BAY LAKE ESTATES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-04-20 | AAA |  | 0.6499
3490090 | BAY LAKE ESTATES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-04-20 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-04-20 | AAA |  | 0.0449
3490090 | BAY LAKE ESTATES | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-04-20 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-04-20 | AAA |  | 0.0249
3490090 | BAY LAKE ESTATES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-04-20 | AAA |  | 0.1499
3490090 | BAY LAKE ESTATES | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-04-20 | AAA |  | 0.2499
3490090 | BAY LAKE ESTATES | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3490090 | BAY LAKE ESTATES | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-05-04 | AAA |  | 0.9499
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | 0.035 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1005 | ARSENIC | 0.0009 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1010 | BARIUM | 0 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1052 | SODIUM | 23.5 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3490090 | BAY LAKE ESTATES | SEC | 1002 | ALUMINUM | 0.0075 | MG/L | 0.2499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1017 | CHLORIDE | 26.9 | MG/L | 250.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1025 | FLUORIDE | 0.19 | MG/L | 2.0499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1028 | IRON | 0.071 | MG/L | 0.3499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1920 | ODOR THRESHOLD | 2 |  | 3.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.6 | LN(10) |  | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 241 | MG/L | 500.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 73.8 | UG/L | 60.4999 | 2018-07-23 | L1 |  |  | 2950 - 6820 BAYSHORE DR.- PLACED ON QTRLY MONITORING-SLB
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 130 | UG/L | 80.4999 | 2018-07-23 | L1 |  |  | 2950 - 6820 BAYSHORE DR.- PLACED ON QTRLY MONITORING-SLB
3490090 | BAY LAKE ESTATES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA
3490090 | BAY LAKE ESTATES | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.5 | UG/L | 60.4999 | 2018-10-24 | L1 |  |  | 2950-6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 47.3 | UG/L | 80.4999 | 2018-10-24 | L1 |  |  | 2950-6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.8 | UG/L | 60.4999 | 2019-01-29 | L1 | 0.48 |  | ON QM/6820 BAYSHORE DR. (HLKD TO KC) [SAMPLED ONE DAY OUTSIDE DESIGNATED WEEK. PN DUE_JMF]
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 68.8 | UG/L | 80.4999 | 2019-01-29 | L1 | 0.32 |  | ON QM/6820 BAYSHORE DR. (HLKD TO KC) [SAMPLED ONE DAY OUTSIDE DESIGNATED WEEK. PN DUE_JMF]
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.7 | UG/L | 60.4999 | 2019-04-26 | L1 |  |  | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 71.2 | UG/L | 80.4999 | 2019-04-26 | L1 |  |  | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49 | UG/L | 60.4999 | 2019-07-26 | L1 |  |  | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 62.1 | UG/L | 80.4999 | 2019-07-26 | L1 |  |  | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 58.7 | UG/L | 80.4999 | 2019-10-25 | L1 | 0.32 |  | HAA5 J QUALIFIED, BIASED HIGH, ACCEPTED_VP
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.1 | UG/L | 60.4999 | 2019-10-25 | L1 |  |  | HAA5 J QUALIFIED, BIASED HIGH, ACCEPTED_VP
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40 | UG/L | 60.4999 | 2020-01-24 | L1 | 0.9 |  | 6820 BAYSHORE. SAMPLED ONE DAY OUTSIDE OF APPROVED SAMPLING PLAN
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 52.5 | UG/L | 80.4999 | 2020-01-24 | L1 | 0.32 |  | 6820 BAYSHORE. SAMPLED ONE DAY OUTSIDE OF APPROVED SAMPLING PLAN
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | AAA
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | AAA
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.3 | UG/L | 60.4999 | 2020-07-28 | L1 | 0.9 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 67.4 | UG/L | 80.4999 | 2020-07-28 | L1 | 0.47 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.5 | UG/L | 60.4999 | 2020-10-26 | L1 | 0.9 |  | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 62.8 | UG/L | 80.4999 | 2020-10-26 | L1 | 0.47 |  | 6820 BAYSHORE DR.
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | 0.028 | MG/L | 10.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, MS 89% LIMIT 90-110, ACEPTED)_VPU
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, MS 89% LIMIT 90-110, ACEPTED)_VPU
3490090 | BAY LAKE ESTATES | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3490090 | BAY LAKE ESTATES | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-02-25 | AAA | 0.0055 | 0.0149 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA | 0.0066 | 0.0249 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-02-25 | AAA | 0.023 | 0.1499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA | 0.68 | 1.4999 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-25 | AAA | 0.23 | 1.4999 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-25 | AAA | 0.16 | 0.4499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-25 | AAA | 3.3 | 9.4999 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-25 | AAA | 4.2 | 6.4999 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-02-25 | AAA | 0.36 | 0.6499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-25 | AAA | 0.46 | 2.4999 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-02-25 | AAA | 0.04 | 0.0749 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-02-25 | AAA | 0.47 | 0.6499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-25 | AAA | 0.04 | 0.1499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-25 | AAA | 0.16 | 0.2499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.034 | UG/L | 54.9999 | 2021-02-25 | AAA | 0.024 | 0.1499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-25 | AAA | 0.59 | 0.9499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA | 0.015 | 0.1499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-02-25 | AAA | 0.029 | 0.2499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-02-25 | AAA | 0.0043 | 0.0055 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-02-25 | AAA | 0.014 | 0.0449 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA | 0.003 | 0.0249 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-25 | AAA | 0.096 | 0.1499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-25 | AAA | 0.053 | 0.2499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-02-25 | AAA | 0.015 | 0.1499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA | 0.02 | 0.0249 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-25 | AAA | 0.014 | 0.0449 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-25 | AAA | 0.044 | 0.1499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA | 0.0063 | 0.0249 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-25 | AAA | 0.0074 | 0.0149 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-25 | AAA | 0.035 | 0.2499 | SOC (2042 HEX... 0.034,
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 59.9 | UG/L | 60.4999 | 2021-04-23 | L1 | 0.9 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 96.1 | UG/L | 80.4999 | 2021-04-23 | L1 | 0.47 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-27 | AAA | 0.025 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.025 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-27 | AAA | 0.0005 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1010 | BARIUM | 0.0086 | MG/L | 2.4999 | 2021-05-27 | AAA | 0.0062 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-27 | AAA | 0.00067 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0026 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.005 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2021-05-27 | AAA | 0.015 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-05-27 | AAA | 0.00022 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-27 | AAA | 9e-05 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.002 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.00083 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1052 | SODIUM | 18.8 | MG/L | 160.4999 | 2021-05-27 | AAA | 0.59 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-27 | AAA | 0.00021 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-27 | AAA | 0.00058 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-27 | AAA | 0.0005 |  | ASBESTOS AT POE/D ENT'D SEPARATELY WITH "S"
3490090 | BAY LAKE ESTATES | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2021-05-27 | AAA | 0.2 |  | ASBESTOS AT POE/D (ENT'D SEPARATELY WITH "S" SINCE POE/D)
3490090 | BAY LAKE ESTATES | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.0072 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1017 | CHLORIDE | 25.2 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1022 | COPPER | 0.001 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.00093 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1025 | FLUORIDE | 0.17 | MG/L | 2.0499 | 2021-05-27 | AAA | 0.015 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1028 | IRON | 5.3 | MG/L | 0.3499 | 2021-05-27 | AAA | 0.016 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1032 | MANGANESE | 0.033 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.0027 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0033 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-05-27 | AAA | 0.0076 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2021-05-27 | AAA | 5 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-05-27 | AAA | 1 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 | LN(10) |  | 2021-05-27 | AAA | 0.1 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 242 | MG/L | 500.4999 | 2021-05-27 | AAA | 5 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-27 | AAA | 0.099 |  | IRON CANNOT POSSIBLY BE 5.3 MG/L - IT'S PROBABLY REPORTED IN THE WRONG UNITS - CHECK WITH TOHO & LAB (HLKD) IF IN WRONG UNITS, MUST REPORT IRON IN MG/L IN REVISION.
3490090 | BAY LAKE ESTATES | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-06-28 | AAA |  |  | BAY LAKE
3490090 | BAY LAKE ESTATES | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-28 | AAA |  | 1.4999 | BAY LAKE
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.1 | UG/L | 60.4999 | 2021-07-23 | L1 | 0.9 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 70.8 | UG/L | 80.4999 | 2021-07-23 | L1 | 0.47 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.7 | UG/L | 60.4999 | 2021-10-26 | L1 | 0.9 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 53.3 | UG/L | 80.4999 | 2021-10-26 | L1 | 0.47 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.5 | UG/L | 60.4999 | 2022-01-27 | L1 |  |  | 6820 BAYSHORE DR. [LRAA TTHM=70.73 ; HAA5=46.05]
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 62.7 | UG/L | 80.4999 | 2022-01-27 | L1 |  |  | 6820 BAYSHORE DR. [LRAA TTHM=70.73 ; HAA5=46.05]
3490090 | BAY LAKE ESTATES | INOR | 1040 | NITRATE | 0.026 | MG/L | 10.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490090 | BAY LAKE ESTATES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.1 | UG/L | 60.4999 | 2022-04-25 | L1 |  |  | 6820 BAYSHORE DR. (LRAA= TTHM= 64.1 HAA5= 41.6)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 69.6 | UG/L | 80.4999 | 2022-04-25 | L1 |  |  | 6820 BAYSHORE DR. (LRAA= TTHM= 64.1 HAA5= 41.6)
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 61.2 | UG/L | 60.4999 | 2022-07-26 | L1 | 0.9 |  | 6820 BAYSHORE DR. (HLKD 8/3/22) (LRAA TTHM: 68.475, HAA5:45.63)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 88.3 | UG/L | 80.4999 | 2022-07-26 | L1 | 0.47 |  | 6820 BAYSHORE DR. (HLKD 8/3/22) (LRAA TTHM: 68.475, HAA5:45.63)
3490090 | BAY LAKE ESTATES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.7 | UG/L | 60.4999 | 2022-10-25 | L1 | 0.9 |  | 6820 BAYSHORE DR. (HLKD)
3490090 | BAY LAKE ESTATES | DBP | 2950 | TOTAL THMS | 61.2 | UG/L | 80.4999 | 2022-10-25 | L1 | 0.47 |  | 6820 BAYSHORE DR. (HLKD)
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.2 | UG/L | 60.4999 | 2018-06-08 | L2 | 0.48 |  |  | 2
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | 47 | UG/L | 80.4999 | 2018-06-08 | L2 | 0.32 |  |  | 2
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.9 | UG/L | 60.4999 | 2018-08-24 | L2 |  |  | REC'D 02/26/19 KAC | 2
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | 49.5 | UG/L | 80.4999 | 2018-08-24 | L2 |  |  | REC'D 02/26/19 KAC | 2
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.7 | UG/L | 60.4999 | 2019-05-24 | L2 | 0.48 |  | 115 WINDY DUNE | 2
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | 50.8 | UG/L | 80.4999 | 2019-05-24 | L2 | 0.32 |  | 115 WINDY DUNE | 2
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.6 | UG/L | 60.4999 | 2019-08-27 | L2 |  |  | 115 WINDY DUNE CT. | 3
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | 55.2 | UG/L | 80.4999 | 2019-08-27 | L2 |  |  | 115 WINDY DUNE CT. | 2
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | AAA
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | AAA |  | 0.5499
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-25 | AAA | 0.58 | 1.4999 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2031 | DALAPON | 0.93 | UG/L | 249.9999 | 2020-03-25 | AAA | 0.89 | 1.4999 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-25 | AAA | 0.16 | 0.4499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-25 | AAA | 3.3 | 9.4999 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-25 | AAA | 4.2 | 6.4999 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-25 | AAA | 0.44 | 2.4999 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-25 | AAA | 0.094 | 0.1499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-25 | AAA | 0.16 | 0.2499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-25 | AAA | 0.67 | 0.9499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-25 | AAA | 0.00071 | 0.0055 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-25 | AAA | 0.096 | 0.1499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-25 | AAA | 0.16 | 0.2499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-25 | AAA | 0.03 | 0.0449 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-25 | AAA | 0.077 | 0.1499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-25 | AAA | 0.0064 | 0.0249 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-25 | AAA | 0.0075 | 0.0149 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-25 | AAA | 0.045 | 0.2499 | BVL WP (35539637001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) DALAPON 0.93, < RDL OF 1 UG/L. RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/18/20 PER LAB SIGNATURE DATE.
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-25 | AAA |  | 0.0149 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-25 | AAA |  | 0.0249 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-25 | AAA |  | 0.1499 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-25 | AAA |  | 0.6499 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-25 | AAA |  | 0.0749 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 2 | UG/L | 6.4999 | 2020-03-25 | AAA |  | 0.6499 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.02 | UG/L | 54.9999 | 2020-03-25 | AAA |  | 0.1499 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-25 | AAA |  | 0.1499 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-25 | AAA |  | 0.2499 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-25 | AAA |  | 0.0449 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-25 | AAA |  | 0.0249 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-25 | AAA |  | 0.1499 | BLV
3490184 | TOHO BUENAVENTURA LAKES | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-25 | AAA |  | 0.0249 | BLV
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-05-27 | AAA | 0.025 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-05-27 | AAA | 0.025 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-05-27 | AAA | 0.0005 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2020-05-27 | AAA | 0.0023 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-05-27 | AAA | 0.00024 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-05-27 | AAA | 0.00081 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2020-05-27 | AAA | 0.015 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-05-27 | AAA | 0.00022 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-05-27 | AAA | 9e-05 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-05-27 | AAA | 0.002 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-05-27 | AAA | 0.00083 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1052 | SODIUM | 21.9 | MG/L | 160.4999 | 2020-05-27 | AAA | 0.59 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-05-27 | AAA | 0.00021 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-05-27 | AAA | 0.00021 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-05-27 | AAA | 0.0005 |  | CY TESTED SEP
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1002 | ALUMINUM | 0.0124 | MG/L | 0.2499 | 2020-05-27 | AAA | 0.0072 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1017 | CHLORIDE | 23.7 | MG/L | 250.4999 | 2020-05-27 | AAA | 2.5 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1022 | COPPER | 0.0011 | MG/L | 1.4999 | 2020-05-27 | AAA | 0.00093 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1025 | FLUORIDE | 0.16 | MG/L | 2.0499 | 2020-05-27 | AAA | 0.015 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1028 | IRON | 0.05 | MG/L | 0.3499 | 2020-05-27 | AAA | 0.016 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1032 | MANGANESE | 0.0026 | MG/L | 0.0549 | 2020-05-27 | AAA | 0.0012 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-05-27 | AAA | 0.0015 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1055 | SULFATE | 9.4 | MG/L | 250.4999 | 2020-05-27 | AAA | 2.5 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2020-05-27 | AAA | 0.0076 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-05-27 | AAA | 5 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1920 | ODOR THRESHOLD | 12 |  | 3.4999 | 2020-05-27 | AAA | 1 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2020-05-27 | AAA | 0.1 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 229 | MG/L | 500.4999 | 2020-05-27 | AAA | 5 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-05-27 | AAA | 0.099 |  | E84129/TDS (ODOR IS 12.0 (> MCL OF 3)
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.8 | UG/L | 60.4999 | 2020-05-27 | L2 | 0.9 |  |  | 3
3490184 | TOHO BUENAVENTURA LAKES | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2020-05-27 | L2 | 0.32 |  |  | 2
3490184 | TOHO BUENAVENTURA LAKES | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-05-27 | AAA | 0.2 |  | POE/D ASBESTOS (?). RESULT IS GIVEN AS
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | 0.079 | MG/L | 10.4999 | 2018-02-28 | AAA
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | AAA
3494427 | HARMONY CDD | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2018-03-26 | AAA |  | 0.0149 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2018-03-26 | AAA |  | 1.4999 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 1.4999 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2018-03-26 | AAA |  | 0.4499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2018-03-26 | AAA |  | 6.4999 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2018-03-26 | AAA |  | 0.6499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2018-03-26 | AAA |  | 2.4999 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2018-03-26 | AAA |  | 0.6499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2018-03-26 | AAA |  | 0.1499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2018-03-26 | AAA |  | 0.2499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2018-03-26 | AAA |  | 0.1499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2018-03-26 | AAA |  | 0.1499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2018-03-26 | AAA |  | 0.2499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2018-03-26 | AAA |  | 0.0055 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2018-03-26 | AAA |  | 0.0449 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2018-03-26 | AAA |  | 0.1499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2018-03-26 | AAA |  | 0.2499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2018-03-26 | AAA |  | 0.1499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2018-03-26 | AAA |  | 0.0449 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2018-03-26 | AAA |  | 0.1499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2018-03-26 | AAA |  | 0.0249 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2018-03-26 | AAA |  | 0.0149 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2018-03-26 | AAA |  | 0.2499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2018-03-26 | AAA |  | 0.1499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2018-03-26 | AAA |  | 9.4999 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2018-03-26 | AAA |  | 0.0749 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2018-03-26 | AAA |  | 0.9499 | QUALIFERS ACCEPTED. SLB
3494427 | HARMONY CDD | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2018-04-25 | AAA |  | 0.5499
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | 0.079 | MG/L | 10.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1005 | ARSENIC | 0.001 | MG/L | 0.0104 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1010 | BARIUM | 0.0088 | MG/L | 2.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1025 | FLUORIDE | 0.25 | MG/L | 4.0499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1052 | SODIUM | 61.4 | MG/L | 160.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2018-05-24 | AAA |  |  | ASBESTOS- POE DOH LAB CERT# E87975
3494427 | HARMONY CDD | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1017 | CHLORIDE | 99.4 | MG/L | 250.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1025 | FLUORIDE | 0.25 | MG/L | 2.0499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1028 | IRON | 0.076 | MG/L | 0.3499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1055 | SULFATE | 15.4 | MG/L | 250.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.2 | LN(10) |  | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 392 | MG/L | 500.4999 | 2018-05-24 | AAA
3494427 | HARMONY CDD | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2018-05-24 | AAA
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.5 | UG/L | 60.4999 | 2018-07-23 | L1 | 0.48 |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 4.5 | UG/L | 80.4999 | 2018-07-23 | L1 | 0.32 |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2018-08-30 | AAA |  |  | DUE 2024
3494427 | HARMONY CDD | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2018-08-30 | AAA |  | 1.4999 | DUE 2024
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | 0.028 | MG/L | 10.4999 | 2019-02-28 | AAA
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | AAA
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.1 | UG/L | 60.4999 | 2019-07-30 | L1 |  |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 14.4 | UG/L | 80.4999 | 2019-07-30 | L1 |  |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | 0.046 | MG/L | 10.4999 | 2020-01-28 | AAA
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | AAA
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11 | UG/L | 60.4999 | 2020-07-28 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 18.5 | UG/L | 80.4999 | 2020-07-28 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | 0.32 | MG/L | 10.4999 | 2021-01-27 | AAA |  |  | POE
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | AAA |  |  | POE
3494427 | HARMONY CDD | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.0149 | POE
3494427 | HARMONY CDD | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA |  | 1.4999 | POE
3494427 | HARMONY CDD | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 1.4999 | POE
3494427 | HARMONY CDD | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-25 | AAA |  | 0.4499 | POE
3494427 | HARMONY CDD | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-25 | AAA |  | 9.4999 | POE
3494427 | HARMONY CDD | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-25 | AAA |  | 6.4999 | POE
3494427 | HARMONY CDD | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-02-25 | AAA |  | 0.6499 | POE
3494427 | HARMONY CDD | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 2.4999 | POE
3494427 | HARMONY CDD | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-02-25 | AAA |  | 0.0749 | POE
3494427 | HARMONY CDD | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-02-25 | AAA |  | 0.6499 | POE
3494427 | HARMONY CDD | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-25 | AAA |  | 0.9499 | POE
3494427 | HARMONY CDD | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-02-25 | AAA |  | 0.0449 | POE
3494427 | HARMONY CDD | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-25 | AAA |  | 0.0449 | POE
3494427 | HARMONY CDD | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-25 | AAA |  | 0.0149 | POE
3494427 | HARMONY CDD | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-02-25 | AAA |  | 0.0055 | POE
3494427 | HARMONY CDD | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.0072 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1017 | CHLORIDE | 107 | MG/L | 250.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.00093 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1025 | FLUORIDE | 0.47 | MG/L | 2.0499 | 2021-05-27 | AAA | 0.029 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1028 | IRON | 0.021 | MG/L | 0.3499 | 2021-05-27 | AAA | 0.016 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.0027 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0033 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1055 | SULFATE | 152 | MG/L | 250.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-05-27 | AAA | 0.0076 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2021-05-27 | AAA | 1 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2021-05-27 | AAA | 0.1 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 515 | MG/L | 500.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-27 | AAA | 0.099 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | 0.27 | MG/L | 10.4999 | 2021-05-27 | AAA | 0.025 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | 0.03 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.025 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-27 | AAA | 0.0005 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2021-05-27 | AAA | 0.0062 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-27 | AAA | 0.00067 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0026 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.005 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1025 | FLUORIDE | 0.47 | MG/L | 4.0499 | 2021-05-27 | AAA | 0.029 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-05-27 | AAA | 0.00022 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-27 | AAA | 9e-05 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.002 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.00083 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1052 | SODIUM | 83.8 | MG/L | 160.4999 | 2021-05-27 | AAA | 0.59 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-27 | AAA | 0.00021 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-27 | AAA | 0.00058 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-27 | AAA | 0.0005 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2021-05-28 | AAA | 0.2 |  | POE/D ASBESTOS (ENT'D W/SMP TYPE "S" SINCE POE/D)
3494427 | HARMONY CDD | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-06-28 | AAA |  |  | HARMONY
3494427 | HARMONY CDD | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-28 | AAA |  | 1.4999 | HARMONY
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.8 | UG/L | 60.4999 | 2021-07-23 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. (HLKD) TTHMS 144 UG/L, EXCEEDS THE MCL OF 80 UG/L, TRIGGERS QTRLY TESTING | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 144 | UG/L | 80.4999 | 2021-07-23 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. (HLKD) TTHMS 144 UG/L, EXCEEDS THE MCL OF 80 UG/L, TRIGGERS QTRLY TESTING | 3
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.7 | UG/L | 60.4999 | 2021-10-26 | L2 |  |  | ENTERED LATE_ MONITORING LOCATIONS JUST UPDATED_AL | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 5.2 | UG/L | 80.4999 | 2021-10-26 | L2 |  |  | ENTERED LATE_ MONITORING LOCATIONS JUST UPDATED_AL | 3
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.5 | UG/L | 60.4999 | 2021-10-26 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. (HLKD-A 2ND SITE WAS TESTED 10/21 BUT 2ND SITE NOT SET UP AS A VALID DBP LOCATION AS OF 1/24/22-THEREFORE, RESULTS CANNOT BE ENTERED IN PWS-BB) | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 5 | UG/L | 80.4999 | 2021-10-26 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. (HLKD-A 2ND SITE WAS TESTED 10/21 BUT 2ND SITE NOT SET UP AS A VALID DBP LOCATION AS OF 1/24/22-THEREFORE, RESULTS CANNOT BE ENTERED IN PWS-BB) | 3
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.6 | UG/L | 60.4999 | 2022-01-27 | L1 |  |  | 3341 SCHOOL HOUSE RD. | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 9.8 | UG/L | 80.4999 | 2022-01-27 | L1 |  |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.1 | UG/L | 60.4999 | 2022-01-27 | L2 |  |  | ENTERED LATE_AL | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 10 | UG/L | 80.4999 | 2022-01-27 | L2 |  |  | ENTERED LATE_AL | 3
3494427 | HARMONY CDD | INOR | 1040 | NITRATE | 0.42 | MG/L | 10.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494427 | HARMONY CDD | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.4 | UG/L | 60.4999 | 2022-04-25 | L1 |  |  | 3341 SCHOOL HOUSE ( LRAA TTHM= 40.6, HAA5= 15.08) | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 3.6 | UG/L | 80.4999 | 2022-04-25 | L1 |  |  | 3341 SCHOOL HOUSE ( LRAA TTHM= 40.6, HAA5= 15.08) | 3
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.9 | UG/L | 60.4999 | 2022-04-25 | L2 |  |  | ENTERED LATE (LRAA TTH= 9.28, HAA5= 7.83) | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 3.6 | UG/L | 80.4999 | 2022-04-25 | L2 |  |  | ENTERED LATE (LRAA TTH= 9.28, HAA5= 7.83) | 1
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.5 | UG/L | 60.4999 | 2022-07-26 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP (HLKD) | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 8.3 | UG/L | 80.4999 | 2022-07-26 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP (HLKD) | 3
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.6 | UG/L | 60.4999 | 2022-07-26 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 6.9 | UG/L | 80.4999 | 2022-07-26 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.8 | UG/L | 60.4999 | 2022-10-25 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 2.9 | UG/L | 80.4999 | 2022-10-25 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 1
3494427 | HARMONY CDD | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.4 | UG/L | 60.4999 | 2022-10-25 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP (HLKD) | 3
3494427 | HARMONY CDD | DBP | 2950 | TOTAL THMS | 5 | UG/L | 80.4999 | 2022-10-25 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP (HLKD) | 1
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.6 | UG/L | 60.4999 | 2018-07-11 | L1 |  |  | 2950-CELEBRATION H.S. L.S. / SUBCONTRACT LAB E87610 | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 14.8 | UG/L | 80.4999 | 2018-07-11 | L1 |  |  | 2950-CELEBRATION H.S. L.S. / SUBCONTRACT LAB E87610 | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 17.19 | UG/L | 80.4999 | 2019-09-06 | L1 |  |  | CELEBRATION H.S. L.S. | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2019-09-06 | L1 |  |  | CELEBRATION H.S. L.S. | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.8 | UG/L | 60.4999 | 2020-07-17 | L1 | 0.5 |  | CELEBRATION H.S. L.S. | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 20.5 | UG/L | 80.4999 | 2020-07-17 | L1 | 0.5 |  | CELEBRATION H.S. L.S. | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-07-12 | L1 | 0.5 |  | CELEBRATION H.S. L.S. LAKE EVELYN WAS SAMPLED BUT NOT ENTERED. NOT REQUIRED. SITE IS INACTIVE_MFC | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 24.8 | UG/L | 80.4999 | 2021-07-12 | L1 | 0.5 |  | CELEBRATION H.S. L.S. LAKE EVELYN WAS SAMPLED BUT NOT ENTERED. NOT REQUIRED. SITE IS INACTIVE_MFC | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.82 | UG/L | 60.4999 | 2022-07-22 | L1 |  |  | CELEBRATION HIGH SCHOOL | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 26.4 | UG/L | 80.4999 | 2022-07-22 | L1 |  |  | CELEBRATION HIGH SCHOOL | 3
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.25 | UG/L | 60.4999 | 2022-07-22 | L2 |  |  | LAKE EVELYN - INACTIVE SYSTEM
3494428 | ENTERPRISE CDD (CONSECUTIVE) | DBP | 2950 | TOTAL THMS | 22.5 | UG/L | 80.4999 | 2022-07-22 | L2 |  |  | LAKE EVELYN - INACTIVE SYSTEM
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-04 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-04 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2018-01-04 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-05 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2018-01-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-19 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-01-22 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-05 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2018-02-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-19 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-19 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2018-02-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-02-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.8 | UG/L | 60.4999 | 2018-02-22 | L2 |  |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 32.6 | UG/L | 80.4999 | 2018-02-22 | L2 |  |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.5 | UG/L | 60.4999 | 2018-02-22 | L1 |  |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 59 | UG/L | 80.4999 | 2018-02-22 | L1 |  |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.4 | UG/L | 60.4999 | 2018-02-22 | L3 |  |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 28.7 | UG/L | 80.4999 | 2018-02-22 | L3 |  |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.8 | UG/L | 60.4999 | 2018-02-22 | L4 |  |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 47.7 | UG/L | 80.4999 | 2018-02-22 | L4 |  |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2018-02-28 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 1.5 | MG/L | 10.4999 | 2018-02-28 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2018-02-28 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-03-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-03-07 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2018-03-12 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-03-12 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-03-22 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-03-23 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2018-03-26 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-03-26 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.5 | MG/L |  | 2018-04-03 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-03 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2018-04-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-19 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-04-24 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2018-05-03 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-03 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-07 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-07 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2018-05-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-18 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-05-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-05 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-07 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2018-06-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.7 | UG/L | 60.4999 | 2018-06-08 | L2 | 0.48 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 45.2 | UG/L | 80.4999 | 2018-06-08 | L2 | 0.32 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2018-06-08 | L1 | 0.48 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 45.1 | UG/L | 80.4999 | 2018-06-08 | L1 | 0.32 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.9 | UG/L | 60.4999 | 2018-06-08 | L3 | 0.48 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 29 | UG/L | 80.4999 | 2018-06-08 | L3 | 0.32 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.1 | UG/L | 60.4999 | 2018-06-08 | L4 | 0.48 |  | 5508 WILLOW BEND TR. (6/18 DISINF BYP REPORT RCVD) HLK'D TO SB 7/17/18 - BB
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 40.5 | UG/L | 80.4999 | 2018-06-08 | L4 | 0.32 |  | 5508 WILLOW BEND TR. (6/18 DISINF BYP REPORT RCVD) HLK'D TO SB 7/17/18 - BB
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-18 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2018-06-18 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-22 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-06-22 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2018-07-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2018-07-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-03 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-11 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2018-07-13 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-13 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-24 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-07-30 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-08-03 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-08-08 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2018-08-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-08-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-08-22 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.1 | UG/L | 60.4999 | 2018-08-24 | L2 | 0.48 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 39.5 | UG/L | 80.4999 | 2018-08-24 | L2 | 0.32 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.8 | UG/L | 60.4999 | 2018-08-24 | L1 | 0.48 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 38.2 | UG/L | 80.4999 | 2018-08-24 | L1 | 0.32 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16 | UG/L | 60.4999 | 2018-08-24 | L3 | 0.48 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 29.8 | UG/L | 80.4999 | 2018-08-24 | L3 | 0.32 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.8 | UG/L | 60.4999 | 2018-08-24 | L4 | 0.48 |  | 5508 WILLOW BEND TR. (HLKD TO SB) 9/18 QTR DISINF BYP REPORT WAS NOT WITH THESE DBPS - MAY COME IN SEPARATELY (?)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 36.4 | UG/L | 80.4999 | 2018-08-24 | L4 | 0.32 |  | 5508 WILLOW BEND TR. (HLKD TO SB) 9/18 QTR DISINF BYP REPORT WAS NOT WITH THESE DBPS - MAY COME IN SEPARATELY (?)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-08-24 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2018-09-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-09-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-09-04 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-09-04 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-09-17 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2018-09-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-09-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-09-21 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2018-10-02 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2018-10-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-10-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-10-07 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2018-10-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.14 | LN(10) |  | 2018-10-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-10-23 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-10-31 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.4 | MG/L |  | 2018-11-02 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-02 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-05 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-05 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-12 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2018-11-16 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-11-16 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-11-22 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.9 | UG/L | 60.4999 | 2018-11-28 | L2
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 45.4 | UG/L | 80.4999 | 2018-11-28 | L2
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.7 | UG/L | 60.4999 | 2018-11-28 | L1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 46.8 | UG/L | 80.4999 | 2018-11-28 | L1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2018-11-28 | L3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 28.7 | UG/L | 80.4999 | 2018-11-28 | L3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2018-11-28 | L4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 43.6 | UG/L | 80.4999 | 2018-11-28 | L4
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-01 | WTP1 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2018-12-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-04 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2018-12-06 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-06 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2018-12-10 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2018-12-10 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2018-12-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2018-12-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2018-12-17 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-17 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-24 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-24 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2018-12-28 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2018-12-28 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-01-02 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-01-02 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-01-03 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-01-04 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-01-21 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-01-22 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-01-24 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-01-24 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2019-02-05 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-02-05 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-05 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-05 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-19 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-19 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2019-02-25 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-02-25 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.1 | UG/L | 60.4999 | 2019-02-27 | L2 | 0.48 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 41.4 | UG/L | 80.4999 | 2019-02-27 | L2 | 0.32 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.9 | UG/L | 60.4999 | 2019-02-27 | L1 | 0.48 |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 46.3 | UG/L | 80.4999 | 2019-02-27 | L1 | 0.32 |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.1 | UG/L | 60.4999 | 2019-02-27 | L3 | 0.48 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 30.8 | UG/L | 80.4999 | 2019-02-27 | L3 | 0.32 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.6 | UG/L | 60.4999 | 2019-02-27 | L4 | 0.48 |  | 5508 WILLOW BEND TR., KISSIMMEE (3/19 DISINF BYP RPRT RCVD SEP IN "WORD") RSLTS & DB REPORT HLKD TOGETHER
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 37.7 | UG/L | 80.4999 | 2019-02-27 | L4 | 0.32 |  | 5508 WILLOW BEND TR., KISSIMMEE (3/19 DISINF BYP RPRT RCVD SEP IN "WORD") RSLTS & DB REPORT HLKD TOGETHER
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | WTP1 |  |  | 2019 NNBELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP1 |  |  | 2019 NNBELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2019-02-28 | WTP3 |  |  | 2019 NN PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP3 |  |  | 2019 NN PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 1.3 | MG/L | 10.4999 | 2019-02-28 | WTP6 |  |  | 2019 NN HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2019-02-28 | WTP6 |  |  | 2019 NN HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-03-05 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-03-07 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-03-11 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-03-11 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-03-20 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-03-20 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-03-22 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-03-22 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.4 | MG/L |  | 2019-04-04 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-04-04 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-04-05 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-04-05 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-04-19 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-04-23 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-04-23 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-04-24 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-07 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-07 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-05-10 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-10 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-17 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.8 | UG/L | 60.4999 | 2019-05-24 | L1 | 0.48 |  | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 56.7 | UG/L | 80.4999 | 2019-05-24 | L1 | 0.32 |  | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.4 | UG/L | 60.4999 | 2019-05-24 | L2 | 0.48 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 42.1 | UG/L | 80.4999 | 2019-05-24 | L2 | 0.32 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.3 | UG/L | 60.4999 | 2019-05-24 | L3 | 0.48 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 44.3 | UG/L | 80.4999 | 2019-05-24 | L3 | 0.32 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16 | UG/L | 60.4999 | 2019-05-24 | L4 | 0.48 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 34.2 | UG/L | 80.4999 | 2019-05-24 | L4 | 0.32 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-25 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2019-05-30 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-05-30 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-06-07 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-06-07 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-06-12 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-06-12 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-06-21 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-06-22 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-06-28 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-06-28 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-07-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-07-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-07-10 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-07-14 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2019-07-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-07-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-07-29 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-07-30 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-08-01 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-08-05 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-08-07 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-08-07 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2019-08-15 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-08-15 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-08-20 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-08-24 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.4 | UG/L | 60.4999 | 2019-08-26 | L2 |  |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 30.7 | UG/L | 80.4999 | 2019-08-26 | L2 |  |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.8 | UG/L | 60.4999 | 2019-08-26 | L1 |  |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 51 | UG/L | 80.4999 | 2019-08-26 | L1 |  |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.9 | UG/L | 60.4999 | 2019-08-26 | L3 |  |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 33.8 | UG/L | 80.4999 | 2019-08-26 | L3 |  |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.3 | UG/L | 60.4999 | 2019-08-26 | L4 |  |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 56.5 | UG/L | 80.4999 | 2019-08-26 | L4 |  |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-05 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-09-06 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-06 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-06 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-19 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-09-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-09-23 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-10-09 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-09 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-09 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-11 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-10-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-10-23 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-10-27 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-11-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-06 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-08 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-08 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-11-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-11-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.3 | UG/L | 60.4999 | 2019-11-26 | L1 | 0.9 |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 47.4 | UG/L | 80.4999 | 2019-11-26 | L1 | 0.32 |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.7 | UG/L | 60.4999 | 2019-11-26 | L2 | 0.9 |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 51.4 | UG/L | 80.4999 | 2019-11-26 | L2 | 0.32 |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.8 | UG/L | 60.4999 | 2019-11-26 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 9.6 | UG/L | 80.4999 | 2019-11-26 | L3 | 0.32 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.8 | UG/L | 60.4999 | 2019-11-26 | L4 | 0.9 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 51.7 | UG/L | 80.4999 | 2019-11-26 | L4 | 0.32 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-11-28 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2019-12-06 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-12-06 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-12-06 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-12-08 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2019-12-21 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-12-23 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2019-12-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2019-12-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-04 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2020-01-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-08 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2020-01-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-24 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-01-26 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | WTP1 | 0.025 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-01-28 | WTP3 | 0.025 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | WTP3 | 0.025 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 1.6 | MG/L | 10.4999 | 2020-01-28 | WTP6 | 0.025 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-01-28 | WTP6 | 0.025 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-02-03 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-02-03 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2020-02-10 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-02-10 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2020-02-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-02-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-02-24 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-02-24 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP1 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP3 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2020-02-24 | WTP6 |  | 0.5499
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.5 | UG/L | 60.4999 | 2020-02-25 | L2 | 0.9 |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2020-02-25 | L2 | 0.32 |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.8 | UG/L | 60.4999 | 2020-02-25 | L1 | 0.9 |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 47.1 | UG/L | 80.4999 | 2020-02-25 | L1 | 0.32 |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.6 | UG/L | 60.4999 | 2020-02-25 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 33.9 | UG/L | 80.4999 | 2020-02-25 | L3 | 0.32 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.1 | UG/L | 60.4999 | 2020-02-25 | L4 | 0.9 |  | 5508 WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 50.5 | UG/L | 80.4999 | 2020-02-25 | L4 | 0.32 |  | 5508 WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-03-03 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-03-04 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2020-03-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-03-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-23 | WTP1 | 0.59 | 1.4999 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-23 | WTP1 | 0.89 | 1.4999 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-23 | WTP1 | 0.16 | 0.4499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-23 | WTP1 | 3.3 | 9.4999 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-23 | WTP1 | 4.2 | 6.4999 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-23 | WTP1 | 0.44 | 2.4999 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-23 | WTP1 | 0.094 | 0.1499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-23 | WTP1 | 0.16 | 0.2499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-23 | WTP1 | 0.67 | 0.9499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-23 | WTP1 | 0.0025 | 0.0055 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-23 | WTP1 | 0.096 | 0.1499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-23 | WTP1 | 0.16 | 0.2499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-23 | WTP1 | 0.03 | 0.0449 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-23 | WTP1 | 0.078 | 0.1499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP1 | 0.0064 | 0.0249 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-23 | WTP1 | 0.0075 | 0.0149 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-23 | WTP1 | 0.046 | 0.2499 | BELLA LAGO WP (35539137001) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-23 | WTP6 | 0.58 | 1.4999 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-23 | WTP6 | 0.89 | 1.4999 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-23 | WTP6 | 0.16 | 0.4499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-23 | WTP6 | 3.3 | 9.4999 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-23 | WTP6 | 4.2 | 6.4999 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-23 | WTP6 | 0.44 | 2.4999 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-23 | WTP6 | 0.094 | 0.1499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-23 | WTP6 | 0.16 | 0.2499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-23 | WTP6 | 0.67 | 0.9499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-23 | WTP6 | 0.0039 | 0.0055 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-23 | WTP6 | 0.096 | 0.1499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-23 | WTP6 | 0.16 | 0.2499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-23 | WTP6 | 0.03 | 0.0449 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-23 | WTP6 | 0.077 | 0.1499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP6 | 0.0066 | 0.0249 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-23 | WTP6 | 0.0077 | 0.0149 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-23 | WTP6 | 0.045 | 0.2499 | HURON WP (35539137002) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-03-23 | WTP3 | 0.58 | 1.4999 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-03-23 | WTP3 | 0.89 | 1.4999 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-03-23 | WTP3 | 0.16 | 0.4499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-03-23 | WTP3 | 3.3 | 9.4999 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-03-23 | WTP3 | 4.2 | 6.4999 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-03-23 | WTP3 | 0.44 | 2.4999 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-03-23 | WTP3 | 0.094 | 0.1499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-03-23 | WTP3 | 0.16 | 0.2499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-03-23 | WTP3 | 0.67 | 0.9499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-03-23 | WTP3 | 0.0027 | 0.0055 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-03-23 | WTP3 | 0.096 | 0.1499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-03-23 | WTP3 | 0.16 | 0.2499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-03-23 | WTP3 | 0.03 | 0.0449 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-03-23 | WTP3 | 0.076 | 0.1499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP3 | 0.0066 | 0.0249 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-03-23 | WTP3 | 0.0077 | 0.0149 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-03-23 | WTP3 | 0.045 | 0.2499 | PEABODY WP (35539137003) 1Q 16 OF 29 SOC PLUS DIOXIN (DIOXIN NOT NEEDED, AN. DATE REVISED TO 3/31/20-OK NOW) RESULTS RCVD 12/23/20 AT DEP (LATE). LAB REPORTED RESULTS 4/20/20 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-23 | WTP1 | 0.01 | 0.0149 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP1 | 0.01 | 0.0249 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-23 | WTP1 | 0.05 | 0.1499 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-23 | WTP1 | 0.6 | 0.6499 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-23 | WTP1 | 0.03 | 0.0749 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-23 | WTP1 | 0.6 | 0.6499 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-23 | WTP1 | 0.01 | 0.1499 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-23 | WTP1 | 0.03 | 0.1499 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-23 | WTP1 | 0.05 | 0.2499 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-23 | WTP1 | 0.01 | 0.0449 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP1 | 0.02 | 0.0249 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-23 | WTP1 | 0.01 | 0.1499 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | 0.01 | UG/L | 0.2499 | 2020-03-23 | WTP1 | 0.01 | 0.0249 | BELLA LAGO WP (481950/35539137001) 1Q 13 OF 29 SOC. RSLTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RSLTS 3/18/21 PER LAB SIGNATURE DATE. BENZO IS 0.01, < RDL OF 0.02 (J QUAL ON BENZO WAS REMOVED)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-23 | WTP6 | 0.01 | 0.0149 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP6 | 0.01 | 0.0249 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-23 | WTP6 | 0.05 | 0.1499 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-23 | WTP6 | 0.6 | 0.6499 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | 0.03 | UG/L | 4.4999 | 2020-03-23 | WTP6 | 0.03 | 0.0749 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-23 | WTP6 | 0.6 | 0.6499 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-23 | WTP6 | 0.01 | 0.1499 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | 0.03 | UG/L | 3.4999 | 2020-03-23 | WTP6 | 0.03 | 0.1499 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-23 | WTP6 | 0.05 | 0.2499 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-23 | WTP6 | 0.01 | 0.0449 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP6 | 0.02 | 0.0249 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-23 | WTP6 | 0.01 | 0.1499 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | 0.01 | UG/L | 0.2499 | 2020-03-23 | WTP6 | 0.01 | 0.0249 | HURON WP(481950/35539137002)1Q 16 OF 29 SOC. RCVD 3/24/21 (LATE). LAB RPRTD RSLTS 3/18/21. J QUAL SIM,ATR,ALA,BENZO REMOVED. SIM 0.03,
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-03-23 | WTP3 | 0.01 | 0.0149 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP3 | 0.01 | 0.0249 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-03-23 | WTP3 | 0.05 | 0.1499 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-03-23 | WTP3 | 0.6 | 0.6499 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-03-23 | WTP3 | 0.03 | 0.0749 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-03-23 | WTP3 | 0.6 | 0.6499 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-03-23 | WTP3 | 0.01 | 0.1499 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-03-23 | WTP3 | 0.03 | 0.1499 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-03-23 | WTP3 | 0.05 | 0.2499 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-03-23 | WTP3 | 0.01 | 0.0449 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP3 | 0.02 | 0.0249 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-03-23 | WTP3 | 0.01 | 0.1499 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-03-23 | WTP3 | 0.01 | 0.0249 | PEABODY WP (481950/35539137003) 1Q 13 OF 29 SOC. RESULTS RCVD 3/24/21 AT DEP (LATE). LAB REPORTED RESULTS 3/18/21 PER LAB SIGNATURE DATE.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7 | LN(10) |  | 2020-03-23 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2020-03-25 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-03-25 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-03-26 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-04-03 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2020-04-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2020-04-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2020-04-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-04-27 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-04-27 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1095 | ZINC | 0.01 | MG/L | 5.4999 | 2020-04-30 | WTP3 | 0.0076 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1095 | ZINC | 0.01 | MG/L | 5.4999 | 2020-04-30 | WTP6 | 0.0076 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1055 | SULFATE | 2.7 | MG/L | 250.4999 | 2020-04-30 | WTP1 | 2.5 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2020-04-30 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-04-30 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1074 | ANTIMONY | 0.0008 | MG/L | 0.0065 | 2020-04-30 | WTP6 | 0.0005 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-04-30 | WTP1 | 0.025 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-04-30 | WTP1 | 0.025 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-04-30 | WTP1 | 0.0005 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2020-04-30 | WTP1 | 0.0023 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP1 | 0.00024 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.00081 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP1 | 0.00492 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1025 | FLUORIDE | 0.086 | MG/L | 4.0499 | 2020-04-30 | WTP1 | 0.015 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP1 | 0.00064 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP1 | 0.0001 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.002 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-04-30 | WTP1 | 0.00083 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1052 | SODIUM | 11.9 | MG/L | 160.4999 | 2020-04-30 | WTP1 | 0.59 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-04-30 | WTP1 | 0.0005 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP1 | 0.00021 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP1 | 0.0005 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP1 | 0.2 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP1 | 0.0072 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1017 | CHLORIDE | 13.9 | MG/L | 250.4999 | 2020-04-30 | WTP1 | 2.5 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1022 | COPPER | 0.0077 | MG/L | 1.4999 | 2020-04-30 | WTP1 | 0.00093 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1025 | FLUORIDE | 0.086 | MG/L | 2.0499 | 2020-04-30 | WTP1 | 0.015 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-04-30 | WTP1 | 0.016 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-04-30 | WTP1 | 0.0012 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP1 | 0.0015 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2020-04-30 | WTP1 | 0.0076 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP1 | 5 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2020-04-30 | WTP1 | 0.1 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 122 | MG/L | 500.4999 | 2020-04-30 | WTP1 | 5 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP1 | 0.099 |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 1.7 | MG/L | 10.4999 | 2020-04-30 | WTP6 | 0.025 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-04-30 | WTP6 | 0.025 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1005 | ARSENIC | 0.0016 | MG/L | 0.0104 | 2020-04-30 | WTP6 | 0.0005 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1010 | BARIUM | 0.017 | MG/L | 2.4999 | 2020-04-30 | WTP6 | 0.0023 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP6 | 0.0024 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP6 | 0.00081 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP6 | 0.00492 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1025 | FLUORIDE | 0.72 | MG/L | 4.0499 | 2020-04-30 | WTP6 | 0.015 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP6 | 0.00064 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP6 | 0.0001 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP6 | 0.002 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1045 | SELENIUM | 0.0011 | MG/L | 0.0549 | 2020-04-30 | WTP6 | 0.00083 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1052 | SODIUM | 7.5 | MG/L | 160.4999 | 2020-04-30 | WTP6 | 0.59 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP6 | 0.00021 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP6 | 0.0005 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP6 | 0.2 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP6 | 0.0072 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1017 | CHLORIDE | 12.5 | MG/L | 250.4999 | 2020-04-30 | WTP6 | 2.5 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1022 | COPPER | 0.0038 | MG/L | 1.4999 | 2020-04-30 | WTP6 | 0.0093 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1025 | FLUORIDE | 0.72 | MG/L | 2.0499 | 2020-04-30 | WTP6 | 0.015 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-04-30 | WTP6 | 0.016 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-04-30 | WTP6 | 0.0012 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP6 | 0.0015 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1055 | SULFATE | 33.2 | MG/L | 250.4999 | 2020-04-30 | WTP6 | 2.5 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP6 | 5 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2020-04-30 | WTP6 | 1 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 156 | MG/L | 500.4999 | 2020-04-30 | WTP6 | 5 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP6 | 0.099 |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2020-04-30 | WTP3 | 0.025 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2020-04-30 | WTP3 | 0.025 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2020-04-30 | WTP3 | 0.0005 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2020-04-30 | WTP3 | 0.0023 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2020-04-30 | WTP3 | 0.00024 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.00081 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2020-04-30 | WTP3 | 0.00492 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1025 | FLUORIDE | 0.61 | MG/L | 4.0499 | 2020-04-30 | WTP3 | 0.015 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2020-04-30 | WTP3 | 0.00064 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2020-04-30 | WTP3 | 0.0001 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.002 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2020-04-30 | WTP3 | 0.00083 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1052 | SODIUM | 11.3 | MG/L | 160.4999 | 2020-04-30 | WTP3 | 0.59 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2020-04-30 | WTP3 | 0.0005 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2020-04-30 | WTP3 | 0.00021 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2020-04-30 | WTP3 | 0.0005 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-04-30 | WTP3 | 0.2 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2020-04-30 | WTP3 | 0.0072 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1017 | CHLORIDE | 13.7 | MG/L | 250.4999 | 2020-04-30 | WTP3 | 2.5 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1022 | COPPER | 0.0021 | MG/L | 1.4999 | 2020-04-30 | WTP3 | 0.00093 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1025 | FLUORIDE | 0.61 | MG/L | 2.0499 | 2020-04-30 | WTP3 | 0.015 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2020-04-30 | WTP3 | 0.016 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2020-04-30 | WTP3 | 0.0012 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2020-04-30 | WTP3 | 0.0015 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2020-04-30 | WTP3 | 2.5 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2020-04-30 | WTP3 | 5 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2020-04-30 | WTP3 | 0.1 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 97 | MG/L | 500.4999 | 2020-04-30 | WTP3 | 5 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2020-04-30 | WTP3 | 0.099 |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-05-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2020-05-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-05-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-05-07 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2020-05-20 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-05-20 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-05-24 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.9 | UG/L | 60.4999 | 2020-05-27 | L1 | 0.9 |  | ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 45.2 | UG/L | 80.4999 | 2020-05-27 | L1 | 0.32 |  | ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.9 | UG/L | 60.4999 | 2020-05-27 | L3 | 0.9 |  | EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 35.4 | UG/L | 80.4999 | 2020-05-27 | L3 | 0.32 |  | EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.3 | UG/L | 60.4999 | 2020-05-27 | L4 | 0.9 |  | WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 33.9 | UG/L | 80.4999 | 2020-05-27 | L4 | 0.32 |  | WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-05-27 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.2 | UG/L | 60.4999 | 2020-05-28 | L2 | 0.9 |  | BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 46 | UG/L | 80.4999 | 2020-05-28 | L2 | 0.32 |  | BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-05-28 | WTP1 |  |  | BELLALAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP1 |  | 1.4999 | BELLALAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.08 | PCI/L | 15.4999 | 2020-05-28 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP6 |  | 1.4999 | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2020-05-28 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2020-05-28 | WTP3 |  | 1.4999 | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-06-01 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-06-01 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2020-06-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2020-06-08 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2020-06-12 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2020-06-12 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-06-24 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-06-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-07-03 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-07-05 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-07-16 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.12 | MG/L |  | 2020-07-16 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-07-22 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-07-22 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-07-23 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.72 | MG/L |  | 2020-07-23 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2020-08-05 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.36 | MG/L |  | 2020-08-05 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-08-07 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-08-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-08-19 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.18 | MG/L |  | 2020-08-19 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-08-24 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-08-25 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35 | UG/L | 60.4999 | 2020-08-26 | L2 | 0.9 |  | BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 52.8 | UG/L | 80.4999 | 2020-08-26 | L2 | 0.47 |  | BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.9 | UG/L | 60.4999 | 2020-08-26 | L1 | 0.9 |  | ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 59.4 | UG/L | 80.4999 | 2020-08-26 | L1 | 0.47 |  | ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.5 | UG/L | 60.4999 | 2020-08-26 | L3 | 0.9 |  | EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 52.1 | UG/L | 80.4999 | 2020-08-26 | L3 | 0.47 |  | EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.7 | UG/L | 60.4999 | 2020-08-26 | L4 | 0.9 |  | WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 39.9 | UG/L | 80.4999 | 2020-08-26 | L4 | 0.47 |  | WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1920 | ODOR THRESHOLD | 8 |  | 3.4999 | 2020-08-26 | WTP1 | 1 |  | BELLA LAGO WP (ODOR 8.0 TON, > MCL OF 3 TON) THESE RESULTS RECEIVED ON 4/14/21-BB
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2020-08-26 | WTP6 | 1 |  | HURON WP (ODOR 3.0 TON) THESE RESULTS RECEIVED ON 4/14/21-BB
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SEC | 1920 | ODOR THRESHOLD | 8 |  | 3.4999 | 2020-08-26 | WTP3 | 1 |  | PEABODY WP (ODOR 8.0 TON, > MCL OF 3 TON) THESE RESULTS RECEIVED ON 4/14/21-BB
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP1 | 0.69 | 1.4999 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP1 | 0.89 | 1.4999 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP1 | 0.16 | 0.4499 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP1 | 3.3 | 9.4999 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP1 | 4.2 | 6.4999 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP1 | 0.44 | 2.4999 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP1 | 0.094 | 0.1499 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP1 | 0.16 | 0.2499 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP1 | 0.67 | 0.9499 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP1 | 0.001 | 0.0055 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP1 | 0.096 | 0.1499 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP1 | 0.16 | 0.2499 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP1 | 0.03 | 0.0449 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP1 | 0.0065 | 0.0249 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP1 | 0.0076 | 0.0149 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP1 | 0.035 | 0.2499 | BELLA LAGO(SMP 35573906001)J QUAL ON ENDO+PCBS:ENTD ENDO SINCE LCS BIASED HIGH. PCBS NOT ENTD-JM1 & JR1(2OF7 AROCHLORS IN PCBS HAD JM1 & JR1 QUAL)LAB SIGNED RSLTS 9/23/20,1ST RCVD 12/16/20, REV 12/23
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP6 | 0.68 | 1.4999 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP6 | 0.89 | 1.4999 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP6 | 0.16 | 0.4499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP6 | 3.3 | 9.4999 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP6 | 4.2 | 6.4999 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP6 | 0.44 | 2.4999 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP6 | 0.094 | 0.1499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP6 | 0.16 | 0.2499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP6 | 0.67 | 0.9499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP6 | 0.00088 | 0.0055 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP6 | 0.096 | 0.1499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP6 | 0.16 | 0.2499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP6 | 0.03 | 0.0449 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-27 | WTP6 | 0.044 | 0.1499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP6 | 0.0065 | 0.0249 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP6 | 0.0077 | 0.0149 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP6 | 0.035 | 0.2499 | HURON (SMP 35573906002) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2020-08-27 | WTP3 | 0.69 | 1.4999 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2020-08-27 | WTP3 | 0.89 | 1.4999 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2020-08-27 | WTP3 | 0.16 | 0.4499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2020-08-27 | WTP3 | 3.3 | 9.4999 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2020-08-27 | WTP3 | 4.2 | 6.4999 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2020-08-27 | WTP3 | 0.44 | 2.4999 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2020-08-27 | WTP3 | 0.094 | 0.1499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2020-08-27 | WTP3 | 0.16 | 0.2499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2020-08-27 | WTP3 | 0.67 | 0.9499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2020-08-27 | WTP3 | 0.00079 | 0.0055 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2020-08-27 | WTP3 | 0.096 | 0.1499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2020-08-27 | WTP3 | 0.16 | 0.2499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2020-08-27 | WTP3 | 0.03 | 0.0449 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2020-08-27 | WTP3 | 0.045 | 0.1499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2020-08-27 | WTP3 | 0.0064 | 0.0249 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2020-08-27 | WTP3 | 0.0075 | 0.0149 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2020-08-27 | WTP3 | 0.035 | 0.2499 | PEABODY (SMP 35573906003) J QUAL ON ENDO: ENTD ENDOTHALL SINCE LCS BIASED HIGH. LAB SIGNED RSLTS 9/23/20, 1ST RCVD 12/16/20, REVISED (SEPARATED) 12/2320.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-09-02 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.25 | MG/L |  | 2020-09-02 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-09-08 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-09-08 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-09-20 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-09-21 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2020-09-23 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.13 | MG/L |  | 2020-09-23 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-10-08 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-10-10 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-10-14 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2020-10-14 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2020-10-22 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-10-22 | WTP3 | 0.0056 | 0.0149 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP3 | 0.0068 | 0.0249 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-10-22 | WTP3 | 0.024 | 0.1499 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-10-22 | WTP3 | 0.37 | 0.6499 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-10-22 | WTP3 | 0.041 | 0.0749 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-10-22 | WTP3 | 0.48 | 0.6499 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-10-22 | WTP3 | 0.025 | 0.1499 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-10-22 | WTP3 | 0.015 | 0.1499 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-10-22 | WTP3 | 0.03 | 0.2499 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-10-22 | WTP3 | 0.014 | 0.0449 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP3 | 0.0031 | 0.0249 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-10-22 | WTP3 | 0.015 | 0.1499 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-10-22 | WTP3 | 0.02 | 0.0249 | PEABODY (SMP 35586923003) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 10/30/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-10-25 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-10-28 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.38 | MG/L |  | 2020-10-28 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2020-11-04 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.7 | MG/L |  | 2020-11-04 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-11-07 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-11-09 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2020-11-19 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.7 | MG/L |  | 2020-11-19 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.3 | UG/L | 60.4999 | 2020-11-25 | L2 | 0.9 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 53.5 | UG/L | 80.4999 | 2020-11-25 | L2 | 0.47 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35 | UG/L | 60.4999 | 2020-11-25 | L1 | 0.9 |  | 4738 ASHURST ST., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 60.2 | UG/L | 80.4999 | 2020-11-25 | L1 | 0.47 |  | 4738 ASHURST ST., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.1 | UG/L | 60.4999 | 2020-11-25 | L3 | 0.9 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 42.4 | UG/L | 80.4999 | 2020-11-25 | L3 | 0.47 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.7 | UG/L | 60.4999 | 2020-11-25 | L4 | 0.9 |  | 5508 WILLOW BEND TR., KISSIMMEE (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 63.8 | UG/L | 80.4999 | 2020-11-25 | L4 | 0.47 |  | 5508 WILLOW BEND TR., KISSIMMEE (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2020-11-26 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-11-26 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-12-02 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2020-12-02 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2020-12-02 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2020-12-02 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2020-12-03 | DIST | 0.2 |  | 871 TOWN CENTER BLVD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-12-03 | WTP1 | 0.0054 | 0.0149 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP1 | 0.0065 | 0.0249 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-12-03 | WTP1 | 0.023 | 0.1499 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-12-03 | WTP1 | 0.35 | 0.6499 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-12-03 | WTP1 | 0.039 | 0.0749 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-12-03 | WTP1 | 0.46 | 0.6499 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-12-03 | WTP1 | 0.024 | 0.1499 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-12-03 | WTP1 | 0.014 | 0.1499 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-12-03 | WTP1 | 0.029 | 0.2499 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-12-03 | WTP1 | 0.013 | 0.0449 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP1 | 0.003 | 0.0249 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-12-03 | WTP1 | 0.014 | 0.1499 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP1 | 0.019 | 0.0249 | BELLA LAGO (SMP 35596240001) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2020-12-03 | WTP6 | 0.0058 | 0.0149 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP6 | 0.0071 | 0.0249 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2020-12-03 | WTP6 | 0.025 | 0.1499 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2020-12-03 | WTP6 | 0.38 | 0.6499 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2020-12-03 | WTP6 | 0.043 | 0.0749 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2020-12-03 | WTP6 | 0.5 | 0.6499 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2020-12-03 | WTP6 | 0.026 | 0.1499 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2020-12-03 | WTP6 | 0.016 | 0.1499 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2020-12-03 | WTP6 | 0.031 | 0.2499 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2020-12-03 | WTP6 | 0.015 | 0.0449 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP6 | 0.0032 | 0.0249 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2020-12-03 | WTP6 | 0.016 | 0.1499 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2020-12-03 | WTP6 | 0.021 | 0.0249 | HURON (SMP 35596240002) 2Q 13 OF 29 SOCS. LAB SIGNED REPORT 12/11/20, 1ST RCVD 12/16/20, REVISION (SEPARATED) 12/23/20
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2020-12-23 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2020-12-23 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2020-12-23 | WTP1
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2020-12-30 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-01-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-01-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-01-06 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-01-21 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-01-22 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-01-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP1 | 0.025 |  | BELLA LAGO WP (NITRATE ENTD. NITRITE HAS J QUALIFIER, NOT ENTD) PLS. ENTER NITRITE RESULT IF ACCEPTABLE. -BB (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP3 | 0.025 |  | PEABODY WP (NO J QUALIFIERS, BOTH NN ENTD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP3 | 0.025 |  | PEABODY WP (NO J QUALIFIERS, BOTH NN ENTD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 2 | MG/L | 10.4999 | 2021-01-27 | WTP6 | 0.025 |  | HURON WP (NITRATE ENTD. NITRITE HAS J QUALIFIER, NOT ENTD) PLS. ENTER NITRITE RESULT IF ACCEPTABLE. -BB (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-02-01 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-02-03 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-02-03 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-08 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-02-17 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-02-17 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2021-02-17 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-02-21 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2021-02-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 35.9 | UG/L | 80.4999 | 2021-02-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.7 | UG/L | 60.4999 | 2021-02-23 | L1 | 0.9 |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 47.7 | UG/L | 80.4999 | 2021-02-23 | L1 | 0.47 |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.2 | UG/L | 60.4999 | 2021-02-23 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 55.1 | UG/L | 80.4999 | 2021-02-23 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.6 | UG/L | 60.4999 | 2021-02-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 46.6 | UG/L | 80.4999 | 2021-02-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-03-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-09 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-03-10 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-03-10 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-03-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-03-23 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2021-03-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-03-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-09 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-12 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-13 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-26 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-04-26 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-28 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-05-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2021-05-06 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-05-06 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-10 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-05-19 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-05-19 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-20 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26 | UG/L | 60.4999 | 2021-05-26 | L2 |  |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 48.2 | UG/L | 80.4999 | 2021-05-26 | L2 |  |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.6 | UG/L | 60.4999 | 2021-05-26 | L1 |  |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 51.9 | UG/L | 80.4999 | 2021-05-26 | L1 |  |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.2 | UG/L | 60.4999 | 2021-05-26 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 36.2 | UG/L | 80.4999 | 2021-05-26 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.9 | UG/L | 60.4999 | 2021-05-26 | L4 |  |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 51.2 | UG/L | 80.4999 | 2021-05-26 | L4 |  |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-05-27 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-07 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-14 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-06-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-25 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2021-06-29 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-06-29 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-07-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-07-07 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-07-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-07-22 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-08-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-09 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-11 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-17 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-18 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-20 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.2 | UG/L | 60.4999 | 2021-08-27 | L2 |  |  | 3546 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 41.3 | UG/L | 80.4999 | 2021-08-27 | L2 |  |  | 3546 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.5 | UG/L | 60.4999 | 2021-08-27 | L1 |  |  | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 40.9 | UG/L | 80.4999 | 2021-08-27 | L1 |  |  | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.9 | UG/L | 60.4999 | 2021-08-27 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 31.6 | UG/L | 80.4999 | 2021-08-27 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.1 | UG/L | 60.4999 | 2021-08-27 | L4 |  |  | 5508 WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 31.3 | UG/L | 80.4999 | 2021-08-27 | L4 |  |  | 5508 WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-04 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-09 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-18 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-23 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-30 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-12 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-12 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | WTP1 | 0.025 |  | BELLA LAGO WP NITRITE RETEST (NITRITE HAS J QUAL, BIASED HIGH MS/MSD=119/119% RECOV, LCS OK) SINCE BIASED HIGH, PROB. OK. IF OK, PLS. CHANGE SMP TYPE "S" TO SMP TYP "N."
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | WTP6 | 0.025 |  | HURON WP NITRITE RETEST (OK)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-26 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-27 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-28 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-10 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-10 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-19 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28 | UG/L | 60.4999 | 2021-11-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 46.5 | UG/L | 80.4999 | 2021-11-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.7 | UG/L | 60.4999 | 2021-11-23 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 52.2 | UG/L | 80.4999 | 2021-11-23 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.3 | UG/L | 60.4999 | 2021-11-23 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 39.2 | UG/L | 80.4999 | 2021-11-23 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.9 | UG/L | 60.4999 | 2021-11-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 43.5 | UG/L | 80.4999 | 2021-11-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-27 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-12-14 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-12-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-22 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-28 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-01-04 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-01-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-08 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2022-01-12 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-12 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-20 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-30 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-02-02 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-02 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-05 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-11 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-02-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-17 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 1.6 | MG/L | 10.4999 | 2022-02-21 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.1 | UG/L | 60.4999 | 2022-02-22 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2022-02-22 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 41.7 | UG/L | 80.4999 | 2022-02-22 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2022-02-22 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.3 | UG/L | 60.4999 | 2022-02-22 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 30.5 | UG/L | 80.4999 | 2022-02-22 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2022-02-22 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 31.3 | UG/L | 80.4999 | 2022-02-22 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-02-23 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-06 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-06 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-03-16 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-16 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-03-20 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-20 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-03-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-04-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-08 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-12 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-04-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-24 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-04-25 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-06 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-09 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-05-11 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-11 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-05-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-21 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.5 | UG/L | 60.4999 | 2022-05-25 | L2 |  |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 40 | UG/L | 80.4999 | 2022-05-25 | L2 |  |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27 | UG/L | 60.4999 | 2022-05-25 | L1 |  |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 45 | UG/L | 80.4999 | 2022-05-25 | L1 |  |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.1 | UG/L | 60.4999 | 2022-05-25 | L3 |  |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 30.9 | UG/L | 80.4999 | 2022-05-25 | L3 |  |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.8 | UG/L | 60.4999 | 2022-05-25 | L4 |  |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 39.1 | UG/L | 80.4999 | 2022-05-25 | L4 |  |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-25 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-06-01 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-01 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-11 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-14 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-06-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-24 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-26 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29 | UG/L | 60.4999 | 2022-08-25 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 51.4 | UG/L | 80.4999 | 2022-08-25 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24 | UG/L | 60.4999 | 2022-08-25 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 48.4 | UG/L | 80.4999 | 2022-08-25 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2022-08-25 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 41.8 | UG/L | 80.4999 | 2022-08-25 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.6 | UG/L | 60.4999 | 2022-08-25 | L4 | 0.9 |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 41.6 | UG/L | 80.4999 | 2022-08-25 | L4 | 0.47 |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.9 | UG/L | 60.4999 | 2022-11-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 39.6 | UG/L | 80.4999 | 2022-11-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.7 | UG/L | 60.4999 | 2022-11-23 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 48.2 | UG/L | 80.4999 | 2022-11-23 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2022-11-23 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 34.8 | UG/L | 80.4999 | 2022-11-23 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.6 | UG/L | 60.4999 | 2022-11-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | DBP | 2950 | TOTAL THMS | 34.1 | UG/L | 80.4999 | 2022-11-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.71 | UG/L | 60.4999 | 2020-09-01 | L2 |  |  | LOT 123
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 32.05 | UG/L | 80.4999 | 2020-09-01 | L2 |  |  | LOT 123
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.11 | UG/L | 60.4999 | 2020-09-01 | L1 |  |  | LOT 292
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 0.39 | UG/L | 80.4999 | 2020-09-01 | L1 |  |  | LOT 292
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 55.85 | UG/L | 60.4999 | 2021-09-13 | L1 |  |  | LOT 292
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 104.94 | UG/L | 80.4999 | 2021-09-13 | L1 |  |  | LOT 292
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.54 | UG/L | 60.4999 | 2021-09-13 | L2 |  |  | LOT 123
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 26.1 | UG/L | 80.4999 | 2021-09-13 | L2 |  |  | LOT 123
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.59 | UG/L | 60.4999 | 2021-11-19 | L2 | 0.98 |  | LOT 123 (NO TTHM LRAA MCL VIOL AS OF 12/21 QTR)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 95.97 | UG/L | 80.4999 | 2021-11-19 | L2 | 0.39 |  | LOT 123 (NO TTHM LRAA MCL VIOL AS OF 12/21 QTR)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.2 | UG/L | 60.4999 | 2021-11-19 | L1 | 0.98 |  | LOT 292 (HLKD) SYSTEM IS IN "NOT CLEARED" STATUS IN PWS AS OF 4/5/21 (?). 10/21/21 REVISED STG2 PLAN IS IN OCULUS.
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 105.19 | UG/L | 80.4999 | 2021-11-19 | L1 | 0.39 |  | LOT 292 (HLKD) SYSTEM IS IN "NOT CLEARED" STATUS IN PWS AS OF 4/5/21 (?). 10/21/21 REVISED STG2 PLAN IS IN OCULUS.
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.52 | UG/L | 60.4999 | 2022-02-16 | L1 |  |  | LOT 292 (LRAA=TTHM= 64.14, HAA5= 38.92)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 46.05 | UG/L | 80.4999 | 2022-02-16 | L1 |  |  | LOT 292 (LRAA=TTHM= 64.14, HAA5= 38.92)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.14 | UG/L | 60.4999 | 2022-02-16 | L2 |  |  | LOT 123 (LRAA= TTHM= 49.99, HAA5=25.99)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 45.85 | UG/L | 80.4999 | 2022-02-16 | L2 |  |  | LOT 123 (LRAA= TTHM= 49.99, HAA5=25.99)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.48 | UG/L | 60.4999 | 2022-05-18 | L1 | 0.98 |  | LOT 292
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 31.36 | UG/L | 80.4999 | 2022-05-18 | L1 | 0.39 |  | LOT 292
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.94 | UG/L | 60.4999 | 2022-05-18 | L2 | 0.98 |  | LOT 123 (HLKD)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2022-05-18 | L2 | 0.39 |  | LOT 123 (HLKD)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.25 | UG/L | 60.4999 | 2022-07-19 | L1 | 0.98 |  | LOT 292_DOES NOT MATCH SAMPLING PLAN_AL
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 1.43 | UG/L | 80.4999 | 2022-07-19 | L1 | 0.39 |  | LOT 292_DOES NOT MATCH SAMPLING PLAN_AL
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.6 | UG/L | 60.4999 | 2022-07-19 | L2 | 0.98 |  | LOT 123 (HLKD)_DOES NOT MATCH SAMPLING PLAN_AL
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 4.58 | UG/L | 80.4999 | 2022-07-19 | L2 | 0.39 |  | LOT 123 (HLKD)_DOES NOT MATCH SAMPLING PLAN_AL
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-08-15 | L1 | 0.98 |  | LOT 292 (RETEST AFTER 7/22 RESULTS)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 16.96 | UG/L | 80.4999 | 2022-08-15 | L1 | 0.44 |  | LOT 292 (RETEST AFTER 7/22 RESULTS)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.82 | UG/L | 60.4999 | 2022-08-15 | L2 | 0.98 |  | LOT 123 (RETEST AFTER 7/22 RESULTS)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 17.18 | UG/L | 80.4999 | 2022-08-15 | L2 | 0.44 |  | LOT 123 (RETEST AFTER 7/22 RESULTS)
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.93 | UG/L | 60.4999 | 2022-11-17 | L1 | 0.98 |  | LOT 292 TTHM HAA5
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 43.15 | UG/L | 80.4999 | 2022-11-17 | L1 | 0.39 |  | LOT 292 TTHM HAA5
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.56 | UG/L | 60.4999 | 2022-11-17 | L2 | 0.98 |  | LOT 123 TTHM HAA5
3494440 | TAVISTOCK EAST (CONSEC.) | DBP | 2950 | TOTAL THMS | 31.45 | UG/L | 80.4999 | 2022-11-17 | L2 | 0.39 |  | LOT 123 TTHM HAA5
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1040 | NITRATE | 0.091 | MG/L | 10.4999 | 2022-02-21 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1017 | CHLORIDE | 49.1 | MG/L | 250.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1055 | SULFATE | 21.3 | MG/L | 250.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1920 | ODOR THRESHOLD | 2 |  | 3.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.6 | LN(10) |  | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 331 | MG/L | 500.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-02-23 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-02-23 | WTP NP. 1 |  | 0.4499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 9.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-02-23 | WTP NP. 1 |  | 6.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-02-23 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-02-23 | WTP NP. 1 |  | 2.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-02-23 | WTP NP. 1 |  | 0.0749 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-02-23 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-02-23 | WTP NP. 1 |  | 0.9499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2022-02-23 | WTP NP. 1 |  | 0.0055 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-02-23 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-02-23 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1010 | BARIUM | 0.0096 | MG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1025 | FLUORIDE | 0.28 | MG/L | 4.0499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1052 | SODIUM | 33.7 | MG/L | 160.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1025 | FLUORIDE | 0.28 | MG/L | 2.0499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2022-02-23 | WTP NP. 1 | 0.2 |  | POE/D ASBESTOS (ENT'D SEPARATELY FROM PRIMARY INORGANICS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-03-14 | L3 |  |  | AT POE_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 10.1 | UG/L | 10.4999 | 2022-04-01 | L3 |  |  | HIGH RESULT_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 0.0149 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 1.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-05-24 | WTP NP. 1 |  | 1.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 9.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-05-24 | WTP NP. 1 |  | 0.6499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-05-24 | WTP NP. 1 |  | 2.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-05-24 | WTP NP. 1 |  | 0.0749 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-05-24 | WTP NP. 1 |  | 0.6499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-05-24 | WTP NP. 1 |  | 0.9499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2022-05-24 | WTP NP. 1 |  | 0.0055 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-05-24 | WTP NP. 1 |  | 0.0449 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.0449 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-05-24 | WTP NP. 1 |  | 0.0149 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2991 | TOLUENE | 0.41 | UG/L | 1499.9999 | 2022-05-24 | WTP NP. 1 | 0.28 | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-05-24 | WTP NP. 1 |  |  | ENTERED LATE_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 1.4999 | ENTERED LATE_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-05-27 | L3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-05-27 | WTP NP. 1 | 1 |  | MARKED "WELL 1 FINISHED WATER" (POE/D)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-05-31 | WTP NP. 1 | 1 |  | MARKED "WELL 2 FINISHED WATER" (POE/D) "SULFIDE" IS REPORTED AS 0.16 MG/L
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-06-03 | L3 |  |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 4 | UG/L | 10.4999 | 2022-07-01 | L3 | 0.22 |  | BROMATE - JULY
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-07-08 | WTP NP. 1 | 0.16 | 0.4499 | DIQUAT RETESTED DUE TO J QUALIFIER 5/22
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-08-02 | WTP NP. 1 | 2.44 |  | RADS
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.615 | 1.4999 | RADS
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-02 | WTP NP. 1 | 0.35 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-02 | WTP NP. 1 | 0.33 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-02 | WTP NP. 1 | 0.11 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-02 | WTP NP. 1 | 0.44 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-02 | WTP NP. 1 | 0.3 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.12 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-02 | WTP NP. 1 | 0.29 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 0.27 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.3 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-02 | WTP NP. 1 | 0.27 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.28 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-02 | WTP NP. 1 | 0.44 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-02 | WTP NP. 1 | 0.28 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.4 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2991 | TOLUENE | 0.28 | UG/L | 1499.9999 | 2022-08-02 | WTP NP. 1 | 0.28 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-02 | WTP NP. 1 | 0.23 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 0.2 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.003 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-02 | WTP NP. 1 | 0.096 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-02 | WTP NP. 1 | 0.053 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.019 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.0449 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-02 | WTP NP. 1 | 0.045 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.0065 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-02 | WTP NP. 1 | 0.0076 | 0.0149 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.036 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-08-02 | WTP NP. 1 | 3.4 | 6.4999 | GLYPHOSATE W/ J QUALIFIER-ONLY 11% MS RECOVERY-UNACCEPTABLE-WILL RETEST 9/22 (NO PAGE 1 FOR THIS REPORT 810-33545-1 E87775, SUBCONTRACTED FROM PACE E83079 SAMPLE 35736874001, WHICH IS THE 8/2/22 SOCS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.0023 | 0.0149 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.0027 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-08-02 | WTP NP. 1 | 0.023 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.7 | 1.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-02 | WTP NP. 1 | 0.49 | 1.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-08-02 | WTP NP. 1 | 0.16 | 0.4499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 3.3 | 9.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-08-02 | WTP NP. 1 | 0.36 | 0.6499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-08-02 | WTP NP. 1 | 0.46 | 2.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-08-02 | WTP NP. 1 | 0.04 | 0.0749 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-08-02 | WTP NP. 1 | 0.46 | 0.6499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-08-02 | WTP NP. 1 | 0.04 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-08-02 | WTP NP. 1 | 0.16 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-08-02 | WTP NP. 1 | 0.024 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-08-02 | WTP NP. 1 | 0.59 | 0.9499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.029 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2022-08-02 | WTP NP. 1 | 0.0021 | 0.0055 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.0449 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-08-05 | L3 | 1.1 |  | 8/22 BROMATE (HLKD)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 6.7 | UG/L | 10.4999 | 2022-09-02 | L3 | 1.1 |  | 9/22 BROMATE (HLKD)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-09-16 | WTP NP. 1 |  | 6.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.6 | UG/L | 60.4999 | 2022-09-23 | L1 | 0.9 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 2950 | TOTAL THMS | 41.7 | UG/L | 80.4999 | 2022-09-23 | L1 | 0.47 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.3 | UG/L | 60.4999 | 2022-09-23 | L2 | 0.9 |  | 5690 BARLETTA DR_AL | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 2950 | TOTAL THMS | 41.1 | UG/L | 80.4999 | 2022-09-23 | L2 | 0.47 |  | 5690 BARLETTA DR_AL | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 15.9 | UG/L | 10.4999 | 2022-10-07 | L3 | 2.2 |  | 10/22 BROMATE (BROMATE 15.9 UG/L, SINGLE SAMPLE OVER MCL OF 10 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 6.5 | UG/L | 10.4999 | 2022-10-25 | L3 | 1.1 |  | 10/22 BROMATE (RE-SAMPLE) BROMATE 6.5 UG/L
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2005 | ENDRIN | 0.0024 | UG/L | 2.4999 | 2022-10-28 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2110 | 2,4,5-TP (Silvex) | 0.053 | UG/L | 54.9999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2010 | LINDANE | 0.0027 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2015 | METHOXYCLOR | 0.024 | UG/L | 44.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2020 | TOXAPHENE | 0.69 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2031 | DALAPON | 0.49 | UG/L | 249.9999 | 2022-10-28 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2032 | DIQUAT | 0.16 | UG/L | 24.9999 | 2022-10-28 | WTP NP. 1 |  | 0.4499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2033 | ENDOTHALL | 3.3 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 9.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2034 | GLYPHOSATE | 4.2 | UG/L | 749.9999 | 2022-10-28 | WTP NP. 1 |  | 6.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0.36 | UG/L | 449.9999 | 2022-10-28 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2040 | PICLORAM | 0.04 | UG/L | 549.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2041 | DINOSEB | 0.16 | UG/L | 7.4999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.024 | UG/L | 54.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2046 | CARBOFURAN | 0.59 | UG/L | 44.9999 | 2022-10-28 | WTP NP. 1 |  | 0.9499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2050 | ATRAZINE | 0.015 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2051 | ALACHLOR (LASSO) | 0.029 | UG/L | 2.4999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2063 | DIOXIN (NG/L) | 0.0037 | NG/L | 0.0349 | 2022-10-28 | WTP NP. 1 |  | 0.0055 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2065 | HEPTACHLOR | 0.014 | UG/L | 0.4499 | 2022-10-28 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2067 | HEPTACHLOR EPOXIDE | 0.003 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2105 | 2,4-D | 0.096 | UG/L | 74.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2274 | HEXACHLOROBENZENE | 0.015 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2306 | BENZO(A)PYRENE | 0.02 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2326 | PENTACHLOROPHENOL | 0.014 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0.044 | UG/L | 0.5499 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2931 | DIBROMOCHLOROPROPANE | 0.0062 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2946 | ETHYLENE DIBROMIDE | 0.0073 | UG/L | 0.0249 | 2022-10-28 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2959 | CHLORDANE | 0.035 | UG/L | 2.4999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2036 | OXAMYL (VYDATE) | 0.46 | UG/L | 249.9999 | 2022-10-28 | WTP NP. 1 |  | 2.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2037 | SIMAZINE | 0.04 | UG/L | 4.4999 | 2022-10-28 | WTP NP. 1 |  | 0.0749 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0.47 | UG/L | 6.4999 | 2022-10-28 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-10-28 | WTP NP. 1 | 2.56 |  | 4Q RADS (HLKD SINCE 4TH QTR RADS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-10-28 | WTP NP. 1 | 0.604 | 1.4999 | 4Q RADS (HLKD SINCE 4TH QTR RADS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 37.9 | UG/L | 10.4999 | 2022-11-09 | L3 | 1.1 |  | 11/22 BROMATE (BROMATE 37.9 UG/L, MCL = 10 UG/L, OVER 3 TIMES MCL) HLKD
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | DBP | 1011 | BROMATE | 8.9 | UG/L | 10.4999 | 2022-11-23 | L3 | 1.1 |  | 11/22 BROMATE (MARKED RESAMPLE)