3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.31 | UG/L | 60.4999 | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 64.8 | UG/L | 80.4999 | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2450 | MONOCHLORACETIC ACID | 1.38 | UG/L |  | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2451 | DICHLOROACETIC ACID | 18.62 | UG/L |  | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2452 | TRICHLOROACETIC ACID | 22.32 | UG/L |  | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2454 | DIBROMOACETIC ACID | 0 | UG/L |  | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2941 | CHLOROFORM | 54.63 | UG/L | 100 | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2943 | BROMODICHLOROMETHANE | 10.17 | UG/L | 100 | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 0 | UG/L | 100 | 2021-07-08 | L1 |  |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.45 | UG/L | 60.4999 | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 69.88 | UG/L | 80.4999 | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2450 | MONOCHLORACETIC ACID | 1.08 | UG/L |  | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2451 | DICHLOROACETIC ACID | 15.9 | UG/L |  | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2452 | TRICHLOROACETIC ACID | 22.48 | UG/L |  | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2454 | DIBROMOACETIC ACID | 0 | UG/L |  | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2941 | CHLOROFORM | 59.43 | UG/L | 100 | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2943 | BROMODICHLOROMETHANE | 10.45 | UG/L | 100 | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 0 | UG/L | 100 | 2021-07-08 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.64 | UG/L | 60.4999 | 2021-10-07 | L4 | 0.98 |  | BARBARA YING CTR
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 61.23 | UG/L | 80.4999 | 2021-10-07 | L4 | 1 |  | BARBARA YING CTR
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.35 | UG/L | 60.4999 | 2021-10-07 | L3 | 0.98 |  | SIEMENS WEST
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 64.87 | UG/L | 80.4999 | 2021-10-07 | L3 | 1 |  | SIEMENS WEST
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.55 | UG/L | 60.4999 | 2021-10-07 | L1 | 0.98 |  | ALPHA TAU OMEGA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 57.94 | UG/L | 80.4999 | 2021-10-07 | L1 | 1 |  | ALPHA TAU OMEGA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.65 | UG/L | 60.4999 | 2021-10-07 | L2 | 0.98 |  | ARENA (HLKD)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 61.3 | UG/L | 80.4999 | 2021-10-07 | L2 | 1 |  | ARENA (HLKD)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.2 | UG/L | 60.4999 | 2022-01-13 | L4 | 0.98 |  | BARBARA YING 71 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 61.31 | UG/L | 80.4999 | 2022-01-13 | L4 | 0.39 |  | BARBARA YING 71 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.09 | UG/L | 60.4999 | 2022-01-13 | L3 | 0.98 |  | SIEMENS 4400 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 62.85 | UG/L | 80.4999 | 2022-01-13 | L3 | 0.39 |  | SIEMENS 4400 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.86 | UG/L | 60.4999 | 2022-01-13 | L1 | 0.98 |  | ALPHA TAU OMEGA 410 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 56.49 | UG/L | 80.4999 | 2022-01-13 | L1 | 0.39 |  | ALPHA TAU OMEGA 410 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.26 | UG/L | 60.4999 | 2022-01-13 | L2 | 0.98 |  | ARENA 50 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 59.1 | UG/L | 80.4999 | 2022-01-13 | L2 | 0.39 |  | ARENA 50 (NO RESIDUAL)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.47 | UG/L | 60.4999 | 2022-04-14 | L4 |  |  | BARBARA YIN
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 67.26 | UG/L | 80.4999 | 2022-04-14 | L4 |  |  | BARBARA YIN
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.94 | UG/L | 60.4999 | 2022-04-14 | L3 |  |  | SIEMENS 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 65.2 | UG/L | 80.4999 | 2022-04-14 | L3 |  |  | SIEMENS 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.37 | UG/L | 60.4999 | 2022-04-14 | L1 |  |  | ALPHA TAU OMEGA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 61.93 | UG/L | 80.4999 | 2022-04-14 | L1 |  |  | ALPHA TAU OMEGA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.92 | UG/L | 60.4999 | 2022-04-14 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 56.08 | UG/L | 80.4999 | 2022-04-14 | L2 |  |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1040 | NITRATE | 0.059 | MG/L | 10.4999 | 2022-04-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.97 | UG/L | 60.4999 | 2022-07-14 | L4 | 0.98 |  | BARBARA YING CENTER 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 43.03 | UG/L | 80.4999 | 2022-07-14 | L4 | 0.39 |  | BARBARA YING CENTER 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.53 | UG/L | 60.4999 | 2022-07-14 | L3 | 0.98 |  | SIEMENS WEST 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 29.05 | UG/L | 80.4999 | 2022-07-14 | L3 | 0.39 |  | SIEMENS WEST 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.9 | UG/L | 60.4999 | 2022-07-14 | L1 | 0.98 |  | ATO (ALPHA TAU OMEGA) 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 46 | UG/L | 80.4999 | 2022-07-14 | L1 | 0.39 |  | ATO (ALPHA TAU OMEGA) 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.38 | UG/L | 60.4999 | 2022-07-14 | L2 | 0.98 |  | ARENA 50 (HLKD)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 22.92 | UG/L | 80.4999 | 2022-07-14 | L2 | 0.39 |  | ARENA 50 (HLKD)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.19 | UG/L | 60.4999 | 2022-10-12 | L4 | 0.98 |  | BARBARA YING CNTR
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 81.19 | UG/L | 80.4999 | 2022-10-12 | L4 | 0.39 |  | BARBARA YING CNTR
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.57 | UG/L | 60.4999 | 2022-10-12 | L3 | 0.98 |  | SIEMENS WEST
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 82.2 | UG/L | 80.4999 | 2022-10-12 | L3 | 0.39 |  | SIEMENS WEST
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.55 | UG/L | 60.4999 | 2022-10-12 | L1 | 0.98 |  | ALPHA TAU OMEGA (ATO)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 83.64 | UG/L | 80.4999 | 2022-10-12 | L1 | 0.39 |  | ALPHA TAU OMEGA (ATO)
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.77 | UG/L | 60.4999 | 2022-10-12 | L2 | 0.98 |  | ARENA (HLKD) 12/22 QTR DISINF BYP RPRT RCVD W/RSLTS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 75.38 | UG/L | 80.4999 | 2022-10-12 | L2 | 0.39 |  | ARENA (HLKD) 12/22 QTR DISINF BYP RPRT RCVD W/RSLTS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.14 | UG/L | 60.4999 | 2023-01-12 | L4 | 0.98 |  | BARBARA YING 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 58.67 | UG/L | 80.4999 | 2023-01-12 | L4 | 0.39 |  | BARBARA YING 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.31 | UG/L | 60.4999 | 2023-01-12 | L3 | 0.98 |  | SIEMENS WEST 400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 62.53 | UG/L | 80.4999 | 2023-01-12 | L3 | 0.39 |  | SIEMENS WEST 400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.58 | UG/L | 60.4999 | 2023-01-12 | L1 | 0.98 |  | ATO 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 63.68 | UG/L | 80.4999 | 2023-01-12 | L1 | 0.39 |  | ATO 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.93 | UG/L | 60.4999 | 2023-01-12 | L2 | 0.98 |  | ARENA 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 46 | UG/L | 80.4999 | 2023-01-12 | L2 | 0.39 |  | ARENA 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1040 | NITRATE | 0.068 | MG/L | 10.4999 | 2023-02-16 | AAA | 0.024 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2023-02-16 | AAA | 0.003 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2023-02-16 | AAA | 0.0099 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2023-02-16 | AAA | 0.8 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1017 | CHLORIDE | 16 | MG/L | 250.4999 | 2023-02-16 | AAA | 0.39 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1022 | COPPER | 0.013 | MG/L | 1.4999 | 2023-02-16 | AAA | 0.01 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2023-02-16 | AAA | 0.0099 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1055 | SULFATE | 2.9 | MG/L | 250.4999 | 2023-02-16 | AAA | 0.034 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-02-16 | AAA | 5 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2023-02-16 | AAA | 1 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.85 | LN(10) |  | 2023-02-16 | AAA |  |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 190 | MG/L | 500.4999 | 2023-02-16 | AAA | 5 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 2905 | FOAMING AGENTS | 0.13 |  | 0.5499 | 2023-02-16 | AAA | 0.04 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-16 | AAA |  | 0.5499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-16 | AAA |  | 0.0149 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-16 | AAA |  | 0.0249 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-16 | AAA |  | 0.1499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-16 | AAA |  | 1.4999 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-16 | AAA |  | 1.4999 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-16 | AAA |  | 0.4499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-16 | AAA |  | 9.4999 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-16 | AAA |  | 6.4999 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-16 | AAA |  | 0.6499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-16 | AAA |  | 2.4999 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-16 | AAA |  | 0.0749 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-16 | AAA |  | 0.6499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-16 | AAA |  | 0.1499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-16 | AAA |  | 0.2499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-16 | AAA |  | 0.1499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-16 | AAA |  | 0.9499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-16 | AAA |  | 0.1499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-16 | AAA |  | 0.2499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-16 | AAA |  | 0.0449 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-16 | AAA |  | 0.0249 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-16 | AAA |  | 0.1499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-16 | AAA |  | 0.2499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-16 | AAA |  | 0.1499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-16 | AAA |  | 0.0249 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-16 | AAA |  | 0.0449 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-16 | AAA |  | 0.1499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-16 | AAA |  | 0.0249 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-16 | AAA |  | 0.0149 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-16 | AAA |  | 0.2499 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0.8 | PCI/L | 15.4999 | 2023-02-16 | AAA | 0.8 |  | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2023-02-16 | AAA | 0.4 | 1.4999 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-02-16 | AAA |  | 1.4999 | POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-27 | AAA | 0.0012 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-27 | AAA | 0.00025 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-27 | AAA | 0.00025 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-27 | AAA | 0.0005 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-27 | AAA | 1e-05 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-27 | AAA | 0.001 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-27 | AAA | 0.00025 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-27 | AAA | 0.0005 |  | LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.05 | UG/L | 60.4999 | 2023-04-13 | L4 | 0.98
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 74.36 | UG/L | 80.4999 | 2023-04-13 | L4 | 0.39
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.66 | UG/L | 60.4999 | 2023-04-13 | L3 | 0.98
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 70.88 | UG/L | 80.4999 | 2023-04-13 | L3 | 0.39
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.57 | UG/L | 60.4999 | 2023-04-13 | L1 | 0.98
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 68.99 | UG/L | 80.4999 | 2023-04-13 | L1 | 0.39
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.4 | UG/L | 60.4999 | 2023-04-13 | L2 | 0.98
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 74.66 | UG/L | 80.4999 | 2023-04-13 | L2 | 0.39
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.11 | UG/L | 60.4999 | 2023-07-13 | L3 | 0.98 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 57.33 | UG/L | 80.4999 | 2023-07-13 | L3 | 1 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.83 | UG/L | 60.4999 | 2023-07-13 | L4 | 0.98 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 56.61 | UG/L | 80.4999 | 2023-07-13 | L4 | 1 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.58 | UG/L | 60.4999 | 2023-07-13 | L1 | 0.98 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 54.69 | UG/L | 80.4999 | 2023-07-13 | L1 | 1 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.79 | UG/L | 60.4999 | 2023-07-13 | L2 | 0.98 |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 45.03 | UG/L | 80.4999 | 2023-07-13 | L2 | 1 |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.62 | UG/L | 60.4999 | 2023-10-12 | L4 | 0.98 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 66.81 | UG/L | 80.4999 | 2023-10-12 | L4 | 0.39 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.23 | UG/L | 60.4999 | 2023-10-12 | L3 | 0.98 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 65.38 | UG/L | 80.4999 | 2023-10-12 | L3 | 0.39 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.47 | UG/L | 60.4999 | 2023-10-12 | L1 | 0.98 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 60.12 | UG/L | 80.4999 | 2023-10-12 | L1 | 0.39 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.03 | UG/L | 60.4999 | 2023-10-12 | L2 | 0.98 |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 59.53 | UG/L | 80.4999 | 2023-10-12 | L2 | 0.39 |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 68.04 | UG/L | 80.4999 | 2024-01-11 | L3 | 0.39 |  | SIEMENS BLDG 4400, HAA5: LRAA, 43.1 OEL, 53.04 TTHM: LRAA, 65.41 OEL, 64.70
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 64.85 | UG/L | 60.4999 | 2024-01-11 | L4 | 0.98 |  | BARBARA YING CENTER BLDG 71 HAA5: LRAA 42.09 OEL 50.29 TTHM: LRAA 66.31 OEL 64.61
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 67.55 | UG/L | 80.4999 | 2024-01-11 | L4 | 0.39 |  | BARBARA YING CENTER BLDG 71 HAA5: LRAA 42.09 OEL 50.29 TTHM: LRAA 66.31 OEL 64.61
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 69.4 | UG/L | 60.4999 | 2024-01-11 | L3 | 0.98 |  | SIEMENS BLDG 4400, HAA5: LRAA, 43.1 OEL, 53.04 TTHM: LRAA, 65.41 OEL, 64.70
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 62.48 | UG/L | 60.4999 | 2024-01-11 | L1 | 0.98 |  | ALPHA TAU OMEGA BLDG 410, HAA5: LRAA, 41.025 OEL, 48.50 TTHM: LRAA, 61.47 OEL, 59.73
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 62.07 | UG/L | 80.4999 | 2024-01-11 | L1 | 0.39 |  | ALPHA TAU OMEGA BLDG 410, HAA5: LRAA, 41.025 OEL, 48.50 TTHM: LRAA, 61.47 OEL, 59.73
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.4 | UG/L | 60.4999 | 2024-01-11 | L2 | 0.98 |  | ARENA BLDG 50, HAA5 LRAA, 33.91 OEL, 39.16 TTHM: LRAA, 57.74 OEL, 52.02
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 51.75 | UG/L | 80.4999 | 2024-01-11 | L2 | 0.39 |  | ARENA BLDG 50, HAA5 LRAA, 33.91 OEL, 39.16 TTHM: LRAA, 57.74 OEL, 52.02
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1040 | NITRATE | 0.057 | MG/L | 10.4999 | 2024-02-15 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008-1041 J QUALIFIER - QA/QC REVIEWED, 1041 ACCEPTED AS IS_LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-02-23 | AAA | 0.007 | 0.0149 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-02-23 | AAA | 0.0072 | 0.0249 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-02-23 | AAA | 0.0069 | 0.1499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-02-23 | AAA | 0.12 | 1.4999 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-02-23 | AAA | 0.9 | 1.4999 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-02-23 | AAA | 0.37 | 0.4499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-02-23 | AAA | 0.37 | 9.4999 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-02-23 | AAA | 0.5 | 0.6499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-02-23 | AAA | 1.8 | 2.4999 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-02-23 | AAA | 0.06 | 0.0749 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-02-23 | AAA | 0.5 | 0.6499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-02-23 | AAA | 0.09 | 0.1499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-02-23 | AAA | 0.18 | 0.2499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-02-23 | AAA | 0.019 | 0.1499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-02-23 | AAA | 0.67 | 0.9499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-02-23 | AAA | 0.09 | 0.1499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-02-23 | AAA | 0.15 | 0.2499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-02-23 | AAA | 0.0061 | 0.0449 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-02-23 | AAA | 0.0053 | 0.0249 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-02-23 | AAA | 0.095 | 0.1499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-02-23 | AAA | 0.09 | 0.2499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-02-23 | AAA | 0.0064 | 0.1499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-02-23 | AAA | 0.015 | 0.0249 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-02-23 | AAA | 0.038 | 0.0449 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-02-23 | AAA | 0.094 | 0.1499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-02-23 | AAA | 0.0061 | 0.0249 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-02-23 | AAA | 0.009 | 0.0149 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-02-23 | AAA | 0.053 | 0.2499 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 65.23 | UG/L | 80.4999 | 2024-04-11 | L1 | 0.39 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-02-15 | AAA | 0.0034 |  | LOCATION CODE SET BY PWS - 03/10/2008-1041 J QUALIFIER - QA/QC REVIEWED, 1041 ACCEPTED AS IS_LMC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | S | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-02-23 | AAA | 5.9 | 6.4999 | 2023 MAKE-UP SAMPLES, GLYPHOSPHATE (2034) OVER HOLD TIME_LMC. GLYPHOSATE ACCEPTED. PER AEL, SAMPLE WAS FROZEN WITHIN 14 DAYS _MFC
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.13 | UG/L | 60.4999 | 2024-04-11 | L4 | 0.98 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 74.05 | UG/L | 80.4999 | 2024-04-11 | L4 | 0.39 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.16 | UG/L | 60.4999 | 2024-04-11 | L3 | 0.98 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 63.66 | UG/L | 80.4999 | 2024-04-11 | L3 | 0.39 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 46.83 | UG/L | 60.4999 | 2024-04-11 | L1 | 0.98 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.1 | UG/L | 60.4999 | 2024-04-11 | L2 | 0.98 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 59.62 | UG/L | 80.4999 | 2024-04-11 | L2 | 0.39 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 70.48 | UG/L | 80.4999 | 2024-07-11 | L3 | 0.39 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.3 | UG/L | 60.4999 | 2024-07-11 | L4 | 0.98 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 69.16 | UG/L | 80.4999 | 2024-07-11 | L4 | 0.39 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.79 | UG/L | 60.4999 | 2024-07-11 | L3 | 0.98 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.009 | UG/L | 60.4999 | 2024-07-11 | L1 | 0.98 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 68.52 | UG/L | 80.4999 | 2024-07-11 | L1 | 0.39 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 50.63 | UG/L | 60.4999 | 2024-07-11 | L2 | 0.98 |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 60.9 | UG/L | 80.4999 | 2024-07-11 | L2 | 0.39 |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.9 | UG/L | 60.4999 | 2024-10-08 | L4 | 0.89 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 67.45 | UG/L | 80.4999 | 2024-10-08 | L4 | 0.39 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.4 | UG/L | 60.4999 | 2024-10-08 | L3 | 0.89 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 67.58 | UG/L | 80.4999 | 2024-10-08 | L3 | 0.39 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.31 | UG/L | 60.4999 | 2024-10-08 | L1 | 0.89 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 63.8 | UG/L | 80.4999 | 2024-10-08 | L1 | 0.39 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 61.37 | UG/L | 80.4999 | 2024-10-08 | L2 | 0.39 |  | ARENA TTHM
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.48 | UG/L | 60.4999 | 2024-10-15 | L2 | 0.98 |  | 4 ARENA RESAMPLE HAA5
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.31 | UG/L | 60.4999 | 2025-01-09 | L4 | 0.98 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 56.46 | UG/L | 80.4999 | 2025-01-09 | L4 | 0.39 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.37 | UG/L | 60.4999 | 2025-01-09 | L3 | 0.98 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 58.94 | UG/L | 80.4999 | 2025-01-09 | L3 | 0.39 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.6 | UG/L | 60.4999 | 2025-01-09 | L1 | 0.98 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 60 | UG/L | 80.4999 | 2025-01-09 | L1 | 0.39 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.41 | UG/L | 60.4999 | 2025-01-09 | L2 | 0.98 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 55.92 | UG/L | 80.4999 | 2025-01-09 | L2 | 0.39 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-22 | AAA |  |  | DIST- POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-22 | AAA |  |  | DIST- POE
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.79 | UG/L | 60.4999 | 2025-04-10 | L4 | 0.98 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 73.95 | UG/L | 80.4999 | 2025-04-10 | L4 | 0.44 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.1 | UG/L | 60.4999 | 2025-04-10 | L3 | 0.98 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 78.12 | UG/L | 80.4999 | 2025-04-10 | L3 | 0.44 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.25 | UG/L | 60.4999 | 2025-04-10 | L1 | 0.98 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 74.18 | UG/L | 80.4999 | 2025-04-10 | L1 | 0.44 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.71 | UG/L | 60.4999 | 2025-04-10 | L2 | 0.98 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 66.85 | UG/L | 80.4999 | 2025-04-10 | L2 | 0.44 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.13 | UG/L | 60.4999 | 2025-07-10 | L3 | 0.98 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 55.05 | UG/L | 80.4999 | 2025-07-10 | L3 | 0.44 |  | SIEMENS
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.1 | UG/L | 60.4999 | 2025-07-10 | L4 | 0.98 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 58.62 | UG/L | 80.4999 | 2025-07-10 | L4 | 0.44 |  | BARBARA YING
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.35 | UG/L | 60.4999 | 2025-07-10 | L1 | 0.98 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 59.01 | UG/L | 80.4999 | 2025-07-10 | L1 | 0.44 |  | ATO
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.27 | UG/L | 60.4999 | 2025-07-10 | L2 | 0.98 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 48.73 | UG/L | 80.4999 | 2025-07-10 | L2 | 0.44 |  | ARENA
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 61.28 | UG/L | 80.4999 | 2025-10-08 | L3 | 0.44 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.44 | UG/L | 60.4999 | 2025-10-08 | L4 | 0.98 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 59.33 | UG/L | 80.4999 | 2025-10-08 | L4 | 0.44 |  | BARBARA YING CENTER BLDG 71
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.23 | UG/L | 60.4999 | 2025-10-08 | L3 | 0.98 |  | SIEMENS BLDG 4400
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.32 | UG/L | 60.4999 | 2025-10-08 | L1 | 0.98 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 58.97 | UG/L | 80.4999 | 2025-10-08 | L1 | 0.44 |  | ALPHA TAU OMEGA BLDG 410
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.73 | UG/L | 60.4999 | 2025-10-08 | L2 | 0.98 |  | ARENA BLDG 50
3480409 | UNIVERSITY OF CENTRAL FLORIDA | D | DBP | 2950 | TOTAL THMS | 58.46 | UG/L | 80.4999 | 2025-10-08 | L2 | 0.44 |  | ARENA BLDG 50
3480502 | VALLEY MHP, THE | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.3 | PCI/L | 15.4999 | 2021-07-21 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-07-21 | AAA |  | 1.4999 | POE
3480502 | VALLEY MHP, THE | N | INOR | 1040 | NITRATE | 1.74 | MG/L | 10.4999 | 2021-07-21 | AAA | 0.2
3480502 | VALLEY MHP, THE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-21 | AAA | 0.2
3480502 | VALLEY MHP, THE | N | INOR | 1005 | ARSENIC | 0.0013 | MG/L | 0.0104 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | INOR | 1010 | BARIUM | 0.0225 | MG/L | 2.4999 | 2021-07-21 | AAA | 0.002
3480502 | VALLEY MHP, THE | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | INOR | 1020 | CHROMIUM | 0.0022 | MG/L | 0.1499 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-07-21 | AAA | 0.005
3480502 | VALLEY MHP, THE | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-07-21 | AAA | 0.2
3480502 | VALLEY MHP, THE | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-07-21 | AAA | 2e-05
3480502 | VALLEY MHP, THE | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-07-21 | AAA | 0.002
3480502 | VALLEY MHP, THE | N | INOR | 1052 | SODIUM | 9.63 | MG/L | 160.4999 | 2021-07-21 | AAA | 0.5
3480502 | VALLEY MHP, THE | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-07-21 | AAA | 0.0005
3480502 | VALLEY MHP, THE | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-07-21 | AAA | 0.01
3480502 | VALLEY MHP, THE | N | SEC | 1017 | CHLORIDE | 21.5 | MG/L | 250.4999 | 2021-07-21 | AAA | 0.4
3480502 | VALLEY MHP, THE | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-07-21 | AAA | 0.001
3480502 | VALLEY MHP, THE | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-07-21 | AAA | 0.2
3480502 | VALLEY MHP, THE | N | SEC | 1028 | IRON | 0.29 | MG/L | 0.3499 | 2021-07-21 | AAA | 0.01
3480502 | VALLEY MHP, THE | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-07-21 | AAA | 0.01
3480502 | VALLEY MHP, THE | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-07-21 | AAA | 0.0005
3480502 | VALLEY MHP, THE | N | SEC | 1055 | SULFATE | 22.5 | MG/L | 250.4999 | 2021-07-21 | AAA | 1
3480502 | VALLEY MHP, THE | N | SEC | 1095 | ZINC | 0.0056 | MG/L | 5.4999 | 2021-07-21 | AAA | 0.002
3480502 | VALLEY MHP, THE | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-07-21 | AAA | 5
3480502 | VALLEY MHP, THE | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-07-21 | AAA | 1
3480502 | VALLEY MHP, THE | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.74 | LN(10) |  | 2021-07-21 | AAA | 0.01
3480502 | VALLEY MHP, THE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 220 | MG/L | 500.4999 | 2021-07-21 | AAA | 2.5
3480502 | VALLEY MHP, THE | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-07-21 | AAA | 0.2
3480502 | VALLEY MHP, THE | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-07-21 | AAA | 0.01 | 0.0149 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-07-21 | AAA | 0.01 | 0.0249 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-07-21 | AAA | 0.05 | 0.1499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-07-21 | AAA | 0.5 | 1.4999 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-07-21 | AAA | 0.1 | 1.4999 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-07-21 | AAA | 0.4 | 0.4499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-07-21 | AAA | 9 | 9.4999 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-07-21 | AAA | 6 | 6.4999 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-07-21 | AAA | 0.6 | 0.6499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-07-21 | AAA | 2 | 2.4999 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-07-21 | AAA | 0.07 | 0.0749 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-07-21 | AAA | 0.6 | 0.6499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-07-21 | AAA | 0.1 | 0.1499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-07-21 | AAA | 0.2 | 0.2499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-07-21 | AAA | 0.1 | 0.1499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-07-21 | AAA | 0.9 | 0.9499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-07-21 | AAA | 0.1 | 0.1499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-07-21 | AAA | 0.2 | 0.2499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-07-21 | AAA | 0.01 | 0.0449 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-07-21 | AAA | 0.01 | 0.0249 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-07-21 | AAA | 0.1 | 0.1499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-07-21 | AAA | 0.2 | 0.2499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-07-21 | AAA | 0.1 | 0.1499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-07-21 | AAA | 0.02 | 0.0249 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-07-21 | AAA | 0.04 | 0.0449 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-07-21 | AAA | 0.1 | 0.1499 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-07-21 | AAA | 0.02 | 0.0249 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-07-21 | AAA | 0.01 | 0.0149 | SOC
3480502 | VALLEY MHP, THE | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-07-21 | AAA | 0.01 | 0.2499 | SOC
3480502 | VALLEY MHP, THE | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0.82 | UG/L | 10499.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-07-21 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.82)
3480502 | VALLEY MHP, THE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.8 | UG/L | 60.4999 | 2021-07-21 | L1 | 1 |  | LOT 27 MARTINGALE | 3
3480502 | VALLEY MHP, THE | D | DBP | 2950 | TOTAL THMS | 1.89 | UG/L | 80.4999 | 2021-07-21 | L1 | 0.5 |  | LOT 27 MARTINGALE | 3
3480502 | VALLEY MHP, THE | N | INOR | 1040 | NITRATE | 1.74 | MG/L | 10.4999 | 2022-02-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480502 | VALLEY MHP, THE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-03-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0.85 | UG/L | 10499.9999 | 2022-04-07 | AAA | 0.5 | 0.5499 | XYLENES 0.85 UG/L
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 1.5 | UG/L | 10499.9999 | 2022-07-21 | AAA | 0.5 | 0.5499 | XYLENES (TOTAL) 1.5 UG/L (HLKD)
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-13 | AAA | 0.5 | 0.5499 | XYLENES (TOTAL) -0- UG/L
3480502 | VALLEY MHP, THE | N | INOR | 1040 | NITRATE | 1.6 | MG/L | 10.4999 | 2023-02-02 | AAA | 0.024 |  | POE - VAL
3480502 | VALLEY MHP, THE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-02 | AAA |  |  | POE - VAL
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-07-12 | AAA |  | 0.5499 | 3Q23 TOT XYLENE
3480502 | VALLEY MHP, THE | N | INOR | 1040 | NITRATE | 1.6 | MG/L | 10.4999 | 2024-05-09 | AAA | 0.2 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1005 | ARSENIC | 0.0011 | MG/L | 0.0104 | 2024-05-09 | AAA | 0.0004 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1010 | BARIUM | 0.025 | MG/L | 2.4999 | 2024-05-09 | AAA | 0.0004 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1020 | CHROMIUM | 0.0007 | MG/L | 0.1499 | 2024-05-09 | AAA | 0.0004 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1025 | FLUORIDE | 0.13 | MG/L | 4.0499 | 2024-05-09 | AAA | 0.025 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1036 | NICKEL | 0.0011 | MG/L | 0.1499 | 2024-05-09 | AAA | 0.0009 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1045 | SELENIUM | 0.0009 | MG/L | 0.0549 | 2024-05-09 | AAA | 0.0005 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2024-05-09 | AAA | 0.13 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1017 | CHLORIDE | 33 | MG/L | 250.4999 | 2024-05-09 | AAA | 0.4 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1022 | COPPER | 0.0039 | MG/L | 1.4999 | 2024-05-09 | AAA | 0.00064 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1025 | FLUORIDE | 0.13 | MG/L | 2.0499 | 2024-05-09 | AAA | 0.025 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1032 | MANGANESE | 0.0026 | MG/L | 0.0549 | 2024-05-09 | AAA | 0.0009 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1050 | SILVER | 0.0002 | MG/L | 0.1499 | 2024-05-09 | AAA | 0 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1055 | SULFATE | 26 | MG/L | 250.4999 | 2024-05-09 | AAA | 2 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1095 | ZINC | 0.0065 | MG/L | 5.4999 | 2024-05-09 | AAA | 0.0013 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2024-05-09 | AAA | 5 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2024-05-09 | AAA | 1 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 140 | MG/L | 500.4999 | 2024-05-09 | AAA | 5 |  | POE
3480502 | VALLEY MHP, THE | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-05-09 | AAA |  |  | POE
3480502 | VALLEY MHP, THE | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-05-09 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-07-31 | L1 | 0.3 |  | LOT 27 MARTINGALE LANE TTHM & HAA5 | 3
3480502 | VALLEY MHP, THE | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-07-31 | L1 | 0.5 |  | LOT 27 MARTINGALE LANE TTHM & HAA5 | 3
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-27 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-07-15 | AAA |  | 0.5499 | POE
3480502 | VALLEY MHP, THE | N | INOR | 1040 | NITRATE | 1.7 | MG/L | 10.4999 | 2025-10-23 | AAA | 0.1 |  | POE
3480502 | VALLEY MHP, THE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-23 | AAA |  |  | POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-09 | AAA |  |  | POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-09 | AAA |  |  | POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-09-20 | AAA | 0.2 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-09-20 | AAA | 0.2 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-09-20 | AAA | 0.002 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1010 | BARIUM | 0.001 | MG/L | 2.4999 | 2022-09-20 | AAA | 0.002 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-09-20 | AAA | 0.001 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-09-20 | AAA | 0.005 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1025 | FLUORIDE | 0.39 | MG/L | 4.0499 | 2022-09-20 | AAA | 0.2 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-09-20 | AAA | 0.001 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-09-20 | AAA | 0.001 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-09-20 | AAA | 0.002 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-09-20 | AAA | 0.002 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1052 | SODIUM | 5.8 | MG/L | 160.4999 | 2022-09-20 | AAA | 0.1 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-09-20 | AAA | 0.001 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-09-20 | AAA | 0.0005 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-09-20 | AAA | 0.005 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-09-20 | AAA | 0.1
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1017 | CHLORIDE | 13 | MG/L | 250.4999 | 2022-09-20 | AAA | 0.4
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1022 | COPPER | 0.044 | MG/L | 1.4999 | 2022-09-20 | AAA | 0.001
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1025 | FLUORIDE | 0.39 | MG/L | 2.0499 | 2022-09-20 | AAA | 0.2
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-09-20 | AAA | 0.011
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-09-20 | AAA | 0.1
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-09-20 | AAA | 0.005
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2022-09-20 | AAA | 2
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-09-20 | AAA | 0.002
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2022-09-20 | AAA | 5
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-09-20 | AAA | 1
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 190 | MG/L | 500.4999 | 2022-09-20 | AAA | 5
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-09-20 | AAA | 0.2
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 0.5 | 0.5499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.0149
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.01 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-09-20 | AAA | 0.05 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 1.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 0.5 | 1.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 9 | 9.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-09-20 | AAA | 3.4 | 6.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-09-20 | AAA | 0.2 | 0.6499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 2 | 2.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-09-20 | AAA | 0.031 | 0.0749
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-09-20 | AAA | 0.1 | 0.6499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-09-20 | AAA | 0.7 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-09-20 | AAA | 0.8 | 0.2499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-09-20 | AAA | 0.9 | 0.9499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.01 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.2499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2022-09-20 | AAA | 0.01 | 0.0055
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-09-20 | AAA | 0.01 | 0.0449
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.01 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-09-20 | AAA | 0.05 | 0.2499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.012 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.02 | 0.0449
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.02 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-09-20 | AAA | 0.01 | 0.0149
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.2499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1025 | FLUORIDE | 0.39 | MG/L | 2.0499 | 2022-09-20 | AAA | 0.2 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-09-20 | AAA | 0.01 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1017 | CHLORIDE | 13 | MG/L | 250.4999 | 2022-09-20 | AAA | 0.04 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1022 | COPPER | 0.044 | MG/L | 1.4999 | 2022-09-20 | AAA | 0.001 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-09-20 | AAA | 0.011 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-09-20 | AAA | 0.01 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-09-20 | AAA | 0.0005 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1055 | SULFATE | 3.2 | MG/L | 250.4999 | 2022-09-20 | AAA | 2 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-09-20 | AAA | 0.002 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2022-09-20 | AAA | 5 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-09-20 | AAA | 1 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 190 | MG/L | 500.4999 | 2022-09-20 | AAA | 5 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-09-20 | AAA | 0.2 |  | PH Q QUALIFIER
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.0149
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.01 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-09-20 | AAA | 0.05 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 1.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 0.5 | 1.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 9 | 9.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-09-20 | AAA | 3.4 | 6.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-09-20 | AAA | 0.02 | 0.6499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 2 | 2.4999
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-09-20 | AAA | 0.031 | 0.0749
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-09-20 | AAA | 0.1 | 0.6499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-09-20 | AAA | 0.07 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-09-20 | AAA | 0.08 | 0.2499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-09-20 | AAA | 0.9 | 0.9499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.01 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.2499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-09-20 | AAA | 0.01 | 0.0449
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.01 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-09-20 | AAA | 0.05 | 0.2499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.012 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.02 | 0.0449
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-09-20 | AAA | 0.1 | 0.1499
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.02 | 0.0249
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-09-20 | AAA | 0.01 | 0.0149
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-09-20 | AAA | 0.001 |  | MISSING DIQUAT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-08 | AAA | 0.4 | 0.4499 | MAKE UP SAMPLE FOR MISSED MONITORING IN 2022_CC
3480457 | LAKESIDE COTTAGES AND RV PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.2 | UG/L | 60.4999 | 2023-07-05 | L1 | 0.28 |  | 2023 ANNUAL | 3
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-06-06 | AAA |  |  | SSP-POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-06-06 | AAA |  |  | SSP-POE
3480457 | LAKESIDE COTTAGES AND RV PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.1 | UG/L | 60.4999 | 2024-07-03 | L1 | 0.28 |  | 2024 ANNUAL | 3
3480457 | LAKESIDE COTTAGES AND RV PARK | D | DBP | 2950 | TOTAL THMS | 12.2 | UG/L | 80.4999 | 2024-07-03 | L1 | 0.5 |  | 2024 ANNUAL | 3
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-04-17 | AAA |  |  | POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-17 | AAA |  |  | POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-06-18 | AAA | 0.1 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-06-18 | AAA | 0.1 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-06-18 | AAA | 0.005 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1040 | NITRATE | 0.3 | MG/L | 10.4999 | 2023-04-11 | AAA | 0.2 |  | 2023 POE N/N
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-11 | AAA | 0.2 |  | 2023 POE N/N
3480457 | LAKESIDE COTTAGES AND RV PARK | D | DBP | 2950 | TOTAL THMS | 24.5 | UG/L | 80.4999 | 2023-07-05 | L1 | 0.5 |  | 2023 ANNUAL | 3
3480457 | LAKESIDE COTTAGES AND RV PARK | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.4 | UG/L | 60.4999 | 2025-03-20 | L1 |  |  | TAKEN OUTSIDE OF MONITORING PERIOD | 3
3480457 | LAKESIDE COTTAGES AND RV PARK | S | DBP | 2950 | TOTAL THMS | 17.2 | UG/L | 80.4999 | 2025-03-20 | L1 |  |  | TAKEN OUTSIDE OF MONITORING PERIOD | 3
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-06-18 | AAA | 0.00035 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1010 | BARIUM | 0.0067 | MG/L | 2.4999 | 2025-06-18 | AAA | 0.00033 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-06-18 | AAA | 0.00022 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1020 | CHROMIUM | 0.0027 | MG/L | 0.1499 | 2025-06-18 | AAA | 0.00035 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2025-06-18 | AAA | 0.1 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-06-18 | AAA | 0.00022 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-06-18 | AAA | 0.0002 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-06-18 | AAA | 0.00082 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-06-18 | AAA | 0.0009 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2025-06-18 | AAA | 0.12 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-06-18 | AAA | 0.00037 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-06-18 | AAA | 0.00029 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-06-18 | AAA | 0.00031 |  | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1002 | ALUMINUM | 0.0036 | MG/L | 0.2499 | 2025-06-18 | AAA | 0.0031 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1017 | CHLORIDE | 20 | MG/L | 250.4999 | 2025-06-18 | AAA | 0.2 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1022 | COPPER | 0.0006 | MG/L | 1.4999 | 2025-06-18 | AAA | 0.00058 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1025 | FLUORIDE | 0.18 | MG/L | 2.0499 | 2025-06-18 | AAA | 0.1 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2025-06-18 | AAA | 0.054 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2025-06-18 | AAA | 0.0076 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2025-06-18 | AAA | 3e-05 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1055 | SULFATE | 77 | MG/L | 250.4999 | 2025-06-18 | AAA | 0.5 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1095 | ZINC | 0.0018 | MG/L | 5.4999 | 2025-06-18 | AAA | 0.0012 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2025-06-18 | AAA | 5 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1920 | ODOR THRESHOLD | 5 |  | 3.4999 | 2025-06-18 | AAA | 5 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2025-06-18 | AAA | 0.1 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 290 | MG/L | 500.4999 | 2025-06-18 | AAA | 5 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SEC | 2905 | FOAMING AGENTS | 0.051 |  | 0.5499 | 2025-06-18 | AAA | 0.026 |  | LC - POE, 1920 EXCEEDANCE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-06-18 | AAA | 0.29 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-06-18 | AAA | 0.19 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-06-18 | AAA | 0.5 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-06-18 | AAA | 0.5 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-06-18 | AAA | 0.32 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-06-18 | AAA | 0.27 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.4 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-06-18 | AAA | 0.39 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 0.33 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.23 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-06-18 | AAA | 0.16 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.28 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-06-18 | AAA | 0.43 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.34 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-06-18 | AAA | 0.39 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.37 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 0.3 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.17 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-06-18 | AAA | 0.23 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-06-18 | AAA | 0.24 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 0.24 | 0.5499 | LC - POE
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-06-18 | AAA | 0.01 | 0.0149 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2031 | DALAPON | 0.37 | UG/L | 249.9999 | 2025-06-18 | AAA | 0.022 | 1.4999 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.01 | 0.0249 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-06-18 | AAA | 0.05 | 0.1499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.5 | 1.4999 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-06-18 | AAA | 0.4 | 0.4499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 9 | 9.4999 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-06-18 | AAA | 6 | 6.4999 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-06-18 | AAA | 0.6 | 0.6499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-06-18 | AAA | 0.4 | 2.4999 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-06-18 | AAA | 0.07 | 0.0749 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-06-18 | AAA | 0.6 | 0.6499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-06-18 | AAA | 0.019 | 0.1499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-06-18 | AAA | 0.028 | 0.2499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-06-18 | AAA | 0.1 | 0.1499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-06-18 | AAA | 0.4 | 0.9499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.1 | 0.1499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-06-18 | AAA | 0.2 | 0.2499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-06-18 | AAA | 0.01 | 0.0449 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.01 | 0.0249 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-06-18 | AAA | 0.022 | 0.1499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-06-18 | AAA | 0.035 | 0.2499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.1 | 0.1499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.02 | 0.0249 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.017 | 0.0449 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-06-18 | AAA | 0.1 | 0.1499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.02 | 0.0249 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-06-18 | AAA | 0.01 | 0.0149 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-06-18 | AAA | 0.01 | 0.2499 | LC - POE, 2031 DETECT
3480457 | LAKESIDE COTTAGES AND RV PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.48 | UG/L | 60.4999 | 2025-07-08 | L1 | 0.2 |  | SSP-TRAILER SPIGOT | 3
3480457 | LAKESIDE COTTAGES AND RV PARK | D | DBP | 2950 | TOTAL THMS | 30.81 | UG/L | 80.4999 | 2025-07-08 | L1 | 0.21 |  | SSP-TRAILER SPIGOT | 3
3484304 | BUNKER HILL CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-30 | AAA |  |  | POE
3484304 | BUNKER HILL CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-30 | AAA |  |  | POE
3484304 | BUNKER HILL CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484304 | BUNKER HILL CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484304 | BUNKER HILL CENTER | N | INOR | 1040 | NITRATE | 0.18 | MG/L | 10.4999 | 2023-01-19 | AAA | 0.024 |  | POE
3484304 | BUNKER HILL CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-19 | AAA |  |  | POE
3484304 | BUNKER HILL CENTER | N | INOR | 1040 | NITRATE | 2.5 | MG/L | 10.4999 | 2024-03-20 | AAA | 0.2 |  | POE
3484304 | BUNKER HILL CENTER | N | INOR | 1041 | NITRITE | 0.25 | MG/L | 1.4999 | 2024-03-20 | AAA | 0.2 |  | POE
3484304 | BUNKER HILL CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-24 | AAA |  |  | POE
3484304 | BUNKER HILL CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-24 | AAA |  |  | POE
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-02-01 | AAA
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-01 | AAA
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1040 | NITRATE | 0.46 | MG/L | 10.4999 | 2022-02-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1040 | NITRATE | 0.19 | MG/L | 10.4999 | 2023-01-31 | AAA | 0.024 |  | POE
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | AAA |  |  | POE
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-26 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE_2024 MAKEUP SAMPLES
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE_2024 MAKEUP SAMPLES
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-11-12 | AAA |  |  | POE
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1040 | NITRATE | 0.091 | MG/L | 10.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480458 | LAKE APOPKA PLACE LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-12 | AAA |  |  | POE
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-05 | AAA |  |  | POE
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-05 | AAA |  |  | POE
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1040 | NITRATE | 0.079 | MG/L | 10.4999 | 2023-10-10 | AAA | 0.024 |  | POE
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-10 | AAA |  |  | POE
3484317 | CIRCLE K #7514/CHRISTMAS | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-03 | AAA |  |  | DIST
3484317 | CIRCLE K #7514/CHRISTMAS | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-03 | AAA |  |  | DIST
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2025-01-28 | AAA | 0.024 |  | POE
3484317 | CIRCLE K #7514/CHRISTMAS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-28 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484321 | PREMIER ACADEMY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484321 | PREMIER ACADEMY | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.88 | UG/L | 60.4999 | 2022-08-11 | L1 | 0.98 |  | SPIGOT AT REAR BLDG ( ) | 3
3484321 | PREMIER ACADEMY | D | DBP | 2950 | TOTAL THMS | 1.97 | UG/L | 80.4999 | 2022-08-11 | L1 | 0.39 |  | SPIGOT AT REAR BLDG ( ) | 3
3484321 | PREMIER ACADEMY | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2022-10-31 | AAA | 0.003 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2022-10-31 | AAA | 0.0099 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2022-10-31 | AAA | 0.8 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-10-31 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-31 | AAA |  | 0.0149 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-31 | AAA |  | 0.1499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 1.4999 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-31 | AAA |  | 1.4999 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-31 | AAA |  | 0.4499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 9.4999 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-31 | AAA |  | 6.4999 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-31 | AAA |  | 0.6499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-31 | AAA |  | 2.4999 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-31 | AAA |  | 0.0749 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-31 | AAA |  | 0.6499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-31 | AAA |  | 0.1499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-31 | AAA |  | 0.2499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-31 | AAA |  | 0.1499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-31 | AAA |  | 0.9499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.1499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-31 | AAA |  | 0.2499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-31 | AAA |  | 0.0449 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-31 | AAA |  | 0.1499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-31 | AAA |  | 0.2499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.1499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.0449 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-31 | AAA |  | 0.1499 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-10-31 | AAA |  | 0.0149 | POE
3484321 | PREMIER ACADEMY | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-31 | AAA |  | 0.2499 | POE
3484321 | PREMIER ACADEMY | N | INOR | 1040 | NITRATE | 0.066 | MG/L | 10.4999 | 2023-10-12 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3484321 | PREMIER ACADEMY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3484321 | PREMIER ACADEMY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 P.O.E
3484321 | PREMIER ACADEMY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 P.O.E
3484321 | PREMIER ACADEMY | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.01 | UG/L | 60.4999 | 2025-08-14 | L1 | 0.98 |  | SPIGOT AT REAR BLDG | 3
3484321 | PREMIER ACADEMY | D | DBP | 2950 | TOTAL THMS | 16.72 | UG/L | 80.4999 | 2025-08-14 | L1 | 0.44 |  | SPIGOT AT REAR BLDG | 3
3484321 | PREMIER ACADEMY | N | INOR | 1040 | NITRATE | 0.058 | MG/L | 10.4999 | 2025-10-21 | AAA | 0.024 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2025-10-21 | AAA | 0.003 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1024 | CYANIDE | 0.013 | MG/L | 0.2499 | 2025-10-21 | AAA | 0.002 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1025 | FLUORIDE | 0.21 | MG/L | 4.0499 | 2025-10-21 | AAA | 0.099 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1052 | SODIUM | 19 | MG/L | 160.4999 | 2025-10-21 | AAA | 0.8 |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-10-21 | AAA |  |  | POE
3484321 | PREMIER ACADEMY | N | SEC | 1025 | FLUORIDE | 0.21 | MG/L | 2.0499 | 2025-10-21 | AAA | 0.0099 |  | POE
3484321 | PREMIER ACADEMY | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-10-21 | AAA |  | 0.5499 | POE
3484321 | PREMIER ACADEMY | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.2 | PCI/L | 15.4999 | 2025-10-21 | AAA |  |  | 2025 RADS
3484321 | PREMIER ACADEMY | N | RAD | 4020 | RADIUM-226 | 1.6 | PCI/L | 3.4999 | 2025-10-21 | AAA |  | 1.4999 | 2025 RADS
3484321 | PREMIER ACADEMY | N | RAD | 4030 | RADIUM-228 | 0.7 | PCI/L | 2.4999 | 2025-10-21 | AAA |  | 1.4999 | 2025 RADS
3480664 | CHRISTMAS RV PARK | N | INOR | 1040 | NITRATE | 0.14 | MG/L | 10.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480664 | CHRISTMAS RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480664 | CHRISTMAS RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-05 | AAA |  |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-05 | AAA |  |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1040 | NITRATE | 0.081 | MG/L | 10.4999 | 2023-10-11 | AAA | 0.024 |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-11 | AAA | 0.0034 |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2024-10-21 | AAA | 0.024 |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-21 | AAA |  |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2025-01-28 | AAA | 0.024 |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-28 | AAA |  |  | POE
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-04-27 | AAA |  |  | POE
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-27 | AAA |  |  | POE
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-05-16 | AAA | 0.2 |  | 5/25/22 POE NN
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-05-16 | AAA | 0.2 |  | 5/25/22 POE NN
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 1.8 | MG/L | 10.4999 | 2023-02-28 | AAA | 0.2 |  | POE
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-28 | AAA |  |  | POE
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 2.3 | MG/L | 10.4999 | 2024-02-26 | AAA | 0.2 |  | POE
3480541 | HILLTOP MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-02-26 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | S | DBP | 2950 | TOTAL THMS | 60.5 | UG/L | 80.4999 | 2021-03-25 | L1 | 0.39 |  | 341 HOLIDAY ACRES (HLKD) RCVD 4/21/21 [EXTRA SAMPLE 2MONTH, 4WEEK OF QUARTER] | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.71 | UG/L | 60.4999 | 2021-03-25 | L1 | 0.98 |  | 341 HOLIDAY ACRES (HLKD) RCVD 4/21/21 [EXTRA SAMPLE 2MONTH, 4WEEK OF QUARTER] | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1010 | BARIUM | 0.027 | MG/L | 2.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480664 | CHRISTMAS RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-05 | AAA |  |  | POE
3480664 | CHRISTMAS RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-05 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 97.1 | UG/L | 60.4999 | 2021-02-23 | L1 | 1 |  | LOT 341 (RCVD 3/15/21, ENTD 3/16/21, HLKD) [LRAA TTHM=56.83 ;HAA5=40.58]_VPU | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 93.9 | UG/L | 80.4999 | 2021-02-23 | L1 | 0.5 |  | LOT 341 (RCVD 3/15/21, ENTD 3/16/21, HLKD) [LRAA TTHM=56.83 ;HAA5=40.58]_VPU | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.44 | UG/L | 60.4999 | 2021-05-26 | L1 |  |  | LRAA TTHM=46.14 HAA5=34.168 (LRAA INCLUDING EXTRA 03/2021 SAMPLE: TTHM=49.012 HAA5=31.876) RETURN TO ROUTINE MONITORING_NMS | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 11.26 | UG/L | 80.4999 | 2021-05-26 | L1 |  |  | LRAA TTHM=46.14 HAA5=34.168 (LRAA INCLUDING EXTRA 03/2021 SAMPLE: TTHM=49.012 HAA5=31.876) RETURN TO ROUTINE MONITORING_NMS | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.42 | UG/L | 60.4999 | 2021-08-26 | L1 |  |  |  | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 5.15 | UG/L | 80.4999 | 2021-08-26 | L1 |  |  |  | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1025 | FLUORIDE | 0.28 | MG/L | 4.0499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1052 | SODIUM | 0 | MG/L | 160.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1017 | CHLORIDE | 76 | MG/L | 250.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1025 | FLUORIDE | 0.28 | MG/L | 2.0499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1028 | IRON | 0.056 | MG/L | 0.3499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1055 | SULFATE | 43 | MG/L | 250.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.73 | LN(10) |  | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 382 | MG/L | 500.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 2905 | FOAMING AGENTS | 0.08 |  | 0.5499 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5 | PCI/L | 15.4999 | 2021-12-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-07 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4020 | RADIUM-226 | 1.7 | PCI/L | 3.4999 | 2021-12-07 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-07 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-07 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-07 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-07 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-07 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-07 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-07 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-07 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-07 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-07 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-07 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-07 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-07 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-07 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-07 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-07 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-07 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-07 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-07 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-07 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-07 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-07 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-07 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-07 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-07 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-07 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-07 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-07 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-07 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E2574, E84025
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.92 | UG/L | 60.4999 | 2022-02-23 | L1 |  |  | REPORT RECIEVED, ENTERED LATE_AL TTHM LRAA 47 | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 111.47 | UG/L | 80.4999 | 2022-02-23 | L1 |  |  | REPORT RECIEVED, ENTERED LATE_AL TTHM LRAA 47 | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.92 | UG/L | 60.4999 | 2022-02-23 | L1 |  |  | AL TTHM LRAA 47.09 | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.72 | UG/L | 60.4999 | 2022-05-24 | L1 | 0.98 |  | 341 HOLIDAY ACRES (HLKD) TTHM LRAA 35.48_AL | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 14.03 | UG/L | 80.4999 | 2022-05-24 | L1 | 0.39 |  | 341 HOLIDAY ACRES (HLKD) TTHM LRAA 35.48_AL | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.24 | UG/L | 60.4999 | 2022-08-23 | L1 | 0.98 |  | 341 HOLIDAY ACRES (HLKD) | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 12.2 | UG/L | 80.4999 | 2022-08-23 | L1 | 0.39 |  | 341 HOLIDAY ACRES (HLKD) | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-11 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-11 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.06 | UG/L | 60.4999 | 2022-11-25 | L2 |  |  | 342 HOLIDAY ACRES TTHM AND HAA5 4Q22 RESULTS | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 13.96 | UG/L | 80.4999 | 2022-11-25 | L2 |  |  | 342 HOLIDAY ACRES TTHM AND HAA5 4Q22 RESULTS | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.43 | UG/L | 60.4999 | 2022-11-25 | L1 |  |  | 341 HOLIDAY ACRES TTHM AND HAA5 4Q22 RESULTS | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 14.89 | UG/L | 80.4999 | 2022-11-25 | L1 |  |  | 341 HOLIDAY ACRES TTHM AND HAA5 4Q22 RESULTS | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 13.26 | UG/L | 80.4999 | 2023-02-23 | L2 | 0.39 |  | 342 HOLIDAY ACRES DR. | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.99 | UG/L | 60.4999 | 2023-02-23 | L1 | 0.98 |  | 341 HOLIDAY ACRES DR. | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 12.77 | UG/L | 80.4999 | 2023-02-23 | L1 | 0.39 |  | 341 HOLIDAY ACRES DR. | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.33 | UG/L | 60.4999 | 2023-02-23 | L2 | 0.98 |  | 342 HOLIDAY ACRES DR. | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.31 | UG/L | 60.4999 | 2023-05-23 | L1 | 0.98 |  |  | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 41.52 | UG/L | 80.4999 | 2023-05-23 | L1 | 0.39 |  |  | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.99 | UG/L | 60.4999 | 2023-05-23 | L2 | 0.98 |  |  | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 40.75 | UG/L | 80.4999 | 2023-05-23 | L2 | 0.39 |  |  | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.17 | UG/L | 60.4999 | 2023-08-23 | L1 | 0.98 |  | 341 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 22.58 | UG/L | 80.4999 | 2023-08-23 | L1 | 0.39 |  | 341 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.95 | UG/L | 60.4999 | 2023-08-23 | L2 | 0.98 |  | 342 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 21.97 | UG/L | 80.4999 | 2023-08-23 | L2 | 0.39 |  | 342 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-17 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1040 | NITRATE | 0.083 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.26 | UG/L | 60.4999 | 2023-11-24 | L1 | 0.98 |  | 341 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 8.54 | UG/L | 80.4999 | 2023-11-24 | L1 | 0.39 |  | 341 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.74 | UG/L | 60.4999 | 2023-11-24 | L2 | 0.98 |  | 342 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 9.06 | UG/L | 80.4999 | 2023-11-24 | L2 | 0.39 |  | 342 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 1.28 | UG/L | 80.4999 | 2024-02-26 | L1 | 0.39 |  | 341 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-02-26 | L2 | 0.98 |  | 342 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 1.31 | UG/L | 80.4999 | 2024-02-26 | L2 | 0.39 |  | 342 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-02-26 | L1 | 0.98 |  | 341 HOLIDAY ACRES | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1010 | BARIUM | 0.027 | MG/L | 2.4999 | 2024-09-04 | AAA | 0.003 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2024-09-04 | AAA | 0.024 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1025 | FLUORIDE | 0.25 | MG/L | 4.0499 | 2024-09-04 | AAA | 0.0099 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1052 | SODIUM | 47 | MG/L | 160.4999 | 2024-09-04 | AAA | 0.8 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1017 | CHLORIDE | 71 | MG/L | 250.4999 | 2024-09-04 | AAA | 0.039 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1025 | FLUORIDE | 0.25 | MG/L | 2.0499 | 2024-09-04 | AAA | 0.0099 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1055 | SULFATE | 39 | MG/L | 250.4999 | 2024-09-04 | AAA | 0.034 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1905 | COLOR | 13 | COLOR UNITS | 15.4999 | 2024-09-04 | AAA | 5 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.15 | LN(10) |  | 2024-09-04 | AAA |  |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 370 | MG/L | 500.4999 | 2024-09-04 | AAA | 10 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | SEC | 2905 | FOAMING AGENTS | 0.098 |  | 0.5499 | 2024-09-04 | AAA | 0.04 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-09-04 | AAA |  | 0.667 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.6 | PCI/L | 15.4999 | 2024-09-04 | AAA | 2.3 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4020 | RADIUM-226 | 1.9 | PCI/L | 3.4999 | 2024-09-04 | AAA | 0.3 | 1.4999 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-04 | AAA |  | 1.4999 | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.7 | UG/L | 60.4999 | 2024-11-26 | L1 | 0.98 |  | 341 HOLIDAY ACRES - HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 13.65 | UG/L | 80.4999 | 2024-11-26 | L1 | 0.44 |  | 341 HOLIDAY ACRES - HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1040 | NITRATE | 0.59 | MG/L | 10.4999 | 2025-01-28 | AAA | 0.024 |  | POE
3480555 | UNIVERSITY SUN ESTATES 2&3 | N | INOR | 1041 | NITRITE | 0.64 | MG/L | 1.4999 | 2025-01-28 | AAA | 0.0034 |  | POE
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 52.7 | UG/L | 60.4999 | 2021-08-02 | L1 | 1 |  | 3426 WALKER RD. | 3
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.64 | UG/L | 60.4999 | 2024-11-26 | L2 | 0.98 |  | 342 HOLIDAY ACRES - HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 4
3480555 | UNIVERSITY SUN ESTATES 2&3 | D | DBP | 2950 | TOTAL THMS | 12.93 | UG/L | 80.4999 | 2024-11-26 | L2 | 0.44 |  | 342 HOLIDAY ACRES - HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 4
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 28.6 | UG/L | 80.4999 | 2021-08-02 | L1 | 0.5 |  | 3426 WALKER RD. | 3
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-14 | AAA | 0.1 | 1.4999 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-14 | AAA | 0.01 | 0.0149 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-14 | AAA | 0.01 | 0.0249 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-14 | AAA | 0.05 | 0.1499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-14 | AAA | 0.5 | 1.4999 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-14 | AAA | 0.4 | 0.4499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-14 | AAA | 9 | 9.4999 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-14 | AAA | 6 | 6.4999 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-14 | AAA | 0.6 | 0.6499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-14 | AAA | 0.07 | 0.0749 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-14 | AAA | 0.6 | 0.6499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-14 | AAA | 0.1 | 0.1499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-14 | AAA | 0.2 | 0.2499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-14 | AAA | 0.1 | 0.1499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-14 | AAA | 0.1 | 0.1499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-14 | AAA | 0.2 | 0.2499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-14 | AAA | 0.01 | 0.0449 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-14 | AAA | 0.01 | 0.0249 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-14 | AAA | 0.1 | 0.1499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-14 | AAA | 0.2 | 0.2499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-14 | AAA | 0.1 | 0.1499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-14 | AAA | 0.02 | 0.0249 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-14 | AAA | 0.04 | 0.0449 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-14 | AAA | 0.1 | 0.1499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-14 | AAA | 0.02 | 0.0249 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-14 | AAA | 0.01 | 0.0149 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-14 | AAA | 0.01 | 0.2499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-09 | AAA |  |  | POE
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-09 | AAA |  |  | POE
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS -
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS -
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1040 | NITRATE | 0.31 | MG/L | 10.4999 | 2023-04-11 | AAA | 0.2 |  | POE
3484362 | CENTRAL FLORIDA HEALTH AND REHAB CLINIC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-11 | AAA |  |  | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-14 | AAA | 0.5 | 0.5499 | VOC
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1040 | NITRATE | 0.422 | MG/L | 10.4999 | 2021-11-14 | AAA | 0.2
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-14 | AAA | 0.2
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1010 | BARIUM | 0.0171 | MG/L | 2.4999 | 2021-11-14 | AAA | 0.002
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1020 | CHROMIUM | 0.0019 | MG/L | 0.1499 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-11-14 | AAA | 0.005
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-11-14 | AAA | 0.2
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-11-14 | AAA | 0.0001
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-11-14 | AAA | 0.002
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1052 | SODIUM | 24.3 | MG/L | 160.4999 | 2021-11-14 | AAA | 0.5
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-11-14 | AAA | 0.0005
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-14 | AAA | 0.01
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1017 | CHLORIDE | 33.6 | MG/L | 250.4999 | 2021-11-14 | AAA | 0.4
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1022 | COPPER | 0.0042 | MG/L | 1.4999 | 2021-11-14 | AAA | 0.001
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-11-14 | AAA | 0.2
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1028 | IRON | 0.0862 | MG/L | 0.3499 | 2021-11-14 | AAA | 0.01
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1032 | MANGANESE | 0.0143 | MG/L | 0.0549 | 2021-11-14 | AAA | 0.01
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-11-14 | AAA | 0.0005
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1055 | SULFATE | 7.88 | MG/L | 250.4999 | 2021-11-14 | AAA | 1
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1095 | ZINC | 0.0287 | MG/L | 5.4999 | 2021-11-14 | AAA | 0.002
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-11-14 | AAA | 5
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-11-14 | AAA | 1
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.83 | LN(10) |  | 2021-11-14 | AAA | 0.01
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 262 | MG/L | 500.4999 | 2021-11-14 | AAA | 2.5
3480681 | HARRISON'S TRAILER PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-11-14 | AAA | 0.2
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-14 | AAA |  | 2.4999 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-14 | AAA |  | 0.9499 | 27 OF 29 SOCS ENTD (OXAMYL & CARBOFURAN HAVE J QUALIFIERS W/NO EXPLANATION-NOT ENTD) HLKD
3480681 | HARRISON'S TRAILER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8.4 | PCI/L | 15.4999 | 2021-12-17 | AAA
3480681 | HARRISON'S TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 2.7 | PCI/L | 3.4999 | 2021-12-17 | AAA |  | 1.4999
3480681 | HARRISON'S TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-17 | AAA |  | 1.4999
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 6.6 | UG/L | 80.4999 | 2022-08-09 | L1 | 0.5 |  | 3426 WALKER RD TTHM (HAA5 J QUALIFERS ON CONSTIUENT ACIDS) | 3
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1040 | NITRATE | 0.41 | MG/L | 10.4999 | 2022-08-09 | AAA | 0.2 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.7 | UG/L | 60.4999 | 2023-08-09 | L1 | 2 |  | 3426 WALKER RD. | 3
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 0.54 | UG/L | 80.4999 | 2023-08-09 | L1 | 0.5 |  | 3426 WALKER RD. | 3
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1040 | NITRATE | 0.66 | MG/L | 10.4999 | 2023-09-26 | AAA | 0.2 |  | POE
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-09-26 | AAA |  |  | POE
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.4 | UG/L | 60.4999 | 2024-08-12 | L1 | 0.3 |  | 3426 WALKER RD. | 3
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 6.6 | UG/L | 80.4999 | 2024-08-12 | L1 | 0.5 |  | 3426 WALKER RD. | 3
3480681 | HARRISON'S TRAILER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.5 | PCI/L | 15.4999 | 2024-10-25 | AAA | 1.8 |  | POE
3480681 | HARRISON'S TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-10-25 | AAA |  | 1.4999 | POE
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1040 | NITRATE | 0.68 | MG/L | 10.4999 | 2024-10-31 | AAA | 0.2 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1005 | ARSENIC | 0.0009 | MG/L | 0.0104 | 2024-10-31 | AAA | 0.0004 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1010 | BARIUM | 0.016 | MG/L | 2.4999 | 2024-10-31 | AAA | 0.0003 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1020 | CHROMIUM | 0.0009 | MG/L | 0.1499 | 2024-10-31 | AAA | 0.0004 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2024-10-31 | AAA | 0.2 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1036 | NICKEL | 0.0009 | MG/L | 0.1499 | 2024-10-31 | AAA | 0.0008 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1052 | SODIUM | 25 | MG/L | 160.4999 | 2024-10-31 | AAA | 0.12 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1017 | CHLORIDE | 35 | MG/L | 250.4999 | 2024-10-31 | AAA | 0.4 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1022 | COPPER | 0.0026 | MG/L | 1.4999 | 2024-10-31 | AAA | 0.0006 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2024-10-31 | AAA | 0.2 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1032 | MANGANESE | 0.015 | MG/L | 0.0549 | 2024-10-31 | AAA | 0.0009 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1055 | SULFATE | 11 | MG/L | 250.4999 | 2024-10-31 | AAA | 2 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1095 | ZINC | 0.072 | MG/L | 5.4999 | 2024-10-31 | AAA | 0.0012 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.1 | LN(10) |  | 2024-10-31 | AAA | 0.01 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 230 | MG/L | 500.4999 | 2024-10-31 | AAA | 5 |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-10-31 | AAA |  |  | POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-10-31 | AAA |  | 0.5499 | POE
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1040 | NITRATE | 0.63 | MG/L | 10.4999 | 2025-10-14 | AAA | 0.1 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE-HTP
3480681 | HARRISON'S TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-14 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE-HTP
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2021-04-28 | AAA
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 28.7 | UG/L | 80.4999 | 2022-11-07 | L1 | 0.5 |  | 3426 WALKER RD. (HLKD) | 3
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.8 | UG/L | 60.4999 | 2022-11-07 | L1 | 1.6 |  | 3426 WALKER RD. (HLKD) | 3
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-10-22 | L1 | 0.2 |  | 3426 WALKER RD. | 3
3480681 | HARRISON'S TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-10-22 | L1 | 0.21 |  | 3426 WALKER RD. | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1040 | NITRATE | 0.694 | MG/L | 10.4999 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1005 | ARSENIC | 0.0041 | MG/L | 0.0104 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1045 | SELENIUM | 0.0031 | MG/L | 0.0549 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1074 | ANTIMONY | 0.0002 | MG/L | 0.0065 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1085 | THALLIUM | 0.0007 | MG/L | 0.0025 | 2021-04-28 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-28 | AAA |  | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1017 | CHLORIDE | 16.5 | MG/L | 250.4999 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1025 | FLUORIDE | 0.18 | MG/L | 2.0499 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1028 | IRON | 0.042 | MG/L | 0.3499 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1032 | MANGANESE | 0.0088 | MG/L | 0.0549 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1055 | SULFATE | 22 | MG/L | 250.4999 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.71 | LN(10) |  | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 339 | MG/L | 500.4999 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 2905 | FOAMING AGENTS | 0.011 |  | 0.5499 | 2021-04-28 | AAA |  |  | CORRECTED IRON FROM -0- TO 0.042 1/14/22-BB
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-28 | AAA |  | 0.0149 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-28 | AAA |  | 0.0249 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-28 | AAA |  | 0.1499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-04-28 | AAA |  | 1.4999 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-04-28 | AAA |  | 1.4999 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-04-28 | AAA |  | 0.4499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-04-28 | AAA |  | 9.4999 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-04-28 | AAA |  | 6.4999 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0.45 | UG/L | 449.9999 | 2021-04-28 | AAA |  | 0.6499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-04-28 | AAA |  | 2.4999 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-28 | AAA |  | 0.0749 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-28 | AAA |  | 0.6499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-04-28 | AAA |  | 0.1499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-04-28 | AAA |  | 0.2499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-28 | AAA |  | 0.1499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-04-28 | AAA |  | 0.9499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-28 | AAA |  | 0.1499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-28 | AAA |  | 0.2499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-28 | AAA |  | 0.0449 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-28 | AAA |  | 0.0249 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-04-28 | AAA |  | 0.1499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-04-28 | AAA |  | 0.2499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-28 | AAA |  | 0.1499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-04-28 | AAA |  | 0.0449 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-04-28 | AAA |  | 0.0249 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0.01 | UG/L | 0.0249 | 2021-04-28 | AAA |  | 0.0149 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-04-28 | AAA |  | 0.2499 | 2015 & 2051 J-QUALIFIED BUT % RECOVERY IS ACCEPTABLE_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 6 | PCI/L | 15.4999 | 2021-04-28 | AAA |  |  | RADS NEXT DUE 2027_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | RAD | 4020 | RADIUM-226 | 1.9 | PCI/L | 3.4999 | 2021-04-28 | AAA |  | 1.4999 | RADS NEXT DUE 2027_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-28 | AAA |  | 1.4999 | RADS NEXT DUE 2027_NMS
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9 | UG/L | 60.4999 | 2021-08-16 | L2 | 1.43 |  | 16201 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 32.18 | UG/L | 80.4999 | 2021-08-16 | L1 | 0.84 |  | 16260 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2941 | CHLOROFORM | 11.28 | UG/L | 100 | 2021-08-16 | L1 | 0.26 |  | 16260 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2942 | BROMOFORM | 1.22 | UG/L | 100 | 2021-08-16 | L1 | 0.25 |  | 16260 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2943 | BROMODICHLOROMETHANE | 11.98 | UG/L | 100 | 2021-08-16 | L1 | 0.32 |  | 16260 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 7.7 | UG/L | 100 | 2021-08-16 | L1 | 0.25 |  | 16260 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-08-17 | AAA |  | 0.0249
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-08-17 | AAA |  | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1015 | CADMIUM | 0.0002 | MG/L | 0.0055 | 2021-10-13 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-13 | AAA
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1040 | NITRATE | 1.29 | MG/L | 10.4999 | 2022-03-16 | AAA | 0.004 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-16 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.07 | UG/L | 60.4999 | 2022-08-16 | L2 | 0.84 |  | 16201 LAKE JOHN CIRCLE (LJT1) | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.48 | UG/L | 60.4999 | 2022-08-16 | L1 |  |  | 16260 LAKE JOHN CIRCLE (LJ3) | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1040 | NITRATE | 0.504 | MG/L | 10.4999 | 2023-01-18 | AAA | 0.004 |  | POE
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1041 | NITRITE | 0.004 | MG/L | 1.4999 | 2023-01-18 | AAA | 0.004 |  | POE
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.25 | UG/L | 60.4999 | 2023-08-15 | L2 | 1.43 |  | 16201 LAKE JOHN CIRCLE | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 37.74 | UG/L | 80.4999 | 2023-08-15 | L2 | 0.84 |  | 16201 LAKE JOHN CIRCLE | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.14 | UG/L | 60.4999 | 2023-08-15 | L1 | 1.43 |  | 16260 LAKE JOHN CIRCLE | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 36.74 | UG/L | 80.4999 | 2023-08-15 | L1 | 0.84 |  | 16260 LAKE JOHN CIRCLE | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1040 | NITRATE | 0.737 | MG/L | 10.4999 | 2024-04-22 | AAA | 0.004
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-04-22 | AAA | 0.004
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1005 | ARSENIC | 0.0039 | MG/L | 0.0104 | 2024-04-22 | AAA | 0.0003
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2024-04-22 | AAA | 0.0038
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1015 | CADMIUM | 0.0001 | MG/L | 0.0055 | 2024-04-22 | AAA | 2e-05
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-04-22 | AAA | 0.0042
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-04-22 | AAA | 0.00014
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-04-22 | AAA | 3e-05
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-04-22 | AAA | 0.0082
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1045 | SELENIUM | 0.0015 | MG/L | 0.0549 | 2024-04-22 | AAA | 0.001
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1052 | SODIUM | 15 | MG/L | 160.4999 | 2024-04-22 | AAA | 0.15
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1074 | ANTIMONY | 0.0003 | MG/L | 0.0065 | 2024-04-22 | AAA | 0.00015
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1017 | CHLORIDE | 21.3 | MG/L | 250.4999 | 2024-04-22 | AAA | 0.0055
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 21.52 | UG/L | 80.4999 | 2022-08-16 | L1 | 0.84 |  | 16260 LAKE JOHN CIRCLE (LJ3) | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.14 | UG/L | 60.4999 | 2022-08-16 | L2 | 1.43 |  | 16201 LAKE JOHN CIRCLE (LJT1) | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-04-22 | AAA | 3e-05
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1085 | THALLIUM | 0.0007 | MG/L | 0.0025 | 2024-04-22 | AAA | 0.00014
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-04-22 | AAA | 0.027
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1022 | COPPER | 0.0043 | MG/L | 1.4999 | 2024-04-22 | AAA | 0.0043
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1028 | IRON | 0.035 | MG/L | 0.3499 | 2024-04-22 | AAA | 0.0099
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1032 | MANGANESE | 0.013 | MG/L | 0.0549 | 2024-04-22 | AAA | 0.0034
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-04-22 | AAA | 0.0098
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1055 | SULFATE | 21 | MG/L | 250.4999 | 2024-04-22 | AAA | 0.0053
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-04-22 | AAA | 0.012
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-04-22 | AAA | 1
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-04-22 | AAA | 1
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.61 | LN(10) |  | 2024-04-22 | AAA | 0.01
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 379 | MG/L | 500.4999 | 2024-04-22 | AAA | 1
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-04-22 | AAA | 0.01
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-04-22 | AAA | 0.24 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-04-22 | AAA | 0.16 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-04-22 | AAA | 0.35 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-04-22 | AAA | 0.12 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-04-22 | AAA | 0.21 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-04-22 | AAA | 0.09 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-04-22 | AAA | 0.25 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-04-22 | AAA | 0.18 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-04-22 | AAA | 0.17 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-04-22 | AAA | 0.23 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-04-22 | AAA | 0.17 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-04-22 | AAA | 0.18 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-04-22 | AAA | 0.13 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-22 | AAA | 0.18 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-04-22 | AAA | 0.22 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-22 | AAA | 0.22 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-04-22 | AAA | 0.17 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-04-22 | AAA | 0.1 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-04-22 | AAA | 0.18 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-04-22 | AAA | 0.1 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-04-22 | AAA | 0.22 | 0.5499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-04-22 | AAA | 0.218 | 0.0149
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-04-22 | AAA | 1.44 | 1.4999
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-04-22 | AAA | 0.48 | 0.4499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-04-22 | AAA | 8.21 | 6.4999
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-04-22 | AAA | 0.307 | 0.6499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-04-22 | AAA | 1.67 | 2.4999
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-04-22 | AAA | 0.188 | 0.0749
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-04-22 | AAA | 0.663 | 0.6499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-04-22 | AAA | 0.248 | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-04-22 | AAA | 1.87 | 0.9499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-04-22 | AAA | 0.188 | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-04-22 | AAA | 0.139 | 0.2499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-04-22 | AAA | 0.109 | 0.0449
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-04-22 | AAA | 0.099 | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-04-22 | AAA | 0.0044 | 0.0249
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-06-21 | AAA | 0.049 | 0.0249
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-06-21 | AAA | 0.0392 | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-06-21 | AAA | 0.37 | 1.4999
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-06-21 | AAA | 2.9 | 9.4999
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-06-21 | AAA | 0.44 | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-06-21 | AAA | 0.16 | 0.2499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-06-21 | AAA | 0.0294 | 0.0249
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-06-21 | AAA | 0.33 | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-06-21 | AAA | 0.09 | 0.2499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-06-21 | AAA | 0.06 | 0.0449
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-06-21 | AAA | 0.0882 | 0.1499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-06-21 | AAA | 0.009 | 0.0149
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-06-21 | AAA | 0.333 | 0.2499
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.71 | UG/L | 60.4999 | 2024-08-15 | L1 | 1.43 |  | 16260 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 22.18 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.89 |  | 16260 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.3 | UG/L | 60.4999 | 2024-08-15 | L2 | 1.43 |  | 16201 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 28.37 | UG/L | 80.4999 | 2024-08-15 | L2 | 0.89 |  | 16201 LAKE JOHN CIR | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1025 | FLUORIDE | 0.207 | MG/L | 4.0499 | 2024-08-16 | AAA | 0.002
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SEC | 1025 | FLUORIDE | 0.207 | MG/L | 2.0499 | 2024-08-16 | AAA | 0.002
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-08-16 | AAA | 0.08 | 0.0249
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1024 | CYANIDE | 0.03 | MG/L | 0.2499 | 2024-10-17 | AAA | 0.0014
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1040 | NITRATE | 0.525 | MG/L | 10.4999 | 2025-04-21 | AAA | 0.004 |  | NN - LAKE JOHN SHORES POE
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-21 | AAA | 0.004 |  | NN - LAKE JOHN SHORES POE
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.03 | UG/L | 60.4999 | 2025-08-15 | L1 | 1.43 |  | 16260 LAKE JOHN CIRCLE (LJ3) | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 32.5 | UG/L | 80.4999 | 2025-08-15 | L1 | 0.4 |  | 16260 LAKE JOHN CIRCLE (LJ3) | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8 | UG/L | 60.4999 | 2025-08-15 | L2 | 1.43 |  | 16201 LAKE JOHN CIRCLE | 3
3480700 | OCUD/LAKE JOHN SHORES WTR SYS | D | DBP | 2950 | TOTAL THMS | 33.4 | UG/L | 80.4999 | 2025-08-15 | L2 | 0.4 |  | 16201 LAKE JOHN CIRCLE | 3
3484341 | AGRI-STARTS INC | N | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2021-07-01 | AAA |  |  | DW POE #2
3484341 | AGRI-STARTS INC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-01 | AAA |  |  | DW POE #2
3484341 | AGRI-STARTS INC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-11 | AAA | 0.22 | 0.5499 | MAY END ANNUAL MONITORING FOLLOWING 3 YRS WITH NO DETECTIONS (ATR)
3484341 | AGRI-STARTS INC | N | INOR | 1040 | NITRATE | 1.3 | MG/L | 10.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1010 | BARIUM | 0.0036 | MG/L | 2.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1025 | FLUORIDE | 0.11 | MG/L | 4.0499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1035 | MERCURY | 0.0001 | MG/L | 0.0024 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1052 | SODIUM | 5.1 | MG/L | 160.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1017 | CHLORIDE | 7 | MG/L | 250.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1025 | FLUORIDE | 0.11 | MG/L | 2.0499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1055 | SULFATE | 4.3 | MG/L | 250.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.12 | LN(10) |  | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 70 | MG/L | 500.4999 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SEC | 2905 | FOAMING AGENTS | 0.05 |  | 0.5499 | 2022-08-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-08-09 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-08-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-08-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-08-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-08-09 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-08-09 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-08-09 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-08-09 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-08-09 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-08-09 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-08-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-08-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-08-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-08-09 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-08-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-08-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-09 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-09 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-09 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0.98 | UG/L | 60.4999 | 2022-08-12 | L1 | 0.98 |  | MANAGER'S BATHROOM SINK (HLKD) | 3
3484341 | AGRI-STARTS INC | D | DBP | 2950 | TOTAL THMS | 0.39 | UG/L | 80.4999 | 2022-08-12 | L1 | 0.39 |  | MANAGER'S BATHROOM SINK (HLKD) | 3
3484341 | AGRI-STARTS INC | N | INOR | 1040 | NITRATE | 0.66 | MG/L | 10.4999 | 2023-05-12 | AAA | 0.024 |  | 2023 ANNUAL N/N
3484341 | AGRI-STARTS INC | N | INOR | 1041 | NITRITE | 0.07 | MG/L | 1.4999 | 2023-05-12 | AAA | 0.0034 |  | 2023 ANNUAL N/N
3484341 | AGRI-STARTS INC | N | INOR | 1040 | NITRATE | 2.22 | MG/L | 10.4999 | 2024-10-21 | AAA | 0.5 |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-21 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1040 | NITRATE | 2.6 | MG/L | 10.4999 | 2024-11-06 | AAA | 0.2 |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-06 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1040 | NITRATE | 0.53 | MG/L | 10.4999 | 2025-02-05 | AAA | 0.2 |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1010 | BARIUM | 0.0091 | MG/L | 2.4999 | 2025-02-05 | AAA | 0.00033 |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1020 | CHROMIUM | 0.0004 | MG/L | 0.1499 | 2025-02-05 | AAA | 0.0004 |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1030 | LEAD | 0.0004 | MG/L | 0.0154 | 2025-02-05 | AAA | 0.00022 |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1052 | SODIUM | 5 | MG/L | 160.4999 | 2025-02-05 | AAA | 0.12 |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2025-02-05 | AAA |  |  | POE
3484341 | AGRI-STARTS INC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-02-05 | AAA |  | 0.5499 | POE
3484341 | AGRI-STARTS INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-27 | L1 | 0.2 |  | MANAGER'S BATHROOM SINK | 3
3484341 | AGRI-STARTS INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-08-27 | L1 | 0.21 |  | MANAGER'S BATHROOM SINK | 3
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-11-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1040 | NITRATE | 0.68 | MG/L | 10.4999 | 2023-11-05 | AAA | 0.024 |  | POE
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-05 | AAA |  |  | POE
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1040 | NITRATE | 0.08 | MG/L | 10.4999 | 2024-11-17 | AAA | 0.024 |  | POE
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-17 | AAA |  |  | POE
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2025-11-17 | AAA | 0.024 |  | POE
3484345 | SPEED WORLD DRAGWAY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-17 | AAA |  |  | POE
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-11-17 | WTP1 |  |  | POE WP1 (OVAL 1/WELL 1)
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-17 | WTP1 |  |  | POE WP1 (OVAL 1/WELL 1)
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-30 | WTP1 |  |  | POE WP1 (OVAL 1/WELL 1)
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-30 | WTP1 |  |  | POE WP1 (OVAL 1/WELL 1)
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-12-05 | WTP1 |  |  | POE
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-12-05 | WTP1 |  |  | POE
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-12-05 | WTP1 |  |  | POE WP1 (OVAL 1/WELL 1) POE
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-12-05 | WTP1 |  |  | POE WP1 (OVAL 1/WELL 1) POE
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-11-17 | WTP1 |  |  | POE PL 1
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-17 | WTP1 |  |  | POE PL 1
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-11-17 | WTP1 |  |  | DIST- POE
3484346 | ORLANDO SPEED WORLD (OVAL TRACK) | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-17 | WTP1 |  |  | DIST- POE
3480709 | RODEWAY INN | N | INOR | 1040 | NITRATE | 0.061 | MG/L | 10.4999 | 2021-12-27 | AAA
3480709 | RODEWAY INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-27 | AAA
3480709 | RODEWAY INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480709 | RODEWAY INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480709 | RODEWAY INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-06-15 | AAA |  |  | POE
3480709 | RODEWAY INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-15 | AAA |  |  | POE
3480709 | RODEWAY INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-06-25 | AAA |  |  | POE
3480709 | RODEWAY INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-06-25 | AAA |  |  | POE
3480709 | RODEWAY INN | N | INOR | 1040 | NITRATE | 0.028 | MG/L | 10.4999 | 2025-03-20 | AAA | 0.025 |  | POE
3480709 | RODEWAY INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-20 | AAA |  |  | POE
3480755 | LIME TREE PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-08-04 | AAA |  |  | POE
3480755 | LIME TREE PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-08-04 | AAA |  |  | POE
3480755 | LIME TREE PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-07-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480755 | LIME TREE PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-07-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480755 | LIME TREE PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-07-11 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 POE
3480755 | LIME TREE PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-11 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 POE
3480755 | LIME TREE PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-05-06 | AAA |  |  | POE
3480755 | LIME TREE PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-05-06 | AAA |  |  | POE
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 19.07 | UG/L | 80.4999 | 2021-08-16 | L1 |  |  | FULLER CROSS TTHM | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.58 | UG/L | 60.4999 | 2021-08-16 | L2 |  |  | TEAGARDEN HAA5 | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.7 | UG/L | 60.4999 | 2022-08-16 | L2 | 1.43 |  |  | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 37.08 | UG/L | 80.4999 | 2022-08-16 | L2 | 0.84 |  |  | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.46 | UG/L | 60.4999 | 2022-08-16 | L1 | 1.43 |  |  | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 20.27 | UG/L | 80.4999 | 2022-08-16 | L1 | 0.84 |  |  | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.5 | UG/L | 60.4999 | 2023-08-15 | L2 | 1.43 |  | MWT1 544 TEAGARDEN CT. | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 28.97 | UG/L | 80.4999 | 2023-08-15 | L2 | 0.84 |  | MWT1 544 TEAGARDEN CT. | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.31 | UG/L | 60.4999 | 2023-08-15 | L1 | 1.43 |  | MWN1 542 FULLERS CROSS RD. (THMS ONLY) | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 18.6 | UG/L | 80.4999 | 2023-08-15 | L1 | 0.84 |  | MWN1 542 FULLERS CROSS RD. (THMS ONLY) | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.03 | UG/L | 60.4999 | 2025-08-15 | L2 | 1.43 |  | 544 TEAGARDEN CT. | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 34.9 | UG/L | 80.4999 | 2025-08-15 | L2 | 0.4 |  | 544 TEAGARDEN CT. | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.29 | UG/L | 60.4999 | 2025-08-15 | L1 | 1.43 |  | 542 FULLERS CROSS | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 19.4 | UG/L | 80.4999 | 2025-08-15 | L1 | 0.4 |  | 542 FULLERS CROSS | 3
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1040 | NITRATE | 0.094 | MG/L | 10.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484341 | AGRI-STARTS INC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-08-12 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3480755 | LIME TREE PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-08-24 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480755 | LIME TREE PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-24 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.61 | UG/L | 60.4999 | 2024-08-15 | L2 | 1.43 |  | 544 TEAGARDEN CT. | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 28.96 | UG/L | 80.4999 | 2024-08-15 | L2 | 0.89 |  | 544 TEAGARDEN CT. | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.48 | UG/L | 60.4999 | 2024-08-15 | L1 | 1.43 |  | 542 FULLERS CROSS RD | 3
3480792 | OCUD/MAGNOLIA WOODS CONSEC.WTR SYSTEM | D | DBP | 2950 | TOTAL THMS | 17.8 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.89 |  | 542 FULLERS CROSS RD | 3
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2022-10-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1040 | NITRATE | 0.072 | MG/L | 10.4999 | 2023-11-05 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-05 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1040 | NITRATE | 0.072 | MG/L | 10.4999 | 2023-11-05 | AAA | 0.024 |  | POE
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-05 | AAA |  |  | POE
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-07-27 | AAA
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-27 | AAA
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-04 | AAA |  |  | POE
3484371 | COUNTY LINE MOOSE LODGE #2427 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-04 | AAA |  |  | POE
3484371 | COUNTY LINE MOOSE LODGE #2427 | D | INOR | 1040 | NITRATE | 0.12 | MG/L | 10.4999 | 2025-05-14 | AAA | 0.1 |  | DIST-SP -4 COUNTRY CLUE NOUSE
3484371 | COUNTY LINE MOOSE LODGE #2427 | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-05-14 | AAA |  |  | DIST-SP -4 COUNTRY CLUE NOUSE
3480901 | EVOLVE CHURCH | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480901 | EVOLVE CHURCH | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2021-12-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480901 | EVOLVE CHURCH | N | INOR | 1040 | NITRATE | 0.4 | MG/L | 10.4999 | 2022-12-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480901 | EVOLVE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480901 | EVOLVE CHURCH | N | INOR | 1040 | NITRATE | 0.081 | MG/L | 10.4999 | 2023-10-12 | AAA | 0.024 |  | POE
3480901 | EVOLVE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-12 | AAA |  |  | POE
3480901 | EVOLVE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-18 | AAA |  |  | POE
3480901 | EVOLVE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-18 | AAA |  |  | POE
3480901 | EVOLVE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3480901 | EVOLVE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-31 | WTP2 |  |  | POE
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-31 | WTP2 |  |  | POE
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.5 | UG/L | 60.4999 | 2021-07-08 | L2 | 2 |  | 1310 JOHNS COVE (PAGE 1 NOT SIGNED AT BOTTOM) CHANGE SMP TYPE "S" TO "D" ONCE PG 1 IS COMPLETED. REVISED REPORTS RCVD 1/3/22_MFC | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 26.3 | UG/L | 80.4999 | 2021-07-08 | L2 | 1 |  | 1310 JOHNS COVE (PAGE 1 NOT SIGNED AT BOTTOM) CHANGE SMP TYPE "S" TO "D" ONCE PG 1 IS COMPLETED. REVISED REPORTS RCVD 1/3/22_MFC | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.3 | UG/L | 60.4999 | 2021-07-08 | L1 | 2 |  | ORANGE / BEE ST. (PAGE 1 NOT SIGNED AT BOTTOM) CHANGE SMP TYPE "S" TO "D" ONCE PG 1 IS COMPLETED. REVISED REPORT RCVD 1/3/22. SAMPLING MONTH UPDATED TO JULY_MFC | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 26.5 | UG/L | 80.4999 | 2021-07-08 | L1 | 1 |  | ORANGE / BEE ST. (PAGE 1 NOT SIGNED AT BOTTOM) CHANGE SMP TYPE "S" TO "D" ONCE PG 1 IS COMPLETED. REVISED REPORT RCVD 1/3/22. SAMPLING MONTH UPDATED TO JULY_MFC | 3
3480913 | OAKLAND TOWN OF | S | INOR | 1040 | NITRATE | 0.52 | MG/L | 10.4999 | 2022-01-04 | AAA | 0.03 |  | POE MAKEUP SAMPLES FOR 2021_MFC
3480913 | OAKLAND TOWN OF | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-04 | AAA | 0.018 |  | POE MAKEUP SAMPLES FOR 2021_MFC
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.7 | UG/L | 60.4999 | 2022-07-13 | L1 | 2 |  | ORANGE PLZ & BEE ST TTHM HAA5 | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 52.1 | UG/L | 80.4999 | 2022-07-13 | L1 | 1 |  | ORANGE PLZ & BEE ST TTHM HAA5 | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.3 | UG/L | 60.4999 | 2022-07-13 | L2 | 2 |  | 1310 JOHNS COVE LANE TTHM HAA5 | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 39.4 | UG/L | 80.4999 | 2022-07-13 | L2 | 1 |  | 1310 JOHNS COVE LANE TTHM HAA5 | 3
3480913 | OAKLAND TOWN OF | N | INOR | 1040 | NITRATE | 0.78 | MG/L | 10.4999 | 2022-07-13 | AAA | 0.02 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-07-13 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | RAD | 4006 | COMBINED URANIUM | 1.2 | PCI/L | 20.4999 | 2023-07-11 | AAA | 0.2 | 0.667 | 4006 REPORTED AS 1.2 UG/L NOT IN PCI/L- CORRECTED 9/2023_SG
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.01 | UG/L | 60.4999 | 2023-07-11 | L1 | 0.98 |  | ORANGE AVE. & BEE ST. | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 32.33 | UG/L | 80.4999 | 2023-07-11 | L1 | 0.39 |  | ORANGE AVE. & BEE ST. | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.29 | UG/L | 60.4999 | 2023-07-11 | L2 | 0.98 |  | 1310 JOHNS COVE LANE | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 32.2 | UG/L | 80.4999 | 2023-07-11 | L2 | 0.39 |  | 1310 JOHNS COVE LANE | 3
3480913 | OAKLAND TOWN OF | N | INOR | 1040 | NITRATE | 0.55 | MG/L | 10.4999 | 2023-07-11 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-07-11 | AAA | 0.0034 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1005 | ARSENIC | 0.0013 | MG/L | 0.0104 | 2023-07-11 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2023-07-11 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-07-11 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-07-11 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-07-11 | AAA | 0.004 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2023-07-11 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-07-11 | AAA | 0.0005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-07-11 | AAA | 1e-05 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-07-11 | AAA | 0.01 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-07-11 | AAA | 0.0012 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2023-07-11 | AAA | 0.8 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-07-11 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-07-11 | AAA | 0.002 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-07-11 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-07-11 | AAA | 0.02 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1017 | CHLORIDE | 16 | MG/L | 250.4999 | 2023-07-11 | AAA | 0.039 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1022 | COPPER | 0.027 | MG/L | 1.4999 | 2023-07-11 | AAA | 0.01 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1025 | FLUORIDE | 0.016 | MG/L | 2.0499 | 2023-07-11 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-07-11 | AAA | 0.0067 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-07-11 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-07-11 | AAA | 0.0005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1055 | SULFATE | 24 | MG/L | 250.4999 | 2023-07-11 | AAA | 0.034 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-07-11 | AAA | 0.05 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-07-11 | AAA | 5 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-07-11 | AAA | 1 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.4 | LN(10) |  | 2023-07-11 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 240 | MG/L | 500.4999 | 2023-07-11 | AAA | 10 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SEC | 2905 | FOAMING AGENTS | 0.092 |  | 0.5499 | 2023-07-11 | AAA | 0.04 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | RAD | 4020 | RADIUM-226 | 1.3 | PCI/L | 3.4999 | 2023-07-11 | AAA | 0.3 | 1.4999 | 4006 REPORTED AS 1.2 UG/L NOT IN PCI/L- CORRECTED 9/2023_SG
3480913 | OAKLAND TOWN OF | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-07-11 | AAA | 0.08 | 1.4999 | 4006 REPORTED AS 1.2 UG/L NOT IN PCI/L- CORRECTED 9/2023_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-07-11 | AAA | 0.28 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-07-11 | AAA | 0.32 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-07-11 | AAA | 0.44 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-07-11 | AAA | 0.46 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-07-11 | AAA | 0.26 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-07-11 | AAA | 0.2 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-07-11 | AAA | 0.18 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-07-11 | AAA | 0.28 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-07-11 | AAA | 0.36 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-07-11 | AAA | 0.39 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-07-11 | AAA | 0.23 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-07-11 | AAA | 0.26 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-11 | AAA | 0.28 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-07-11 | AAA | 0.12 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-11 | AAA | 0.24 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-07-11 | AAA | 0.12 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-07-11 | AAA | 0.17 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-07-11 | AAA | 0.22 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-07-11 | AAA | 0.17 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-07-11 | AAA | 0.39 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-07-11 | AAA | 0.0077 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-07-11 | AAA | 0.0079 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-07-11 | AAA | 0.0076 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-07-11 | AAA | 0.13 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-07-11 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-07-11 | AAA | 0.37 | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-07-11 | AAA | 6 | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-07-11 | AAA | 5.9 | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-07-11 | AAA | 0.05 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-07-11 | AAA | 1.8 | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-07-11 | AAA | 0.06 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-07-11 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-07-11 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-07-11 | AAA | 0.18 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-07-11 | AAA | 0.21 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-07-11 | AAA | 0.51 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-07-11 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-07-11 | AAA | 0.15 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-07-11 | AAA | 0.0067 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-07-11 | AAA | 0.0058 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-07-11 | AAA | 0.095 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-07-11 | AAA | 0.09 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-07-11 | AAA | 0.007 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-07-11 | AAA | 0.015 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-07-11 | AAA | 0.038 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-07-11 | AAA | 0.1 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-11 | AAA | 0.0062 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-11 | AAA | 0.0092 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-07-11 | AAA | 0.059 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3480913 | OAKLAND TOWN OF | S | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-02-07 | AAA |  | 0.0149 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-02-07 | AAA |  | 0.0249 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-02-07 | AAA |  | 0.1499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-02-07 | AAA |  | 1.4999 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-02-07 | AAA |  | 1.4999 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-02-07 | AAA |  | 0.4499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-02-07 | AAA |  | 9.4999 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-02-07 | AAA |  | 6.4999 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-02-07 | AAA |  | 0.6499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-02-07 | AAA |  | 2.4999 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-02-07 | AAA |  | 0.0749 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-02-07 | AAA |  | 0.6499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-02-07 | AAA |  | 0.1499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-02-07 | AAA |  | 0.0449 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-07-11 | AAA | 0.26 | 0.5499 | 2955 XYLENE RESULT/QUALIFIER/MDL MISMATCH- CORRECTED_SG
3480913 | OAKLAND TOWN OF | S | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-02-07 | AAA |  | 0.2499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-02-07 | AAA |  | 0.1499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-02-07 | AAA |  | 0.9499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-02-07 | AAA |  | 0.1499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-02-07 | AAA |  | 0.2499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-02-07 | AAA |  | 0.0249 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-02-07 | AAA |  | 0.1499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-02-07 | AAA |  | 0.2499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-02-07 | AAA |  | 0.1499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-02-07 | AAA |  | 0.0249 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-02-07 | AAA |  | 0.0449 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-02-07 | AAA |  | 0.1499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-02-07 | AAA |  | 0.0249 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-02-07 | AAA |  | 0.0149 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | S | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-02-07 | AAA |  | 0.2499 | MAKE UP SAMPLES FOR 2023_LMC
3480913 | OAKLAND TOWN OF | N | INOR | 1040 | NITRATE | 0.095 | MG/L | 10.4999 | 2024-07-23 | AAA | 0.024 |  | POE - NO2-NO3
3480913 | OAKLAND TOWN OF | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-23 | AAA | 0.0034 |  | POE - NO2-NO3
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.54 | UG/L | 60.4999 | 2024-07-30 | L1 | 0.98 |  | ORANGE AVE AND BEE STREET; SUBCONTRACTED TO E84589 (CONTAM. 2456) AND E82535 (CONTAM. 2950) | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 45.21 | UG/L | 80.4999 | 2024-07-30 | L1 | 0.39 |  | ORANGE AVE AND BEE STREET; SUBCONTRACTED TO E84589 (CONTAM. 2456) AND E82535 (CONTAM. 2950) | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.02 | UG/L | 60.4999 | 2024-07-30 | L2 | 0.98 |  | 1310 JOHNS COVE LANE; SUBCONTRACTED TO E84589 (CONTAM. 2456) AND E82535 (CONTAM. 2950) | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 47.45 | UG/L | 80.4999 | 2024-07-30 | L2 | 0.39 |  | 1310 JOHNS COVE LANE; SUBCONTRACTED TO E84589 (CONTAM. 2456) AND E82535 (CONTAM. 2950) | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 38.31 | UG/L | 80.4999 | 2025-07-23 | L2 | 0.39 |  | 1310 JOHNS COVE LANE | 3
3480913 | OAKLAND TOWN OF | N | INOR | 1040 | NITRATE | 0.26 | MG/L | 10.4999 | 2025-03-26 | AAA | 0.024 |  | POE
3480913 | OAKLAND TOWN OF | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-26 | AAA |  |  | POE
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.47 | UG/L | 60.4999 | 2025-07-23 | L1 | 0.98 |  | ORANGE AVE. & BEE ST. | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2950 | TOTAL THMS | 33.16 | UG/L | 80.4999 | 2025-07-23 | L1 | 0.39 |  | ORANGE AVE. & BEE ST. | 3
3480913 | OAKLAND TOWN OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.53 | UG/L | 60.4999 | 2025-07-23 | L2 | 0.98 |  | 1310 JOHNS COVE LANE | 3
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-14 | AAA |  |  | POE
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-14 | AAA |  |  | POE
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1040 | NITRATE | 0.077 | MG/L | 10.4999 | 2023-11-16 | AAA | 0.024 |  | POE -
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-16 | AAA |  |  | POE -
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1040 | NITRATE | 0.077 | MG/L | 10.4999 | 2023-11-16 | AAA | 0.024 |  | POE - CG
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-16 | AAA |  |  | POE - CG
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1040 | NITRATE | 2.9 | MG/L | 10.4999 | 2024-02-26 | AAA | 0.2 |  | POE
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-02-26 | AAA |  |  | POE
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1040 | NITRATE | 1.9 | MG/L | 10.4999 | 2025-08-27 | AAA | 0.1 |  | POE
3484379 | CHEVRON GAS / LINAS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-27 | AAA | 0.1 |  | POE
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1052 | SODIUM | 24.7 | MG/L | 160.4999 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2022-04-19 | WTP2 |  |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-04-19 | WTP2 |  | 0.5499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-04-19 | WTP2 |  | 0.0149 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-04-19 | WTP2 |  | 0.0249 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-04-19 | WTP2 |  | 0.1499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-04-19 | WTP2 |  | 1.4999 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-04-19 | WTP2 |  | 1.4999 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-04-19 | WTP2 |  | 0.4499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-04-19 | WTP2 |  | 9.4999 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-04-19 | WTP2 |  | 6.4999 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-04-19 | WTP2 |  | 0.6499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-04-19 | WTP2 |  | 2.4999 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-04-19 | WTP2 |  | 0.0749 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-04-19 | WTP2 |  | 0.6499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-04-19 | WTP2 |  | 0.1499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-04-19 | WTP2 |  | 0.2499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-04-19 | WTP2 |  | 0.1499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-04-19 | WTP2 |  | 0.9499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-04-19 | WTP2 |  | 0.1499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-04-19 | WTP2 |  | 0.2499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-04-19 | WTP2 |  | 0.0449 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-04-19 | WTP2 |  | 0.0249 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-04-19 | WTP2 |  | 0.1499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-04-19 | WTP2 |  | 0.2499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-04-19 | WTP2 |  | 0.1499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-04-19 | WTP2 |  | 0.0249 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-04-19 | WTP2 |  | 0.0149 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-04-19 | WTP2 |  | 0.0449 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-04-19 | WTP2 |  | 0.1499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-04-19 | WTP2 |  | 0.0249 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-04-19 | WTP2 |  | 0.2499 | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | D | DBP | 2950 | TOTAL THMS | 3.17 | UG/L | 80.4999 | 2022-08-08 | L1 | 0.5 |  | REAR MEN'S RESTROOM (J QUALIFIERS ON 4 OF 5 HAA'S, HAA LAB MDLS EXCEED REGULATORY MRLS, DISCREPANCIES IN ANALYTICAL METHODS & ANALYSIS DATES BETWEEN HAA ACIDS & TOTAL HAA5) HAS QC PGS | 3
3480911 | HERMANN ENGELMANN #6 | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.3 | UG/L | 60.4999 | 2022-12-09 | L1 | 1.6 |  | MAKE UP DBP SAMPLE FOR MISSED DBPS DUE TO EUROFINS_CC | 3
3480911 | HERMANN ENGELMANN #6 | S | DBP | 2950 | TOTAL THMS | 5.6 | UG/L | 80.4999 | 2022-12-09 | L1 | 0.5 |  | MAKE UP DBP FOR MISSED DBPS DUE TO EUROFINS_CC | 3
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-17 | WTP2 |  |  | POE - HE #6
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-17 | WTP2 |  |  | POE - HE #6
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1040 | NITRATE | 2.9 | MG/L | 10.4999 | 2024-02-26 | AAA | 0.2 |  | POE - HE #6
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-02-26 | AAA |  |  | POE - HE #6
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-07-24 | WTP2 | 0.00025 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-07-24 | WTP2 |  |  | J-QUALIFIED ACCEPTED
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-07-24 | WTP2 |  |  | J-QUALIFIED ACCEPTED
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-07-24 | WTP2 |  | 0.5499 | J-QUALIFIED ACCEPTED
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1005 | ARSENIC | 0.0008 | MG/L | 0.0104 | 2025-07-24 | WTP2 | 0.00039 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2025-07-24 | WTP2 | 0.00037 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1020 | CHROMIUM | 0.001 | MG/L | 0.1499 | 2025-07-24 | WTP2 | 0.00039 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-07-24 | WTP2 | 0.0005 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2025-07-24 | WTP2 | 0.1 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1030 | LEAD | 0.0003 | MG/L | 0.0154 | 2025-07-24 | WTP2 | 0.00024 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-07-24 | WTP2 | 0.0002 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1036 | NICKEL | 0.003 | MG/L | 0.1499 | 2025-07-24 | WTP2 | 0.00092 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-07-24 | WTP2 | 0.001 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1052 | SODIUM | 47 | MG/L | 160.4999 | 2025-07-24 | WTP2 | 0.13 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-07-24 | WTP2 | 0.00041 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-07-24 | WTP2 | 0.00032 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-07-24 | WTP2 | 0.00035 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-07-24 | WTP2 | 0.29 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-07-24 | WTP2 | 0.19 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | SEC | 1025 | FLUORIDE | 0.17 | MG/L | 2.0499 | 2025-07-24 | WTP2 | 0.1 |  | NEW WP POE ACCPTD 7/09
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-07-24 | WTP2 | 0.5 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-07-24 | WTP2 | 0.5 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-07-24 | WTP2 | 0.32 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-07-24 | WTP2 | 0.27 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-07-24 | WTP2 | 0.39 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-07-24 | WTP2 | 0.33 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-07-24 | WTP2 | 0.23 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-07-24 | WTP2 | 0.16 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-07-24 | WTP2 | 0.28 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-07-24 | WTP2 | 0.43 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-07-24 | WTP2 | 0.34 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-07-24 | WTP2 | 0.39 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-07-24 | WTP2 | 0.37 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-07-24 | WTP2 | 0.3 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-07-24 | WTP2 | 0.17 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-07-24 | WTP2 | 0.23 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-07-24 | WTP2 | 0.24 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1010 | BARIUM | 0.0164 | MG/L | 2.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-13 | AAA |  |  | POE
3480911 | HERMANN ENGELMANN #6 | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-07-24 | WTP2 | 0.24 | 0.5499 | NEW WP POE ACCPTD 7/09 2976 J QUALIFIER
3480911 | HERMANN ENGELMANN #6 | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-27 | L1 | 0.2 |  | REAR MEN'S RESTROOM | 3
3480911 | HERMANN ENGELMANN #6 | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-08-27 | L1 | 0.21 |  | REAR MEN'S RESTROOM | 3
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1052 | SODIUM | 14.1 | MG/L | 160.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1017 | CHLORIDE | 20.9 | MG/L | 250.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1028 | IRON | 0.242 | MG/L | 0.3499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1055 | SULFATE | 1.94 | MG/L | 250.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1095 | ZINC | 0.007 | MG/L | 5.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.1 | LN(10) |  | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 170 | MG/L | 500.4999 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-13 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-05-13 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-05-13 | AAA |  | 0.0149 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-05-13 | AAA |  | 0.0249 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-05-13 | AAA |  | 0.1499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-05-13 | AAA |  | 1.4999 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-05-13 | AAA |  | 1.4999 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-05-13 | AAA |  | 0.4499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-05-13 | AAA |  | 9.4999 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-05-13 | AAA |  | 6.4999 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-05-13 | AAA |  | 0.6499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-05-13 | AAA |  | 2.4999 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-05-13 | AAA |  | 0.0749 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-05-13 | AAA |  | 0.6499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-05-13 | AAA |  | 0.1499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-05-13 | AAA |  | 0.2499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-05-13 | AAA |  | 0.1499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-05-13 | AAA |  | 0.9499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-05-13 | AAA |  | 0.1499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-05-13 | AAA |  | 0.2499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-05-13 | AAA |  | 0.0449 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-05-13 | AAA |  | 0.0249 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-05-13 | AAA |  | 0.1499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-05-13 | AAA |  | 0.2499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-05-13 | AAA |  | 0.1499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-05-13 | AAA |  | 0.0249 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-05-13 | AAA |  | 0.0449 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-05-13 | AAA |  | 0.1499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-05-13 | AAA |  | 0.0249 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-05-13 | AAA |  | 0.0149 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-05-13 | AAA |  | 0.2499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.3 | PCI/L | 15.4999 | 2021-05-17 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-05-17 | AAA |  | 1.4999 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.2 | UG/L | 60.4999 | 2021-09-20 | L1 |  |  |  | 3
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | D | DBP | 2950 | TOTAL THMS | 4.87 | UG/L | 80.4999 | 2021-09-20 | L1 |  |  |  | 3
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-20 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-20 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1010 | BARIUM | 0.016 | MG/L | 2.4999 | 2024-04-29 | AAA | 0.00037 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1020 | CHROMIUM | 0.0007 | MG/L | 0.1499 | 2024-04-29 | AAA | 0.0004 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2024-04-29 | AAA | 0.025 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1036 | NICKEL | 0.0014 | MG/L | 0.1499 | 2024-04-29 | AAA | 0.00092 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2024-04-29 | AAA | 0.13 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1017 | CHLORIDE | 15 | MG/L | 250.4999 | 2024-04-29 | AAA | 0.4 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1022 | COPPER | 0.0042 | MG/L | 1.4999 | 2024-04-29 | AAA | 0.0006 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2024-04-29 | AAA | 0.025 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1032 | MANGANESE | 0.0055 | MG/L | 0.0549 | 2024-04-29 | AAA | 0.0009 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1095 | ZINC | 0.0036 | MG/L | 5.4999 | 2024-04-29 | AAA | 0.00013 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2024-04-29 | AAA | 5 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 86 | MG/L | 500.4999 | 2024-04-29 | AAA | 5 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-04-29 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-04-29 | AAA |  | 0.5499 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-09-16 | AAA |  |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-16 | AAA |  | 1.4999 | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-09-16 | L1 | 0.3 |  | 4635 OLA BEACH DRIVE | 3
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-09-16 | L1 | 0.5 |  | 4635 OLA BEACH DRIVE | 3
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1040 | NITRATE | 1.7 | MG/L | 10.4999 | 2025-10-23 | AAA | 0.1 |  | POE
3480940 | OLA BEACH IMPROVEMENT ASSOCIATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-23 | AAA |  |  | POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.47 | UG/L | 10.4999 | 2021-01-04 | L7 | 0.77 |  | 1/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.53 | UG/L | 10.4999 | 2021-01-04 | L7 | 0.77 |  | 1/21 BROMATE - KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.1 | UG/L | 10.4999 | 2021-01-04 | L7 | 0.77 |  | 1/21 BROMATE - PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.78 | UG/L | 10.4999 | 2021-01-04 | L7 | 0.77 |  | 1/21 BROMATE - HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.95 | UG/L | 10.4999 | 2021-01-04 | L7 | 0.77 |  | 1/21 BROMATE - NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.83 | UG/L | 10.4999 | 2021-01-04 | L7 | 0.77 |  | 1/21 BROMATE - CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.78 | UG/L | 10.4999 | 2021-01-04 | L7 | 0.77 |  | 1/21 BROMATE - SKY LAKE WP (HLKD)
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-01-06 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-01-05 | WTP11 | 0.5 | 0.6499 | SW WP PHTHALATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.5 | MG/L | 0 | 2021-01-06 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-01-06 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-01-06 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-01-06 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-01-06 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-01-06 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.6 | MG/L | 0 | 2021-01-06 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-01-06 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-01-06 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2021-01-06 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-01-06 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.7 | MG/L | 0 | 2021-01-06 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-01-06 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-01-06 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-01-06 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.8 | MG/L | 0 | 2021-01-06 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-01-06 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-01-06 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.1 | MG/L | 0 | 2021-01-06 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2021-01-06 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-01-20 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-01-20 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-01-20 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2021-01-20 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-01-20 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-01-20 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-01-20 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-01-20 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-01-20 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2021-01-20 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-01-20 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-01-20 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.7 | MG/L | 0 | 2021-01-20 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-01-20 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-01-20 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2021-01-20 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2021-01-20 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-01-20 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2021-01-20 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-01-20 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-01-20 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.54 | UG/L | 10.4999 | 2021-02-01 | L7 | 0.55 |  | 2/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.16 | UG/L | 10.4999 | 2021-02-01 | L7 | 0.55 |  | 2/21 BROMATE - KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.81 | UG/L | 10.4999 | 2021-02-01 | L7 | 0.55 |  | 2/21 BROMATE - PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.54 | UG/L | 10.4999 | 2021-02-01 | L7 | 0.55 |  | 2/21 BROMATE - HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.85 | UG/L | 10.4999 | 2021-02-01 | L7 | 0.55 |  | 2/21 BROMATE - NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.86 | UG/L | 10.4999 | 2021-02-01 | L7 | 0.55 |  | 2/21 BROMATE - CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.02 | UG/L | 10.4999 | 2021-02-01 | L7 | 0.55 |  | 2/21 BROMATE - SKY LAKE WP (HLKD)
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 61.74 | UG/L | 80.4999 | 2021-02-01 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.73 | UG/L | 60.4999 | 2021-02-01 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 44.19 | UG/L | 80.4999 | 2021-02-01 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.91 | UG/L | 60.4999 | 2021-02-01 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.77 | UG/L | 60.4999 | 2021-02-01 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 60.63 | UG/L | 80.4999 | 2021-02-01 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.71 | UG/L | 60.4999 | 2021-02-01 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 72.1 | UG/L | 80.4999 | 2021-02-01 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.19 | UG/L | 60.4999 | 2021-02-01 | L5 | 2 |  | LANDSTAR BLVD. & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 67.53 | UG/L | 80.4999 | 2021-02-01 | L5 | 0.12 |  | LANDSTAR BLVD. & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.48 | UG/L | 60.4999 | 2021-02-01 | L6 | 2 |  | 5512 BAYSIDE DR. (3/21 QTR DISINF BYP REPORT RCVD SEP)
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 37.45 | UG/L | 80.4999 | 2021-02-01 | L6 | 0.12 |  | 5512 BAYSIDE DR. (3/21 QTR DISINF BYP REPORT RCVD SEP)
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2021-02-03 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2021-02-03 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2021-02-03 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2021-02-03 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-02-03 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-02-03 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2021-02-03 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-02-03 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-02-03 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-02-03 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-02-03 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-02-03 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.8 | MG/L | 0 | 2021-02-03 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-02-03 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2021-02-03 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.4 | MG/L | 0 | 2021-02-03 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2021-02-03 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-02-03 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.7 | MG/L | 0 | 2021-02-03 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-02-03 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-02-03 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2021-02-17 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-02-17 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-02-17 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2021-02-17 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-02-17 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2021-02-17 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2021-02-17 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-02-17 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-02-17 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-02-17 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-02-17 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2021-02-17 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-02-17 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2021-02-17 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-02-17 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2021-02-17 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-02-17 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 139 | MG/L |  | 2021-02-17 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2021-02-17 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2021-02-17 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-02-17 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.96 | UG/L | 10.4999 | 2021-03-01 | L7 | 0.55 |  | 3/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.66 | UG/L | 10.4999 | 2021-03-01 | L7 | 0.55 |  | 3/21 BROMATE - KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-03-01 | L7 | 0.55 |  | 3/21 BROMATE - PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.94 | UG/L | 10.4999 | 2021-03-01 | L7 | 0.55 |  | 3/21 BROMATE - HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-03-01 | L7 | 0.55 |  | 3/21 BROMATE - NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.75 | UG/L | 10.4999 | 2021-03-01 | L7 | 0.55 |  | 3/21 BROMATE - CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.66 | UG/L | 10.4999 | 2021-03-01 | L7 | 0.55 |  | 3/21 BROMATE - SKY LAKE WP (3/21 QTR BROMATE RAA RCVD SEP) HLKD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.05 | MG/L | 10.4999 | 2021-03-02 | WTP8 |  |  | NAVY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-02 | WTP5 |  |  | PINES HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | WTP5 |  |  | PINES HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-02 | WTP7 |  |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | WTP7 |  |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-02 | WTP11 |  |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | WTP11 |  |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-02 | WTP6 |  |  | CONWAY ENTRY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | WTP8 |  |  | NAVY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2021-03-02 | WTP1 |  |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | WTP1 |  |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | WTP6 |  |  | CONWAY ENTRY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-02 | WTP10 |  |  | SKY LAKE POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | WTP10 |  |  | SKY LAKE POINT OF ENTRY
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.75 | UG/L | 60.4999 | 2021-06-16 | L1 | 0.98 |  | 501 PINE ISLE DR. (PROBABLY LOT #501) NOTE: 3/21 T/H MISSED PER VIOL SCREEN
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 20.24 | UG/L | 80.4999 | 2021-06-16 | L1 | 1 |  | 501 PINE ISLE DR. (PROBABLY LOT #501) NOTE: 3/21 T/H MISSED PER VIOL SCREEN
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.44 | UG/L | 60.4999 | 2021-09-17 | L1 | 0.98 |  | LOT 501 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 25.74 | UG/L | 80.4999 | 2021-09-17 | L1 | 0.39 |  | LOT 501 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.44 | UG/L | 60.4999 | 2021-09-17 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 25.74 | UG/L | 80.4999 | 2021-09-17 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2450 | MONOCHLORACETIC ACID | 1.62 | UG/L |  | 2021-09-17 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2451 | DICHLOROACETIC ACID | 6.47 | UG/L |  | 2021-09-17 | L1 | 0.42 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2452 | TRICHLOROACETIC ACID | 10.06 | UG/L |  | 2021-09-17 | L1 | 0.94 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-09-17 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2454 | DIBROMOACETIC ACID | 1.29 | UG/L |  | 2021-09-17 | L1 | 0.74 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2941 | CHLOROFORM | 16.02 | UG/L | 100 | 2021-09-17 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-09-17 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2943 | BROMODICHLOROMETHANE | 9.72 | UG/L | 100 | 2021-09-17 | L1 | 0.14 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 0 | UG/L | 100 | 2021-09-17 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22 | UG/L | 60.4999 | 2021-09-21 | L2 | 0.98 |  | LOT 607 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 29.06 | UG/L | 80.4999 | 2021-09-21 | L2 | 0.39 |  | LOT 607 (HLKD) IF TESTING IS OKAY, CHANGE "S" SAMPLE TYPE TO "D" SAMPLE TYPE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.75 | UG/L | 60.4999 | 2021-11-04 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 30.91 | UG/L | 80.4999 | 2021-11-04 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.65 | UG/L | 60.4999 | 2021-11-04 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 28.42 | UG/L | 80.4999 | 2021-11-04 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.75 | UG/L | 60.4999 | 2021-11-04 | L2 | 0.98 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2950 | TOTAL THMS | 30.91 | UG/L | 80.4999 | 2021-11-04 | L2 | 0.39 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2450 | MONOCHLORACETIC ACID | 0 | UG/L |  | 2021-11-04 | L2 |  |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2451 | DICHLOROACETIC ACID | 6.96 | UG/L |  | 2021-11-04 | L2 |  |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2452 | TRICHLOROACETIC ACID | 9.17 | UG/L |  | 2021-11-04 | L2 | 0.94 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-11-04 | L2 |  |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2454 | DIBROMOACETIC ACID | 1.61 | UG/L |  | 2021-11-04 | L2 | 0.74 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2941 | CHLOROFORM | 17.68 | UG/L | 100 | 2021-11-04 | L2 | 0.39 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-11-04 | L2 |  |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2943 | BROMODICHLOROMETHANE | 8.56 | UG/L | 100 | 2021-11-04 | L2 | 0.14 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | DBP | 2944 | DIBROMOCHLOROMETHANE | 4.66 | UG/L | 100 | 2021-11-04 | L2 | 0.32 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1010 | BARIUM | 0.021 | MG/L | 2.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1025 | FLUORIDE | 0.3 | MG/L | 4.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.5 | MG/L | 0 | 2021-03-03 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2021-03-03 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-03-03 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2021-03-03 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-03-03 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2021-03-03 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.1 | MG/L | 0 | 2021-03-03 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-03 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-03-03 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.5 | MG/L | 0 | 2021-03-03 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2021-03-03 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-03-03 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2021-03-03 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2021-03-03 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-03-03 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.9 | MG/L | 0 | 2021-03-03 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-03-03 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 138 | MG/L |  | 2021-03-03 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.1 | MG/L | 0 | 2021-03-03 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-03-03 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-03-03 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-03 | WTP12 |  |  | SOUTHEAST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-03 | WTP12 |  |  | SOUTHEAST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-03 | WTP12 | 0.04 |  | SE BOOSTER STATION (NOT COMPLIANCE TESTS - SE WP IS ONLY A BOOSTER STATION) RESULTS ENTD' WITH "S" FOR SPECIAL SAMPLE
3480962 | ORLANDO UTILITIES COMMISSION | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-03 | WTP12 | 0.02 |  | SE BOOSTER STATION (NOT COMPLIANCE TESTS - SE WP IS ONLY A BOOSTER STATION) RESULTS ENTD' WITH "S" FOR SPECIAL SAMPLE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2021-03-16 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-03-16 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2021-03-16 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.2 | MG/L | 0 | 2021-03-16 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-03-16 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-03-16 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.3 | MG/L | 0 | 2021-03-16 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-03-16 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-03-16 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2021-03-16 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-03-16 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-03-16 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.6 | MG/L | 0 | 2021-03-16 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-03-16 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-03-16 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.4 | MG/L | 0 | 2021-03-16 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2021-03-16 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-03-16 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.4 | MG/L | 0 | 2021-03-16 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-03-16 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-03-16 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2021-03-31 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2021-03-31 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-03-31 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2021-03-31 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-03-31 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-03-31 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-03-31 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-03-31 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2021-03-31 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-03-31 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-03-31 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-03-31 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.3 | MG/L | 0 | 2021-03-31 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-03-31 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-03-31 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2021-03-31 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-03-31 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-03-31 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2021-03-31 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-03-31 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-03-31 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.99 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.28 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.02 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.84 | UG/L | 10.4999 | 2021-04-05 | L7 | 0.55 |  | 4/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2021-04-14 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2021-04-14 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-04-14 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2021-04-14 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-04-14 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-04-14 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2021-04-14 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-04-14 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-04-14 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-04-14 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2021-04-14 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-04-14 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2021-04-14 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-04-14 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-04-14 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2021-04-14 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2021-04-14 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-04-14 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2021-04-14 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-04-14 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-04-14 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-14 | WTP11 | 0.5 | 0.6499 | SW WP PHTHALATE (EXTRA)
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.4 | MG/L | 0 | 2021-04-28 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-04-28 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2021-04-28 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-04-28 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-04-28 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-04-28 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.3 | MG/L | 0 | 2021-04-28 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2021-04-28 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-04-28 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2021-04-28 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-04-28 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-04-28 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2021-04-28 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-04-28 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-04-28 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2021-04-28 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-04-28 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-04-28 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.9 | MG/L | 0 | 2021-04-28 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-04-28 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-04-28 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.79 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.49 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.05 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.62 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.63 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.98 | UG/L | 10.4999 | 2021-05-03 | L7 | 0.55 |  | 5/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.71 | UG/L | 60.4999 | 2021-05-07 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 45.33 | UG/L | 80.4999 | 2021-05-07 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.3 | UG/L | 60.4999 | 2021-05-07 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 56.28 | UG/L | 80.4999 | 2021-05-07 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.07 | UG/L | 60.4999 | 2021-05-07 | L6 | 2 |  | 5512 BAYSIDE DR. (6/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 35.63 | UG/L | 80.4999 | 2021-05-07 | L6 | 0.12 |  | 5512 BAYSIDE DR. (6/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.99 | UG/L | 60.4999 | 2021-05-07 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 57.69 | UG/L | 80.4999 | 2021-05-07 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.11 | UG/L | 60.4999 | 2021-05-07 | L5 | 2 |  | LANDSTAR (BLVD.) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 65.71 | UG/L | 80.4999 | 2021-05-07 | L5 | 0.12 |  | LANDSTAR (BLVD.) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.16 | UG/L | 60.4999 | 2021-05-07 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 66.27 | UG/L | 80.4999 | 2021-05-07 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.9 | MG/L | 0 | 2021-05-12 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-05-12 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2021-05-12 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2021-05-12 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-12 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-05-12 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2021-05-12 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-05-12 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-05-12 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.4 | MG/L | 0 | 2021-05-12 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-05-12 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-05-12 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2021-05-12 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-12 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-05-12 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.6 | MG/L | 0 | 2021-05-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-05-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-05-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.6 | MG/L | 0 | 2021-05-12 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-05-12 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-05-12 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2021-05-26 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2021-05-26 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-05-26 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2021-05-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-05-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-05-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2021-05-26 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-26 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-05-26 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-05-26 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-26 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-05-26 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-05-26 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2021-05-26 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-05-26 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2021-05-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-05-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-05-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2021-05-26 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-26 | WTP5 |  |  | PINEHILLS
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 9.3 | PCI/L | 15.4999 | 2021-02-08 | AAA | 1.5 |  | 1Q2021
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 2.6 | PCI/L | 3.4999 | 2021-02-08 | AAA | 0.4 | 1.4999 | 1Q2021
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-02-08 | AAA | 0.7 | 1.4999 | 1Q2021
3481155 | SHADY OAKS TRAILER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.3 | UG/L | 60.4999 | 2021-08-26 | L1 |  |  |  | 3
3481155 | SHADY OAKS TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 6.36 | UG/L | 80.4999 | 2021-08-26 | L1 |  |  |  | 3
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5.3 | PCI/L | 15.4999 | 2021-09-28 | AAA
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-05-26 | WTP5 |  |  | PINEHILLS
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-28 | AAA | 0.7 | 1.4999 | R228 VALUE CORRECTED (FROM 0.7 TO -0-) ON 10/25/22 FROM DUPLICATE REPORT-BB
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-09-28 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 1.7 | PCI/L | 3.4999 | 2021-09-28 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 0.5499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-06 | AAA |  | 0.0149 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 1.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-06 | AAA |  | 1.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-06 | AAA |  | 0.4499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-06 | AAA |  | 9.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-06 | AAA |  | 6.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-06 | AAA |  | 0.6499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-06 | AAA |  | 2.4999 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-06 | AAA |  | 0.0749 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-06 | AAA |  | 0.6499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-06 | AAA |  | 0.9499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-06 | AAA |  | 0.0449 | LATE REPORTING RCVD 02/23/22_NMS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.28 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE SW POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.33 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.87 | UG/L | 60.4999 | 2021-06-07 | L7 |  |  | BROMATE HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.12 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.52 | UG/L | 10.4999 | 2021-06-07 | L7 |  |  | BROMATE SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.7 | MG/L | 0 | 2021-06-09 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-06-09 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-06-09 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2021-06-09 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-06-09 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-06-09 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2021-06-09 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-06-09 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-06-09 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2021-06-09 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-06-09 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-06-09 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2021-06-09 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-06-09 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-06-09 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-06-09 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2021-06-09 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-06-09 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.5 | MG/L | 0 | 2021-06-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-06-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-06-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.3 | MG/L | 0 | 2021-06-23 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-06-23 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-06-23 | WTP5 |  |  | PINEHILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2021-06-23 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-06-23 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2021-06-23 | WTP1 |  |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2021-06-23 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-06-23 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-06-23 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.4 | MG/L | 0 | 2021-06-23 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-06-23 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2021-06-23 | WTP10 |  |  | SKY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.1 | MG/L | 0 | 2021-06-23 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-06-23 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-06-23 | WTP8 |  |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2021-06-23 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2021-06-23 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-06-23 | WTP11 |  |  | SOUTH
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2021-06-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2021-06-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-06-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.08 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.88 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.85 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.74 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.69 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.26 | UG/L | 10.4999 | 2021-07-01 | L7 | 0.55 |  | 7/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-07-06 | WTP11 | 0.5 | 0.6499 | SW WP PHTHALATE (EXTRA) HLKD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.7 | MG/L | 0 | 2021-07-07 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-07 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-07-07 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.8 | MG/L | 0 | 2021-07-07 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-07-07 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-07-07 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-07-07 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2021-07-07 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-07-07 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-07-07 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.1 | MG/L | 0 | 2021-07-07 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-07-07 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2021-07-07 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-07-07 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-07-07 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-07-07 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2021-07-07 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-07 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-07-07 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.8 | MG/L | 0 | 2021-07-07 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-07-07 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.5 | MG/L | 0 | 2021-07-21 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-07-21 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-07-21 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2021-07-21 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-07-21 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-07-21 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2021-07-21 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-07-21 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-07-21 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44 | MG/L | 0 | 2021-07-21 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-07-21 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2021-07-21 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2021-07-21 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-07-21 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-07-21 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-07-21 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-07-21 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-07-21 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.5 | MG/L | 0 | 2021-07-21 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2021-07-21 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-07-21 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.86 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | SW POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.24 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | KIRKMAN POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.69 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | PINE HILLS POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.68 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | HIGHLAND POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.27 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | NAVY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.71 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | CONWAY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.13 | UG/L | 10.4999 | 2021-08-02 | L7 |  |  | SKY LAKE POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.26 | UG/L | 60.4999 | 2021-08-02 | L1 |  |  | SMP PT 10 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 20.91 | UG/L | 80.4999 | 2021-08-02 | L1 |  |  | SMP PT 10 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.6 | UG/L | 60.4999 | 2021-08-02 | L2 |  |  | SMP PT 23 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.93 | UG/L | 80.4999 | 2021-08-02 | L2 |  |  | SMP PT 23 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.62 | UG/L | 60.4999 | 2021-08-02 | L3 |  |  | SMP PT 169 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 62.5 | UG/L | 80.4999 | 2021-08-02 | L3 |  |  | SMP PT 169 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.74 | UG/L | 60.4999 | 2021-08-02 | L4 |  |  | SMP PT SE5 LAKE NONA
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 67.51 | UG/L | 80.4999 | 2021-08-02 | L4 |  |  | SMP PT SE5 LAKE NONA
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.28 | UG/L | 60.4999 | 2021-08-02 | L5 |  |  | SMP PT 124 LANDSTAR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 66.19 | UG/L | 80.4999 | 2021-08-02 | L5 |  |  | SMP PT 124 LANDSTAR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.43 | UG/L | 60.4999 | 2021-08-02 | L6 |  |  | SMP PT 121 BAYSIDE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 38.98 | UG/L | 80.4999 | 2021-08-02 | L6 |  |  | SMP PT 121 BAYSIDE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2021-08-04 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2021-08-04 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-08-04 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-08-04 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-08-04 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-08-04 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-08-04 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-08-04 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-08-04 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.9 | MG/L | 0 | 2021-08-04 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-08-04 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-08-04 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34 | MG/L | 0 | 2021-08-04 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-08-04 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2021-08-04 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-08-04 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-08-04 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-08-04 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.7 | MG/L | 0 | 2021-08-04 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-08-04 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-08-04 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.3 | MG/L | 0 | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-08-18 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-08-18 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-08-18 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-08-18 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-08-18 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-08-18 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-08-18 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2021-08-18 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-08-18 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2021-08-18 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2021-08-18 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-08-18 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-08-18 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2021-08-18 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-08-18 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2021-08-18 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.9 | MG/L | 0 | 2021-09-01 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-09-01 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-09-01 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2021-09-01 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-09-01 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2021-09-01 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2021-09-01 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-09-01 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-09-01 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.6 | MG/L | 0 | 2021-09-01 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-09-01 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2021-09-01 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.6 | MG/L | 0 | 2021-09-01 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-09-01 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-09-01 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2021-09-01 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-09-01 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-09-01 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.8 | MG/L | 0 | 2021-09-01 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-09-01 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-09-01 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.01 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.03 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.16 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.14 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.68 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.18 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.1 | UG/L | 10.4999 | 2021-09-07 | L7 | 0.71 |  | 9/21 BROMATE - SKY LAKE (HLKD) 9/21 BROMATE RAA ALREADY HLKD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2021-09-15 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-09-15 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-09-15 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2021-09-15 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-09-15 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-09-15 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2021-09-15 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2021-09-15 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-09-15 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2021-09-15 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-09-15 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2021-09-15 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2021-09-15 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-09-15 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-09-15 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-09-15 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-09-15 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-09-15 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.2 | MG/L | 0 | 2021-09-15 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2021-09-15 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-09-15 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.2 | MG/L | 0 | 2021-09-29 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-09-29 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2021-09-29 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-09-29 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2021-09-29 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-09-29 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2021-09-29 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-09-29 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-09-29 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-09-29 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-09-29 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-09-29 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 32.6 | MG/L | 0 | 2021-09-29 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-09-29 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2021-09-29 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-09-29 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-09-29 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2021-09-29 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.5 | MG/L | 0 | 2021-09-29 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-29 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-09-29 | WTP5
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-06 | AAA |  | 0.0449 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-06 | AAA |  | 0.1499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-06 | AAA |  | 0.0249 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-06 | AAA |  | 0.0149 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-06 | AAA |  | 0.2499 | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 7 | PCI/L | 15.4999 | 2021-12-06 | AAA
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-06 | AAA |  | 0.667
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 3.8 | PCI/L | 3.4999 | 2021-12-06 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-06 | AAA |  | 1.4999
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1025 | FLUORIDE | 0.27 | MG/L | 4.0499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1052 | SODIUM | 25 | MG/L | 160.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1017 | CHLORIDE | 36 | MG/L | 250.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1025 | FLUORIDE | 0.27 | MG/L | 2.0499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1028 | IRON | 0.0078 | MG/L | 0.3499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1055 | SULFATE | 4.5 | MG/L | 250.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.21 | LN(10) |  | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 231 | MG/L | 500.4999 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 2905 | FOAMING AGENTS | 0.07 |  | 0.5499 | 2021-12-06 | AAA |  |  | LATE REPORTING RCVD 02/23/22_NMS
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 3.8 | PCI/L | 3.4999 | 2022-03-15 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-03-15 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 4.9 | PCI/L | 3.4999 | 2022-06-07 | AAA | 0.5 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-06-07 | AAA | 0.7 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8.6 | PCI/L | 15.4999 | 2022-07-12 | AAA | 2.6 |  | RADS
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 2.5 | PCI/L | 3.4999 | 2022-07-12 | AAA | 0.4 | 1.4999 | RADS
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-07-12 | AAA | 0.6 | 1.4999 | RADS
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1041 | NITRITE | 0.01 | MG/L | 1.4999 | 2022-10-17 | AAA | 34 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-17 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1040 | NITRATE | 0.057 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-17 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.1 | UG/L | 60.4999 | 2024-08-20 | L1 | 0.89 |  | SITE#8 1761 SHADY OAKS - SUBCONTRACTED TO E82574,E82535 | 3
3481155 | SHADY OAKS TRAILER PARK | D | DBP | 2950 | TOTAL THMS | 28.33 | UG/L | 80.4999 | 2024-08-20 | L1 | 0.39 |  | SITE#8 1761 SHADY OAKS - SUBCONTRACTED TO E82574,E82535 | 3
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 13.9 | PCI/L | 15.4999 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4020 | RADIUM-226 | 4.3 | PCI/L | 3.4999 | 2024-11-13 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-11-13 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-11-13 | AAA |  | 0.2499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-11-13 | AAA |  | 0.1499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-11-13 | AAA |  | 0.0249 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-11-13 | AAA |  | 0.0449 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-11-13 | AAA |  | 0.1499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-11-13 | AAA |  | 0.0249 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-11-13 | AAA |  | 0.0149 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-11-13 | AAA |  | 0.2499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1040 | NITRATE | 0.085 | MG/L | 10.4999 | 2024-11-13 | AAA | 0.024 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1010 | BARIUM | 0.016 | MG/L | 2.4999 | 2024-11-13 | AAA | 0.003 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1025 | FLUORIDE | 0.26 | MG/L | 4.0499 | 2024-11-13 | AAA | 0.0099 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1052 | SODIUM | 34 | MG/L | 160.4999 | 2024-11-13 | AAA | 0.8 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-11-13 | AAA |  | 0.1499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1017 | CHLORIDE | 46 | MG/L | 250.4999 | 2024-11-13 | AAA | 0.039 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1022 | COPPER | 0.018 | MG/L | 1.4999 | 2024-11-13 | AAA | 0.005 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1025 | FLUORIDE | 0.26 | MG/L | 2.0499 | 2024-11-13 | AAA | 0.0099 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1055 | SULFATE | 4.8 | MG/L | 250.4999 | 2024-11-13 | AAA | 0.034 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-11-13 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 290 | MG/L | 500.4999 | 2024-11-13 | AAA | 1 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | SEC | 2905 | FOAMING AGENTS | 0.11 |  | 0.5499 | 2024-11-13 | AAA | 0.04 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-11-13 | AAA |  | 0.667 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-11-13 | AAA |  | 0.5499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-11-13 | AAA |  | 0.0149 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-11-13 | AAA |  | 0.0249 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-11-13 | AAA |  | 0.1499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-11-13 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-11-13 | AAA |  | 1.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-11-13 | AAA |  | 0.4499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-11-13 | AAA |  | 9.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-11-13 | AAA |  | 6.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-11-13 | AAA |  | 0.6499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-11-13 | AAA |  | 2.4999 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-11-13 | AAA |  | 0.0749 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-11-13 | AAA |  | 0.6499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-11-13 | AAA |  | 0.1499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-11-13 | AAA |  | 0.2499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-11-13 | AAA |  | 0.1499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-11-13 | AAA |  | 0.9499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-11-13 | AAA |  | 0.1499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-11-13 | AAA |  | 0.2499 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-11-13 | AAA |  | 0.0449 | POE
3481155 | SHADY OAKS TRAILER PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-11-13 | AAA |  | 0.0249 | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2024-11-19 | AAA | 5 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1064 | CONDUCTIVITY | 510 | MG/L | 0 | 2024-11-19 | AAA | 2 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1919 | HARDNESS - CALCIUM | 55 | MG/L | 0 | 2024-11-19 | AAA | 0.2 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-11-19 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1022 | COPPER | 0 | MG/L | 1.5499 | 2024-11-19 | AAA | 0.025 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-11-19 | AAA | 0.001 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1064 | CONDUCTIVITY | 510 | MG/L | 0 | 2024-11-19 | AAA | 2 |  | 1718 TOWNSEND OAKS CIRCLE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1919 | HARDNESS - CALCIUM | 56 | MG/L | 0 | 2024-11-19 | AAA | 0.2 |  | 1718 TOWNSEND OAKS CIRCLE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-11-19 | AAA |  |  | 1718 TOWNSEND OAKS CIRCLE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2024-11-19 | AAA | 5 |  | 1718 TOWNSEND OAKS CIRCLE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 21.8 |  |  | 2024-11-19 | AAA |  |  | 1718 TOWNSEND OAKS CIRCLE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 21.8 |  |  | 2024-11-19 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1022 | COPPER | 0 | MG/L | 1.5499 | 2024-11-19 | AAA | 0.025 |  | 1718 TOWNSEND OAKS CIRCLE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-11-19 | AAA | 0.001 |  | 1718 TOWNSEND OAKS CIRCLE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1040 | NITRATE | 0.087 | MG/L | 10.4999 | 2025-02-06 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3481155 | SHADY OAKS TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-06 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1064 | CONDUCTIVITY | 460 | MG/L | 0 | 2025-02-06 | AAA | 2 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1919 | HARDNESS - CALCIUM | 57 | MG/L | 0 | 2025-02-06 | AAA | 0.2 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2025-02-06 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2025-02-06 | AAA | 5 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 22.1 |  |  | 2025-02-06 | AAA |  |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1064 | CONDUCTIVITY | 470 | MG/L | 0 | 2025-02-06 | AAA | 2 |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1919 | HARDNESS - CALCIUM | 57 | MG/L | 0 | 2025-02-06 | AAA | 0.2 |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2025-02-06 | AAA |  |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2025-02-06 | AAA | 5 |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 22.1 |  |  | 2025-02-06 | AAA |  |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1064 | CONDUCTIVITY | 420 | MG/L | 0 | 2025-06-12 | AAA | 2 |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1064 | CONDUCTIVITY | 420 | MG/L | 0 | 2025-06-12 | AAA | 2 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1919 | HARDNESS - CALCIUM | 58 | MG/L | 0 | 2025-06-12 | AAA | 0.2 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2025-06-12 | AAA | 5 |  | POE
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1919 | HARDNESS - CALCIUM | 59 | MG/L | 0 | 2025-06-12 | AAA | 0.2 |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | N | WQP | 1927 | TOTAL ALKALINITY | 180 | MG/L |  | 2025-06-12 | AAA | 5 |  | LOT 4
3481155 | SHADY OAKS TRAILER PARK | R | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-06-12 | AAA | 0.001 |  | WELL - LEAD, COPPER
3481155 | SHADY OAKS TRAILER PARK | R | WQP | 1022 | COPPER | 0 | MG/L | 1.5499 | 2025-06-12 | AAA | 0.025 |  | WELL - LEAD, COPPER
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.81 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - SW
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.68 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.12 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.03 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.8 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.98 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.09 | UG/L | 10.4999 | 2021-10-04 | L7 | 0.71 |  | 10/21 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2021-10-13 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2021-10-13 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-10-13 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2021-10-13 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-10-13 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-10-13 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-10-13 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-10-13 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-10-13 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.8 | MG/L | 0 | 2021-10-13 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2021-10-13 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-10-13 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2021-10-13 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2021-10-13 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-10-13 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-10-13 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-13 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-10-13 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.9 | MG/L | 0 | 2021-10-13 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-10-13 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-10-13 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2021-10-27 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-10-27 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-10-27 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2021-10-27 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-10-27 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-10-27 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2021-10-27 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2021-10-27 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-10-27 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45 | MG/L | 0 | 2021-10-27 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-10-27 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-10-27 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.9 | MG/L | 0 | 2021-10-27 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-10-27 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-10-27 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2021-10-27 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2021-10-27 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2021-10-27 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2021-10-27 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-10-27 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-10-27 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.75 | UG/L | 60.4999 | 2021-11-01 | L1 |  |  | 1642 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 19.72 | UG/L | 80.4999 | 2021-11-01 | L1 |  |  | 1642 SILVER STAR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.63 | UG/L | 60.4999 | 2021-11-01 | L2 |  |  | 2714 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.43 | UG/L | 80.4999 | 2021-11-01 | L2 |  |  | 2714 ILLINOIS ST
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.64 | UG/L | 60.4999 | 2021-11-01 | L3 |  |  | 758 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.28 | UG/L | 80.4999 | 2021-11-01 | L3 |  |  | 758 DENNIS AVE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.56 | UG/L | 60.4999 | 2021-11-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 69.94 | UG/L | 80.4999 | 2021-11-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.95 | UG/L | 60.4999 | 2021-11-01 | L5 |  |  | 124 LANDSTAR RD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 68.61 | UG/L | 80.4999 | 2021-11-01 | L5 |  |  | 124 LANDSTAR RD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.31 | UG/L | 60.4999 | 2021-11-01 | L6 |  |  | 5512 BAY SIDE DR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 39.91 | UG/L | 80.4999 | 2021-11-01 | L6 |  |  | 5512 BAY SIDE DR
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.99 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | SOUTHWEST BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.36 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.61 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.21 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.7 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.07 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.64 | UG/L | 10.4999 | 2021-11-01 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.2 | MG/L | 0 | 2021-11-10 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-11-10 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-11-10 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2021-11-10 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-11-10 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2021-11-10 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-11-10 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-11-10 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-11-10 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.8 | MG/L | 0 | 2021-11-10 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-11-10 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-11-10 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.8 | MG/L | 0 | 2021-11-10 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-11-10 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-11-10 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2021-11-10 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2021-11-10 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2021-11-10 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.4 | MG/L | 0 | 2021-11-10 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2021-11-10 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-11-10 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2021-11-23 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.658 | LN(10) |  | 2021-11-23 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-11-23 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2021-11-23 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-11-23 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-11-23 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-11-23 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-11-23 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2021-11-23 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.2 | MG/L | 0 | 2021-11-23 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-11-23 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2021-11-23 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2021-11-23 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-11-23 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-11-23 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2021-11-23 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-11-23 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-11-23 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31 | MG/L | 0 | 2021-11-23 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2021-11-23 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-11-23 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.11 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | SW POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.43 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.35 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 10.1 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.67 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.77 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.51 | UG/L | 10.4999 | 2021-12-06 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2021-12-08 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-12-08 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-12-08 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2021-12-08 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-12-08 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-12-08 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2021-12-08 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-12-08 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-12-08 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.5 | MG/L | 0 | 2021-12-08 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-12-08 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-12-08 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37 | MG/L | 0 | 2021-12-08 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-12-08 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-12-08 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2021-12-08 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-12-08 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-12-08 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30 | MG/L | 0 | 2021-12-08 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-12-08 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-12-08 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2021-12-22 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2021-12-22 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-12-22 | WTP1
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2021-12-22 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2021-12-22 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-12-22 | WTP7
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41 | MG/L | 0 | 2021-12-22 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-12-22 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-12-22 | WTP8
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.5 | MG/L | 0 | 2021-12-22 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-12-22 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2021-12-22 | WTP10
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.5 | MG/L | 0 | 2021-12-22 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2021-12-22 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-12-22 | WTP11
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2021-12-22 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-12-22 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-12-22 | WTP6
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.08 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.57 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.27 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.96 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.62 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.62 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.31 | UG/L | 10.4999 | 2022-01-03 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-01-05 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-01-05 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-01-05 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-01-05 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2021-12-22 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-12-22 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-12-22 | WTP5
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2022-01-05 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-01-05 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2022-01-05 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2022-01-05 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2022-01-05 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-01-05 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-01-05 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2022-01-05 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-01-05 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-01-05 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-01-05 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-01-05 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-01-05 | WTP11 |  | 0.6499 | 1 AM POE SW WP [ JQ RESULTS ACCEPTED BASED ON QC_MFC]
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2022-01-05 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-01-05 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-01-05 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2022-01-05 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2022-01-05 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-01-19 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2022-01-19 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-01-19 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2022-01-19 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-01-19 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-01-19 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.9 | MG/L | 0 | 2022-01-19 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-01-19 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-01-19 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2022-01-19 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-01-19 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-01-19 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.1 | MG/L | 0 | 2022-01-19 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2022-01-19 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-01-19 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2022-01-19 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-01-19 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-01-19 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.3 | MG/L | 0 | 2022-01-19 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2022-01-19 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-01-19 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1052 | SODIUM | 40 | MG/L | 160.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1017 | CHLORIDE | 61 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1025 | FLUORIDE | 0.3 | MG/L | 2.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1055 | SULFATE | 18 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.07 | LN(10) |  | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 309 | MG/L | 500.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 2905 | FOAMING AGENTS | 0.06 |  | 0.5499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.3 | PCI/L | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-08 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4020 | RADIUM-226 | 1.4 | PCI/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-08 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-08 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.18 | UG/L | 60.4999 | 2021-12-16 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 24.02 | UG/L | 80.4999 | 2021-12-16 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.89 | UG/L | 60.4999 | 2021-12-16 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 30.63 | UG/L | 80.4999 | 2021-12-16 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.18 | UG/L | 60.4999 | 2021-12-16 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 24.02 | UG/L | 80.4999 | 2021-12-16 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2450 | MONOCHLORACETIC ACID | 2.18 | UG/L |  | 2021-12-16 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2451 | DICHLOROACETIC ACID | 6.9 | UG/L |  | 2021-12-16 | L1 | 0.42 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2452 | TRICHLOROACETIC ACID | 9.15 | UG/L |  | 2021-12-16 | L1 | 0.94 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2021-12-16 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2454 | DIBROMOACETIC ACID | 0.96 | UG/L |  | 2021-12-16 | L1 | 0.74 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2941 | CHLOROFORM | 12.58 | UG/L | 100 | 2021-12-16 | L1 | 0.39 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2021-12-16 | L1 |  |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2943 | BROMODICHLOROMETHANE | 7.5 | UG/L | 100 | 2021-12-16 | L1 | 0.14 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 3.93 | UG/L | 100 | 2021-12-16 | L1 | 0.32 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.91 | UG/L | 60.4999 | 2022-03-16 | L2 | 0.98
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 39.6 | UG/L | 80.4999 | 2022-03-16 | L2 | 0.44
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2450 | MONOCHLORACETIC ACID | 0 | UG/L |  | 2022-03-16 | L2
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2451 | DICHLOROACETIC ACID | 7.38 | UG/L |  | 2022-03-16 | L2 | 0.42
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2452 | TRICHLOROACETIC ACID | 11.5 | UG/L |  | 2022-03-16 | L2 | 0.94
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2022-03-16 | L2
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2454 | DIBROMOACETIC ACID | 4.02 | UG/L |  | 2022-03-16 | L2 | 0.74
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2941 | CHLOROFORM | 24.85 | UG/L | 100 | 2022-03-16 | L2 | 0.32
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2022-03-16 | L2
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2943 | BROMODICHLOROMETHANE | 10.18 | UG/L | 100 | 2022-03-16 | L2 | 0.42
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 39.6 | UG/L | 100 | 2022-03-16 | L2 | 0.44
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.91 | UG/L | 60.4999 | 2022-03-16 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 39.6 | UG/L | 80.4999 | 2022-03-16 | L2 |  |  | LOT 607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.07 | UG/L | 60.4999 | 2022-03-16 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 38.84 | UG/L | 80.4999 | 2022-03-16 | L1 |  |  | LOT 501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.05 | UG/L | 60.4999 | 2022-06-17 | L2 | 0.98 |  | LOT #607 (HLKD) J QUALIFIER ON 2941 CHLOROFORM IN THE TTHMS-NO EXPLANATION PROVIDED. CHANGE SAMPLE TYPE FROM "S" TO "D" IF ACCEPTABLE.
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 58.25 | UG/L | 80.4999 | 2022-06-17 | L2 | 0.39 |  | LOT #607 (HLKD) J QUALIFIER ON 2941 CHLOROFORM IN THE TTHMS-NO EXPLANATION PROVIDED. CHANGE SAMPLE TYPE FROM "S" TO "D" IF ACCEPTABLE.
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.89 | UG/L | 60.4999 | 2022-06-17 | L1 | 0.98 |  | LOT #501 (NO J QUALIFIERS ON THIS SAMPLE - OK)
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 56.67 | UG/L | 80.4999 | 2022-06-17 | L1 | 0.39 |  | LOT #501 (NO J QUALIFIERS ON THIS SAMPLE - OK)
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.5 | UG/L | 60.4999 | 2022-06-17 | L2 | 0.98 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 58.25 | UG/L | 80.4999 | 2022-06-17 | L2 | 0.39 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2450 | MONOCHLORACETIC ACID | 1.08 | UG/L |  | 2022-06-17 | L2 | 0.98 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2451 | DICHLOROACETIC ACID | 10.84 | UG/L |  | 2022-06-17 | L2 | 0.42 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2452 | TRICHLOROACETIC ACID | 16.21 | UG/L |  | 2022-06-17 | L2 | 0.94 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2453 | MONOBROMACETIC ACID | 9.52 | UG/L |  | 2022-06-17 | L2 | 0.41 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2454 | DIBROMOACETIC ACID | 1.41 | UG/L |  | 2022-06-17 | L2 | 0.74 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2941 | CHLOROFORM | 36.47 | UG/L | 100 | 2022-06-17 | L2 | 0.39 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2022-06-17 | L2 |  |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2943 | BROMODICHLOROMETHANE | 5.98 | UG/L | 100 | 2022-06-17 | L2 | 0.32 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 5.98 | UG/L | 100 | 2022-06-17 | L2 | 0.39 |  | A2205216001-LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.89 | UG/L | 60.4999 | 2022-06-17 | L1 | 0.98 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 56.67 | UG/L | 80.4999 | 2022-06-17 | L1 | 0.39 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2450 | MONOCHLORACETIC ACID | 2.07 | UG/L |  | 2022-06-17 | L1 | 0.98 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2451 | DICHLOROACETIC ACID | 10.73 | UG/L |  | 2022-06-17 | L1 | 0.42 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2452 | TRICHLOROACETIC ACID | 17.63 | UG/L |  | 2022-06-17 | L1 | 0.94 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2453 | MONOBROMACETIC ACID | 7.95 | UG/L |  | 2022-06-17 | L1 | 0.41 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2454 | DIBROMOACETIC ACID | 1.52 | UG/L |  | 2022-06-17 | L1 | 0.74 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2941 | CHLOROFORM | 35.67 | UG/L | 100 | 2022-06-17 | L1 | 0.39 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2022-06-17 | L1 |  |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2943 | BROMODICHLOROMETHANE | 15.02 | UG/L | 100 | 2022-06-17 | L1 | 0.14 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 5.98 | UG/L | 100 | 2022-06-17 | L1 | 0.32 |  | A2205216002 - LOT #501
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-14 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1041 | NITRITE | 0.11 | MG/L | 1.4999 | 2022-10-14 | AAA | 0.0034 |  | POE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 38.41 | UG/L | 80.4999 | 2023-06-21 | L2 | 0.39
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.74 | UG/L | 60.4999 | 2023-06-21 | L1 | 0.98
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2023-10-11 | AAA | 0.024 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-11 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 12.29 | UG/L | 80.4999 | 2024-06-19 | L2 | 0.39 |  | LOT #607-TTHM ONLY
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.52 | UG/L | 60.4999 | 2024-06-19 | L1 | 0.98 |  | LOT #501-HAA5 ONLY
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1040 | NITRATE | 0.052 | MG/L | 10.4999 | 2024-09-04 | AAA | 0.024 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1010 | BARIUM | 0.022 | MG/L | 2.4999 | 2024-09-04 | AAA | 0.003 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1025 | FLUORIDE | 0.23 | MG/L | 4.0499 | 2024-09-04 | AAA | 0.0099 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1052 | SODIUM | 36 | MG/L | 160.4999 | 2024-09-04 | AAA | 0.8 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1017 | CHLORIDE | 51 | MG/L | 250.4999 | 2024-09-04 | AAA | 0.039 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1025 | FLUORIDE | 0.23 | MG/L | 2.0499 | 2024-09-04 | AAA | 0.0099 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1055 | SULFATE | 17 | MG/L | 250.4999 | 2024-09-04 | AAA | 0.034 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1905 | COLOR | 120 | COLOR UNITS | 15.4999 | 2024-09-04 | AAA | 10 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.82 | LN(10) |  | 2024-09-04 | AAA |  |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 310 | MG/L | 500.4999 | 2024-09-04 | AAA | 10 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 2905 | FOAMING AGENTS | 0.065 |  | 0.5499 | 2024-09-04 | AAA | 0.04 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-09-04 | AAA |  | 0.667 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-04 | AAA |  | 0.5499 | POE
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.5 | PCI/L | 15.4999 | 2024-09-04 | AAA | 1.1 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4020 | RADIUM-226 | 1.8 | PCI/L | 3.4999 | 2024-09-04 | AAA | 0.2 | 1.4999 | POE
3481016 | PINE ISLE MOBILE VILLA | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-04 | AAA |  | 1.4999 | POE
3481016 | PINE ISLE MOBILE VILLA | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2024-10-01 | AAA | 10 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1040 | NITRATE | 0.31 | MG/L | 10.4999 | 2025-01-28 | AAA | 0.024 |  | POE
3481016 | PINE ISLE MOBILE VILLA | N | INOR | 1041 | NITRITE | 0.26 | MG/L | 1.4999 | 2025-01-28 | AAA | 0.0034 |  | POE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 229.34 | UG/L | 80.4999 | 2025-06-16 | L2 | 0.44 |  | LOT #607-EXCEEDANCE
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 54.54 | UG/L | 60.4999 | 2025-06-16 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.45 | UG/L | 60.4999 | 2025-09-05 | L1 | 0.98 |  | LOT 501 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 31.43 | UG/L | 80.4999 | 2025-09-05 | L1 | 0.44 |  | LOT 501 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.64 | UG/L | 60.4999 | 2025-09-05 | L2 | 0.98 |  | LOT 607 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 46.06 | UG/L | 80.4999 | 2025-09-05 | L2 | 0.44 |  | LOT 607 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.55 | UG/L | 60.4999 | 2025-09-18 | L1 | 0.98 |  | LOT 501 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 78.16 | UG/L | 80.4999 | 2025-09-18 | L1 | 0.44 |  | LOT 501 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.55 | UG/L | 60.4999 | 2025-09-18 | L2 | 0.98 |  | LOT 607 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 47.46 | UG/L | 80.4999 | 2025-09-18 | L2 | 0.44 |  | LOT 607 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.36 | UG/L | 60.4999 | 2025-12-17 | L1 | 0.98 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 77.41 | UG/L | 80.4999 | 2025-12-17 | L1 | 0.44 |  | LOT #501
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.16 | UG/L | 60.4999 | 2025-12-17 | L2 | 0.98 |  | LOT #607
3481016 | PINE ISLE MOBILE VILLA | D | DBP | 2950 | TOTAL THMS | 76.04 | UG/L | 80.4999 | 2025-12-17 | L2 | 0.44 |  | LOT #607
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.49 | UG/L | 60.4999 | 2022-02-01 | L1 |  |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 41.75 | UG/L | 80.4999 | 2022-02-01 | L1 |  |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.03 | UG/L | 60.4999 | 2022-02-01 | L2 |  |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 52.37 | UG/L | 80.4999 | 2022-02-01 | L2 |  |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.58 | UG/L | 60.4999 | 2022-02-01 | L3 |  |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 62.95 | UG/L | 80.4999 | 2022-02-01 | L3 |  |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.43 | UG/L | 60.4999 | 2022-02-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.19 | UG/L | 80.4999 | 2022-02-01 | L4 |  |  | 10093 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.76 | UG/L | 60.4999 | 2022-02-01 | L5 |  |  | 124 LANDSTAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 61.08 | UG/L | 80.4999 | 2022-02-01 | L5 |  |  | 124 LANDSTAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.36 | UG/L | 60.4999 | 2022-02-01 | L6 |  |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 32.37 | UG/L | 80.4999 | 2022-02-01 | L6 |  |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.3 | MG/L | 0 | 2022-02-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2022-02-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-02-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.7 | MG/L | 0 | 2022-02-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-02-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-02-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2022-02-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-02-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-02-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2022-02-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-02-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-02-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 32.2 | MG/L | 0 | 2022-02-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-02-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2022-02-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.2 | MG/L | 0 | 2022-02-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2022-02-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-02-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.2 | MG/L | 0 | 2022-02-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-02-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-02-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.59 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.34 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | NAVY PPOE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.57 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.33 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.9 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | SOUTHWEST POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.79 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.27 | UG/L | 10.4999 | 2022-02-07 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2022-02-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-02-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-02-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.1 | MG/L | 0 | 2022-02-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-02-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-02-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.1 | MG/L | 0 | 2022-02-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-02-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-02-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2022-02-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2022-02-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2022-02-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.4 | MG/L | 0 | 2022-02-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-02-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-02-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2022-02-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2022-02-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 137 | MG/L |  | 2022-02-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.1 | MG/L | 0 | 2022-02-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-02-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-02-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-03-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.04 | MG/L | 10.4999 | 2022-03-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2022-03-01 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-03-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2022-03-01 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2022-03-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2022-03-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2022-03-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-03-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-03-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2022-03-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-03-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-03-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.2 | MG/L | 0 | 2022-03-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-03-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-03-02 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2022-03-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2022-03-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2022-03-02 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2022-03-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2022-03-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-03-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-03-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2022-03-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-03-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.4 | MG/L | 0 | 2022-03-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2022-03-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-03-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.64 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.06 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.6 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | PINE HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.74 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.78 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | NAVY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.57 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | CONWAY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.24 | UG/L | 10.4999 | 2022-03-07 | L7 |  |  | SKY LAKE POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2022-03-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2022-03-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-03-16 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2022-03-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-03-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-03-16 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2022-03-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2022-03-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-03-16 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-03-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2022-03-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-03-16 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.9 | MG/L | 0 | 2022-03-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2022-03-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-03-16 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.6 | MG/L | 0 | 2022-03-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-03-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-03-16 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.4 | MG/L | 0 | 2022-03-30 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2022-03-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-03-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-03-16 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-03-30 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-03-30 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2022-03-30 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-03-30 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-03-30 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 46.2 | MG/L | 0 | 2022-03-30 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-03-30 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-03-30 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2022-03-30 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-03-30 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-03-30 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2022-03-30 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-03-30 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2022-03-30 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2022-03-30 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-03-30 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-03-30 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 32.6 | MG/L | 0 | 2022-03-30 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-03-30 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-03-30 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.45 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | SOUTHWEST ENTRY PPOINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.2 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | KIRKMAN ENTRY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.99 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.01 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.25 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.39 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.71 | UG/L | 10.4999 | 2022-04-04 | L7 |  |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2022-04-13 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-04-13 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-04-13 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41 | MG/L | 0 | 2022-04-13 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-04-13 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-04-13 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2022-04-13 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-04-13 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-04-13 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2022-04-13 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2022-04-13 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-04-13 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-04-13 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2022-04-13 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-04-13 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2022-04-13 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-04-13 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-04-13 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.6 | MG/L | 0 | 2022-04-13 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-04-13 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-04-13 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2022-04-27 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-04-27 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-04-27 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2022-04-27 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-04-27 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-04-27 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-04-27 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-04-27 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-04-27 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2022-04-27 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-04-27 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-04-27 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-04-27 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-04-27 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-04-27 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2022-04-27 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2022-04-27 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-04-27 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.1 | MG/L | 0 | 2022-04-27 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-04-27 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-04-27 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.12 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.43 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.32 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.15 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.5 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.38 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.6 | UG/L | 10.4999 | 2022-05-02 | L7 | 0.59 |  | 5/22 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.96 | UG/L | 60.4999 | 2022-05-02 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 16.73 | UG/L | 80.4999 | 2022-05-02 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.32 | UG/L | 60.4999 | 2022-05-02 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 53.3 | UG/L | 80.4999 | 2022-05-02 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.64 | UG/L | 60.4999 | 2022-05-02 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 53.2 | UG/L | 80.4999 | 2022-05-02 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.1 | UG/L | 60.4999 | 2022-05-02 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 60.54 | UG/L | 80.4999 | 2022-05-02 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.8 | UG/L | 60.4999 | 2022-05-02 | L5 | 2 |  | LANDSTAR BLVD. & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 61.41 | UG/L | 80.4999 | 2022-05-02 | L5 | 0.12 |  | LANDSTAR BLVD. & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.18 | UG/L | 60.4999 | 2022-05-02 | L6 | 2 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 32.97 | UG/L | 80.4999 | 2022-05-02 | L6 | 0.12 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2022-05-11 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-05-11 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-05-11 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2022-05-11 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2022-05-11 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-05-11 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-05-11 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-05-11 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-05-11 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2022-05-11 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2022-05-11 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-05-11 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-05-11 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-05-11 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2022-05-11 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-05-11 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-05-11 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.7 | MG/L | 0 | 2022-05-11 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-05-11 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-05-11 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.26 | MG/L | 10.4999 | 2021-10-27 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0.22 | MG/L | 1.4999 | 2021-10-27 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1025 | FLUORIDE | 0.22 | MG/L | 4.0499 | 2022-10-18 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0.26 | MG/L | 1.4999 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1010 | BARIUM | 0.036 | MG/L | 2.4999 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-05-11 | WTP1 |  |  | 1020 HIGHLAND AVE.
3484383 | BITHLO COMMUNITY PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.05 | UG/L | 60.4999 | 2022-08-15 | L1 | 0.98 |  | EAST BALL PARK TAP | 3
3484383 | BITHLO COMMUNITY PARK | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2022-08-15 | L1 | 0.39 |  | EAST BALL PARK TAP | 3
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1052 | SODIUM | 100 | MG/L | 160.4999 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-10-18 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2022-05-25 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-05-25 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-05-25 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2022-05-25 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-05-25 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-05-25 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.3 | MG/L | 0 | 2022-05-25 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-05-25 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-05-25 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2022-05-25 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2022-05-25 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-05-25 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2022-05-25 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-05-25 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-05-25 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2022-05-25 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2022-05-25 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-05-25 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.6 | MG/L | 0 | 2022-05-25 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-05-25 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-05-25 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.95 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.99 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.46 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.17 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.91 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.1 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.68 | UG/L | 10.4999 | 2022-06-06 | L7 | 0.59 |  | 6/22 BROMATE - SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2022-06-08 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-06-08 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2022-06-08 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2022-06-08 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-06-08 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-06-08 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2022-06-08 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2022-06-08 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-06-08 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-06-08 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2022-06-08 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2022-06-08 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.4 | MG/L | 0 | 2022-06-08 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-06-08 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-06-08 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2022-06-08 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-06-08 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-06-08 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.3 | MG/L | 0 | 2022-06-08 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-06-08 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-06-08 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-06-22 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-06-22 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-06-22 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2022-06-22 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-06-22 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2022-06-22 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-06-22 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-06-22 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-06-22 | WTP10 |  |  | SKY LAKE WTP @ 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.5 | MG/L | 0 | 2022-06-22 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2022-06-22 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-06-22 | WTP1 |  |  | 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.6 | MG/L | 0 | 2022-06-22 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-06-22 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-06-22 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2022-06-22 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-06-22 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-06-22 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.6 | MG/L | 0 | 2022-06-22 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-06-22 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-06-22 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.06 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.32 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.52 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.74 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.95 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.96 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.29 | UG/L | 10.4999 | 2022-07-05 | L7 | 0.59 |  | 7/22 BROMATE - SKY LAKE (HLKD)
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.1 | MG/L | 0 | 2022-07-06 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-07-06 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-07-06 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-07-06 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2022-07-06 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-07-06 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-07-06 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.2 | MG/L | 0 | 2022-07-06 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-07-06 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2022-07-06 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-07-06 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-07-06 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-07-06 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2022-07-06 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-07-06 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-07-06 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2022-07-06 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-07-06 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.4 | MG/L | 0 | 2022-07-06 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-07-06 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-07-06 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-07-12 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-07-12 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-07-12 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 26.7 | MG/L |  | 2022-07-12 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.3 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-07-12 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-07-12 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 635 W CONCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 635 W CONCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-07-12 | WTP1 |  |  | 635 W CONCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-07-12 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-07-12 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-07-12 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-07-12 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-07-12 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2022-07-20 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-07-20 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-07-20 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.3 | MG/L | 0 | 2022-07-20 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-07-20 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-07-20 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2022-07-20 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-07-20 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-07-20 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2022-07-20 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-07-20 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-07-20 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2022-07-20 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-07-20 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-07-20 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2022-07-20 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2022-07-20 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-07-20 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.6 | MG/L | 0 | 2022-07-20 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-07-20 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-07-20 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.41 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.36 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.32 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.53 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.54 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.16 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.18 | UG/L | 10.4999 | 2022-08-01 | L7 | 0.59 |  | 8/22 BROMATE - SKYLAKE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.04 | UG/L | 60.4999 | 2022-08-01 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 24.86 | UG/L | 80.4999 | 2022-08-01 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.04 | UG/L | 60.4999 | 2022-08-01 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 61.33 | UG/L | 80.4999 | 2022-08-01 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.84 | UG/L | 60.4999 | 2022-08-01 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 60.76 | UG/L | 80.4999 | 2022-08-01 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.98 | UG/L | 60.4999 | 2022-08-01 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 67.08 | UG/L | 80.4999 | 2022-08-01 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.84 | UG/L | 60.4999 | 2022-08-01 | L5 | 2 |  | LANDSTAR (BLVD) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 66.16 | UG/L | 80.4999 | 2022-08-01 | L5 | 0.12 |  | LANDSTAR (BLVD) & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.71 | UG/L | 60.4999 | 2022-08-01 | L6 | 2 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 37.12 | UG/L | 80.4999 | 2022-08-01 | L6 | 0.12 |  | 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2022-08-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-08-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-08-02 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2022-08-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-08-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-08-02 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.2 | MG/L | 0 | 2022-08-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2022-08-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-08-02 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.4 | MG/L | 0 | 2022-08-02 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-08-02 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-08-02 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2022-08-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-08-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.5 | MG/L | 0 | 2022-08-02 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-08-02 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-08-02 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-08-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-08-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2022-08-02 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2022-08-17 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-08-17 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-08-17 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2022-08-17 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2022-08-17 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-08-17 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2022-08-17 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2022-08-17 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-08-17 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2022-08-17 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-08-17 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-08-17 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2022-08-17 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-08-17 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-08-17 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.3 | MG/L | 0 | 2022-08-17 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-08-17 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-08-31 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-08-31 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-08-31 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2022-08-31 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2022-08-31 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-08-31 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.3 | MG/L | 0 | 2022-08-31 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-08-31 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-08-31 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2022-08-31 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-08-31 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-08-31 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-08-31 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-08-02 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2022-08-17 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-08-17 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-08-17 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-08-17 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2022-08-31 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2022-08-31 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41 | MG/L | 0 | 2022-08-31 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-08-31 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-08-31 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2022-08-31 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-08-31 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-08-31 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.83 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | SOUTHWEST POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.55 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | KIRKMAN POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.97 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | PINE HILLS POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.88 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | HIGHLAND POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.31 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.47 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | CONWAY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.78 | UG/L | 10.4999 | 2022-09-06 | L7 | 0.59 |  | SKY LAKE POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2022-09-14 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-09-14 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-09-14 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2022-09-14 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-09-14 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2022-09-14 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.3 | MG/L | 0 | 2022-09-14 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-09-14 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-09-14 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2022-09-14 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-09-14 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-09-14 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.3 | MG/L | 0 | 2022-09-14 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-09-14 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-09-14 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2022-09-14 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-09-14 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-09-14 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2022-09-14 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-09-14 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-09-14 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-18 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-18 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-18 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-18 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-18 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-18 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-18 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-18 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-18 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-18 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-18 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-18 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-18 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-18 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-18 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-18 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-18 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-18 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-18 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-18 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-18 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-18 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-18 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-18 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-18 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-18 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-18 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-18 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-11-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-11-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.099 | MG/L | 10.4999 | 2023-10-18 | AAA | 0.024 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-18 | AAA |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2024-09-03 | AAA | 0.024 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-03 | AAA |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2025-06-09 | AAA |  | 0.667 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-06-09 | AAA |  | 0.5499 | POE
3484383 | BITHLO COMMUNITY PARK | N | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2025-06-09 | AAA | 0.0099 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2025-06-09 | AAA |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | RAD | 4020 | RADIUM-226 | 1.6 | PCI/L | 3.4999 | 2025-06-09 | AAA | 0.2 | 1.4999 | POE
3484383 | BITHLO COMMUNITY PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-06-09 | AAA |  | 1.4999 | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.14 | MG/L | 10.4999 | 2025-06-09 | E53076 | 0.024 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0.084 | MG/L | 1.4999 | 2025-06-09 | E53076 | 0.0034 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1010 | BARIUM | 0.038 | MG/L | 2.4999 | 2025-06-09 | E53076 | 0.003 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1024 | CYANIDE | 0.016 | MG/L | 0.2499 | 2025-06-09 | E53076 | 0.002 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2025-06-09 | E53076 | 0.0099 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1052 | SODIUM | 120 | MG/L | 160.4999 | 2025-06-09 | E53076 | 0.8 |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-06-09 | E53076 |  |  | POE
3484383 | BITHLO COMMUNITY PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-19 | L1 | 4.9 |  | EAST BALL PARK TAP | 3
3484383 | BITHLO COMMUNITY PARK | D | DBP | 2950 | TOTAL THMS | 5.15 | UG/L | 80.4999 | 2025-08-19 | L1 | 0.44 |  | EAST BALL PARK TAP | 3
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 74.2 | UG/L | 60.4999 | 2021-03-11 | L1 | 1 |  | HANDWASH SINK (J QUAL ON 2451 DIC ACID & 2452 TRI ACID, L QUAL ON 2941 CHLOR) LOOKS LIKE TTHMS LRAA MCL VIOL @ 84.0275 (HLKD)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 130 | UG/L | 80.4999 | 2021-03-11 | L1 | 0.5 |  | HANDWASH SINK (J QUAL ON 2451 DIC ACID & 2452 TRI ACID, L QUAL ON 2941 CHLOR) LOOKS LIKE TTHMS LRAA MCL VIOL @ 84.0275 (HLKD)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 80.8 | UG/L | 60.4999 | 2021-06-17 | L1 | 1 |  | HANDWASH SINK(TOT TTHM DID NOT INCLUDE 2941 CHLOROFORM 119 UG/L W/ L QUALIFIER. TOT GIVEN AS 6.65 BUT ACT. TOTAL IS 125.65(**LAB REVISED 8/10/21 TO 126)3/21 TTHM MCL VIOL DID NOT GEN./POST(BB7/24/21)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 126 | UG/L | 80.4999 | 2021-06-17 | L1 | 0.5 |  | HANDWASH SINK(TOT TTHM DID NOT INCLUDE 2941 CHLOROFORM 119 UG/L W/ L QUALIFIER. TOT GIVEN AS 6.65 BUT ACT. TOTAL IS 125.65(**LAB REVISED 8/10/21 TO 126)3/21 TTHM MCL VIOL DID NOT GEN./POST(BB7/24/21)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1040 | NITRATE | 0.377 | MG/L | 10.4999 | 2021-08-04 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-08-04 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 67.5 | UG/L | 60.4999 | 2021-09-17 | L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 96.6 | UG/L | 80.4999 | 2021-09-17 | L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 51.8 | UG/L | 60.4999 | 2021-12-22 | L1 | 1 |  | TTHM LRAA = 104.02 UG/L, HAA5 LRAA = 68.57 UG/L (ATR)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 63.5 | UG/L | 80.4999 | 2021-12-22 | L1 | 0.5 |  | TTHM LRAA = 104.02 UG/L, HAA5 LRAA = 68.57 UG/L (ATR)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.4 | UG/L | 60.4999 | 2022-03-22 | L1 | 1 |  | HAND WASH SINK TTHM LRAA = 81.00 UG/L & HAA5 LRAA = 54.62; TTHM OE = 58.97 UG/L & HAA5 OE =39.02 (ATR)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 37.9 | UG/L | 80.4999 | 2022-03-22 | L1 | 0.5 |  | HAND WASH SINK TTHM LRAA = 81.00 UG/L & HAA5 LRAA = 54.62; TTHM OE = 58.97 UG/L & HAA5 OE =39.02 (ATR)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1010 | BARIUM | 0.0196 | MG/L | 2.4999 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1025 | FLUORIDE | 0.206 | MG/L | 4.0499 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1052 | SODIUM | 12.2 | MG/L | 160.4999 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SEC | 1025 | FLUORIDE | 0.206 | MG/L | 2.0499 | 2022-04-19 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-04-19 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-04-19 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-04-19 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-04-19 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-04-19 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-04-19 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-04-19 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-04-19 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-04-19 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-04-19 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-04-19 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-04-19 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-04-19 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-04-19 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-04-19 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-04-19 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-04-19 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-04-19 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-04-19 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-04-19 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | DBP | 2950 | TOTAL THMS | 4.02 | UG/L | 80.4999 | 2022-06-23 | L1 | 0.5 |  | HAND WASH SINK L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | DBP | 2941 | CHLOROFORM | 3.7 | UG/L | 100 | 2022-06-23 | L1 | 0.5 |  | HAND WASH SINK L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2022-06-23 | L1 |  |  | HAND WASH SINK L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | DBP | 2943 | BROMODICHLOROMETHANE | 0 | UG/L | 100 | 2022-06-23 | L1 |  |  | HAND WASH SINK L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | DBP | 2944 | DIBROMOCHLOROMETHANE | 0 | UG/L | 100 | 2022-06-23 | L1 |  |  | HAND WASH SINK L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.1 | UG/L | 60.4999 | 2022-08-29 | L1 | 0.38 |  | HAND WASH SINK TTHM V QUALIFIER PROCESSED BY E83018/ HAA5
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 4.02 | UG/L | 80.4999 | 2022-06-23 | L1 | 0.5 |  | HAND WASH SINK (TTHMS ONLY) RCVD 8/5/22 (HLKD)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 3.3 | UG/L | 80.4999 | 2022-08-29 | L1 | 0.5 |  | HAND WASH SINK TTHM V QUALIFIER PROCESSED BY E83018/ HAA5
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.1 | UG/L | 60.4999 | 2022-09-13 | L1 | 0.38 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 5.3 | UG/L | 80.4999 | 2022-09-13 | L1 | 0.5 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 39.88 | UG/L | 80.4999 | 2022-12-21 | L1 | 0.39 |  | 4TH QUARTER DBP SAMPLES_CC
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.15 | UG/L | 60.4999 | 2022-12-21 | L1 | 0.98 |  | 4TH QUARTER DBP SAMPLES_CC
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-17 | AAA |  |  | DISTRIBUTION
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-17 | AAA |  |  | DISTRIBUTION
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2023-03-21 | L1 | 0.98 |  | HAND WASH SINK (MISSING DISINF RESIDUAL)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 2.02 | UG/L | 80.4999 | 2023-03-21 | L1 | 0.39 |  | HAND WASH SINK (MISSING DISINF RESIDUAL)
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2023-06-27 | L1 | 0.98
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2023-06-27 | L1 | 0.39
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.6 | UG/L | 60.4999 | 2023-09-26 | L1 | 0.3 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 42.6 | UG/L | 80.4999 | 2023-09-26 | L1 | 0.5 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 17.63 | UG/L | 80.4999 | 2023-12-14 | L1 | 0.39 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.1 | UG/L | 60.4999 | 2023-12-14 | L1 | 0.98 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-03-20 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-20 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.1 | UG/L | 60.4999 | 2024-03-21 | L1 | 0.3 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 9.9 | UG/L | 80.4999 | 2024-03-21 | L1 | 0.5 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-06-27 | L1 | 0.3 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-06-27 | L1 | 0.5 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 105.6 | UG/L | 60.4999 | 2024-09-17 | L1 | 0.3 |  | L1 HAND WASH SINK - TTHM/HAA5 EXCEEDANCE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 179.2 | UG/L | 80.4999 | 2024-09-17 | L1 | 0.5 |  | L1 HAND WASH SINK - TTHM/HAA5 EXCEEDANCE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 18.3 | UG/L | 80.4999 | 2024-12-23 | L1 | 0.5 |  | L1 HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.2 | UG/L | 60.4999 | 2024-12-23 | L1 | 0.2 |  | L1 HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-03-19 | L1 | 0.2 |  | L1 HANDWASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-03-19 | L1 | 0.5 |  | L1 HANDWASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0.91 | UG/L | 60.4999 | 2025-06-24 | L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-06-24 | L1
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0.91 | UG/L | 60.4999 | 2025-06-24 | L1 | 0.2 |  | L1 HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-06-24 | L1 | 0.21 |  | L1 HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-09-16 | L1 | 0.2 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-09-16 | L1 | 0.21 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2025-09-16 | AAA | 0.0004 |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1020 | CHROMIUM | 0.0018 | MG/L | 0.1499 | 2025-09-16 | AAA | 0.0004 |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2025-09-16 | AAA | 0.1 |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1035 | MERCURY | 0.0004 | MG/L | 0.0024 | 2025-09-16 | AAA | 0.0002 |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1052 | SODIUM | 15 | MG/L | 160.4999 | 2025-09-16 | AAA | 0.13 |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-09-16 | AAA |  |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | SEC | 1025 | FLUORIDE | 0.16 | MG/L | 2.0499 | 2025-09-16 | AAA | 0.1 |  | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-09-16 | AAA |  | 0.5499 | POE
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-12-16 | L1 | 0.2 |  | HAND WASH SINK
3484384 | SUNSHINE LEARNERS ACADEMY INC. | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-12-16 | L1 | 0.21 |  | HAND WASH SINK
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.1 | MG/L | 0 | 2022-09-26 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-09-26 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-09-26 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.8 | MG/L | 0 | 2022-09-26 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-09-26 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-09-26 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.1 | MG/L | 0 | 2022-09-26 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2022-09-26 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-09-26 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-09-26 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-09-26 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-09-26 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2022-09-26 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-09-26 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-09-26 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2022-09-26 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-09-26 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-09-26 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2022-09-26 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-09-26 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-09-26 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.84 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.4 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.97 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.22 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.12 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.74 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.6 | UG/L | 10.4999 | 2022-10-03 | L7 | 0.59 |  | 10/22 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-10-05 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-10-05 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-10-05 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 1128 W PRINCETONST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 1128 W PRINCETONST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-10-05 | WTP1 |  |  | 1128 W PRINCETONST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-10-05 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-10-05 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2022-10-05 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-10-05 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-10-05 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2022-10-05 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-10-05 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-10-05 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2022-10-12 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-10-12 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-10-12 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.1 | MG/L | 0 | 2022-10-12 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-10-12 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-10-12 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.2 | MG/L | 0 | 2022-10-12 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-10-12 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-10-12 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2022-10-12 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-10-12 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2022-10-12 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2022-10-12 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-10-12 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-10-12 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-10-12 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-10-12 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2022-10-12 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.3 | MG/L | 0 | 2022-10-12 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-10-12 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-10-12 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2022-10-26 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-10-26 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2022-10-26 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2022-10-26 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2022-10-26 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-10-26 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2022-10-26 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-10-26 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-10-26 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2022-10-26 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-10-26 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2022-10-26 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.3 | MG/L | 0 | 2022-10-26 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-10-26 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-10-26 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2022-10-26 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.4 | MG/L | 0 | 2022-10-26 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2022-10-26 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2022-10-26 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-10-26 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-10-26 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.27 | UG/L | 60.4999 | 2022-11-01 | L1 | 2 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 44.98 | UG/L | 80.4999 | 2022-11-01 | L1 | 0.12 |  | 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.32 | UG/L | 60.4999 | 2022-11-01 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.57 | UG/L | 80.4999 | 2022-11-01 | L2 | 0.12 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.09 | UG/L | 60.4999 | 2022-11-01 | L3 | 2 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 74.86 | UG/L | 80.4999 | 2022-11-01 | L3 | 0.12 |  | 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.24 | UG/L | 60.4999 | 2022-11-01 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 66.29 | UG/L | 80.4999 | 2022-11-01 | L4 | 0.12 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.06 | UG/L | 60.4999 | 2022-11-01 | L5 | 2 |  | LANDSTAR & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 68.94 | UG/L | 80.4999 | 2022-11-01 | L5 | 0.12 |  | LANDSTAR & IOWA WOODS CIR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.12 | UG/L | 60.4999 | 2022-11-01 | L6 | 2 |  | 5512 BAYSIDE DR. (12/22 QTR DISINF BYP RPRT RCVD SEPARATELY) HLKD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 36.59 | UG/L | 80.4999 | 2022-11-01 | L6 | 0.12 |  | 5512 BAYSIDE DR. (12/22 QTR DISINF BYP RPRT RCVD SEPARATELY) HLKD
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.07 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - SW
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.65 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.63 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.55 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.49 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.48 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.63 | UG/L | 10.4999 | 2022-11-07 | L7 | 0.59 |  | 11/22 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2022-11-09 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-11-09 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-11-09 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2022-11-09 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-11-09 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2022-11-09 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.3 | MG/L | 0 | 2022-11-09 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-11-09 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-11-09 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2022-11-09 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-11-09 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-11-09 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2022-11-09 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-11-09 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-11-09 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2022-11-09 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2022-11-09 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2022-11-09 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.3 | MG/L | 0 | 2022-11-09 | WTP10 |  |  | SKY LAKE WTP 502 SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-11-09 | WTP10 |  |  | SKY LAKE WTP 502 SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2022-11-09 | WTP10 |  |  | SKY LAKE WTP 502 SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2022-11-23 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2022-11-23 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2022-11-23 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.3 | MG/L | 0 | 2022-11-23 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-11-23 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2022-11-23 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.2 | MG/L | 0 | 2022-11-23 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-11-23 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-11-23 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2022-11-23 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-11-23 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-11-23 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2022-11-23 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-11-23 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-11-23 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2022-11-23 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2022-11-23 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-11-23 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.7 | MG/L | 0 | 2022-11-23 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2022-11-23 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-11-23 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.19 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - SW
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.92 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.54 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 11.4 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.19 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.97 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.99 | UG/L | 10.4999 | 2022-12-05 | L7 | 0.59 |  | 12/22 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2022-12-07 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2022-12-07 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-12-07 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3481093 | ROCK SPRINGS MHP | N | INOR | 1040 | NITRATE | 0.361 | MG/L | 10.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-06-07 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1010 | BARIUM | 0.0143 | MG/L | 2.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1020 | CHROMIUM | 0.0011 | MG/L | 0.1499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1052 | SODIUM | 13.9 | MG/L | 160.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1017 | CHLORIDE | 20.2 | MG/L | 250.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1022 | COPPER | 0.0017 | MG/L | 1.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1028 | IRON | 0.0303 | MG/L | 0.3499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1055 | SULFATE | 19.1 | MG/L | 250.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2022-12-07 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2022-12-07 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-12-07 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.1 | MG/L | 0 | 2022-12-07 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-12-07 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-12-07 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2022-12-07 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2022-12-07 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-12-07 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2022-12-07 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-12-07 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-12-07 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2022-12-07 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-12-07 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2022-12-07 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2022-12-07 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2022-12-07 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2022-12-07 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2022-12-21 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-12-21 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2022-12-21 | WTP7 |  |  | KIRKMAN WTP 4070 S. KIRKMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2022-12-21 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2022-12-21 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 137 | MG/L |  | 2022-12-21 | WTP6 |  |  | CONWAY WTP 2725 S. CONWAY RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2022-12-21 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-12-21 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-12-21 | WTP5 |  |  | PINE HILLS WTP 5601 SANTA ANITA ST.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2022-12-21 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2022-12-21 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-12-21 | WTP1 |  |  | HIGHLAND WTP 1020 HIGHLAND AVE.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2022-12-21 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-12-21 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-12-21 | WTP11 |  |  | SOUTH WEST WTP 6825 WALLACE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.7 | MG/L | 0 | 2022-12-21 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2022-12-21 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2022-12-21 | WTP8 |  |  | NAVY WTP 1360 TRUMAN RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.7 | MG/L | 0 | 2022-12-21 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2022-12-21 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2022-12-21 | WTP10 |  |  | SKY LAKE WTP 502 W. SAND LAKE RD.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.73 | UG/L | 10.4999 | 2023-01-03 | L7 | 0.59 |  | 1/23 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.84 | UG/L | 10.4999 | 2023-01-03 | L7 | 0.59 |  | 1/23 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.21 | UG/L | 10.4999 | 2023-01-03 | L7 | 0.59 |  | 1/23 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.83 | UG/L | 10.4999 | 2023-01-03 | L7 | 0.59 |  | 1/23 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.78 | UG/L | 10.4999 | 2023-01-03 | L7 | 0.59 |  | 1/23 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.24 | UG/L | 10.4999 | 2023-01-03 | L7 | 0.59 |  | 1/23 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.99 | UG/L | 10.4999 | 2023-01-03 | L7 | 0.59 |  | 1/23 BROMATE - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-01-04 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2023-01-04 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-01-04 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-01-04 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2023-01-04 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 136 | MG/L |  | 2023-01-04 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2023-01-04 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-01-04 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-01-04 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-01-04 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2023-01-04 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2023-01-04 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2023-01-04 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2023-01-04 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-01-04 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2023-01-04 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.3 | MG/L | 0 | 2023-01-04 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-01-04 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2023-01-04 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2023-01-04 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-01-04 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-01-10 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-01-10 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-01-10 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-01-10 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-01-10 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-01-10 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-01-10 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.5 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2023-01-10 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-01-10 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2023-01-10 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-01-10 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-01-10 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2023-01-18 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-01-18 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-01-18 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2023-01-18 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-01-18 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2023-01-18 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2023-01-18 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-01-18 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-01-18 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.9 | MG/L | 0 | 2023-01-18 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-01-18 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-01-18 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2023-01-18 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2023-01-18 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-01-18 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.6 | MG/L | 0 | 2023-01-18 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-01-18 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-01-18 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2023-01-18 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-01-18 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2023-01-18 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2023-01-23 | WTP7 | 0.03 |  | POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-23 | WTP7 |  |  | POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2023-02-01 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-02-01 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-02-01 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2023-02-01 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-02-01 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2023-02-01 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.3 | MG/L | 0 | 2023-02-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-02-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2023-02-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.3 | MG/L | 0 | 2023-02-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-02-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-02-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2023-02-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-02-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-02-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.95 | UG/L | 60.4999 | 2023-02-01 | L1 | 2 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 38.94 | UG/L | 80.4999 | 2023-02-01 | L1 | 0.13 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.79 | UG/L | 60.4999 | 2023-02-01 | L2 | 2 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.27 | UG/L | 80.4999 | 2023-02-01 | L2 | 0.13 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.34 | UG/L | 60.4999 | 2023-02-01 | L3 | 2 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.18 | UG/L | 80.4999 | 2023-02-01 | L3 | 0.13 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.3 | UG/L | 60.4999 | 2023-02-01 | L4 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 60.76 | UG/L | 80.4999 | 2023-02-01 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.73 | UG/L | 60.4999 | 2023-02-01 | L5 | 2 |  | SMP PT 124 LANDSTAR RD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 67.38 | UG/L | 80.4999 | 2023-02-01 | L5 | 0.13 |  | SMP PT 124 LANDSTAR RD
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.72 | UG/L | 60.4999 | 2023-02-01 | L6 | 2 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 37.79 | UG/L | 80.4999 | 2023-02-01 | L6 | 0.13 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.6 | MG/L | 0 | 2023-02-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-02-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-02-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-02-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-02-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-02-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.12 | UG/L | 10.4999 | 2023-02-06 | L7 | 0.59 |  | POE - SOUTHWEST BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.55 | UG/L | 10.4999 | 2023-02-06 | L7 | 0.59 |  | POE - KIRKMAN BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.1 | UG/L | 10.4999 | 2023-02-06 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 10.3 | UG/L | 10.4999 | 2023-02-06 | L7 | 0.59 |  | HIGHLAND POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.21 | UG/L | 10.4999 | 2023-02-06 | L7 | 0.59 |  | NAVY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.99 | UG/L | 10.4999 | 2023-02-06 | L7 | 0.59 |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.51 | UG/L | 10.4999 | 2023-02-06 | L7 | 0.59 |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-07 | WTP1 | 0.0092 | 0.0149 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP1 | 0.0062 | 0.0249 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP8 | 0.0062 | 0.0249 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP5 | 0.0062 | 0.0249 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP7 | 0.0062 | 0.0249 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP11 | 0.0063 | 0.0249 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-07 | WTP11 | 0.0093 | 0.0149 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP6 | 0.0062 | 0.0249 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-07 | WTP10 | 0.12 | 1.4999 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-07 | WTP10 | 0.09 | 0.1499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-07 | WTP10 | 0.18 | 0.2499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-07 | WTP10 | 0.095 | 0.1499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-07 | WTP10 | 0.09 | 0.2499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-07 | WTP10 | 0.038 | 0.0449 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP10 | 0.02 | 0.0249 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-07 | WTP10 | 0.0092 | 0.0149 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-02-07 | WTP1 | 0.0003 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-07 | WTP1 | 0.0005 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1036 | NICKEL | 0.002 | MG/L | 0.1499 | 2023-02-07 | WTP1 | 0.002 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-02-07 | WTP1 | 0.0006 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1052 | SODIUM | 11.5 | MG/L | 160.4999 | 2023-02-07 | WTP1 | 0.08 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-02-07 | WTP1 | 0.001 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-07 | WTP1 | 0.001 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-02-07 | WTP1 | 0.0008 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-07 | WTP1 | 0.004 |  | HIGHLAND CYANIDE ONLY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-07 | WTP1 | 0.006 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1017 | CHLORIDE | 17.2 | MG/L | 250.4999 | 2023-02-07 | WTP1 | 0.11 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-02-07 | WTP1 | 0.003 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1025 | FLUORIDE | 0.7 | MG/L | 2.0499 | 2023-02-07 | WTP1 | 0.025 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-02-07 | WTP1 | 0.005 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-02-07 | WTP1 | 0.002 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-02-07 | WTP1 | 0.0001 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1055 | SULFATE | 6.99 | MG/L | 250.4999 | 2023-02-07 | WTP1 | 0.16 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1905 | COLOR | 2 | COLOR UNITS | 15.4999 | 2023-02-07 | WTP1 | 1 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1920 | ODOR THRESHOLD | 4 |  | 3.4999 | 2023-02-07 | WTP1 | 1 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.34 | LN(10) |  | 2023-02-07 | WTP1 | 1 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 200 | MG/L | 500.4999 | 2023-02-07 | WTP1 | 5 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 2905 | FOAMING AGENTS | 0.064 |  | 0.5499 | 2023-02-07 | WTP1 | 0.04 |  | HIGHLAND FOAMING AGENTS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP1 | 0.12 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP1 | 0.16 | 0.5499 | HIGHLAND
3481093 | ROCK SPRINGS MHP | N | SEC | 1095 | ZINC | 0.002 | MG/L | 5.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.19 | LN(10) |  | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 238 | MG/L | 500.4999 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-08-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-08-12 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-08-12 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-08-12 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-08-12 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-08-12 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-08-12 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-08-12 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-08-12 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-08-12 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-08-12 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-08-12 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-08-12 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-08-12 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-08-12 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-08-12 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-08-12 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-08-12 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-08-12 | AAA | 0.5 | 0.5499 | 3YR VOC
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-09-03 | L1 |  |  | BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-09-03 | L1 |  |  | BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-09-03 | L2 |  |  | SEWER PLANT | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-09-03 | L2 |  |  | SEWER PLANT | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.3 | UG/L | 60.4999 | 2021-12-08 | L1 | 60 |  |  | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 30.9 | UG/L | 80.4999 | 2021-12-08 | L1 | 80 |  |  | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.3 | UG/L | 60.4999 | 2021-12-08 | L1 | 60 |  |  | 3
3481093 | ROCK SPRINGS MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1040 | NITRATE | 0.339 | MG/L | 10.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-09-20 | L1 | 0.38 |  | 314 BAHIA MAR (HLKD) HAA5/E87052 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2022-09-20 | L1 | 0.5 |  | 314 BAHIA MAR (HLKD) HAA5/E87052 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0.38 | UG/L | 60.4999 | 2022-09-20 | L2 |  |  | SEWER PLANT (HLKD) HAA5/E87052 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 0.5 | UG/L | 80.4999 | 2022-09-20 | L2 |  |  | SEWER PLANT (HLKD) HAA5/E87052 | 3
3481093 | ROCK SPRINGS MHP | N | INOR | 1040 | NITRATE | 0.092 | MG/L | 10.4999 | 2023-01-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.32 | UG/L | 60.4999 | 2023-09-27 | L1 | 0.98 |  | 314 BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 19.44 | UG/L | 80.4999 | 2023-09-27 | L1 | 0.39 |  | 314 BAHIA MAR | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.39 | UG/L | 60.4999 | 2023-09-27 | L2 | 0.98 |  | SEWER PLANT (WWTF) | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 7.24 | UG/L | 80.4999 | 2023-09-27 | L2 | 0.39 |  | SEWER PLANT (WWTF) | 3
3481093 | ROCK SPRINGS MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-01-30 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2024-05-14 | AAA | 0.00033 |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1020 | CHROMIUM | 0.0008 | MG/L | 0.1499 | 2024-05-14 | AAA | 0.0004 |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2024-05-14 | AAA | 0.025 |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1030 | LEAD | 0.0003 | MG/L | 0.0154 | 2024-05-14 | AAA | 0.0002 |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1052 | SODIUM | 19 | MG/L | 160.4999 | 2024-05-14 | AAA | 0.12 |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1017 | CHLORIDE | 39 | MG/L | 250.4999 | 2024-05-14 | AAA | 0.4 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1022 | COPPER | 0.019 | MG/L | 1.4999 | 2024-05-14 | AAA | 0.0006 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2024-05-14 | AAA | 0.025 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1032 | MANGANESE | 0.0033 | MG/L | 0.0549 | 2024-05-14 | AAA | 0.00089 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1055 | SULFATE | 17 | MG/L | 250.4999 | 2024-05-14 | AAA | 2 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1095 | ZINC | 0.0041 | MG/L | 5.4999 | 2024-05-14 | AAA | 0.0012 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2024-05-14 | AAA | 5 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 170 | MG/L | 500.4999 | 2024-05-14 | AAA | 5 |  | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-05-14 | AAA |  |  | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-05-14 | AAA |  | 0.5499 | POE
3481093 | ROCK SPRINGS MHP | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2024-08-22 | AAA | 1 |  | POE
3481093 | ROCK SPRINGS MHP | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-09-16 | AAA | 2.4 |  | POE
3481093 | ROCK SPRINGS MHP | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-16 | AAA | 1 | 1.4999 | POE
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-09-16 | L1 | 0.3 |  | 314 BAHIA MAR - TTHM & HAA5 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-09-16 | L1 | 0.5 |  | 314 BAHIA MAR - TTHM & HAA5 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-09-16 | L2 | 0.3 |  | SEWER PLANT - TTHM & HAA5 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-09-16 | L2 | 0.5 |  | SEWER PLANT - TTHM & HAA5 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.21 | UG/L | 60.4999 | 2025-09-19 | L1 | 0.98 |  | BAHIA MAR - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 15.78 | UG/L | 80.4999 | 2025-09-19 | L1 | 0.44 |  | BAHIA MAR - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3481093 | ROCK SPRINGS MHP | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2025-09-19 | AAA | 0.024 |  | NN
3481093 | ROCK SPRINGS MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-09-19 | AAA | 0.0034 |  | NN
3481093 | ROCK SPRINGS MHP | D | DBP | 2950 | TOTAL THMS | 9.6 | UG/L | 80.4999 | 2025-10-29 | L2 | 0.45 |  | SEWER PLANT (WWTF) | 3
3481093 | ROCK SPRINGS MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.13 | UG/L | 60.4999 | 2025-10-29 | L2 | 0.98 |  | SEWER PLANT (WWTF) | 3
3481093 | ROCK SPRINGS MHP | N | INOR | 1040 | NITRATE | 0.18 | MG/L | 10.4999 | 2025-10-29 | AAA | 0.092 |  | LOCATION CODE SET BY PWS - 03/10/2008
3481093 | ROCK SPRINGS MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-29 | AAA | 0.081 |  | LOCATION CODE SET BY PWS - 03/10/2008
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-07 | WTP1 | 0.37 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP1 | 0.16 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-07 | WTP1 | 0.1 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-07 | WTP1 | 0.12 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP1 | 0.26 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-07 | WTP1 | 0.3 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP1 | 0.27 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP1 | 0.08 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-07 | WTP1 | 0.15 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP1 | 0.15 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP1 | 0.13 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP1 | 0.15 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP1 | 0.07 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP1 | 0.17 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP1 | 0.13 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP1 | 0.15 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-07 | WTP1 | 0.14 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP1 | 0.13 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP1 | 0.13 | 0.5499 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-02-07 | WTP1 | 1.2 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-02-07 | WTP1 | 0.9 | 1.4999 | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-07 | WTP1 | 0.0069 | 0.0149 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP1 | 0.0071 | 0.0249 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-07 | WTP1 | 0.0068 | 0.1499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP1 | 0.12 | 1.4999 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-07 | WTP1 | 0.9 | 1.4999 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-07 | WTP1 | 0.37 | 0.4499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-07 | WTP1 | 6 | 9.4999 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-07 | WTP1 | 0.5 | 0.6499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP1 | 5.9 | 6.4999 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-07 | WTP1 | 1.8 | 2.4999 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-07 | WTP1 | 0.06 | 0.0749 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-07 | WTP1 | 0.5 | 0.6499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-07 | WTP1 | 0.09 | 0.1499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-07 | WTP1 | 0.18 | 0.2499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-07 | WTP1 | 0.019 | 0.1499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-07 | WTP1 | 0.51 | 0.9499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP1 | 0.09 | 0.1499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-07 | WTP1 | 0.15 | 0.2499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-07 | WTP1 | 0.006 | 0.0449 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP1 | 0.0052 | 0.0249 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-07 | WTP1 | 0.095 | 0.1499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-07 | WTP1 | 0.09 | 0.2499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP1 | 0.0063 | 0.1499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP1 | 0.015 | 0.0249 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-07 | WTP1 | 0.038 | 0.0449 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-07 | WTP1 | 0.093 | 0.1499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-07 | WTP1 | 0.053 | 0.2499 | HIGHLAND 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.04 | MG/L | 10.4999 | 2023-02-07 | WTP7 | 0.03 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-07 | WTP7 | 0.03 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-02-07 | WTP7 | 0.0007 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2023-02-07 | WTP7 | 0.002 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-02-07 | WTP7 | 0.002 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-07 | WTP7 | 0.002 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1025 | FLUORIDE | 0.56 | MG/L | 4.0499 | 2023-02-07 | WTP7 | 0.025 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-07 | WTP7 | 0.0005 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-02-07 | WTP7 | 0.0003 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-02-07 | WTP7 | 0.002 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-02-07 | WTP7 | 0.0006 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1052 | SODIUM | 9.35 | MG/L | 160.4999 | 2023-02-07 | WTP7 | 0.08 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-02-07 | WTP7 | 0.001 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-07 | WTP7 | 0.001 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-02-07 | WTP7 | 0.0008 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-07 | WTP7 | 0.004 |  | KIRKMAN CYANIDE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-07 | WTP7 | 0.006 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1017 | CHLORIDE | 13.6 | MG/L | 250.4999 | 2023-02-07 | WTP7 | 0.11 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1022 | COPPER | 0.006 | MG/L | 1.4999 | 2023-02-07 | WTP7 | 0.003 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1025 | FLUORIDE | 0.56 | MG/L | 2.0499 | 2023-02-07 | WTP7 | 0.025 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-02-07 | WTP7 | 0.005 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-02-07 | WTP7 | 0.002 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-02-07 | WTP7 | 0.0001 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1055 | SULFATE | 8.31 | MG/L | 250.4999 | 2023-02-07 | WTP7 | 0.16 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-07 | WTP7 | 0.004 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1905 | COLOR | 1 | COLOR UNITS | 15.4999 | 2023-02-07 | WTP7 | 1 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1920 | ODOR THRESHOLD | 4 |  | 3.4999 | 2023-02-07 | WTP7 | 1 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.43 | LN(10) |  | 2023-02-07 | WTP7 | 1 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 160 | MG/L | 500.4999 | 2023-02-07 | WTP7 | 5 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 2905 | FOAMING AGENTS | 0.11 |  | 0.5499 | 2023-02-07 | WTP7 | 0.04 |  | KIRKMAN FOAMING AGENTS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP7 | 0.12 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP7 | 0.16 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP7 | 0.16 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-07 | WTP7 | 0.37 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-07 | WTP7 | 0.1 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-07 | WTP7 | 0.12 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP7 | 0.26 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-07 | WTP7 | 0.3 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP7 | 0.27 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP7 | 0.08 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-07 | WTP7 | 0.15 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP7 | 0.15 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP7 | 0.13 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP7 | 0.15 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP7 | 0.07 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP7 | 0.17 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP7 | 0.13 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP7 | 0.15 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-07 | WTP7 | 0.14 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP7 | 0.13 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP7 | 0.13 | 0.5499 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-02-07 | WTP7 | 2.1 |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4030 | RADIUM-228 | 1.5 | PCI/L | 2.4999 | 2023-02-07 | WTP7 | 1 | 1.4999 | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-07 | WTP7 | 0.0069 | 0.0149 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP7 | 0.0071 | 0.0249 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-07 | WTP7 | 0.0068 | 0.1499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP7 | 0.12 | 1.4999 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-07 | WTP7 | 0.9 | 1.4999 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-07 | WTP7 | 0.37 | 0.4499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-07 | WTP7 | 6 | 9.4999 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP7 | 5.9 | 6.4999 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-07 | WTP7 | 0.5 | 0.6499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-07 | WTP7 | 1.8 | 2.4999 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-07 | WTP7 | 0.06 | 0.0749 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-07 | WTP7 | 0.05 | 0.6499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-07 | WTP7 | 0.09 | 0.1499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-07 | WTP7 | 0.18 | 0.2499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-07 | WTP7 | 0.019 | 0.1499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-07 | WTP7 | 0.51 | 0.9499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP7 | 0.09 | 0.1499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-07 | WTP7 | 0.15 | 0.2499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-07 | WTP7 | 0.006 | 0.0449 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP7 | 0.0052 | 0.0249 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-07 | WTP7 | 0.095 | 0.1499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-07 | WTP7 | 0.09 | 0.2499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP7 | 0.0063 | 0.1499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP7 | 0.015 | 0.0249 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-07 | WTP7 | 0.038 | 0.0449 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-07 | WTP7 | 0.093 | 0.1499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-07 | WTP7 | 0.0091 | 0.0149 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-07 | WTP7 | 0.053 | 0.2499 | KIRKMAN 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.05 | MG/L | 10.4999 | 2023-02-07 | WTP8 | 0.03 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-07 | WTP8 | 0.03 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-02-07 | WTP8 | 0.0007 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-02-07 | WTP8 | 0.002 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2023-02-07 | WTP8 | 0.002 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-07 | WTP8 | 0.002 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1025 | FLUORIDE | 0.86 | MG/L | 4.0499 | 2023-02-07 | WTP8 | 0.025 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-07 | WTP8 | 0.0005 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-02-07 | WTP8 | 0.0003 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-02-07 | WTP8 | 0.002 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-02-07 | WTP8 | 0.0006 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1052 | SODIUM | 12.2 | MG/L | 160.4999 | 2023-02-07 | WTP8 | 0.08 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-02-07 | WTP8 | 0.001 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-07 | WTP8 | 0.001 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-02-07 | WTP8 | 0.0008 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-07 | WTP8 | 0.004 |  | NAVY CYANIDE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-07 | WTP8 | 0.006 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1017 | CHLORIDE | 17.5 | MG/L | 250.4999 | 2023-02-07 | WTP8 | 0.11 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1022 | COPPER | 0.004 | MG/L | 1.4999 | 2023-02-07 | WTP8 | 0.003 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1025 | FLUORIDE | 0.86 | MG/L | 2.0499 | 2023-02-07 | WTP8 | 0.025 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-02-07 | WTP8 | 0.005 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-02-07 | WTP8 | 0.002 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-02-07 | WTP8 | 0.0001 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1055 | SULFATE | 6.57 | MG/L | 250.4999 | 2023-02-07 | WTP8 | 0.16 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-07 | WTP8 | 0.004 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1905 | COLOR | 1 | COLOR UNITS | 15.4999 | 2023-02-07 | WTP8 | 1 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1920 | ODOR THRESHOLD | 4 |  | 3.4999 | 2023-02-07 | WTP8 | 1 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.48 | LN(10) |  | 2023-02-07 | WTP8 | 1 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 197 | MG/L | 500.4999 | 2023-02-07 | WTP8 | 5 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 2905 | FOAMING AGENTS | 0.04 |  | 0.5499 | 2023-02-07 | WTP8 | 0.04 |  | NAVY FOAMING AGENTS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP8 | 0.12 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP8 | 0.16 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-07 | WTP8 | 0.37 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP8 | 0.16 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-07 | WTP8 | 0.1 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-07 | WTP8 | 0.12 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP8 | 0.26 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-07 | WTP8 | 0.3 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP8 | 0.27 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP8 | 0.08 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-07 | WTP8 | 0.15 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP8 | 0.15 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP8 | 0.13 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP8 | 0.15 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP8 | 0.07 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP8 | 0.17 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP8 | 0.13 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP8 | 0.16 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-07 | WTP8 | 0.14 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP8 | 0.13 | 0.5499 | NAVY
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1041 | NITRITE | 0.09 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-08-02 | L1 | 0.98 |  | WWTP SINK | 3
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | D | DBP | 2950 | TOTAL THMS | 55.6 | UG/L | 80.4999 | 2022-08-02 | L1 | 0.39 |  | WWTP SINK | 3
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1040 | NITRATE | 0.18 | MG/L | 10.4999 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1041 | NITRITE | 0.11 | MG/L | 1.4999 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1025 | FLUORIDE | 0.08 | MG/L | 4.0499 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1052 | SODIUM | 20 | MG/L | 160.4999 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2021-01-19 | AAA | 0.03
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1041 | NITRITE | 0.018 | MG/L | 1.4999 | 2021-01-19 | AAA | 0.018
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-11 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-11 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-09 | AAA |  |  | POE
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-09 | AAA |  |  | POE
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-08 | AAA |  |  | POE
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-08 | AAA |  |  | POE
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-15 | AAA |  |  | POE
3484395 | BAD DOG DRIVING RANGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-15 | AAA |  |  | POE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP8 | 0.13 | 0.5499 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-02-07 | WTP8 | 1.4 |  | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-02-07 | WTP8 | 1 | 1.4999 | NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-07 | WTP8 | 0.0069 | 0.0149 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP8 | 0.0071 | 0.0249 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP8 | 0.12 | 1.4999 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-07 | WTP8 | 0.0068 | 0.1499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-07 | WTP8 | 0.9 | 1.4999 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-07 | WTP8 | 0.37 | 0.4499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-07 | WTP8 | 6 | 9.4999 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP8 | 5.9 | 6.4999 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-07 | WTP8 | 0.5 | 0.6499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-07 | WTP8 | 1.8 | 2.4999 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-07 | WTP8 | 0.06 | 0.0749 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-07 | WTP8 | 0.5 | 0.6499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-07 | WTP8 | 0.09 | 0.1499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-07 | WTP8 | 0.18 | 0.2499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-07 | WTP8 | 0.019 | 0.1499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-07 | WTP8 | 0.51 | 0.9499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP8 | 0.09 | 0.1499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-07 | WTP8 | 0.15 | 0.2499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-07 | WTP8 | 0.006 | 0.0449 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP8 | 0.0052 | 0.0249 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-07 | WTP8 | 0.095 | 0.1499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-07 | WTP8 | 0.09 | 0.2499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP8 | 0.0063 | 0.1499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP8 | 0.015 | 0.0249 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-07 | WTP8 | 0.038 | 0.0449 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-07 | WTP8 | 0.093 | 0.1499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-07 | WTP8 | 0.0091 | 0.0149 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-07 | WTP8 | 0.053 | 0.2499 | NAVY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.04 | MG/L | 10.4999 | 2023-02-07 | WTP10 | 0.03 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-07 | WTP10 | 0.03 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-02-07 | WTP10 | 0.007 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1010 | BARIUM | 0.034 | MG/L | 2.4999 | 2023-02-07 | WTP10 | 0.002 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-02-07 | WTP10 | 0.002 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-07 | WTP10 | 0.002 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1025 | FLUORIDE | 0.72 | MG/L | 4.0499 | 2023-02-07 | WTP10 | 0.025 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-07 | WTP10 | 0.0005 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-02-07 | WTP10 | 0.0003 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-02-07 | WTP10 | 0.002 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-02-07 | WTP10 | 0.0006 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1052 | SODIUM | 12.5 | MG/L | 160.4999 | 2023-02-07 | WTP10 | 0.08 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-02-07 | WTP10 | 0.001 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-07 | WTP10 | 0.001 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-02-07 | WTP10 | 0.0008 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-07 | WTP10 | 0.004 |  | SKY LAKE CYANIDE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-07 | WTP10 | 0.006 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1017 | CHLORIDE | 15 | MG/L | 250.4999 | 2023-02-07 | WTP10 | 0.11 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-02-07 | WTP10 | 0.003 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1025 | FLUORIDE | 0.72 | MG/L | 2.0499 | 2023-02-07 | WTP10 | 0.025 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1028 | IRON | 0.005 | MG/L | 0.3499 | 2023-02-07 | WTP10 | 0.005 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1032 | MANGANESE | 0.002 | MG/L | 0.0549 | 2023-02-07 | WTP10 | 0.002 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-02-07 | WTP10 | 0.0001 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1055 | SULFATE | 22.2 | MG/L | 250.4999 | 2023-02-07 | WTP10 | 0.62 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-07 | WTP10 | 0.004 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1920 | ODOR THRESHOLD | 4 |  | 3.4999 | 2023-02-07 | WTP10 | 1 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1905 | COLOR | 1 | COLOR UNITS | 15.4999 | 2023-02-07 | WTP10 | 1 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.73 | LN(10) |  | 2023-02-07 | WTP10 | 1 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 205 | MG/L | 500.4999 | 2023-02-07 | WTP10 | 5 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 2905 | FOAMING AGENTS | 0.047 |  | 0.5499 | 2023-02-07 | WTP10 | 0.04 |  | SKY LAKE FOAMING AGENTS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP10 | 0.12 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP10 | 0.16 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-07 | WTP10 | 0.37 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP10 | 0.16 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-07 | WTP10 | 0.1 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-07 | WTP10 | 0.12 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP10 | 0.26 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-07 | WTP10 | 0.3 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP10 | 0.27 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP10 | 0.08 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-07 | WTP10 | 0.15 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP10 | 0.15 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP10 | 0.13 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP10 | 0.15 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP10 | 0.07 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP10 | 0.17 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP10 | 0.13 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP10 | 0.15 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-07 | WTP10 | 0.14 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP10 | 0.13 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP10 | 0.13 | 0.5499 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-02-07 | WTP10 | 2 |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-02-07 | WTP10 | 1 | 1.4999 | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-07 | WTP10 | 0.0069 | 0.0149 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP10 | 0.0071 | 0.0249 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-07 | WTP10 | 0.0068 | 0.1499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP10 | 0.12 | 1.4999 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-07 | WTP10 | 0.37 | 0.4499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-07 | WTP10 | 6 | 9.4999 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP10 | 5.9 | 6.4999 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-07 | WTP10 | 0.5 | 0.6499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-07 | WTP10 | 1.8 | 2.4999 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-07 | WTP10 | 0.06 | 0.0749 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-07 | WTP10 | 0.5 | 0.6499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-07 | WTP10 | 0.019 | 0.1499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-07 | WTP10 | 0.51 | 0.9499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP10 | 0.09 | 0.1499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-07 | WTP10 | 0.15 | 0.2499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-07 | WTP10 | 0.006 | 0.0449 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP10 | 0.0052 | 0.0249 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP10 | 0.0063 | 0.1499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP10 | 0.015 | 0.0249 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-07 | WTP10 | 0.093 | 0.1499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-07 | WTP10 | 0.053 | 0.2499 | SKY LAKE 2031 2040 2041 2105 2110 2326 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.04 | MG/L | 10.4999 | 2023-02-07 | WTP11 | 0.03 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-07 | WTP11 | 0.03 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1010 | BARIUM | 0.036 | MG/L | 2.4999 | 2023-02-07 | WTP11 | 0.0002 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-02-07 | WTP11 | 0.0007 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-02-07 | WTP11 | 0.002 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-07 | WTP11 | 0.002 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1025 | FLUORIDE | 0.76 | MG/L | 4.0499 | 2023-02-07 | WTP11 | 0.025 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-07 | WTP11 | 0.0005 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-02-07 | WTP11 | 0.0003 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1036 | NICKEL | 0.002 | MG/L | 0.1499 | 2023-02-07 | WTP11 | 0.002 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-02-07 | WTP11 | 0.0006 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1052 | SODIUM | 9.33 | MG/L | 160.4999 | 2023-02-07 | WTP11 | 0.08 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-02-07 | WTP11 | 0.001 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-07 | WTP11 | 0.001 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-02-07 | WTP11 | 0.0008 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-07 | WTP11 | 0.004 |  | SW CYANIDE
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-07 | WTP11 | 0.006 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1017 | CHLORIDE | 12.4 | MG/L | 250.4999 | 2023-02-07 | WTP11 | 0.11 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-02-07 | WTP11 | 0.003 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1025 | FLUORIDE | 0.76 | MG/L | 2.0499 | 2023-02-07 | WTP11 | 0.025 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1028 | IRON | 0.006 | MG/L | 0.3499 | 2023-02-07 | WTP11 | 0.005 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1032 | MANGANESE | 0.002 | MG/L | 0.0549 | 2023-02-07 | WTP11 | 0.002 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-02-07 | WTP11 | 0.0001 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1055 | SULFATE | 24 | MG/L | 250.4999 | 2023-02-07 | WTP11 | 0.62 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-07 | WTP11 | 0.004 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1905 | COLOR | 1 | COLOR UNITS | 15.4999 | 2023-02-07 | WTP11 | 1 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2023-02-07 | WTP11 | 1 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.41 | LN(10) |  | 2023-02-07 | WTP11 | 1 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 176 | MG/L | 500.4999 | 2023-02-07 | WTP11 | 5 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 2905 | FOAMING AGENTS | 0.076 |  | 0.5499 | 2023-02-07 | WTP11 | 0.04 |  | SW FOAMING AGENTS
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-02-07 | WTP11 | 2 |  | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-02-07 | WTP11 | 1 | 1.4999 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP11 | 0.12 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP11 | 0.16 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-07 | WTP11 | 0.37 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP11 | 0.16 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-07 | WTP11 | 0.1 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-07 | WTP11 | 0.12 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP11 | 0.26 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-07 | WTP11 | 0.3 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP11 | 0.27 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP11 | 0.08 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-07 | WTP11 | 0.15 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP11 | 0.15 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP11 | 0.13 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP11 | 0.15 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP11 | 0.07 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP11 | 0.17 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP11 | 0.13 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP11 | 0.15 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-07 | WTP11 | 0.14 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP11 | 0.13 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP11 | 0.13 | 0.5499 | SW
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-07 | WTP11 | 0.0069 | 0.0149 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP11 | 0.0071 | 0.0249 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-07 | WTP11 | 0.0068 | 0.1499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP11 | 0.12 | 1.4999 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-07 | WTP11 | 0.9 | 1.4999 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-07 | WTP11 | 0.37 | 0.4499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-07 | WTP11 | 6 | 9.4999 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP11 | 5.9 | 6.4999 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-07 | WTP11 | 0.5 | 0.6499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-07 | WTP11 | 1.8 | 2.4999 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-07 | WTP11 | 0.06 | 0.0749 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-07 | WTP11 | 0.5 | 0.6499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-07 | WTP11 | 0.09 | 0.1499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-07 | WTP11 | 0.18 | 0.2499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-07 | WTP11 | 0.019 | 0.1499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-07 | WTP11 | 0.51 | 0.9499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP11 | 0.09 | 0.1499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-07 | WTP11 | 0.15 | 0.2499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-07 | WTP11 | 0.006 | 0.0449 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP11 | 0.0052 | 0.0249 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-07 | WTP11 | 0.095 | 0.1499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-07 | WTP11 | 0.09 | 0.2499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP11 | 0.0063 | 0.1499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP11 | 0.015 | 0.0249 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-07 | WTP11 | 0.038 | 0.0449 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-07 | WTP11 | 0.093 | 0.1499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-07 | WTP11 | 0.053 | 0.2499 | SW 2931 2946 J QUALIFIERS, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-07 | WTP1 | 0.03 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2023-02-07 | WTP1 | 0.03 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-02-07 | WTP1 | 0.0007 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2023-02-07 | WTP1 | 0.002 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-02-07 | WTP1 | 0.002 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-07 | WTP1 | 0.002 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1025 | FLUORIDE | 0.7 | MG/L | 4.0499 | 2023-02-07 | WTP1 | 0.025 |  | HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-07 | WTP1 | 0.004 |  | HIGHLAND - ZINC ADDED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-02-07 | WTP5 | 0.03 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-07 | WTP5 | 0.03 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-02-07 | WTP5 | 0.0007 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2023-02-07 | WTP5 | 0.002 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-02-07 | WTP5 | 0.002 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-07 | WTP5 | 0.002 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1025 | FLUORIDE | 0.64 | MG/L | 4.0499 | 2023-02-07 | WTP5 | 0.025 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-07 | WTP5 | 0.0005 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-02-07 | WTP5 | 0.0003 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-02-07 | WTP5 | 0.002 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-02-07 | WTP5 | 0.0006 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1052 | SODIUM | 7.27 | MG/L | 160.4999 | 2023-02-07 | WTP5 | 0.08 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-02-07 | WTP5 | 0.001 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-07 | WTP5 | 0.001 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-02-07 | WTP5 | 0.0008 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-07 | WTP5 | 0.004 |  | PINE HILLS CYANIDE ONLY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-07 | WTP5 | 0.006 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1017 | CHLORIDE | 11.8 | MG/L | 250.4999 | 2023-02-07 | WTP5 | 0.11 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-02-07 | WTP5 | 0.003 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1025 | FLUORIDE | 0.64 | MG/L | 2.0499 | 2023-02-07 | WTP5 | 0.025 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-02-07 | WTP5 | 0.005 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-02-07 | WTP5 | 0.002 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-02-07 | WTP5 | 0.0001 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1055 | SULFATE | 6.63 | MG/L | 250.4999 | 2023-02-07 | WTP5 | 0.16 |  | PINE HILLS
3484398 | SUBCO BEELINE | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-03-30 | AAA |  |  | MAKEUP SAMPLES FOR 2021 MISSED MONITORING, NOT FOR 2022 COMPLIANCE. SMD
3484398 | SUBCO BEELINE | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-30 | AAA |  |  | MAKEUP SAMPLES FOR 2021 MISSED MONITORING, NOT FOR 2022 COMPLIANCE. SMD
3484398 | SUBCO BEELINE | N | INOR | 1040 | NITRATE | 0.038 | MG/L | 10.4999 | 2022-12-27 | AAA | 0.025 |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1040 | NITRATE | 0.038 | MG/L | 10.4999 | 2022-12-27 | AAA | 0.025 |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-27 | AAA |  |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-06-15 | AAA |  |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-15 | AAA |  |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-06-25 | AAA |  |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-06-25 | AAA |  |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-19 | AAA |  |  | POE
3484398 | SUBCO BEELINE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-19 | AAA |  |  | POE
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-31 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-31 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-31 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-31 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-31 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-31 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-31 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-31 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-31 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-31 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-31 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-31 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-31 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-31 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-31 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-31 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-31 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-31 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-31 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-10-31 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-10-31 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-31 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-10-16 | AAA |  |  | POE
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | POE
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-08 | AAA |  |  | POE
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-08 | AAA |  |  | POE
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.44 | UG/L | 60.4999 | 2025-08-07 | L1 | 0.98 |  | WWTP SINK | 3
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | D | DBP | 2950 | TOTAL THMS | 17.88 | UG/L | 80.4999 | 2025-08-07 | L1 | 0.44 |  | WWTP SINK | 3
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1040 | NITRATE | 0.062 | MG/L | 10.4999 | 2025-10-16 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1005 | ARSENIC | 0.0004 | MG/L | 0.0104 | 2025-10-16 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1010 | BARIUM | 0.016 | MG/L | 2.4999 | 2025-10-16 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-10-16 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-10-16 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1024 | CYANIDE | 0.021 | MG/L | 0.2499 | 2025-10-16 | AAA | 0.002 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-10-16 | AAA | 0.0005 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-10-16 | AAA | 3e-05 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-10-16 | AAA | 0.008 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-10-16 | AAA | 0.0012 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1052 | SODIUM | 34 | MG/L | 160.4999 | 2025-10-16 | AAA | 0.8 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-10-16 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-10-16 | AAA | 0.002 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-10-16 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-10-16 | AAA | 0.5 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-10-16 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-16 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-10-16 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-10-16 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-10-16 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-10-16 | AAA | 0.28 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-10-16 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-10-16 | AAA | 0.41 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-10-16 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-10-16 | AAA | 0.32 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-10-16 | AAA | 0.36 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-10-16 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-16 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-10-16 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-16 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-10-16 | AAA | 0.37 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-10-16 | AAA | 0.42 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-10-16 | AAA | 0.46 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-10-16 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-10-16 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-10-16 | AAA | 0.0071 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-10-16 | AAA | 0.0068 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-10-16 | AAA | 0.12 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-10-16 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-10-16 | AAA | 0.31 | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-10-16 | AAA | 6 | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-10-16 | AAA | 5.9 | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-10-16 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-10-16 | AAA | 1.8 | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-10-16 | AAA | 0.006 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-10-16 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-10-16 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-10-16 | AAA | 0.18 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-10-16 | AAA | 0.019 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-10-16 | AAA | 0.67 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-10-16 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-10-16 | AAA | 0.15 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-10-16 | AAA | 0.006 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-10-16 | AAA | 0.0052 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-10-16 | AAA | 0.097 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-10-16 | AAA | 0.09 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-10-16 | AAA | 0.0063 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-10-16 | AAA | 0.015 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-10-16 | AAA | 0.038 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-10-16 | AAA | 0.093 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-10-16 | AAA | 0.0061 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-10-16 | AAA | 0.0091 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-10-16 | AAA | 0.053 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-16 | AAA
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | INOR | 1025 | FLUORIDE | 0.11 | MG/L | 4.0499 | 2025-10-16 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008- 1041, 1025 J QUALIFIERS ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-10-16 | AAA | 0.0069 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008- 2005 J QUALIFIER. ENDRIN ACCEPTED_ALP
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.5 | PCI/L | 15.4999 | 2025-10-16 | AAA | 1.8 |  | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | RAD | 4020 | RADIUM-226 | 1.3 | PCI/L | 3.4999 | 2025-10-16 | AAA | 0.2 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3484390 | ORANGE COUNTY NATIONAL GOLF CENTER | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-10-16 | AAA | 0.6 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-07 | WTP5 | 0.004 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1905 | COLOR | 1 | COLOR UNITS | 15.4999 | 2023-02-07 | WTP5 | 1 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2023-02-07 | WTP5 | 1 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.53 | LN(10) |  | 2023-02-07 | WTP5 | 1 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 141 | MG/L | 500.4999 | 2023-02-07 | WTP5 | 5 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 2905 | FOAMING AGENTS | 0.056 |  | 0.5499 | 2023-02-07 | WTP5 | 0.04 |  | FOAMING AGENTS ONLY PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP5 | 0.12 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP5 | 0.16 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-07 | WTP5 | 0.37 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP5 | 0.16 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-07 | WTP5 | 0.1 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-07 | WTP5 | 0.12 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP5 | 0.26 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-07 | WTP5 | 0.3 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP5 | 0.27 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP5 | 0.08 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-07 | WTP5 | 0.15 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP5 | 0.15 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP5 | 0.13 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP5 | 0.15 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP5 | 0.07 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP5 | 0.17 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP5 | 0.13 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP5 | 0.15 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-07 | WTP5 | 0.14 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP5 | 0.13 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP5 | 0.13 | 0.5499 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.5 | PCI/L | 15.4999 | 2023-02-07 | WTP5 | 1.1 |  | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-02-07 | WTP5 | 1 | 1.4999 | PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-07 | WTP5 | 0.0069 | 0.0149 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP5 | 0.0071 | 0.0249 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-07 | WTP5 | 0.0068 | 0.1499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP5 | 0.12 | 1.4999 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-07 | WTP5 | 0.9 | 1.4999 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-07 | WTP5 | 0.37 | 0.4499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-07 | WTP5 | 6 | 9.4999 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP5 | 5.9 | 6.4999 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-07 | WTP5 | 0.5 | 0.6499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-07 | WTP5 | 1.8 | 2.4999 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-07 | WTP5 | 0.06 | 0.0749 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-07 | WTP5 | 0.5 | 0.6499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-07 | WTP5 | 0.09 | 0.1499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-07 | WTP5 | 0.18 | 0.2499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-07 | WTP5 | 0.019 | 0.1499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-07 | WTP5 | 0.51 | 0.9499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP5 | 0.09 | 0.1499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-07 | WTP5 | 0.15 | 0.2499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-07 | WTP5 | 0.006 | 0.0449 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP5 | 0.0052 | 0.0249 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-07 | WTP5 | 0.095 | 0.1499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-07 | WTP5 | 0.09 | 0.2499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP5 | 0.0063 | 0.1499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP5 | 0.015 | 0.0249 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-07 | WTP5 | 0.038 | 0.0449 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-07 | WTP5 | 0.093 | 0.1499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-07 | WTP5 | 0.0091 | 0.0149 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-07 | WTP5 | 0.053 | 0.2499 | PINE HILLS 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2023-02-07 | WTP6 | 0.03 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-07 | WTP6 | 0.03 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-02-07 | WTP6 | 0.0007 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2023-02-07 | WTP6 | 0.0002 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-02-07 | WTP6 | 0.002 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-02-07 | WTP6 | 0.002 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1025 | FLUORIDE | 0.89 | MG/L | 4.0499 | 2023-02-07 | WTP6 | 0.025 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-07 | WTP6 | 0.0005 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-02-07 | WTP6 | 0.0003 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-02-07 | WTP6 | 0.002 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-02-07 | WTP6 | 0.0006 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1052 | SODIUM | 12.6 | MG/L | 160.4999 | 2023-02-07 | WTP6 | 0.08 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-02-07 | WTP6 | 0.001 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-02-07 | WTP6 | 0.001 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-02-07 | WTP6 | 0.0008 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-02-07 | WTP6 | 0.004 |  | CONWAY CYANIDE ONLY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-02-07 | WTP6 | 0.006 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1017 | CHLORIDE | 18.4 | MG/L | 250.4999 | 2023-02-07 | WTP6 | 0.11 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-02-07 | WTP6 | 0.003 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1025 | FLUORIDE | 0.89 | MG/L | 2.0499 | 2023-02-07 | WTP6 | 0.025 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-02-07 | WTP6 | 0.005 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-02-07 | WTP6 | 0.002 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-02-07 | WTP6 | 0.0001 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1055 | SULFATE | 7.02 | MG/L | 250.4999 | 2023-02-07 | WTP6 | 0.16 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-02-07 | WTP6 | 0.004 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1905 | COLOR | 1 | COLOR UNITS | 15.4999 | 2023-02-07 | WTP6 | 1 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1920 | ODOR THRESHOLD | 8 |  | 3.4999 | 2023-02-07 | WTP6 | 1 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.42 | LN(10) |  | 2023-02-07 | WTP6 | 1 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 179 | MG/L | 500.4999 | 2023-02-07 | WTP6 | 5 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SEC | 2905 | FOAMING AGENTS | 0.27 |  | 0.5499 | 2023-02-07 | WTP6 | 0.04 |  | CONWAY FOAMING AGENTS ONLY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP6 | 0.12 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-07 | WTP6 | 0.16 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-07 | WTP6 | 0.37 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP6 | 0.16 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-07 | WTP6 | 0.1 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-07 | WTP6 | 0.12 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP6 | 0.26 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-07 | WTP6 | 0.3 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP6 | 0.27 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP6 | 0.08 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-07 | WTP6 | 0.15 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP6 | 0.15 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP6 | 0.13 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP6 | 0.15 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-07 | WTP6 | 0.07 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP6 | 0.17 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP6 | 0.13 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP6 | 0.15 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-07 | WTP6 | 0.14 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP6 | 0.13 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-07 | WTP6 | 0.13 | 0.5499 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-02-07 | WTP6 | 2.1 |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | RAD | 4030 | RADIUM-228 | 1.1 | PCI/L | 2.4999 | 2023-02-07 | WTP6 | 0.9 | 1.4999 | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-07 | WTP6 | 0.0069 | 0.0149 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP6 | 0.0071 | 0.0249 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-07 | WTP6 | 0.0068 | 0.1499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP6 | 0.12 | 1.4999 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-02-07 | WTP6 | 0.9 | 1.4999 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-07 | WTP6 | 0.37 | 0.4499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-02-07 | WTP6 | 6 | 9.4999 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-02-07 | WTP6 | 5.9 | 6.4999 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-02-07 | WTP6 | 0.5 | 0.6499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-02-07 | WTP6 | 1.8 | 2.4999 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-02-07 | WTP6 | 0.06 | 0.0749 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-02-07 | WTP6 | 0.5 | 0.6499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-02-07 | WTP6 | 0.09 | 0.1499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-02-07 | WTP6 | 0.18 | 0.2499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-07 | WTP6 | 0.019 | 0.1499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-02-07 | WTP6 | 0.51 | 0.9499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-02-07 | WTP6 | 0.09 | 0.1499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-02-07 | WTP6 | 0.15 | 0.2499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-07 | WTP6 | 0.006 | 0.0449 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP6 | 0.0052 | 0.0249 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-02-07 | WTP6 | 0.095 | 0.1499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-02-07 | WTP6 | 0.09 | 0.2499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-07 | WTP6 | 0.0063 | 0.1499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-02-07 | WTP6 | 0.015 | 0.0249 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-02-07 | WTP6 | 0.038 | 0.0449 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-07 | WTP6 | 0.093 | 0.1499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-02-07 | WTP6 | 0.0092 | 0.0149 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-07 | WTP6 | 0.053 | 0.2499 | CONWAY 2931 J QUALIFIER, ACCEPTED BASED ON QC DATA_SMD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2023-02-15 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-02-15 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-02-15 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2023-02-15 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2023-02-15 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2023-02-15 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2023-02-15 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2023-02-15 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-02-15 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2023-02-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-02-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2023-02-15 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-02-15 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-02-15 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.1 | MG/L | 0 | 2023-02-15 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2023-02-15 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 43.1 | MG/L |  | 2023-02-15 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2023-02-15 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-02-15 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-02-15 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34 | MG/L | 0 | 2023-03-01 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-03-01 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-03-01 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2023-03-01 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-03-01 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 134 | MG/L |  | 2023-03-01 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2023-03-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2023-03-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-03-01 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2023-03-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-03-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2023-03-01 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2023-03-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2023-03-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-03-01 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2023-03-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2023-03-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-03-01 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.5 | MG/L | 0 | 2023-03-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2023-03-01 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-03-01 | WTP5 |  |  | PINE HILLS WP
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1040 | NITRATE | 0.12 | MG/L | 10.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2022-10-11 | AAA | 0.024 |  | POE
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-11 | AAA |  |  | POE
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1040 | NITRATE | 0.061 | MG/L | 10.4999 | 2023-10-11 | AAA | 0.024 |  | POE
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1041 | NITRITE | 0.071 | MG/L | 1.4999 | 2023-10-11 | AAA | 0.0034 |  | POE
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-03 | AAA |  |  | POE
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-03 | AAA |  |  | POE
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2025-01-28 | AAA | 0.024 |  | POE
3481171 | CIRCLE K #7340/BITHLO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-28 | AAA |  |  | POE
3481175 | THREE POINT FOOD MART | N | INOR | 1040 | NITRATE | 1.62 | MG/L | 10.4999 | 2021-08-03 | AAA
3481175 | THREE POINT FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-08-03 | AAA
3481175 | THREE POINT FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-08-08 | AAA |  |  | POE
3481175 | THREE POINT FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-08 | AAA |  |  | POE
3481175 | THREE POINT FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-08-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3481175 | THREE POINT FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3481175 | THREE POINT FOOD MART | N | INOR | 1040 | NITRATE | 0.053 | MG/L | 10.4999 | 2024-08-23 | AAA | 0.024 |  | POE
3481175 | THREE POINT FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-23 | AAA |  |  | POE
3481175 | THREE POINT FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-09-09 | AAA | 0.024 |  | 2025 N/N
3481175 | THREE POINT FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-09-09 | AAA | 0.0034 |  | 2025 N/N
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.29 | UG/L | 10.4999 | 2023-03-06 | L7 | 0.59 |  | 3/23 BROMATE - SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.4 | UG/L | 10.4999 | 2023-03-06 | L7 | 0.59 |  | 3/23 BROMATE - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.61 | UG/L | 10.4999 | 2023-03-06 | L7 | 0.59 |  | 3/23 BROMATE - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 10.3 | UG/L | 10.4999 | 2023-03-06 | L7 | 0.59 |  | 3/23 BROMATE - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.07 | UG/L | 10.4999 | 2023-03-06 | L7 | 0.59 |  | 3/23 BROMATE - NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.78 | UG/L | 10.4999 | 2023-03-06 | L7 | 0.59 |  | 3/23 BROMATE - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.84 | UG/L | 10.4999 | 2023-03-06 | L7 | 0.59 |  | 3/23 BROMATE - SKY LAKE (3/23 BROMATE RAA RCVD SEPARATELY)
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2023-03-15 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-03-15 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-03-15 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2023-03-15 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2023-03-15 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-03-15 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2023-03-15 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2023-03-15 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2023-03-15 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2023-03-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-03-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-03-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2023-03-15 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-03-15 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-03-15 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.7 | MG/L | 0 | 2023-03-15 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-03-15 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-03-15 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.2 | MG/L | 0 | 2023-03-15 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-03-15 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-03-15 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-03-29 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-03-29 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-03-29 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2023-03-29 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-03-29 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-03-29 | WTP6 |  |  | CONWAY WP-2725 S CONWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.5 | MG/L | 0 | 2023-03-29 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2023-03-29 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2023-03-29 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.1 | MG/L | 0 | 2023-03-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-03-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-03-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2023-03-29 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2023-03-29 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-03-29 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2023-03-29 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2023-03-29 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-03-29 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2023-03-29 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-03-29 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-03-29 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.1 | UG/L | 10.4999 | 2023-04-03 | L7 | 0.59 |  | SOUTHWEST POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.84 | UG/L | 10.4999 | 2023-04-03 | L7 | 0.59 |  | KIRKMAN POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.8 | UG/L | 10.4999 | 2023-04-03 | L7 | 0.59 |  | PINE HILLS POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.57 | UG/L | 10.4999 | 2023-04-03 | L7 | 0.59 |  | HIGHLAND POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.43 | UG/L | 10.4999 | 2023-04-03 | L7 | 0.59 |  | NAVY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.82 | UG/L | 10.4999 | 2023-04-03 | L7 | 0.59 |  | CONWAY POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.31 | UG/L | 10.4999 | 2023-04-03 | L7 | 0.59 |  | SKY LAKE POE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-04-11 | WTP1 |  |  | 740 HIGHLAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-04-11 | WTP1 |  |  | 900 N WESTMORELAND AVE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-04-11 | WTP1 |  |  | 1226 MAURY RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-04-11 | WTP1 |  |  | 1128 W PRINCETON ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-04-11 | WTP1 |  |  | 405 NIBLICK WAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-04-11 | WTP1 |  |  | 16 E HAZEL ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-04-11 | WTP1 |  |  | 21 E PAR ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.5 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2023-04-11 | WTP1 |  |  | 1415 SLIGH BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-04-11 | WTP1 |  |  | 709 W CENTRAL BLVD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2023-04-11 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-04-11 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-04-11 | WTP1 |  |  | 635 W COCNCORD ST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2023-04-12 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-04-12 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-04-12 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2023-04-12 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-04-12 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-04-12 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2023-04-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-04-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-04-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2023-04-12 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-04-12 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-04-12 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2023-04-12 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2023-04-12 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-04-12 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2023-04-12 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2023-04-12 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-04-12 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.2 | MG/L | 0 | 2023-04-12 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-04-12 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-04-12 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2023-04-26 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2023-04-26 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-04-26 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2023-04-26 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2023-04-26 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-04-26 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2023-04-26 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-04-26 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-04-26 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.5 | MG/L | 0 | 2023-04-26 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-04-26 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-04-26 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2023-04-26 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2023-04-26 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2023-04-26 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2023-04-26 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2023-04-26 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-04-26 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2023-04-26 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-04-26 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-04-26 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.35 | UG/L | 60.4999 | 2023-05-01 | L1 | 2
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 16.81 | UG/L | 80.4999 | 2023-05-01 | L1 | 0.13
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.17 | UG/L | 60.4999 | 2023-05-01 | L2 | 2
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 65.05 | UG/L | 80.4999 | 2023-05-01 | L2 | 0.13
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.28 | UG/L | 60.4999 | 2023-05-01 | L3 | 2
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 59.28 | UG/L | 80.4999 | 2023-05-01 | L3 | 0.13
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.59 | UG/L | 60.4999 | 2023-05-01 | L4 | 2
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 63.55 | UG/L | 80.4999 | 2023-05-01 | L4 | 0.13
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.54 | UG/L | 60.4999 | 2023-05-01 | L5 | 2
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 64.78 | UG/L | 80.4999 | 2023-05-01 | L5 | 0.13
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.41 | UG/L | 60.4999 | 2023-05-01 | L6 | 2
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 40.61 | UG/L | 80.4999 | 2023-05-01 | L6 | 0.13
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.3 | UG/L | 10.4999 | 2023-05-01 | L7 | 0.59 |  | SW POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.61 | UG/L | 10.4999 | 2023-05-01 | L7 | 0.59 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1 | UG/L | 10.4999 | 2023-05-01 | L7 | 0.59 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.26 | UG/L | 10.4999 | 2023-05-01 | L7 | 0.59 |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.89 | UG/L | 10.4999 | 2023-05-01 | L7 | 0.59 |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.79 | UG/L | 10.4999 | 2023-05-01 | L7 | 0.59 |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.1 | UG/L | 10.4999 | 2023-05-01 | L7 | 0.59 |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2023-05-10 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2023-05-10 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-05-10 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37 | MG/L | 0 | 2023-05-10 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-05-10 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-05-10 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2023-05-10 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2023-05-10 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-05-10 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2023-05-10 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-05-10 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-05-10 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2023-05-10 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-05-10 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-05-10 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2023-05-10 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2023-05-10 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2023-05-10 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2023-05-10 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-05-10 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-05-10 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2023-05-24 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-05-24 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-05-24 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2023-05-24 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-05-24 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2023-05-24 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2023-05-24 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2023-05-24 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 35.8 | MG/L |  | 2023-05-24 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2023-05-24 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2023-05-24 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-05-24 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.5 | MG/L | 0 | 2023-05-24 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-05-24 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-05-24 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2023-05-24 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-05-24 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-05-24 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.2 | MG/L | 0 | 2023-05-24 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-05-24 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-05-24 | WTP5 |  |  | PINE HILLS WP
3481199 | SILVER STAR VILLAGE (2 WPS) | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-02-01 | WTP2 |  |  | WELL 4 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-01 | WTP2 |  |  | WELL 4 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-02-01 | WTP3 |  |  | WELL 5 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-01 | WTP3 |  |  | WELL 5 POE (MAKEUP SAMPLE, MISSED 2020)_VPU
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.77 | UG/L | 60.4999 | 2021-02-22 | L1 | 1 |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 0.81 | UG/L | 80.4999 | 2021-02-22 | L1 | 0.5 |  | 7189 LINMAR | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.79 | UG/L | 60.4999 | 2021-02-22 | L2 | 1 |  | 7006 ALAMENA | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 0.8 | UG/L | 80.4999 | 2021-02-22 | L2 | 0.5 |  | 7006 ALAMENA
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.7 | PCI/L | 15.4999 | 2021-05-18 | WTP3 |  |  | POE-SSV
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-05-18 | WTP3 |  | 1.4999 | POE-SSV
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0.202 | MG/L | 10.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1010 | BARIUM | 0.0084 | MG/L | 2.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1030 | LEAD | 0.0046 | MG/L | 0.0154 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1052 | SODIUM | 12.8 | MG/L | 160.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1017 | CHLORIDE | 22.9 | MG/L | 250.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1022 | COPPER | 0.0317 | MG/L | 1.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1028 | IRON | 0.31 | MG/L | 0.3499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.0449 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-05-18 | WTP3 |  | 0.0149 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1055 | SULFATE | 20.1 | MG/L | 250.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1095 | ZINC | 0.0877 | MG/L | 5.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.04 | LN(10) |  | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 200 | MG/L | 500.4999 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-18 | WTP3 |  |  | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 0.5499 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-05-18 | WTP3 |  | 0.0149 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-05-18 | WTP3 |  | 0.0249 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 1.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-05-18 | WTP3 |  | 1.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-05-18 | WTP3 |  | 0.4499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-05-18 | WTP3 |  | 9.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-05-18 | WTP3 |  | 6.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-05-18 | WTP3 |  | 0.6499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-05-18 | WTP3 |  | 2.4999 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-05-18 | WTP3 |  | 0.0749 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-05-18 | WTP3 |  | 0.6499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-05-18 | WTP3 |  | 0.9499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-05-18 | WTP3 |  | 0.1499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-05-18 | WTP3 |  | 0.2499 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-05-18 | WTP3 |  | 0.0449 | POE-WTP3
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.86 | UG/L | 60.4999 | 2021-05-24 | L1 | 1 |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 8.57 | UG/L | 80.4999 | 2021-05-24 | L1 | 0.5 |  | 7189 LINMAR | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.53 | UG/L | 60.4999 | 2021-05-24 | L2 | 1 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 7.26 | UG/L | 80.4999 | 2021-05-24 | L2 | 0.5 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.5 | PCI/L | 15.4999 | 2021-06-10 | WTP2 |  |  | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-10 | WTP2 |  | 1.4999 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1010 | BARIUM | 0.0093 | MG/L | 2.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1036 | NICKEL | 0.0016 | MG/L | 0.1499 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1052 | SODIUM | 12.9 | MG/L | 160.4999 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-06-10 | WTP2 |  |  | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1017 | CHLORIDE | 22.3 | MG/L | 250.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1022 | COPPER | 0.003 | MG/L | 1.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1028 | IRON | 0.231 | MG/L | 0.3499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1032 | MANGANESE | 0.0113 | MG/L | 0.0549 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1055 | SULFATE | 18 | MG/L | 250.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1095 | ZINC | 0.259 | MG/L | 5.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.18 | LN(10) |  | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 226 | MG/L | 500.4999 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-06-10 | WTP2 |  |  | POE- WTP 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 0.5499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-06-10 | WTP2 |  | 0.0149 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 1.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-06-10 | WTP2 |  | 1.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-06-10 | WTP2 |  | 0.4499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-06-10 | WTP2 |  | 9.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-06-10 | WTP2 |  | 6.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-06-10 | WTP2 |  | 0.6499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-06-10 | WTP2 |  | 2.4999 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-06-10 | WTP2 |  | 0.0749 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-06-10 | WTP2 |  | 0.6499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-06-10 | WTP2 |  | 0.9499 | POE-WTP2
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-01 | WTP1 |  | 0.0149 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP1 |  | 0.0249 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-01 | WTP1 |  | 0.1499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP1 |  | 1.4999 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-01 | WTP1 |  | 1.4999 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-01 | WTP1 |  | 0.4499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-01 | WTP1 |  | 9.4999 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-01 | WTP1 |  | 6.4999 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-01 | WTP1 |  | 0.6499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-01 | WTP1 |  | 2.4999 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-01 | WTP1 |  | 0.0749 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-01 | WTP1 |  | 0.6499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-01 | WTP1 |  | 0.1499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-01 | WTP1 |  | 0.2499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-01 | WTP1 |  | 0.1499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-01 | WTP1 |  | 0.9499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP1 |  | 0.1499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-01 | WTP1 |  | 0.2499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-01 | WTP1 |  | 0.0449 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP1 |  | 0.0249 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-01 | WTP1 |  | 0.1499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-01 | WTP1 |  | 0.2499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-01 | WTP1 |  | 0.1499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP1 |  | 0.0249 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-01 | WTP1 |  | 0.0449 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-01 | WTP1 |  | 0.1499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP1 |  | 0.0249 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-01 | WTP1 |  | 0.0149 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-01 | WTP1 |  | 0.2499 | HIGHLAND WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-01 | WTP6 |  | 0.0149 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP6 |  | 0.0249 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-01 | WTP6 |  | 0.1499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP6 |  | 1.4999 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-01 | WTP6 |  | 1.4999 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-01 | WTP6 |  | 0.4499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-01 | WTP6 |  | 9.4999 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-01 | WTP6 |  | 6.4999 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-01 | WTP6 |  | 0.6499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-01 | WTP6 |  | 2.4999 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-01 | WTP6 |  | 0.0749 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-01 | WTP6 |  | 0.6499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-01 | WTP6 |  | 0.1499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-01 | WTP6 |  | 0.2499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-01 | WTP6 |  | 0.1499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-01 | WTP6 |  | 0.9499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP6 |  | 0.1499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-01 | WTP6 |  | 0.2499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-01 | WTP6 |  | 0.0449 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP6 |  | 0.0249 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-01 | WTP6 |  | 0.1499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-01 | WTP6 |  | 0.2499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-01 | WTP6 |  | 0.1499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP6 |  | 0.0249 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-01 | WTP6 |  | 0.0449 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-01 | WTP6 |  | 0.1499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP6 |  | 0.0249 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-01 | WTP6 |  | 0.0149 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-01 | WTP6 |  | 0.2499 | CONWAY WP - ENTERD 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-01 | WTP8 |  | 0.0149 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP8 |  | 0.0249 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-01 | WTP8 |  | 0.1499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP8 |  | 1.4999 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-01 | WTP8 |  | 1.4999 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-01 | WTP8 |  | 0.4499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-01 | WTP8 |  | 9.4999 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-01 | WTP8 |  | 6.4999 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-01 | WTP8 |  | 0.6499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-01 | WTP8 |  | 2.4999 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-01 | WTP8 |  | 0.0749 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-01 | WTP8 |  | 0.6499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-01 | WTP8 |  | 0.1499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-01 | WTP8 |  | 0.2499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-01 | WTP8 |  | 0.1499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-01 | WTP8 |  | 0.9499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP8 |  | 0.1499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-01 | WTP8 |  | 0.2499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-01 | WTP8 |  | 0.0449 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP8 |  | 0.0249 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-01 | WTP8 |  | 0.1499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-01 | WTP8 |  | 0.2499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-01 | WTP8 |  | 0.1499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP8 |  | 0.0249 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-01 | WTP8 |  | 0.0449 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-01 | WTP8 |  | 0.1499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP8 |  | 0.0249 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-01 | WTP8 |  | 0.0149 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-01 | WTP8 |  | 0.2499 | NAVY WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-01 | WTP10 |  | 0.0149 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP10 |  | 0.0249 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-01 | WTP10 |  | 0.1499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP10 |  | 1.4999 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-01 | WTP10 |  | 1.4999 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-01 | WTP10 |  | 0.4499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-01 | WTP10 |  | 9.4999 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-01 | WTP10 |  | 6.4999 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-01 | WTP10 |  | 0.6499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-01 | WTP10 |  | 2.4999 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-01 | WTP10 |  | 0.0749 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-01 | WTP10 |  | 0.6499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-01 | WTP10 |  | 0.1499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-01 | WTP10 |  | 0.2499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-01 | WTP10 |  | 0.1499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-01 | WTP10 |  | 0.9499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP10 |  | 0.1499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-01 | WTP10 |  | 0.2499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-01 | WTP10 |  | 0.0449 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP10 |  | 0.0249 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-01 | WTP10 |  | 0.1499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-01 | WTP10 |  | 0.2499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-01 | WTP10 |  | 0.1499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP10 |  | 0.0249 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-01 | WTP10 |  | 0.0449 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-01 | WTP10 |  | 0.1499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP10 |  | 0.0249 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-01 | WTP10 |  | 0.0149 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-01 | WTP10 |  | 0.2499 | SKY LAKE WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-01 | WTP11 |  | 0.0149 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP11 |  | 0.0249 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-01 | WTP11 |  | 0.1499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP11 |  | 1.4999 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-01 | WTP11 |  | 1.4999 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-01 | WTP11 |  | 0.4499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-01 | WTP11 |  | 9.4999 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-01 | WTP11 |  | 6.4999 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-01 | WTP11 |  | 0.6499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-01 | WTP11 |  | 2.4999 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-01 | WTP11 |  | 0.0749 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-01 | WTP11 |  | 0.6499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-01 | WTP11 |  | 0.1499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-01 | WTP11 |  | 0.2499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-01 | WTP11 |  | 0.1499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-01 | WTP11 |  | 0.9499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP11 |  | 0.1499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-01 | WTP11 |  | 0.2499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-01 | WTP11 |  | 0.0449 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP11 |  | 0.0249 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-01 | WTP11 |  | 0.1499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-01 | WTP11 |  | 0.2499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-01 | WTP11 |  | 0.1499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP11 |  | 0.0249 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-01 | WTP11 |  | 0.0449 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-01 | WTP11 |  | 0.1499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP11 |  | 0.0249 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-01 | WTP11 |  | 0.0149 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-01 | WTP11 |  | 0.2499 | SOUTHWEST WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-01 | WTP7 |  | 0.0149 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP7 |  | 0.0249 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-01 | WTP7 |  | 0.1499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP7 |  | 1.4999 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-01 | WTP7 |  | 1.4999 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-01 | WTP7 |  | 0.4499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-01 | WTP7 |  | 9.4999 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-01 | WTP7 |  | 6.4999 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-01 | WTP7 |  | 0.6499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-01 | WTP7 |  | 2.4999 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-01 | WTP7 |  | 0.0749 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-01 | WTP7 |  | 0.6499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-01 | WTP7 |  | 0.1499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-01 | WTP7 |  | 0.2499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-01 | WTP7 |  | 0.1499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-01 | WTP7 |  | 0.9499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP7 |  | 0.1499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-01 | WTP7 |  | 0.2499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-01 | WTP7 |  | 0.0449 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP7 |  | 0.0249 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-01 | WTP7 |  | 0.1499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-01 | WTP7 |  | 0.2499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-01 | WTP7 |  | 0.1499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP7 |  | 0.0249 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-01 | WTP7 |  | 0.0449 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-01 | WTP7 |  | 0.1499 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP7 |  | 0.0249 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-01 | WTP7 |  | 0.0149 | KIRKMAN WP - ENTERED 2/2/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-01 | WTP7 |  | 0.2499 | KIRKMAN WP - ENTERED 2/2/24_KES
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-06-10 | WTP2 |  | 0.0449 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-06-10 | WTP2 |  | 0.0449 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-06-10 | WTP2 |  | 0.1499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-06-10 | WTP2 |  | 0.0249 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-06-10 | WTP2 |  | 0.0149 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-06-10 | WTP2 |  | 0.2499 | POE-WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.4 | UG/L | 60.4999 | 2021-08-23 | L1
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 3.51 | UG/L | 80.4999 | 2021-08-23 | L1 |  |  |  | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.7 | UG/L | 60.4999 | 2021-08-23 | L2 |  |  | ALAMENA | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 3.43 | UG/L | 80.4999 | 2021-08-23 | L2 |  |  | ALAMENA
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-11-23 | L1 | 1 |  | 7189 LINMAR
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-11-23 | L1 | 0.5 |  | 7189 LINMAR | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-11-23 | L2 | 1 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-11-23 | L2 | 0.5 |  | 7006 ALAMENA (HLKD) | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-27 | WTP2 |  |  | WP4
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-27 | WTP2 |  |  | WP4
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0.042 | MG/L | 10.4999 | 2022-01-27 | WTP3 |  |  | WP5
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-27 | WTP3 |  |  | WP5
3481199 | SILVER STAR VILLAGE (2 WPS) | S | DBP | 2950 | TOTAL THMS | 1.5 | UG/L | 80.4999 | 2022-06-09 | L1 |  |  | 7189 LINMAR- SAMPLED WRONG MONTH_AL | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.6 | UG/L | 60.4999 | 2022-11-22 | L2 | 60 |  | MAKEUP FROM Q3 2022 HAA5 J QUALIFIER | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-19 | WTP2 | 1 |  | 2023 N/N SAMPLES
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2023-01-19 | WTP2 | 10 |  | 2023 N/N SAMPLES
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0.068 | MG/L | 10.4999 | 2023-05-18 | WTP3 | 0.024 |  | WP5 POE-SS#3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-05-18 | WTP3 |  |  | WP5 POE-SS#3
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 4.2 | UG/L | 80.4999 | 2023-05-18 | L1 | 0.39 |  | TTHM ONLY | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.6 | UG/L | 60.4999 | 2023-08-09 | L2 | 2 |  | 7006 ALAMENA | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-20 | WTP2 |  |  | POE SS#2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-05-20 | L1 |  |  | 7189 LINMAR - TTHM | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.7 | UG/L | 60.4999 | 2024-08-12 | L2 | 0.3 |  | 7006 ALAMENA HAA5 | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.7 | PCI/L | 15.4999 | 2024-10-24 | WTP2 | 1 |  | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-10-24 | WTP2 |  | 1.4999 | POE
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-10-24 | WTP3 |  |  | POE SILVER STAR 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-10-24 | WTP3 |  | 1.4999 | POE SILVER STAR 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-24 | WTP2 | 0.2 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-24 | WTP2 | 0.2 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-10-24 | WTP2 | 0.00035 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1010 | BARIUM | 0.0083 | MG/L | 2.4999 | 2024-10-24 | WTP2 | 0.00033 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-10-24 | WTP2 | 0.00022 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1020 | CHROMIUM | 0.0011 | MG/L | 0.1499 | 2024-10-24 | WTP2 | 0.00035 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-10-24 | WTP2 | 0.005 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-10-24 | WTP2 | 0.2 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-10-24 | WTP2 | 0.00022 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-10-24 | WTP2 | 0.0002 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-10-24 | WTP2 | 0.00082 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-10-24 | WTP2 | 0.0009 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2024-10-24 | WTP2 | 0.12 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-10-24 | WTP2 | 0.00037 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-10-24 | WTP2 | 0.0029 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-10-24 | WTP2 | 0.00031 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1002 | ALUMINUM | 0.0031 | MG/L | 0.2499 | 2024-10-24 | WTP2 | 0.0031 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1017 | CHLORIDE | 20 | MG/L | 250.4999 | 2024-10-24 | WTP2 | 0.4 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1022 | COPPER | 0.0055 | MG/L | 1.4999 | 2024-10-24 | WTP2 | 0.00058 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2024-10-24 | WTP2 | 0.2 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-10-24 | WTP2 | 0.096 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1032 | MANGANESE | 0.0032 | MG/L | 0.0549 | 2024-10-24 | WTP2 | 0.0009 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-10-24 | WTP2 | 3e-05 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1055 | SULFATE | 17 | MG/L | 250.4999 | 2024-10-24 | WTP2 | 2 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1095 | ZINC | 0.012 | MG/L | 5.4999 | 2024-10-24 | WTP2 | 0.0012 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-10-24 | WTP2 | 5 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-10-24 | WTP2 | 1 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2024-10-24 | WTP2 | 1 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 150 | MG/L | 500.4999 | 2024-10-24 | WTP2 | 5 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-10-24 | WTP2 | 0.2 |  | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-10-24 | WTP2 | 0.5 | 0.5499 | WTP2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-24 | WTP3 | 0.2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-24 | WTP3 | 0.2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-10-24 | WTP3 | 0.00035
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1010 | BARIUM | 0.0082 | MG/L | 2.4999 | 2024-10-24 | WTP3 | 0.00033
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-10-24 | WTP3 | 0.00022
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1020 | CHROMIUM | 0.001 | MG/L | 0.1499 | 2024-10-24 | WTP3 | 0.00035
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-10-24 | WTP3 | 0.005
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-10-24 | WTP3 | 0.2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-10-24 | WTP3 | 0.00022
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-10-24 | WTP3 | 0.0002
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-10-24 | WTP3 | 0.00082
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-10-24 | WTP3 | 0.0009
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2024-10-24 | WTP3 | 0.12
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-10-24 | WTP3 | 0.00037
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-10-24 | WTP3 | 0.00029
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-10-24 | WTP3 | 0.00031
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1002 | ALUMINUM | 0.0037 | MG/L | 0.2499 | 2024-10-24 | WTP3 | 0.0031
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1017 | CHLORIDE | 20 | MG/L | 250.4999 | 2024-10-24 | WTP3 | 0.4
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1022 | COPPER | 0.0023 | MG/L | 1.4999 | 2024-10-24 | WTP3 | 0.00058
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2024-10-24 | WTP3 | 0.2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-10-24 | WTP3 | 0.096
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1032 | MANGANESE | 0.0034 | MG/L | 0.0549 | 2024-10-24 | WTP3 | 0.0009
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-10-24 | WTP3 | 3e-05
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1055 | SULFATE | 18 | MG/L | 250.4999 | 2024-10-24 | WTP3 | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1095 | ZINC | 0.0079 | MG/L | 5.4999 | 2024-10-24 | WTP3 | 0.0012
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-10-24 | WTP3 | 5
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-10-24 | WTP3 | 1
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.7 | LN(10) |  | 2024-10-24 | WTP3 | 1
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 160 | MG/L | 500.4999 | 2024-10-24 | WTP3 | 5
3481199 | SILVER STAR VILLAGE (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-10-24 | WTP3 | 0.2
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-10-24 | WTP3 | 0.5 | 0.5499 | MDL AND RDL BOTH REPORTED AS 0.5 FOR ALL PARAM
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-05-20 | L1 | 0.21 |  | 7189 LINMAR - TTHM ONLY | 2
3481199 | SILVER STAR VILLAGE (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-27 | L2 | 0.2 |  | 7006 ALAMENA - HAA5 ONLY | 3
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 1.7 | MG/L | 10.4999 | 2025-10-23 | WTP3 | 0.1 |  | POE SS WELL 5
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-23 | WTP3 |  |  | POE SS WELL 5
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1040 | NITRATE | 1.7 | MG/L | 10.4999 | 2025-10-23 | WTP2 | 0.1 |  | POE SS WELL 4
3481199 | SILVER STAR VILLAGE (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-23 | WTP2 |  |  | POE SS WELL 4
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-01 | WTP5 |  | 0.0149 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP5 |  | 0.0249 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-01 | WTP5 |  | 0.1499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP5 |  | 1.4999 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-01 | WTP5 |  | 1.4999 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-01 | WTP5 |  | 0.4499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-01 | WTP5 |  | 9.4999 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-01 | WTP5 |  | 6.4999 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-01 | WTP5 |  | 0.6499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-01 | WTP5 |  | 2.4999 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-01 | WTP5 |  | 0.0749 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-01 | WTP5 |  | 0.6499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-01 | WTP5 |  | 0.1499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-01 | WTP5 |  | 0.2499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-01 | WTP5 |  | 0.1499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-01 | WTP5 |  | 0.9499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-01 | WTP5 |  | 0.1499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-01 | WTP5 |  | 0.2499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-01 | WTP5 |  | 0.0449 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP5 |  | 0.0249 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-01 | WTP5 |  | 0.1499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-01 | WTP5 |  | 0.2499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-01 | WTP5 |  | 0.1499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP5 |  | 0.0249 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-01 | WTP5 |  | 0.0449 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-01 | WTP5 |  | 0.1499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-01 | WTP5 |  | 0.0249 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-01 | WTP5 |  | 0.0149 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-01 | WTP5 |  | 0.2499 | PINE HILLS - ENTERED 2/1/24_KES
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.24 | UG/L | 10.4999 | 2023-06-05 | L7 | 0.59 |  | SOUTHWEST POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.21 | UG/L | 10.4999 | 2023-06-05 | L7 | 0.59 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-06-05 | L7 | 0.59 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.09 | UG/L | 10.4999 | 2023-06-05 | L7 | 0.59 |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.31 | UG/L | 10.4999 | 2023-06-05 | L7 | 0.59 |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.89 | UG/L | 10.4999 | 2023-06-05 | L7 | 0.59 |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.2 | UG/L | 10.4999 | 2023-06-05 | L7 | 0.59 |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2023-06-07 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-06-07 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2023-06-07 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.3 | MG/L | 0 | 2023-06-07 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2023-06-07 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-06-07 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2023-06-07 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-06-07 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-06-07 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2023-06-07 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2023-06-07 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-06-07 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.5 | MG/L | 0 | 2023-06-07 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-06-07 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-06-07 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.2 | MG/L | 0 | 2023-06-07 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-06-07 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-06-07 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2023-06-13 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.4 |  |  | 2023-06-13 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-06-13 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.1 |  |  | 2023-06-13 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-06-13 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.3 |  |  | 2023-06-13 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-06-13 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.5 |  |  | 2023-06-13 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-06-13 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.1 |  |  | 2023-06-13 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-06-13 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.7 |  |  | 2023-06-13 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2023-06-13 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.1 |  |  | 2023-06-13 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43.1 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-06-13 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.9 |  |  | 2023-06-13 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 42.3 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-06-13 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-06-13 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.4 |  |  | 2023-06-13 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2023-06-13 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 32.3 | MG/L | 0 | 2023-06-21 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-06-21 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-06-21 | WTP11 |  |  | SW WP-6825 WALLACE RD
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.7 | MG/L | 0 | 2023-06-21 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2023-06-21 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2023-06-21 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33 | MG/L | 0 | 2023-06-21 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-06-21 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-06-21 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2023-06-21 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2023-06-21 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-06-21 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2023-06-21 | WTP8 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-06-21 | WTP8 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-06-21 | WTP8 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.6 | MG/L | 0 | 2023-06-21 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2023-06-21 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-06-21 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 28.2 | MG/L | 0 | 2023-06-21 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-06-21 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-06-21 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.7 | UG/L | 10.4999 | 2023-07-03 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.14 | UG/L | 10.4999 | 2023-07-03 | L7 | 0.59 |  | POE-KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.69 | UG/L | 10.4999 | 2023-07-03 | L7 | 0.59 |  | POE-PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 10.2 | UG/L | 10.4999 | 2023-07-03 | L7 | 0.59 |  | POE-HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.96 | UG/L | 10.4999 | 2023-07-03 | L7 | 0.59 |  | POE-NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.61 | UG/L | 10.4999 | 2023-07-03 | L7 | 0.59 |  | POE-CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.09 | UG/L | 10.4999 | 2023-07-03 | L7 | 0.59 |  | POE-SKY LAKE POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2023-07-05 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2023-07-05 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-07-05 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2023-07-05 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2023-07-05 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-07-05 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.4 | MG/L | 0 | 2023-07-05 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2023-07-05 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-07-05 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29 | MG/L | 0 | 2023-07-05 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-07-05 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-07-05 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2023-07-05 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2023-07-05 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-07-05 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2023-07-05 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-07-05 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-07-05 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2023-07-05 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-07-05 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-07-05 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.8 | MG/L | 0 | 2023-07-19 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2023-07-19 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-07-19 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2023-07-19 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2023-07-19 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-07-19 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.9 | MG/L | 0 | 2023-07-19 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-07-19 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-07-19 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39 | MG/L | 0 | 2023-07-19 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2023-07-19 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2023-07-19 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.8 | MG/L | 0 | 2023-07-19 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-07-19 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-07-19 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.3 | MG/L | 0 | 2023-07-19 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-07-19 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-07-19 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2023-07-19 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2023-07-19 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-07-19 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.83 | UG/L | 60.4999 | 2023-08-01 | L1 | 2 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 64.7 | UG/L | 80.4999 | 2023-08-01 | L1 | 0.13 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.18 | UG/L | 60.4999 | 2023-08-01 | L2 | 2 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 49.51 | UG/L | 80.4999 | 2023-08-01 | L2 | 0.13 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.02 | UG/L | 60.4999 | 2023-08-01 | L3 | 2 |  | 2950 EXCEEDENCE- LRAA < MCL, NO ENFORCEMENT- LRAA 68.82
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 82.94 | UG/L | 80.4999 | 2023-08-01 | L3 | 0.13 |  | 2950 EXCEEDENCE- LRAA < MCL, NO ENFORCEMENT- LRAA 68.82
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.18 | UG/L | 60.4999 | 2023-08-01 | L4 | 4 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 68.75 | UG/L | 80.4999 | 2023-08-01 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.72 | UG/L | 60.4999 | 2023-08-01 | L5 | 2 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 68.15 | UG/L | 80.4999 | 2023-08-01 | L5 | 0.13 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.62 | UG/L | 60.4999 | 2023-08-01 | L6 | 2 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 40.96 | UG/L | 80.4999 | 2023-08-01 | L6 | 0.13 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2023-08-02 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2023-08-02 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2023-08-02 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.8 | MG/L | 0 | 2023-08-02 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-08-02 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-08-02 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30 | MG/L | 0 | 2023-08-02 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-08-02 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-08-02 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2023-08-02 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2023-08-02 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-08-02 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.1 | MG/L | 0 | 2023-08-02 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-08-02 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-08-02 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2023-08-02 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-08-02 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-08-02 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2023-08-02 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2023-08-02 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-08-02 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.15 | UG/L | 10.4999 | 2023-08-07 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.1 | UG/L | 10.4999 | 2023-08-07 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.99 | UG/L | 10.4999 | 2023-08-07 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.49 | UG/L | 10.4999 | 2023-08-07 | L7 | 0.59 |  | POE-HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.95 | UG/L | 10.4999 | 2023-08-07 | L7 | 0.59 |  | POE NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.72 | UG/L | 10.4999 | 2023-08-07 | L7 | 0.59 |  | POE CONWAY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.15 | UG/L | 10.4999 | 2023-08-07 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.3 | MG/L | 0 | 2023-08-16 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2023-08-16 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-08-16 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.2 | MG/L | 0 | 2023-08-16 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2023-08-16 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-08-16 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.6 | MG/L | 0 | 2023-08-16 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-08-16 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-08-16 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2023-08-16 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2023-08-16 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-08-16 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2023-08-16 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-08-16 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-08-16 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2023-08-16 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-08-16 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-08-16 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41 | MG/L | 0 | 2023-08-16 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2023-08-16 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-08-16 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.3 | MG/L | 0 | 2023-08-29 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-08-29 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-08-29 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.4 | MG/L | 0 | 2023-08-29 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-08-29 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-08-29 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.2 | MG/L | 0 | 2023-08-29 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2023-08-29 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2023-08-29 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.2 | MG/L | 0 | 2023-08-29 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-08-29 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-08-29 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2023-08-29 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2023-08-29 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-08-29 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2023-08-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-08-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-08-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 4.09 | MG/L | 0 | 2023-08-29 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2023-08-29 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-08-29 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.47 | UG/L | 10.4999 | 2023-09-05 | L7 | 0.59 |  | POE-SW
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.84 | UG/L | 10.4999 | 2023-09-05 | L7 | 0.59 |  | POE-PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.53 | UG/L | 10.4999 | 2023-09-05 | L7 | 0.59 |  | POE-KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 10.5 | UG/L | 10.4999 | 2023-09-05 | L7 | 0.59 |  | POE- HIGHLAND-EXCEEDENCE- NOT A VIOLATION. RAA (4.19)
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.38 | UG/L | 10.4999 | 2023-09-05 | L7 | 0.59 |  | POE-NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.96 | UG/L | 10.4999 | 2023-09-05 | L7 | 0.59 |  | POE-CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.42 | UG/L | 10.4999 | 2023-09-05 | L7 | 0.59 |  | POE-SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2023-09-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.9 |  |  | 2023-09-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 42.5 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-09-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 27.9 |  |  | 2023-09-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 42.9 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2023-09-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.2 |  |  | 2023-09-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2023-09-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2023-09-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.1 |  |  | 2023-09-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.8 |  |  | 2023-09-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2023-09-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 30 |  |  | 2023-09-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2023-09-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 29.1 |  |  | 2023-09-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43.8 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-09-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 29.3 |  |  | 2023-09-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 43.3 | MG/L | 0 | 2023-09-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2023-09-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2023-09-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.6 |  |  | 2023-09-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.3 | MG/L | 0 | 2023-09-13 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2023-09-13 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-09-13 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34 | MG/L | 0 | 2023-09-13 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2023-09-13 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-09-13 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2023-09-13 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2023-09-13 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-09-13 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.3 | MG/L | 0 | 2023-09-13 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-09-13 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2023-09-13 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2023-09-13 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2023-09-13 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-09-13 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2023-09-13 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2023-09-13 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-09-13 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2023-09-13 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-09-13 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-09-13 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2023-09-27 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2023-09-27 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-09-27 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.8 | MG/L | 0 | 2023-09-27 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2023-09-27 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-09-27 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2023-09-27 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2023-09-27 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2023-09-27 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30 | MG/L | 0 | 2023-09-27 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-09-27 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-09-27 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2023-09-27 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2023-09-27 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2023-09-27 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2023-09-27 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2023-09-27 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-09-27 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2023-09-27 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-09-27 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-09-27 | WTP8 |  |  | NAVY WP
3484405 | PENANG NURSERY | D | INOR | 1040 | NITRATE | 0.055 | MG/L | 10.4999 | 2021-07-01 | AAA |  |  | POE
3484405 | PENANG NURSERY | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-01 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 3 | MG/L | 10.4999 | 2022-08-10 | AAA | 0.024 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1005 | ARSENIC | 0.0005 | MG/L | 0.0104 | 2022-08-10 | AAA | 0.00025 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1010 | BARIUM | 0.0063 | MG/L | 2.4999 | 2022-08-10 | AAA | 0.003 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2022-08-10 | AAA | 0.0099 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1030 | LEAD | 0.0012 | MG/L | 0.0154 | 2022-08-10 | AAA | 0.0005 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1035 | MERCURY | 0.0001 | MG/L | 0.0024 | 2022-08-10 | AAA | 1e-05 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2022-08-10 | AAA | 0.8 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1085 | THALLIUM | 0.0013 | MG/L | 0.0025 | 2022-08-10 | AAA | 0.00025 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | SEC | 1017 | CHLORIDE | 16 | MG/L | 250.4999 | 2022-08-10 | AAA | 0.039 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1022 | COPPER | 0.0092 | MG/L | 1.4999 | 2022-08-10 | AAA | 0.005 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2022-08-10 | AAA | 0.0099 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1028 | IRON | 0.028 | MG/L | 0.3499 | 2022-08-10 | AAA | 0.0067 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | SEC | 1055 | SULFATE | 7.8 | MG/L | 250.4999 | 2022-08-10 | AAA | 0.034 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1095 | ZINC | 0.059 | MG/L | 5.4999 | 2022-08-10 | AAA | 0.05 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2022-08-10 | AAA | 5 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.83 | LN(10) |  | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 129 | MG/L | 500.4999 | 2022-08-10 | AAA | 5 |  | POE
3484405 | PENANG NURSERY | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-08-10 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-08-10 | AAA |  | 0.0149 | POE
3484405 | PENANG NURSERY | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-08-10 | AAA |  | 0.0249 | POE
3484405 | PENANG NURSERY | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-08-10 | AAA |  | 0.1499 | POE
3484405 | PENANG NURSERY | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-08-10 | AAA |  | 1.4999 | POE
3484405 | PENANG NURSERY | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-10 | AAA |  | 1.4999 | POE
3484405 | PENANG NURSERY | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-08-10 | AAA |  | 0.4499 | POE
3484405 | PENANG NURSERY | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-08-10 | AAA |  | 9.4999 | POE
3484405 | PENANG NURSERY | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-08-10 | AAA |  | 6.4999 | POE
3484405 | PENANG NURSERY | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-08-10 | AAA |  | 0.6499 | POE
3484405 | PENANG NURSERY | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-08-10 | AAA |  | 2.4999 | POE
3484405 | PENANG NURSERY | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-08-10 | AAA |  | 0.0749 | POE
3484405 | PENANG NURSERY | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-08-10 | AAA |  | 0.6499 | POE
3484405 | PENANG NURSERY | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-08-10 | AAA |  | 0.1499 | POE
3484405 | PENANG NURSERY | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-08-10 | AAA |  | 0.2499 | POE
3484405 | PENANG NURSERY | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-08-10 | AAA |  | 0.1499 | POE
3484405 | PENANG NURSERY | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-08-10 | AAA |  | 0.9499 | POE
3484405 | PENANG NURSERY | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-08-10 | AAA |  | 0.1499 | POE
3484405 | PENANG NURSERY | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-08-10 | AAA |  | 0.2499 | POE
3484405 | PENANG NURSERY | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-10 | AAA |  | 0.0449 | POE
3484405 | PENANG NURSERY | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-10 | AAA |  | 0.0249 | POE
3484405 | PENANG NURSERY | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-10 | AAA |  | 0.1499 | POE
3484405 | PENANG NURSERY | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-10 | AAA |  | 0.2499 | POE
3484405 | PENANG NURSERY | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-10 | AAA |  | 0.1499 | POE
3484405 | PENANG NURSERY | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-10 | AAA |  | 0.0249 | POE
3484405 | PENANG NURSERY | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-10 | AAA |  | 0.0449 | POE
3484405 | PENANG NURSERY | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-10 | AAA |  | 0.1499 | POE
3484405 | PENANG NURSERY | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-10 | AAA |  | 0.0249 | POE
3484405 | PENANG NURSERY | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-10 | AAA |  | 0.0149 | POE
3484405 | PENANG NURSERY | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-10 | AAA |  | 0.2499 | POE
3484405 | PENANG NURSERY | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.19 | UG/L | 60.4999 | 2022-08-12 | L1 | 0.98 |  | BREAKROOM SINK (HLKD) | 3
3484405 | PENANG NURSERY | D | DBP | 2950 | TOTAL THMS | 9.56 | UG/L | 80.4999 | 2022-08-12 | L1 | 0.39 |  | BREAKROOM SINK (HLKD) | 3
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 1.9 | MG/L | 10.4999 | 2023-05-12 | AAA | 0.024 |  | 2023 ANNUAL N/N
3484405 | PENANG NURSERY | N | INOR | 1041 | NITRITE | 0.084 | MG/L | 1.4999 | 2023-05-12 | AAA | 0.0034 |  | 2023 ANNUAL N/N
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 11 | MG/L | 10.4999 | 2024-07-12 | AAA | 0.024 |  | MCL EXCEEDANCE
3484405 | PENANG NURSERY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-12 | AAA | 0.0034 |  | MCL EXCEEDANCE
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 12 | MG/L | 10.4999 | 2024-07-17 | AAA | 0.024 |  | NITRATE MCL EXCEEDANCE
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 11 | MG/L | 10.4999 | 2024-10-07 | AAA | 0.024 |  | MCL EXCEEDANCE - INITIAL SAMPLE
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 8.6 | MG/L | 10.4999 | 2024-11-06 | AAA | 0.024 |  | NOV NITRATE
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 3.4 | MG/L | 10.4999 | 2025-01-08 | AAA | 0.024 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-08 | AAA | 0.0034 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1005 | ARSENIC | 0.0007 | MG/L | 0.0104 | 2025-04-07 | AAA | 0.0003 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1010 | BARIUM | 0.008 | MG/L | 2.4999 | 2025-04-07 | AAA | 0.003 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1020 | CHROMIUM | 0.0005 | MG/L | 0.1499 | 2025-04-07 | AAA | 0.0005 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1052 | SODIUM | 8.2 | MG/L | 160.4999 | 2025-04-07 | AAA | 0.8 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-04-07 | AAA |  |  | POE
3484405 | PENANG NURSERY | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 1.5 | MG/L | 10.4999 | 2025-04-23 | AAA | 0.024 |  | POE - NO2/NO3/FLUORIDE
3484405 | PENANG NURSERY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-23 | AAA | 0.0034 |  | POE - NO2/NO3/FLUORIDE
3484405 | PENANG NURSERY | N | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2025-04-23 | AAA | 0.0099 |  | POE - NO2/NO3/FLUORIDE
3484405 | PENANG NURSERY | N | SEC | 1025 | FLUORIDE | 0.17 | MG/L | 2.0499 | 2025-04-23 | AAA | 0.0099 |  | POE - FLUORIDE ONLY
3484405 | PENANG NURSERY | N | INOR | 1040 | NITRATE | 1.6 | MG/L | 10.4999 | 2025-07-07 | AAA | 0.024 |  | POE
3484405 | PENANG NURSERY | N | INOR | 1025 | FLUORIDE | 0.047 | MG/L | 4.0499 | 2025-07-07 | AAA | 0.0099 |  | POE
3484405 | PENANG NURSERY | N | SEC | 1025 | FLUORIDE | 0.047 | MG/L | 2.0499 | 2025-07-07 | AAA | 0.0099 |  | POE
3484405 | PENANG NURSERY | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-07-07 | AAA | 0.0069 | 0.0149 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-07-07 | AAA | 0.0071 | 0.0249 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-07-07 | AAA | 0.0068 | 0.1499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-07-07 | AAA | 0.12 | 1.4999 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-07-07 | AAA | 0.9 | 1.4999 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-07-07 | AAA | 0.31 | 0.4499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-07-07 | AAA | 5.9 | 6.4999 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-07-07 | AAA | 0.5 | 0.6499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-07-07 | AAA | 1.8 | 2.4999 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-07-07 | AAA | 0.06 | 0.0749 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-07-07 | AAA | 0.5 | 0.6499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-07-07 | AAA | 0.09 | 0.1499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-07-07 | AAA | 0.18 | 0.2499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-07-07 | AAA | 0.019 | 0.1499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-07-07 | AAA | 0.67 | 0.9499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-07-07 | AAA | 0.09 | 0.1499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-07-07 | AAA | 0.15 | 0.2499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-07-07 | AAA | 0.006 | 0.0449 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-07-07 | AAA | 0.0052 | 0.0249 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-07-07 | AAA | 0.095 | 0.1499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-07-07 | AAA | 0.09 | 0.2499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-07-07 | AAA | 0.0063 | 0.1499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-07-07 | AAA | 0.015 | 0.0249 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-07-07 | AAA | 0.038 | 0.0449 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-07-07 | AAA | 0.093 | 0.1499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-07-07 | AAA | 0.0062 | 0.0249 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-07-07 | AAA | 0.0092 | 0.0149 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-07-07 | AAA | 0.053 | 0.2499 | POE - 2033 J QUALIFIER
3484405 | PENANG NURSERY | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-04 | L1 | 0.98 |  | BREAKROOM SINK - TTHM, HAA5 | 3
3484405 | PENANG NURSERY | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-08-04 | L1 | 0.44 |  | BREAKROOM SINK - TTHM, HAA5 | 3
3484405 | PENANG NURSERY | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-08-20 | AAA | 6 | 9.4999
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.95 | UG/L | 10.4999 | 2023-10-02 | L7 | 0.59 |  | SOUTHWEST POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.9 | UG/L | 10.4999 | 2023-10-02 | L7 | 0.59 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.72 | UG/L | 10.4999 | 2023-10-02 | L7 | 0.59 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.4 | UG/L | 10.4999 | 2023-10-02 | L7 | 0.59 |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.41 | UG/L | 10.4999 | 2023-10-02 | L7 | 0.59 |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.04 | UG/L | 10.4999 | 2023-10-02 | L7 | 0.59 |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.28 | UG/L | 10.4999 | 2023-10-02 | L7 | 0.59 |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2023-10-11 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2023-10-11 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-10-11 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2023-10-11 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-10-11 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-10-11 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2023-10-11 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2023-10-11 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2023-10-11 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2023-10-11 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-10-11 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-10-11 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37 | MG/L | 0 | 2023-10-11 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2023-10-11 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-10-11 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2023-10-11 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-10-11 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-10-11 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.4 | MG/L | 0 | 2023-10-11 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-10-11 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2023-10-11 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2023-10-25 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-10-25 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-10-25 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2023-10-25 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-10-25 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-10-25 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2023-10-25 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-10-25 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-10-25 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2023-10-25 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2023-10-25 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2023-10-25 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2023-10-25 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-10-25 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-10-25 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2023-10-25 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-10-25 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2023-10-25 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.3 | MG/L | 0 | 2023-10-25 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-10-25 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-10-25 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.6 | UG/L | 60.4999 | 2023-11-01 | L1 | 2 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 24.65 | UG/L | 80.4999 | 2023-11-01 | L1 | 0.13 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.13 | UG/L | 60.4999 | 2023-11-01 | L2 | 2 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 60.74 | UG/L | 80.4999 | 2023-11-01 | L2 | 0.13 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.88 | UG/L | 60.4999 | 2023-11-01 | L3 | 2 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 56.41 | UG/L | 80.4999 | 2023-11-01 | L3 | 0.13 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.45 | UG/L | 60.4999 | 2023-11-01 | L5 | 2 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 66.34 | UG/L | 80.4999 | 2023-11-01 | L5 | 0.13 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.78 | UG/L | 60.4999 | 2023-11-01 | L6 | 2 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 28.2 | UG/L | 80.4999 | 2023-11-01 | L6 | 0.13 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.85 | UG/L | 60.4999 | 2023-11-01 | L4 | 2 |  | SMP 5 SE - 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 65.44 | UG/L | 80.4999 | 2023-11-01 | L4 | 2 |  | SMP 5 SE - 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.85 | UG/L | 60.4999 | 2023-11-02 | L4 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD. J QUALIFIER-2450
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 65.44 | UG/L | 80.4999 | 2023-11-02 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD. J QUALIFIER-2450
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4 | UG/L | 10.4999 | 2023-11-06 | L7 | 0.59 |  | POE SOUTHWEST-BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.2 | UG/L | 10.4999 | 2023-11-06 | L7 | 0.59 |  | POE-KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.1 | UG/L | 10.4999 | 2023-11-06 | L7 | 0.59 |  | POE-PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.57 | UG/L | 10.4999 | 2023-11-06 | L7 | 0.59 |  | POE HIGHLAND POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.59 | UG/L | 10.4999 | 2023-11-06 | L7 | 0.59 |  | POE NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.6 | UG/L | 10.4999 | 2023-11-06 | L7 | 0.59 |  | POE CONWAY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.18 | UG/L | 10.4999 | 2023-11-06 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2023-11-08 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-11-08 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-11-08 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2023-11-08 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-11-08 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-11-08 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2023-11-08 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-11-08 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-11-08 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2023-11-08 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-11-08 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-11-08 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2023-11-08 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-11-08 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-11-08 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2023-11-08 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2023-11-08 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-11-08 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2023-11-08 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-11-08 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-11-08 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2023-11-22 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2023-11-22 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-11-22 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.2 | MG/L | 0 | 2023-11-22 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-11-22 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-11-22 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2023-11-22 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2023-11-22 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-11-22 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2023-11-22 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2023-11-22 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-11-22 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.8 | MG/L | 0 | 2023-11-22 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-11-22 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-22 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2023-11-22 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2023-11-22 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-11-22 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2023-11-22 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2023-11-22 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-11-22 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.4 | UG/L | 10.4999 | 2023-12-04 | L7 | 0.59 |  | POE- SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.25 | UG/L | 10.4999 | 2023-12-04 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-12-04 | L7 | 0.59 |  | POE -PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.74 | UG/L | 10.4999 | 2023-12-04 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.77 | UG/L | 10.4999 | 2023-12-04 | L7 | 0.59 |  | POE-NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.95 | UG/L | 10.4999 | 2023-12-04 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.58 | UG/L | 10.4999 | 2023-12-04 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2023-12-06 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-12-06 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-12-06 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2023-12-06 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-12-06 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2023-12-06 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2023-12-06 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2023-12-06 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-12-06 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2023-12-06 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2023-12-06 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-12-06 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.8 | MG/L | 0 | 2023-12-06 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2023-12-06 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-12-06 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2023-12-06 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2023-12-06 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-12-06 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2023-12-06 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-12-06 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-12-06 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2023-12-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.4 |  |  | 2023-12-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-12-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.7 |  |  | 2023-12-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-12-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.6 |  |  | 2023-12-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-12-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.3 |  |  | 2023-12-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-12-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.2 |  |  | 2023-12-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-12-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.2 |  |  | 2023-12-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-12-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.4 |  |  | 2023-12-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 42.3 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2023-12-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 21.7 |  |  | 2023-12-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2023-12-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-12-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-12-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.5 |  |  | 2023-12-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2023-12-20 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2023-12-20 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-12-20 | WTP11 |  |  | SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2023-12-20 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-12-20 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2023-12-20 | WTP8 |  |  | NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.3 | MG/L | 0 | 2023-12-20 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-12-20 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2023-12-20 | WTP10 |  |  | SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2023-12-20 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2023-12-20 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2023-12-20 | WTP6 |  |  | CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.2 | MG/L | 0 | 2023-12-20 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2023-12-20 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-12-20 | WTP5 |  |  | PINE HILLS WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.5 | MG/L | 0 | 2023-12-20 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2023-12-20 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-12-20 | WTP1 |  |  | HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2023-12-20 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2023-12-20 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-12-20 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.54 | UG/L | 10.4999 | 2024-01-02 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.99 | UG/L | 10.4999 | 2024-01-02 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.14 | UG/L | 10.4999 | 2024-01-02 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.54 | UG/L | 10.4999 | 2024-01-02 | L7 | 0.59 |  | POE HIGHLAND POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.8 | UG/L | 10.4999 | 2024-01-02 | L7 | 0.59 |  | POE NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.16 | UG/L | 10.4999 | 2024-01-02 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.02 | UG/L | 10.4999 | 2024-01-02 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2024-01-03 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2024-01-03 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-01-03 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.4 | MG/L | 0 | 2024-01-03 | WTP5 |  |  | PINE HILL WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-01-03 | WTP5 |  |  | PINE HILL WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2024-01-03 | WTP5 |  |  | PINE HILL WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.7 | MG/L | 0 | 2024-01-03 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-01-03 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-01-03 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.8 | MG/L | 0 | 2024-01-03 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2024-01-03 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-01-03 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2024-01-03 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2024-01-03 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-01-03 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2024-01-03 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2024-01-03 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-01-03 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2024-01-03 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2024-01-03 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-01-03 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.58 | UG/L | 10.4999 | 2024-01-06 | L7 | 0.59 |  | POE SOUTH WEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2024-01-17 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2024-01-17 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-01-17 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.7 | MG/L | 0 | 2024-01-17 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2024-01-17 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2024-01-17 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2024-01-17 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-01-17 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2024-01-17 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2024-01-17 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-01-17 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-01-17 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2024-01-17 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-01-17 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-01-17 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 32.5 | MG/L | 0 | 2024-01-17 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2024-01-17 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2024-01-17 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2024-01-17 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-01-17 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-01-17 | WTP1 |  |  | HIGHLAND WTP
3484402 | ORLANDO WETLANDS PARK | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-11 | AAA | 0.2 |  | "NITRATE RAW" PER LAB REPORT YET MARKED POE/D, C.R. 0.06
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-08 | AAA | 0.2
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-08 | AAA | 0.2
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-03 | AAA | 0.2 |  | NITRATE J QUALIFIER- APPROVED_AL
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0.643 | MG/L | 10.4999 | 2022-01-03 | AAA | 0.2 |  | NITRATE J QUALIFIER- APPROVED_AL
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-23 | AAA | 0.2
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-23 | AAA | 0.2
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-04-22 | AAA |  |  | POE - EXCEEDENCE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 1.2 | MG/L | 1.4999 | 2024-04-22 | AAA | 0.2 |  | POE - EXCEEDENCE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-11-04 | AAA |  |  | POE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-04 | AAA |  |  | POE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-03 | AAA | 0.2 |  | POE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-03 | AAA | 0.2 |  | POE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-05-21 | AAA |  |  | POE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-05-21 | AAA |  |  | POE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-08-04 | AAA | 0.1 |  | POE- MARKED RESAMPLE
3484402 | ORLANDO WETLANDS PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-04 | AAA | 0.1 |  | POE- MARKED RESAMPLE
3480962 | ORLANDO UTILITIES COMMISSION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-01-23 | WTP11 |  | 0.6499 | POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2024-01-23 | WTP5 | 0.03 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-23 | WTP5 |  |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2024-01-23 | WTP7 | 0.03 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-23 | WTP7 | 0.03 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.04 | MG/L | 10.4999 | 2024-01-23 | WTP11 | 0.03 |  | POE SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-23 | WTP11 |  |  | POE SW WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.05 | MG/L | 10.4999 | 2024-01-23 | WTP10 | 0.03 |  | POE SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-23 | WTP10 |  |  | POE SKY LAKE WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.05 | MG/L | 10.4999 | 2024-01-23 | WTP6 | 0.03 |  | POE CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-23 | WTP6 |  |  | POE CONWAY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2024-01-23 | WTP1 | 0.03 |  | POE HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-23 | WTP1 |  |  | POE HIGHLAND WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.07 | MG/L | 10.4999 | 2024-01-23 | WTP8 | 0.03 |  | POE NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-23 | WTP8 |  |  | POE NAVY WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.1 | MG/L | 0 | 2024-01-30 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-01-30 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-01-30 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2024-01-30 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2024-01-30 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2024-01-30 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.1 | MG/L | 0 | 2024-01-30 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-01-30 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2024-01-30 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2024-01-30 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-01-30 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-01-30 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.4 | MG/L | 0 | 2024-01-30 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-01-30 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2024-01-30 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.1 | MG/L | 0 | 2024-01-30 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2024-01-30 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2024-01-30 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2024-01-30 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2024-01-30 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-01-30 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.24 | UG/L | 60.4999 | 2024-02-01 | L1 | 2 |  | SMP PT 10 1642 SILVER STAR RD. HAA5 LRAA: 21.00 TTHM LRAA: 38.40
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 47.43 | UG/L | 80.4999 | 2024-02-01 | L1 | 0.13 |  | SMP PT 10 1642 SILVER STAR RD. HAA5 LRAA: 21.00 TTHM LRAA: 38.40
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.99 | UG/L | 60.4999 | 2024-02-01 | L2 | 2 |  | SMP PT 23 2714 ILLINOIS ST. HAA5 LRAA: 26.87 TTHM LRAA: 57.25
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 53.7 | UG/L | 80.4999 | 2024-02-01 | L2 | 0.13 |  | SMP PT 23 2714 ILLINOIS ST. HAA5 LRAA: 26.87 TTHM LRAA: 57.25
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.52 | UG/L | 60.4999 | 2024-02-01 | L3 | 2 |  | SMP PT 169 758 DENNIS AVE. HAA5 LRAA: 26.87 TTHM LRAA: 63.68
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 56.09 | UG/L | 80.4999 | 2024-02-01 | L3 | 0.13 |  | SMP PT 169 758 DENNIS AVE. HAA5 LRAA: 26.87 TTHM LRAA: 63.68
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.36 | UG/L | 60.4999 | 2024-02-01 | L4 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD. HAA5 LRAA: 30.00 TTHM LRAA: 62.28
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 51.4 | UG/L | 80.4999 | 2024-02-01 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD. HAA5 LRAA: 30.00 TTHM LRAA: 62.28
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.22 | UG/L | 60.4999 | 2024-02-01 | L5 | 2 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR HAA5 LRAA: 26.98 TTHM LRAA: 65.33
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 62.04 | UG/L | 80.4999 | 2024-02-01 | L5 | 0.13 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR HAA5 LRAA: 26.98 TTHM LRAA: 65.33
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.11 | UG/L | 60.4999 | 2024-02-01 | L6 | 2 |  | SMP PT 121 5512 BAYSIDE DR. HAA5 LRAA: 16.23 TTHM LRAA: 34.68
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 28.95 | UG/L | 80.4999 | 2024-02-01 | L6 | 0.13 |  | SMP PT 121 5512 BAYSIDE DR. HAA5 LRAA: 16.23 TTHM LRAA: 34.68
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.23 | UG/L | 10.4999 | 2024-02-05 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.81 | UG/L | 10.4999 | 2024-02-05 | L7 | 0.59 |  | POE-KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.86 | UG/L | 10.4999 | 2024-02-05 | L7 | 0.59 |  | POE-PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.81 | UG/L | 10.4999 | 2024-02-05 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.54 | UG/L | 10.4999 | 2024-02-05 | L7 | 0.59 |  | POE NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.51 | UG/L | 10.4999 | 2024-02-05 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.08 | UG/L | 10.4999 | 2024-02-05 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.7 | MG/L | 0 | 2024-02-14 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2024-02-14 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2024-02-14 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.1 | MG/L | 0 | 2024-02-14 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2024-02-14 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-02-14 | WTP11 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29 | MG/L | 0 | 2024-02-14 | WTP6 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-02-14 | WTP6 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2024-02-14 | WTP6 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.4 | MG/L | 0 | 2024-02-14 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2024-02-14 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-02-14 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.8 | MG/L | 0 | 2024-02-14 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2024-02-14 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2024-02-14 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2024-02-14 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-02-14 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-02-14 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2024-02-14 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2024-02-14 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-02-14 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34 | MG/L | 0 | 2024-02-28 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2024-02-28 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2024-02-28 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2024-02-28 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2024-02-28 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-02-28 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.8 | MG/L | 0 | 2024-02-28 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-02-28 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-02-28 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.4 | MG/L | 0 | 2024-02-28 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-02-28 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2024-02-28 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.8 | MG/L | 0 | 2024-02-28 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2024-02-28 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-02-28 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2024-02-28 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2024-02-28 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2024-02-28 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2024-02-28 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2024-02-28 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-02-28 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.32 | UG/L | 10.4999 | 2024-03-04 | L7 | 0.59 |  | SOUTHWEST POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.21 | UG/L | 10.4999 | 2024-03-04 | L7 | 0.59 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.76 | UG/L | 10.4999 | 2024-03-04 | L7 | 0.59 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.79 | UG/L | 10.4999 | 2024-03-04 | L7 | 0.59 |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-03-04 | L7 | 0.59 |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.34 | UG/L | 10.4999 | 2024-03-04 | L7 | 0.59 |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.21 | UG/L | 10.4999 | 2024-03-04 | L7 | 0.59 |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.9 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2024-03-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.6 |  |  | 2024-03-12 | WTP12 |  |  | 9576 TAVISTOK RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2024-03-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.6 |  |  | 2024-03-12 | WTP12 |  |  | 10694 CROMWELL RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-03-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24 |  |  | 2024-03-12 | WTP12 |  |  | 8773 NORTHLAKE PKWY
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.3 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2024-03-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.4 |  |  | 2024-03-12 | WTP12 |  |  | 12385 LAKE NONA GATEWAY BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-03-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.4 |  |  | 2024-03-12 | WTP12 |  |  | 10080 LAKE NONA BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-03-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2024-03-12 | WTP12 |  |  | 12500 NARCOOSSEE RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.6 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-03-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2024-03-12 | WTP12 |  |  | 10100 EMERSON LAKE BLVD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 42.2 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-03-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23 |  |  | 2024-03-12 | WTP12 |  |  | 11601 KIRBY SMITH RD
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2024-03-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-03-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2024-03-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.8 |  |  | 2024-03-12 | WTP12 |  |  | 7228 HUMBOLDT DR
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.1 | MG/L | 0 | 2024-03-13 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2024-03-13 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2024-03-13 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.8 | MG/L | 0 | 2024-03-13 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-03-13 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-03-13 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.6 | MG/L | 0 | 2024-03-13 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-03-13 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2024-03-13 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.3 | MG/L | 0 | 2024-03-13 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-03-13 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-03-13 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.6 | MG/L | 0 | 2024-03-13 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2024-03-13 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-03-13 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42 | MG/L | 0 | 2024-03-13 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2024-03-13 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2024-03-13 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2024-03-13 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2024-03-13 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-03-13 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2024-03-27 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2024-03-27 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-03-27 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.6 | MG/L | 0 | 2024-03-27 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2024-03-27 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-03-27 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.3 | MG/L | 0 | 2024-03-27 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2024-03-27 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2024-03-27 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.3 | MG/L | 0 | 2024-03-27 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2024-03-27 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-03-27 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.5 | MG/L | 0 | 2024-03-27 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2024-03-27 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2024-03-27 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.5 | MG/L | 0 | 2024-03-27 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2024-03-27 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2024-03-27 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2024-03-27 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2024-03-27 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2024-03-27 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.41 | UG/L | 10.4999 | 2024-04-01 | L7 | 0.59 |  | BROMATE - SW POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.88 | UG/L | 10.4999 | 2024-04-01 | L7 | 0.59 |  | BROMATE - KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.14 | UG/L | 10.4999 | 2024-04-01 | L7 | 0.59 |  | BROMATE - PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.9 | UG/L | 10.4999 | 2024-04-01 | L7 | 0.59 |  | BROMATE - HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.01 | UG/L | 10.4999 | 2024-04-01 | L7 | 0.59 |  | BROMATE - NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.95 | UG/L | 10.4999 | 2024-04-01 | L7 | 0.59 |  | BROMATE - CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.11 | UG/L | 10.4999 | 2024-04-01 | L7 | 0.59 |  | BROMATE - SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2024-04-10 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-04-10 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2024-04-10 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.9 | MG/L | 0 | 2024-04-10 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-04-10 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-04-10 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2024-04-10 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2024-04-10 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-04-10 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.5 | MG/L | 0 | 2024-04-10 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2024-04-10 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2024-04-10 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2024-04-10 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-04-10 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2024-04-10 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.8 | MG/L | 0 | 2024-04-10 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2024-04-10 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-04-10 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2024-04-10 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2024-04-10 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-04-10 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.1 | MG/L | 0 | 2024-04-23 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2024-04-23 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2024-04-23 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.5 | MG/L | 0 | 2024-04-23 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2024-04-23 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2024-04-23 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.6 | MG/L | 0 | 2024-04-23 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2024-04-23 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-04-23 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2024-04-23 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-04-23 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-04-23 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.4 | MG/L | 0 | 2024-04-23 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-04-23 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-04-23 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2024-04-23 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-04-23 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-04-23 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2024-04-23 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2024-04-23 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2024-04-23 | WTP1 |  |  | HIGHLAND WTP
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-01-11 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-06 | AAA | 0.5 | 0.5499 | 4QM/DIC (HLKD)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-09 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-09 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-04-07 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-09-20 | AAA | 0.2
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-09-20 | AAA | 0.2
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-09-20 | AAA | 0.002
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2022-09-20 | AAA | 0.002
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-09-20 | AAA | 0.001
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-09-20 | AAA | 0.001
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-09-20 | AAA | 0.005
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1025 | FLUORIDE | 0.39 | MG/L | 4.0499 | 2022-09-20 | AAA | 0.2
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-09-20 | AAA | 0.001
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-09-20 | AAA | 0.0001
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-09-20 | AAA | 0.002
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-09-20 | AAA | 0.002
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1052 | SODIUM | 6.2 | MG/L | 160.4999 | 2022-09-20 | AAA | 0.1
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-09-20 | AAA | 0.001
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-09-20 | AAA | 0.0005
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-09-20 | AAA | 0.0005
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-09-20 | AAA | 0.01 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1017 | CHLORIDE | 14 | MG/L | 250.4999 | 2022-09-20 | AAA | 0.4 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1022 | COPPER | 0.065 | MG/L | 1.4999 | 2022-09-20 | AAA | 0.001 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1025 | FLUORIDE | 0.39 | MG/L | 2.0499 | 2022-09-20 | AAA | 0.2 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-09-20 | AAA | 0.011 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-09-20 | AAA | 0.01 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-09-20 | AAA | 0.0005 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1055 | SULFATE | 3.4 | MG/L | 250.4999 | 2022-09-20 | AAA | 2 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1095 | ZINC | 0.0026 | MG/L | 5.4999 | 2022-09-20 | AAA | 0.002 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2022-09-20 | AAA | 5 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-09-20 | AAA | 1 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2022-09-20 | AAA | 0.01 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 190 | MG/L | 500.4999 | 2022-09-20 | AAA | 5 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-09-20 | AAA | 0.2 |  | SECONDARIES NOT RQRD BUT TESTED
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 0.5 | 0.5499 | VOC (J QUALIFIER ON 2964 DICHLOROMETHANE-NOT ENT'D)
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.0149 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.01 | 0.0249 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-09-20 | AAA | 0.05 | 0.1499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.5 | 1.4999 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 0.5 | 1.4999 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-09-20 | AAA | 9 | 9.4999 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-09-20 | AAA | 3.4 | 6.4999 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-09-20 | AAA | 0.02 | 0.6499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-09-20 | AAA | 2 | 2.4999 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-09-20 | AAA | 0.03 | 0.0749 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-09-20 | AAA | 0.1 | 0.6499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-09-20 | AAA | 0.07 | 0.1499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-09-20 | AAA | 0.08 | 0.2499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-09-20 | AAA | 0.1 | 0.1499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-09-20 | AAA | 0.9 | 0.9499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-09-20 | AAA | 0.01 | 0.1499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.2499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-09-20 | AAA | 0.01 | 0.0449 | SOC MISSING DIQUAT
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.16 | UG/L | 60.4999 | 2024-05-01 | L1 | 2 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 32.81 | UG/L | 80.4999 | 2024-05-01 | L1 | 0.13 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.27 | UG/L | 60.4999 | 2024-05-01 | L2 | 2 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 33.8 | UG/L | 80.4999 | 2024-05-01 | L2 | 0.13 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.72 | UG/L | 60.4999 | 2024-05-01 | L3 | 2 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 54.01 | UG/L | 80.4999 | 2024-05-01 | L3 | 0.13 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.41 | UG/L | 60.4999 | 2024-05-01 | L4 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 52.27 | UG/L | 80.4999 | 2024-05-01 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.81 | UG/L | 60.4999 | 2024-05-01 | L5 | 2 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 62.93 | UG/L | 80.4999 | 2024-05-01 | L5 | 0.13 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.8 | UG/L | 60.4999 | 2024-05-01 | L6 | 2 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 26.07 | UG/L | 80.4999 | 2024-05-01 | L6 | 0.13 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.44 | UG/L | 10.4999 | 2024-05-06 | L7 | 0.59 |  | POE SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.88 | UG/L | 10.4999 | 2024-05-06 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.79 | UG/L | 10.4999 | 2024-05-06 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.06 | UG/L | 10.4999 | 2024-05-06 | L7 | 0.59 |  | POE HIGHLAND POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.44 | UG/L | 10.4999 | 2024-05-06 | L7 | 0.59 |  | POE NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.88 | UG/L | 10.4999 | 2024-05-06 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.7 | UG/L | 10.4999 | 2024-05-06 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2024-05-08 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-05-08 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-05-08 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2024-05-08 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-05-08 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-05-08 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2024-05-08 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-05-08 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2024-05-08 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2024-05-08 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-05-08 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-05-08 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.9 | MG/L | 0 | 2024-05-08 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2024-05-08 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-05-08 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31 | MG/L | 0 | 2024-05-08 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-05-08 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2024-05-08 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2024-05-08 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2024-05-08 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-05-08 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2024-05-22 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2024-05-22 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2024-05-22 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2024-05-22 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2024-05-22 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2024-05-22 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2024-05-22 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2024-05-22 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2024-05-22 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.7 | MG/L | 0 | 2024-05-22 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2024-05-22 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2024-05-22 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.5 | MG/L | 0 | 2024-05-22 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2024-05-22 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2024-05-22 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.8 | MG/L | 0 | 2024-05-22 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2024-05-22 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-05-22 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.5 | MG/L | 0 | 2024-05-22 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-05-22 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2024-05-22 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.26 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | SOUTHWEST POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.54 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.18 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.64 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | NAVY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.79 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.14 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | SKY LAKE POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.44 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.85 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.18 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.64 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | POE NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.79 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.14 | UG/L | 10.4999 | 2024-06-03 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.5 | MG/L | 0 | 2024-06-05 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2024-06-05 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2024-06-05 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2024-06-05 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2024-06-05 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2024-06-05 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2024-06-05 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2024-06-05 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-06-05 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.7 | MG/L | 0 | 2024-06-05 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2024-06-05 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-06-05 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2024-06-05 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2024-06-05 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-06-05 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.5 | MG/L | 0 | 2024-06-05 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2024-06-05 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-06-05 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2024-06-05 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-06-05 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-06-05 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40 | MG/L | 0 | 2024-06-10 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-06-10 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-06-10 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.8 | MG/L | 0 | 2024-06-10 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2024-06-10 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-06-10 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.9 | MG/L | 0 | 2024-06-19 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2024-06-19 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2024-06-19 | WTP11 |  |  | SOUTHWEST WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.7 | MG/L | 0 | 2024-06-19 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-06-19 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-06-19 | WTP6 |  |  | CONWAY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2024-06-19 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2024-06-19 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-06-19 | WTP7 |  |  | KIRKMAN WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.9 | MG/L | 0 | 2024-06-19 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2024-06-19 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2024-06-19 | WTP8 |  |  | NAVY WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.8 | MG/L | 0 | 2024-06-19 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2024-06-19 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2024-06-19 | WTP10 |  |  | SKY LAKE WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.7 | MG/L | 0 | 2024-06-19 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2024-06-19 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-06-19 | WTP5 |  |  | PINE HILLS WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.2 | MG/L | 0 | 2024-06-19 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2024-06-19 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-06-19 | WTP1 |  |  | HIGHLAND WTP
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.34 | UG/L | 10.4999 | 2024-07-01 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.31 | UG/L | 10.4999 | 2024-07-01 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.76 | UG/L | 10.4999 | 2024-07-01 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.26 | UG/L | 10.4999 | 2024-07-01 | L7 | 0.59 |  | POE-HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.83 | UG/L | 10.4999 | 2024-07-01 | L7 | 0.59 |  | POE NAVY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.02 | UG/L | 10.4999 | 2024-07-01 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.17 | UG/L | 10.4999 | 2024-07-01 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.3 | MG/L | 0 | 2024-07-03 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-07-03 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2024-07-03 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.5 | MG/L | 0 | 2024-07-03 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-07-03 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-07-03 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2024-07-03 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-07-03 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-07-03 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2024-07-03 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2024-07-03 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-07-03 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.4 | MG/L | 0 | 2024-07-03 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-07-03 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2024-07-03 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 40.2 | MG/L | 0 | 2024-07-03 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2024-07-03 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2024-07-03 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2024-07-17 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2024-07-17 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-07-17 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.4 | MG/L | 0 | 2024-07-17 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-07-17 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2024-07-17 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37 | MG/L | 0 | 2024-07-17 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2024-07-17 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-07-17 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36 | MG/L | 0 | 2024-07-17 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2024-07-17 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2024-07-17 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.2 | MG/L | 0 | 2024-07-17 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2024-07-17 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 93 | MG/L |  | 2024-07-17 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2024-07-17 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2024-07-17 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2024-07-17 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-07-31 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.6 | MG/L | 0 | 2024-07-31 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2024-07-31 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33 | MG/L | 0 | 2024-07-31 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2024-07-31 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-07-31 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.5 | MG/L | 0 | 2024-07-31 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2024-07-31 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2024-07-31 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.1 | MG/L | 0 | 2024-07-31 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2024-07-31 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-07-31 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.1 | MG/L | 0 | 2024-07-31 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2024-07-31 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2024-07-31 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.6 | MG/L | 0 | 2024-07-31 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-07-31 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-07-31 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.98 | UG/L | 60.4999 | 2024-08-01 | L8 | 2 |  | NEW SAMPLING LOCATION_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 34.31 | UG/L | 80.4999 | 2024-08-01 | L8 | 0.13 |  | NEW SAMPLING LOCATION_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.58 | UG/L | 60.4999 | 2024-08-01 | L9 | 2 |  | NEW SAMPLING LOCATION_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 67.54 | UG/L | 80.4999 | 2024-08-01 | L9 | 0.13 |  | NEW SAMPLING LOCATION_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.66 | UG/L | 60.4999 | 2024-08-01 | L1 | 2 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 21.66 | UG/L | 80.4999 | 2024-08-01 | L1 | 0.13 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.54 | UG/L | 60.4999 | 2024-08-01 | L2 | 2 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 31.66 | UG/L | 80.4999 | 2024-08-01 | L2 | 0.13 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.63 | UG/L | 60.4999 | 2024-08-01 | L3 | 2 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 52.46 | UG/L | 80.4999 | 2024-08-01 | L3 | 0.13 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.57 | UG/L | 60.4999 | 2024-08-01 | L4 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 61.26 | UG/L | 80.4999 | 2024-08-01 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.18 | UG/L | 60.4999 | 2024-08-01 | L5 | 2 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 73.85 | UG/L | 80.4999 | 2024-08-01 | L5 | 0.13 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.2 | UG/L | 60.4999 | 2024-08-01 | L6 | 2 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 28.35 | UG/L | 80.4999 | 2024-08-01 | L6 | 0.13 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.58 | UG/L | 60.4999 | 2024-08-01 | L4 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 67.54 | UG/L | 80.4999 | 2024-08-01 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.01 | 0.0249 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-09-20 | AAA | 0.1 | 0.1499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-09-20 | AAA | 0.05 | 0.2499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.1 | 0.1499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.012 | 0.0249 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-09-20 | AAA | 0.02 | 0.0449 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-09-20 | AAA | 0.1 | 0.1499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-09-20 | AAA | 0.02 | 0.0249 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-09-20 | AAA | 0.01 | 0.0149 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-09-20 | AAA | 0.01 | 0.2499 | SOC MISSING DIQUAT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | DBP | 2950 | TOTAL THMS | 16 | UG/L | 80.4999 | 2022-11-10 | L1 | 0.5 |  | MAKE UP DBPS SAMPLES FROM 2022_CC | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.9 | UG/L | 60.4999 | 2022-11-10 | L1 | 1.6 |  | MAKE UP FOR MISSED DBPS_CC | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-12-05 | AAA | 0.5 | 0.5499 | RESAMPLE OF DICHLOROMETHANE_CC
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-02-08 | AAA | 0.4 | 0.4499 | MAKE UP SAMPLE FOR MISSED MONITORING IN 2022_CC
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0.3 | MG/L | 10.4999 | 2023-04-11 | AAA | 0.2 |  | 2023 POE N/N
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-11 | AAA | 0.2 |  | 2023 POE N/N
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-04-26 | AAA |  | 0.5499 | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.1 | UG/L | 60.4999 | 2023-07-05 | L1 | 0.28 |  | ANNUAL 2023 | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | N | DBP | 2950 | TOTAL THMS | 23.5 | UG/L | 80.4999 | 2023-07-05 | L1 | 0.5 |  | ANNUAL 2023 | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-06-06 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-06-06 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.3 | UG/L | 60.4999 | 2024-07-03 | L1 | 0.28 |  | ANNUAL 2024 | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | D | DBP | 2950 | TOTAL THMS | 10.8 | UG/L | 80.4999 | 2024-07-03 | L1 | 0.5 |  | ANNUAL 2024 | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.25 | UG/L | 60.4999 | 2025-03-20 | L1 |  |  | TAKEN AT POE OUTSIDE OF MONITORING PERIOD | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | S | DBP | 2950 | TOTAL THMS | 15.5 | UG/L | 80.4999 | 2025-03-20 | L1 |  |  | TAKEN AT POE OUTSIDE OF MONITORING PERIOD | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-04-17 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-17 | AAA |  |  | POE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-06-18 | AAA | 0.29 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-06-18 | AAA | 0.19 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-06-18 | AAA | 0.5 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-06-18 | AAA | 0.5 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-06-18 | AAA | 0.32 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-06-18 | AAA | 0.27 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.4 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-06-18 | AAA | 0.39 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 0.33 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.23 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-06-18 | AAA | 0.16 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.28 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-06-18 | AAA | 0.43 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.34 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-06-18 | AAA | 0.39 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.37 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 0.3 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.17 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-06-18 | AAA | 0.23 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-06-18 | AAA | 0.24 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 0.24 | 0.5499
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-06-18 | AAA | 0.1 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-06-18 | AAA | 0.1 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-06-18 | AAA | 0.00035 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1010 | BARIUM | 0.0064 | MG/L | 2.4999 | 2025-06-18 | AAA | 0.00033 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-06-18 | AAA | 0.00022 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1020 | CHROMIUM | 0.0027 | MG/L | 0.1499 | 2025-06-18 | AAA | 0.00035 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-06-18 | AAA | 0.005 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2025-06-18 | AAA | 0.1 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-06-18 | AAA | 0.00022 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-06-18 | AAA | 0.0002 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-06-18 | AAA | 0.00082 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-06-18 | AAA | 0.0009 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2025-06-18 | AAA | 0.12 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-06-18 | AAA | 0.00037 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-06-18 | AAA | 0.00029 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-06-18 | AAA | 0.00031 |  | ALL BUT ASBESTOS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2025-06-18 | AAA |  |  | 2025 RADS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2025-06-18 | AAA |  | 1.4999 | 2025 RADS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-06-18 | AAA |  | 1.4999 | 2025 RADS
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1002 | ALUMINUM | 0.0036 | MG/L | 0.2499 | 2025-06-18 | AAA | 0.0031 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1017 | CHLORIDE | 20 | MG/L | 250.4999 | 2025-06-18 | AAA | 0.2 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1022 | COPPER | 0.0006 | MG/L | 1.4999 | 2025-06-18 | AAA | 0.00058 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1025 | FLUORIDE | 0.18 | MG/L | 2.0499 | 2025-06-18 | AAA | 0.1 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2025-06-18 | AAA | 0.054 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2025-06-18 | AAA | 0.0076 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2025-06-18 | AAA | 3e-05 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1055 | SULFATE | 77 | MG/L | 250.4999 | 2025-06-18 | AAA | 0.5 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1095 | ZINC | 0.0013 | MG/L | 5.4999 | 2025-06-18 | AAA | 0.0012 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2025-06-18 | AAA | 5 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1920 | ODOR THRESHOLD | 5 |  | 3.4999 | 2025-06-18 | AAA | 5 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 | LN(10) |  | 2025-06-18 | AAA | 0.1 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 250 | MG/L | 500.4999 | 2025-06-18 | AAA | 5 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SEC | 2905 | FOAMING AGENTS | 0.053 |  | 0.5499 | 2025-06-18 | AAA | 0.026 |  | PH V QUALIFIED; ODOR EXCEEDANCE
3484399 | CHRIST CHAPEL FLORIDA INC. | N | DBP | 2950 | TOTAL THMS | 28 | UG/L | 80.4999 | 2025-06-18 | L1 | 0.21 |  | TAKEN AT POE OUTSIDE OF MON PERIOD | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-06-18 | AAA | 0.01 | 0.0149 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.01 | 0.0249 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-06-18 | AAA | 0.055 | 0.1499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.5 | 1.4999 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2031 | DALAPON | 0.35 | UG/L | 249.9999 | 2025-06-18 | AAA | 0.5 | 1.4999 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-06-18 | AAA | 0.4 | 0.4499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-06-18 | AAA | 9 | 9.4999 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-06-18 | AAA | 6 | 6.4999 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-06-18 | AAA | 0.6 | 0.6499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-06-18 | AAA | 0.4 | 2.4999 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-06-18 | AAA | 0.07 | 0.0749 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-06-18 | AAA | 0.6 | 0.6499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-06-18 | AAA | 0.019 | 0.1499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-06-18 | AAA | 0.028 | 0.2499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-06-18 | AAA | 0.1 | 0.1499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-06-18 | AAA | 0.4 | 0.9499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-06-18 | AAA | 0.1 | 0.1499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-06-18 | AAA | 0.2 | 0.2499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-06-18 | AAA | 0.1 | 0.0449 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.01 | 0.0249 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-06-18 | AAA | 0.022 | 0.1499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-06-18 | AAA | 0.035 | 0.2499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.1 | 0.1499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.02 | 0.0249 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-06-18 | AAA | 0.017 | 0.0449 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-06-18 | AAA | 0.1 | 0.1499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-06-18 | AAA | 0.02 | 0.0249 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-06-18 | AAA | 0.01 | 0.0149 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-06-18 | AAA | 0.01 | 0.2499 | DALAPON DETECT
3484399 | CHRIST CHAPEL FLORIDA INC. | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.96 | UG/L | 60.4999 | 2025-07-08 | L1 | 0.2 |  | SOUTH BLDG HSBB (FKA EAST SAMPLE TAP) | 3
3484399 | CHRIST CHAPEL FLORIDA INC. | D | DBP | 2950 | TOTAL THMS | 31.8 | UG/L | 80.4999 | 2025-07-08 | L1 | 0.21 |  | SOUTH BLDG HSBB (FKA EAST SAMPLE TAP) | 3
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.89 | UG/L | 10.4999 | 2024-08-05 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.54 | UG/L | 10.4999 | 2024-08-05 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.08 | UG/L | 10.4999 | 2024-08-05 | L7 | 0.59 |  | POE-KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.06 | UG/L | 10.4999 | 2024-08-05 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.56 | UG/L | 10.4999 | 2024-08-05 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.82 | UG/L | 10.4999 | 2024-08-05 | L7 | 0.59 |  | POE NAVY POINT
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.19 | UG/L | 10.4999 | 2024-08-05 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.8 | MG/L | 0 | 2024-08-14 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2024-08-14 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-08-14 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2024-08-14 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-08-14 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-08-14 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.8 | MG/L | 0 | 2024-08-14 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2024-08-14 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2024-08-14 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2024-08-14 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2024-08-14 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2024-08-14 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2024-08-14 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2024-08-14 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-08-14 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.8 | MG/L | 0 | 2024-08-14 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2024-08-14 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-08-14 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.9 | MG/L | 0 | 2024-08-28 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-08-28 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2024-08-28 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.2 | MG/L | 0 | 2024-08-28 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2024-08-28 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2024-08-28 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-08-28 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 29.9 | MG/L | 0 | 2024-08-28 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2024-08-28 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2024-08-28 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2024-08-28 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-08-28 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-08-28 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 33.1 | MG/L | 0 | 2024-08-28 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2024-08-28 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2024-08-28 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.9 | MG/L | 0 | 2024-08-28 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-08-28 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.75 | UG/L | 10.4999 | 2024-09-03 | L7 | 0.59 |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.36 | UG/L | 10.4999 | 2024-09-03 | L7 | 0.59 |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-09-03 | L7 | 0.59 |  | PINE HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.93 | UG/L | 10.4999 | 2024-09-03 | L7 | 0.59 |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.96 | UG/L | 10.4999 | 2024-09-03 | L7 | 0.59 |  | NAVY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.82 | UG/L | 10.4999 | 2024-09-03 | L7 | 0.59 |  | CONWAY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.5 | UG/L | 10.4999 | 2024-09-03 | L7 | 0.59 |  | SKY LAKE POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.1 | MG/L | 0 | 2024-09-11 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2024-09-11 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-09-11 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2024-09-11 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2024-09-11 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2024-09-11 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2024-09-11 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-09-11 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-09-11 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 32.2 | MG/L | 0 | 2024-09-11 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-09-11 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-09-11 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 39.2 | MG/L | 0 | 2024-09-11 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2024-09-11 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2024-09-11 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2024-09-11 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2024-09-11 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2024-09-11 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.68 | UG/L | 10.4999 | 2024-10-07 | L7 | 0.59 |  | SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.3 | UG/L | 10.4999 | 2024-10-07 | L7 | 0.59 |  | KIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.98 | UG/L | 10.4999 | 2024-10-07 | L7 | 0.59 |  | PINE HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.96 | UG/L | 10.4999 | 2024-10-07 | L7 | 0.59 |  | HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.24 | UG/L | 10.4999 | 2024-10-07 | L7 | 0.59 |  | CONWAY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.55 | UG/L | 10.4999 | 2024-10-07 | L7 | 0.59 |  | SKY LAKE POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.5 | MG/L | 0 | 2024-10-07 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-10-07 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-10-07 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2024-10-07 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2024-10-07 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-10-07 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2024-10-07 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2024-10-07 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-10-07 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.3 | MG/L | 0 | 2024-10-07 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-10-07 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-10-07 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2024-10-07 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2024-10-07 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2024-10-07 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2024-10-07 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2024-10-07 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2024-10-07 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.1 | MG/L | 0 | 2024-10-23 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2024-10-23 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-10-23 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2024-10-23 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2024-10-23 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2024-10-23 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.1 | MG/L | 0 | 2024-10-23 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-10-23 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-10-23 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.8 | MG/L | 0 | 2024-10-23 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-10-23 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2024-10-23 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.6 | MG/L | 0 | 2024-10-23 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-10-23 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2024-10-23 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2024-10-23 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2024-10-23 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-10-23 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 18.87 | UG/L | 80.4999 | 2024-11-01 | L1 | 0.13 |  | 1642 SILVER STAR RD., HAA5 J QUALIFIER
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.07 | UG/L | 60.4999 | 2024-11-01 | L2 | 2 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 35.83 | UG/L | 80.4999 | 2024-11-01 | L2 | 0.13 |  | 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 41.82 | UG/L | 80.4999 | 2024-11-01 | L3 | 0.13 |  | 169 758 DENNIS AVE., HAA5 J QUALIFIER - HAA5 APRROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.74 | UG/L | 60.4999 | 2024-11-01 | L4 | 2 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 57.59 | UG/L | 80.4999 | 2024-11-01 | L4 | 0.13 |  | 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.22 | UG/L | 60.4999 | 2024-11-01 | L5 | 2 |  | 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 64.14 | UG/L | 80.4999 | 2024-11-01 | L5 | 0.13 |  | 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 30.81 | UG/L | 80.4999 | 2024-11-01 | L6 | 0.13 |  | 5512 BAYSIDE DR., HAA5 J QUALIFIER - HAA5 APPROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 29.57 | UG/L | 80.4999 | 2024-11-01 | L8 | 0.13 |  | 7933 ARABIAN PLACE, HAA5 J QUALIFIER - HAA5 APPROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 67.51 | UG/L | 80.4999 | 2024-11-01 | L9 | 0.13 |  | 14177 LAKE NONA BLVD, HAA5 J QUALIFIER - HAA5 APPROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.22 | UG/L | 60.4999 | 2024-11-01 | L3 | 2 |  | 169 758 DENNIS AVE., HAA5 J QUALIFIER - HAA5 APRROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.86 | UG/L | 60.4999 | 2024-11-01 | L6 | 2 |  | 5512 BAYSIDE DR., HAA5 J QUALIFIER - HAA5 APPROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.56 | UG/L | 60.4999 | 2024-11-01 | L8 | 2 |  | 7933 ARABIAN PLACE, HAA5 J QUALIFIER - HAA5 APPROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.07 | UG/L | 60.4999 | 2024-11-01 | L9 | 2 |  | 14177 LAKE NONA BLVD, HAA5 J QUALIFIER - HAA5 APPROVED_LMC
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.04 | UG/L | 60.4999 | 2024-11-01 | L1 | 2 |  | 1642 SILVER STAR RD., HAA5 J QUALIFIER
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.07 | UG/L | 10.4999 | 2024-11-04 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.94 | UG/L | 10.4999 | 2024-11-04 | L7 | 0.59 |  | KIRKMAN POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.67 | UG/L | 10.4999 | 2024-11-04 | L7 | 0.59 |  | PINE HILLS POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.05 | UG/L | 10.4999 | 2024-11-04 | L7 | 0.59 |  | HIGHLAND POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.44 | UG/L | 10.4999 | 2024-11-04 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.58 | UG/L | 10.4999 | 2024-11-04 | L7 | 0.59 |  | SKY LAKE POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.3 | MG/L | 0 | 2024-11-20 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-11-20 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-11-20 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.6 | MG/L | 0 | 2024-11-20 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2024-11-20 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2024-11-20 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.2 | MG/L | 0 | 2024-11-20 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2024-11-20 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-11-20 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 30.6 | MG/L | 0 | 2024-11-20 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-11-20 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-11-20 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.1 | MG/L | 0 | 2024-11-20 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-11-20 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-11-20 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2024-11-20 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-11-20 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-11-20 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.57 | UG/L | 10.4999 | 2024-12-02 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.8 | UG/L | 10.4999 | 2024-12-02 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.96 | UG/L | 10.4999 | 2024-12-02 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.83 | UG/L | 10.4999 | 2024-12-02 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.69 | UG/L | 10.4999 | 2024-12-02 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.53 | UG/L | 10.4999 | 2024-12-02 | L7 | 0.59 |  | POE SKYLAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.9 | MG/L | 0 | 2024-12-04 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2024-12-04 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2024-12-04 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2024-12-04 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-12-04 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2024-12-04 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2024-12-04 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2024-12-04 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 131 | MG/L |  | 2024-12-04 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.6 | MG/L | 0 | 2024-12-04 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-12-04 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2024-12-04 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.1 | MG/L | 0 | 2024-12-04 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2024-12-04 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-12-04 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.6 | MG/L | 0 | 2024-12-04 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2024-12-04 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2024-12-04 | WTP11 |  |  | POE 7 - SOUTHWEST
3484401 | MJM FOOD STORE-BITHLO | S | INOR | 1040 | NITRATE | 0.025 | MG/L | 10.4999 | 2021-02-17 | AAA | 0.025 |  | UNACCEPTABLE-RETEST NN. ANNUAL SMPLS TKN IN CONSEC. YRS. MUST BE AT LEAST 90 DAYS APART (62-550.500, F.A.C.) 2020 NN: 12/29/20. 2021 NN: 2/17/21. RESULTS ARE ENT'D W/SMP TYPE "S" FOR INFO. PURPOSES.
3484401 | MJM FOOD STORE-BITHLO | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-17 | AAA | 0.025 |  | UNACCEPTABLE-RETEST NN. ANNUAL SMPLS TKN IN CONSEC. YRS. MUST BE AT LEAST 90 DAYS APART (62-550.500, F.A.C.) 2020 NN: 12/29/20. 2021 NN: 2/17/21. RESULTS ARE ENT'D W/SMP TYPE "S" FOR INFO. PURPOSES.
3484401 | MJM FOOD STORE-BITHLO | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-21 | AAA |  |  | 2021 MAKE UP SAMPLES. SMD NOT FOR 2022 COMPLIANCE.
3484401 | MJM FOOD STORE-BITHLO | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-21 | AAA |  |  | 2021 MAKE UP SAMPLES. SMD NOT FOR 2022 COMPLIANCE.
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-11-18 | AAA |  |  | POE
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-11-18 | AAA |  |  | POE
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2023-06-09 | AAA |  |  | POE NN_2023_JGP
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1041 | NITRITE | 0.025 | MG/L | 1.4999 | 2023-06-09 | AAA |  |  | POE NN_2023_JGP
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2024-02-13 | AAA
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-02-13 | AAA
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2025-05-28 | AAA | 0.025 |  | POE
3484401 | MJM FOOD STORE-BITHLO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-05-28 | AAA |  |  | POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44 | MG/L | 0 | 2024-12-18 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2024-12-18 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2024-12-18 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.6 | MG/L | 0 | 2024-12-18 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-12-18 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-12-18 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.7 | MG/L | 0 | 2024-12-18 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2024-12-18 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2024-12-18 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 32 | MG/L | 0 | 2024-12-18 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2024-12-18 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-12-18 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.5 | MG/L | 0 | 2024-12-18 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2024-12-18 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-12-18 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2024-12-18 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2024-12-18 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2024-12-18 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.2 | MG/L | 0 | 2024-12-31 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2024-12-31 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2024-12-31 | WTP10 |  |  | POE 6 - SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2024-12-31 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2024-12-31 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-12-31 | WTP7 |  |  | POE 3 - KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2024-12-31 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-12-31 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2024-12-31 | WTP6 |  |  | POE 1 - CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 31.4 | MG/L | 0 | 2024-12-31 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2024-12-31 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2024-12-31 | WTP5 |  |  | POE 5 - PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38.2 | MG/L | 0 | 2024-12-31 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.53 | LN(10) |  | 2024-12-31 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2024-12-31 | WTP1 |  |  | POE 2 - HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.4 | MG/L | 0 | 2024-12-31 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2024-12-31 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2024-12-31 | WTP11 |  |  | POE 7 - SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.04 | UG/L | 10.4999 | 2025-01-06 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.26 | UG/L | 10.4999 | 2025-01-06 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.24 | UG/L | 10.4999 | 2025-01-06 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.81 | UG/L | 10.4999 | 2025-01-06 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.48 | UG/L | 10.4999 | 2025-01-06 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2025-01-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2025-01-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-01-15 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.6 | MG/L | 0 | 2025-01-15 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2025-01-15 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2025-01-15 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35 | MG/L | 0 | 2025-01-15 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2025-01-15 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2025-01-15 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2025-01-15 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2025-01-15 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2025-01-15 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2025-01-15 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2025-01-15 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2025-01-15 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.5 | MG/L | 0 | 2025-01-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2025-01-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-01-29 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.8 | MG/L | 0 | 2025-01-29 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2025-01-29 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2025-01-29 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.2 | MG/L | 0 | 2025-01-29 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2025-01-29 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2025-01-29 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2025-01-29 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2025-01-29 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2025-01-29 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.66 | UG/L | 10.4999 | 2025-02-02 | L7 | 0.57 |  | SOUTHWEST POE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.48 | UG/L | 60.4999 | 2025-02-03 | L1 | 2 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 43.53 | UG/L | 80.4999 | 2025-02-03 | L1 | 0.13 |  | SMP PT 10 1642 SILVER STAR RD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.46 | UG/L | 60.4999 | 2025-02-03 | L2 | 2 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 41.94 | UG/L | 80.4999 | 2025-02-03 | L2 | 0.13 |  | SMP PT 23 2714 ILLINOIS ST.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.97 | UG/L | 60.4999 | 2025-02-03 | L3 | 2 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 43.03 | UG/L | 80.4999 | 2025-02-03 | L3 | 0.13 |  | SMP PT 169 758 DENNIS AVE.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.83 | UG/L | 60.4999 | 2025-02-03 | L4 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 53.17 | UG/L | 80.4999 | 2025-02-03 | L4 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.48 | UG/L | 60.4999 | 2025-02-03 | L5 | 2 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 58.41 | UG/L | 80.4999 | 2025-02-03 | L5 | 0.13 |  | SMP PT 124 LANDSTAR RD. & IOWA WOODS CIR
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.76 | UG/L | 60.4999 | 2025-02-03 | L6 | 2 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 39.1 | UG/L | 80.4999 | 2025-02-03 | L6 | 0.13 |  | SMP PT 121 5512 BAYSIDE DR.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.83 | UG/L | 60.4999 | 2025-02-03 | L8 | 2 |  | SMP PT 100 7933 ARABIAN PLACE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 25.68 | UG/L | 80.4999 | 2025-02-03 | L8 | 0.13 |  | SMP PT 100 7933 ARABIAN PLACE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.43 | UG/L | 60.4999 | 2025-02-03 | L9 | 2 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 61.47 | UG/L | 80.4999 | 2025-02-03 | L9 | 0.13 |  | SMP PT SE5 10093 LAKE NONA BLVD.
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.26 | UG/L | 10.4999 | 2025-02-03 | L7 | 0.59 |  | POE-SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.06 | UG/L | 10.4999 | 2025-02-03 | L7 | 0.59 |  | POE- KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-02-03 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.24 | UG/L | 10.4999 | 2025-02-03 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.71 | UG/L | 10.4999 | 2025-02-03 | L7 | 0.59 |  | POE-CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.13 | UG/L | 10.4999 | 2025-02-03 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.5 | MG/L | 0 | 2025-02-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2025-02-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2025-02-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44 | MG/L | 0 | 2025-02-12 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2025-02-12 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2025-02-12 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2025-02-12 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2025-02-12 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2025-02-12 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2025-02-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2025-02-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2025-02-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-18 | WTP5 | 0 |  | PINE HILLS WP PINE HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-18 | WTP5 | 0 |  | PINE HILLS WP PINE HILLS POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-18 | WTP7 | 0 |  | KIRKMAN WPKIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-18 | WTP7 | 0 |  | KIRKMAN WPKIRKMAN POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2025-02-18 | WTP11 | 0.03 |  | SW WP SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-18 | WTP11 | 0 |  | SW WP SOUTHWEST POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-18 | WTP10 | 0 |  | SKY LAKE WP SKY LAKE POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-18 | WTP10 | 0 |  | SKY LAKE WP SKY LAKE POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2025-02-18 | WTP6 | 0.03 |  | CONWAY WP CONWAY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-18 | WTP6 | 0 |  | CONWAY WP CONWAY POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1040 | NITRATE | 0.07 | MG/L | 10.4999 | 2025-02-18 | WTP1 | 0.03 |  | HIGHLAND WP HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-18 | WTP1 | 0 |  | HIGHLAND WP HIGHLAND POINT OF ENTRY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2025-02-26 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2025-02-26 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-02-26 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.7 | MG/L | 0 | 2025-02-26 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2025-02-26 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2025-02-26 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.7 | MG/L | 0 | 2025-02-26 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2025-02-26 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2025-02-26 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.4 | MG/L | 0 | 2025-02-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2025-02-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2025-02-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.85 | UG/L | 10.4999 | 2025-03-03 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.05 | UG/L | 10.4999 | 2025-03-03 | L7 | 0.59 |  | KIRKMAN POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.34 | UG/L | 10.4999 | 2025-03-03 | L7 | 0.59 |  | PINE HILLS POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.16 | UG/L | 10.4999 | 2025-03-03 | L7 | 0.59 |  | HIGHLAND POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.25 | UG/L | 10.4999 | 2025-03-03 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.56 | UG/L | 10.4999 | 2025-03-03 | L7 | 0.59 |  | SKY LAKE POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37 | MG/L | 0 | 2025-03-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2025-03-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-03-12 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45 | MG/L | 0 | 2025-03-12 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2025-03-12 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2025-03-12 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.9 | MG/L | 0 | 2025-03-12 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2025-03-12 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2025-03-12 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.9 | MG/L | 0 | 2025-03-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2025-03-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 127 | MG/L |  | 2025-03-12 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.4 | MG/L | 0 | 2025-03-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2025-03-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-03-26 | WTP7 |  |  | KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.3 | MG/L | 0 | 2025-03-26 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2025-03-26 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2025-03-26 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2025-03-26 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2025-03-26 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2025-03-26 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.8 | MG/L | 0 | 2025-03-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2025-03-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2025-03-26 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.12 | UG/L | 10.4999 | 2025-04-07 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.05 | UG/L | 10.4999 | 2025-04-07 | L7 | 0.59 |  | KIRKMAN POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.14 | UG/L | 10.4999 | 2025-04-07 | L7 | 0.59 |  | PINE HILLS POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.45 | UG/L | 10.4999 | 2025-04-07 | L7 | 0.59 |  | HIGHLAND POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.66 | UG/L | 10.4999 | 2025-04-07 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.28 | UG/L | 10.4999 | 2025-04-07 | L7 | 0.59 |  | SKY LAKE POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.2 | MG/L | 0 | 2025-04-09 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2025-04-09 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-04-09 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.9 | MG/L | 0 | 2025-04-09 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2025-04-09 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2025-04-09 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2025-04-09 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2025-04-09 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2025-04-09 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.9 | MG/L | 0 | 2025-04-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2025-04-09 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2025-04-09 | WTP6 |  |  | CONWAY
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-09 | AAA |  |  | POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-09 | AAA |  |  | POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS- POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA |  |  | LOCATION CODE SET BY PWS- POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1040 | NITRATE | 0.31 | MG/L | 10.4999 | 2023-04-11 | AAA | 0.2 |  | POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-11 | AAA |  |  | POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-06-06 | AAA |  |  | POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-06-06 | AAA |  |  | POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2025-04-17 | AAA | 0.1 |  | POE
3484414 | WEST ORANGE GIRLS CLUB | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-17 | AAA |  |  | POE
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.78 | UG/L | 60.4999 | 2021-08-16 | L1 |  |  |  | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 55.47 | UG/L | 80.4999 | 2021-08-16 | L1 |  |  |  | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.59 | UG/L | 60.4999 | 2022-08-15 | L1 | 1.43 |  |  | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 49.76 | UG/L | 80.4999 | 2022-08-15 | L1 | 0.84 |  |  | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.77 | UG/L | 60.4999 | 2023-08-15 | L1 | 1.43 |  | 10126 ENCHANTED OAK | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 58.07 | UG/L | 80.4999 | 2023-08-15 | L1 | 0.84 |  | 10126 ENCHANTED OAK | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.48 | UG/L | 60.4999 | 2023-08-15 | L2 | 1.43 |  | 10501 DREAM TREE BLVD LOCATION ADDED 10/18/2023_KS | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 41.39 | UG/L | 80.4999 | 2023-08-15 | L2 | 0.84 |  | 10501 DREAM TREE BLVD LOCATION ADDED 10/18/2023_KS | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.25 | UG/L | 60.4999 | 2024-08-15 | L1 | 1.43 |  | 10126 ENCHANTED OAK | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 58.46 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.89 |  | 10126 ENCHANTED OAK | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.5 | UG/L | 60.4999 | 2024-08-15 | L2 | 1.43 |  | 10501 DREAM TREE BLVD | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 37.32 | UG/L | 80.4999 | 2024-08-15 | L2 | 0.89 |  | 10501 DREAM TREE BLVD | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.15 | UG/L | 60.4999 | 2025-08-18 | L1 | 1.43 |  | 10126 ENCHANTED OAK | 3
3484422 | OCUD/NORTHEAST RESORT (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 47.7 | UG/L | 80.4999 | 2025-08-18 | L1 | 0.4 |  | 10126 ENCHANTED OAK | 3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-12-09 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-09 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-09 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-02 | AAA | 0.24 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-02 | AAA | 0.034 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-06-02 | AAA | 0.00025 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1010 | BARIUM | 0.0079 | MG/L | 2.4999 | 2022-06-02 | AAA | 0.003 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-06-02 | AAA | 0.001 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-06-02 | AAA | 0.005 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-06-02 | AAA | 0.004 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2022-06-02 | AAA | 0.099 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-06-02 | AAA | 0.0005 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-06-02 | AAA | 1e-05 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-06-02 | AAA | 0.008 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-06-02 | AAA | 0.0012 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2022-06-02 | AAA | 0.8 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-06-02 | AAA | 0.001 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-06-02 | AAA | 0.002 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-06-02 | AAA | 0.00025 |  | E53076/NN,FL, E82574/ARS,PB,SEL,ANT,TH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-06-02 | AAA | 0.0069 | 0.0149 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-06-02 | AAA | 0.0071 | 0.0249 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-06-02 | AAA | 0.0068 | 0.1499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-06-02 | AAA | 0.12 | 1.4999 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-06-02 | AAA | 0.9 | 1.4999 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-06-02 | AAA | 0.37 | 0.4499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-06-02 | AAA | 6 | 9.4999 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-06-02 | AAA | 5.9 | 6.4999 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-06-02 | AAA | 0.5 | 0.6499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-06-02 | AAA | 1.8 | 2.4999 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-06-02 | AAA | 0.06 | 0.0749 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-06-02 | AAA | 0.5 | 0.6499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-06-02 | AAA | 0.09 | 0.1499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-06-02 | AAA | 0.18 | 0.2499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-06-02 | AAA | 0.019 | 0.1499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-06-02 | AAA | 0.51 | 0.9499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-06-02 | AAA | 0.09 | 0.1499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-06-02 | AAA | 0.15 | 0.2499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-06-02 | AAA | 0.006 | 0.0449 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-06-02 | AAA | 0.0052 | 0.0249 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-06-02 | AAA | 0.095 | 0.1499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-06-02 | AAA | 0.09 | 0.2499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-06-02 | AAA | 0.0063 | 0.1499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-06-02 | AAA | 0.015 | 0.0249 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-06-02 | AAA | 0.038 | 0.0449 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-06-02 | AAA | 0.093 | 0.1499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-06-02 | AAA | 0.0056 | 0.0249 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-06-02 | AAA | 0.0047 | 0.0149 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-06-02 | AAA | 0.053 | 0.2499 | SOC
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2022-06-02 | AAA | 0.099
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-06-02 | AAA | 0.44 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0.73 | UG/L | 74.9999 | 2022-06-02 | AAA | 0.27 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-06-02 | AAA | 0.44 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-06-02 | AAA | 0.44 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-06-02 | AAA | 0.39 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-06-02 | AAA | 0.33 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0.79 | UG/L | 1.4999 | 2022-06-02 | AAA | 0.29 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0.45 | UG/L | 7.4999 | 2022-06-02 | AAA | 0.22 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-06-02 | AAA | 0.21 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-06-02 | AAA | 0.24 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-06-02 | AAA | 0.29 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-06-02 | AAA | 0.25 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-06-02 | AAA | 0.26 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-06-02 | AAA | 0.14 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-06-02 | AAA | 0.27 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-06-02 | AAA | 0.42 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-06-02 | AAA | 0.36 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-06-02 | AAA | 0.26 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-06-02 | AAA | 0.33 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-06-02 | AAA | 0.31 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-06-02 | AAA | 0.25 | 0.5499 | VOC (CIS-1,2 0.73, VC 0.79, 1,1-DIC 0.45)
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 1.6 | UG/L | 74.9999 | 2022-08-10 | AAA | 0.27 | 0.5499 | CIS-1,2 1.60, V.C. -0-, 1,1-DIC 1.10
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-10 | AAA | 0.29 | 0.5499 | CIS-1,2 1.60, V.C. -0-, 1,1-DIC 1.10
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 1.1 | UG/L | 7.4999 | 2022-08-10 | AAA | 0.22 | 0.5499 | CIS-1,2 1.60, V.C. -0-, 1,1-DIC 1.10
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 1.6 | UG/L | 74.9999 | 2022-08-10 | AAA | 0.27 | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-10 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 1.1 | UG/L | 7.4999 | 2022-08-10 | AAA | 0.22 | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.44 | UG/L | 60.4999 | 2022-08-11 | L1 | 0.98 |  | OFFICE KITCHEN SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | S | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2022-08-11 | L1 | 0.39 |  | OFFICE KITCHEN SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-31 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-11-03 | AAA | 0.001 |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1022 | COPPER | 0.027 | MG/L | 1.5499 | 2022-11-03 | AAA | 0.025 |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1016 | CALCIUM | 54 | MG/L |  | 2022-11-03 | AAA | 0.2 |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1044 | ORTHOPHOSPHATE | 0.17 | MG/L |  | 2022-11-03 | AAA | 0.012 |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-11-03 | AAA | 0.001 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1064 | CONDUCTIVITY | 490 | MG/L | 0 | 2022-11-03 | AAA | 2 |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-11-03 | AAA | 0.001 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1022 | COPPER | 0.18 | MG/L | 1.5499 | 2022-11-03 | AAA | 0.025 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1016 | CALCIUM | 53 | MG/L |  | 2022-11-03 | AAA | 0.2 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2022-11-03 | AAA | 0.012 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2022-11-03 | AAA | 5 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1064 | CONDUCTIVITY | 510 | MG/L | 0 | 2022-11-03 | AAA | 2 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1927 | TOTAL ALKALINITY | 240 | MG/L |  | 2022-11-03 | AAA | 5 |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1022 | COPPER | 0.21 | MG/L | 1.5499 | 2022-11-03 | AAA | 0.025 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1016 | CALCIUM | 54 | MG/L |  | 2022-11-03 | AAA | 0.2 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2022-11-03 | AAA | 0.012 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2022-11-03 | AAA |  |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1064 | CONDUCTIVITY | 500 | MG/L | 0 | 2022-11-03 | AAA | 2 |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 28.6 |  |  | 2022-11-03 | AAA |  |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1997 | PHS | 7.5 | MG/L |  | 2022-11-03 | AAA |  |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #2_BUILDING A WATER COOLER
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.6 |  |  | 2022-11-03 | AAA |  |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1997 | PHS | 7.5 | MG/L |  | 2022-11-03 | AAA |  |  | QWP SET #1_DISTRIBUTION SAMPLING SITE #1_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2022-11-03 | AAA |  |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1997 | PHS | 7.5 | MG/L |  | 2022-11-03 | AAA |  |  | QWP_POE_ SET #1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.3 |  |  | 2022-11-17 | AAA |  |  | WQP_POE_SET #2
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1064 | CONDUCTIVITY | 510 | MG/L | 0 | 2022-11-17 | AAA | 2 |  | WQP_POE_SET #2
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 |  |  | 2022-11-17 | AAA |  |  | WQP_POE_SET #2
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1016 | CALCIUM | 57 | MG/L |  | 2022-11-17 | AAA | 0.2 |  | WQP_POE_SET #2
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2022-11-17 | AAA | 0.012 |  | WQP_POE_SET #2
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1049 | SILICA | 0 | MG/L | 0 | 2022-11-17 | AAA | 0.11 |  | WQP_POE_SET #2
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | WQP | 1927 | TOTAL ALKALINITY | 240 | MG/L |  | 2022-11-17 | AAA | 5 |  | WQP_POE_SET #2
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.7 |  |  | 2022-11-17 | AAA |  |  | WQP_DISTRIBUTION SET #2_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1064 | CONDUCTIVITY | 520 | MG/L | 0 | 2022-11-17 | AAA | 2 |  | WQP_DISTRIBUTION SET #2_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 |  |  | 2022-11-17 | AAA |  |  | WQP_DISTRIBUTION SET #2_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1016 | CALCIUM | 58 | MG/L |  | 2022-11-17 | AAA | 0.2 |  | WQP_DISTRIBUTION SET #2_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2022-11-17 | AAA | 5 |  | WQP_DISTRIBUTION SET #2_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1049 | SILICA | 23 | MG/L | 0 | 2022-11-17 | AAA | 0.11 |  | WQP_DISTRIBUTION SET #2_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2022-11-17 | AAA | 0.0012 |  | WQP_DISTRIBUTION SET #2_BUILDING C BREAK ROOM SINK
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.6 |  |  | 2022-11-17 | AAA |  |  | WQP_DISTRIBUTION SET #2_SAMPLE #2_BUILDING A
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1064 | CONDUCTIVITY | 510 | MG/L | 0 | 2022-11-17 | AAA | 2 |  | WQP_DISTRIBUTION SET #2_SAMPLE #2_BUILDING A
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 |  |  | 2022-11-17 | AAA |  |  | WQP_DISTRIBUTION SET #2_SAMPLE #2_BUILDING A
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1016 | CALCIUM | 58 | MG/L |  | 2022-11-17 | AAA | 0.2 |  | WQP_DISTRIBUTION SET #2_SAMPLE #2_BUILDING A
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2022-11-17 | AAA | 5 |  | WQP_DISTRIBUTION SET #2_SAMPLE #2_BUILDING A
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2022-11-17 | AAA | 12 |  | WQP_DISTRIBUTION SET #2_SAMPLE #2_BUILDING A
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | WQP | 1049 | SILICA | 22 | MG/L | 0 | 2022-11-17 | AAA | 0.11 |  | WQP_DISTRIBUTION SET #2_SAMPLE #2_BUILDING A
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 1 | UG/L | 74.9999 | 2023-03-21 | AAA |  | 0.5499 | LATE DATA ENTRY, INVALID VIOLATION - KH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-03-21 | AAA |  | 0.5499 | LATE DATA ENTRY, INVALID VIOLATION - KH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-03-21 | AAA |  | 0.5499 | LATE DATA ENTRY, INVALID VIOLATION - KH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-03-21 | AAA |  | 0.5499 | LATE DATA ENTRY, INVALID VIOLATION - KH
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-06-27 | AAA | 0.24 | 0.5499
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-06-27 | AAA | 0.28 | 0.5499
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-06-27 | AAA | 0.4 | 0.5499
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-06-27 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-06-27 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-06-27 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-09-06 | AAA | 0.24 | 0.5499 | Q3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-09-06 | AAA | 0.28 | 0.5499 | Q3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-09-06 | AAA | 0.4 | 0.5499 | Q3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-12-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-12-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-20 | AAA | 0.24 | 0.5499 | Q1 VOCS
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-20 | AAA | 0.28 | 0.5499 | Q1 VOCS
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-20 | AAA | 0.4 | 0.5499 | Q1 VOCS
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 1.5 | UG/L | 74.9999 | 2024-04-19 | AAA | 0.24 | 0.5499 | POE - 2380 AND 2977 DETECT
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-04-19 | AAA | 0.28 | 0.5499 | POE - 2380 AND 2977 DETECT
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 1.4 | UG/L | 7.4999 | 2024-04-19 | AAA | 0.4 | 0.5499 | POE - 2380 AND 2977 DETECT
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 1.7 | UG/L | 74.9999 | 2024-09-03 | AAA | 0.24 | 0.5499 | Q3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-03 | AAA | 0.28 | 0.5499 | Q3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 1.3 | UG/L | 7.4999 | 2024-09-03 | AAA | 0.4 | 0.5499 | Q3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-03 | AAA | 0.41 | 0.5499 | Q3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-10 | AAA | 0.024 |  | POE - NO2 NO3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-10 | AAA | 0.0034 |  | POE - NO2 NO3
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 1.8 | UG/L | 74.9999 | 2024-10-21 | AAA | 0.24 | 0.5499 | CONTAM 2976 EXCEEDANCE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 1.9 | UG/L | 1.4999 | 2024-10-21 | AAA | 0.28 | 0.5499 | CONTAM 2976 EXCEEDANCE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-21 | AAA | 0.4 | 0.5499 | CONTAM 2976 EXCEEDANCE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1040 | NITRATE | 0.081 | MG/L | 10.4999 | 2025-01-28 | AAA | 0.024 |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-28 | AAA | 0 |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-02-27 | AAA |  | 0.5499 | Q1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-02-27 | AAA |  | 0.5499 | Q1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0.68 | UG/L | 7.4999 | 2025-02-27 | AAA | 0.4 | 0.5499 | Q1
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-05-29 | AAA | 0.45 | 0.5499 | POE - 2976 DETECT - NOT TECHNICALLY OVER MCL. WILL CONTINUE ANNU MONIT_ALP
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 1.4 | UG/L | 1.4999 | 2025-05-29 | AAA | 0.28 | 0.5499 | POE - 2976 DETECT - NOT TECHNICALLY OVER MCL. WILL CONTINUE ANNU MONIT_ALP
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-05-29 | AAA | 0.4 | 0.5499 | POE - 2976 DETECT - NOT TECHNICALLY OVER MCL. WILL CONTINUE ANNU MONIT_ALP
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 125.42 | UG/L | 60.4999 | 2025-08-13 | L1 | 0.98 |  | OFFICE KITCHEN SINK- EXCEEDANCE- 2456, 2950
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | DBP | 2950 | TOTAL THMS | 118.43 | UG/L | 80.4999 | 2025-08-13 | L1 | 0.44 |  | OFFICE KITCHEN SINK- EXCEEDANCE- 2456, 2950
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-08-13 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-08-13 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-08-13 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-08-13 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1010 | BARIUM | 0.006 | MG/L | 2.4999 | 2025-10-15 | AAA | 0.003 |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1025 | FLUORIDE | 0.26 | MG/L | 4.0499 | 2025-10-15 | AAA | 0.0099 |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2025-10-15 | AAA | 0.8 |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-10-15 | AAA |  |  | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0.67 | UG/L | 7.4999 | 2025-10-15 | AAA | 0.4 | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-10-15 | AAA |  | 0.5499 | POE
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.56 | UG/L | 60.4999 | 2025-11-12 | L1 | 0.98 |  | OFFICE KITCHEN SINK - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | DBP | 2950 | TOTAL THMS | 62.51 | UG/L | 80.4999 | 2025-11-12 | L1 | 0.44 |  | OFFICE KITCHEN SINK - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 56.52 | UG/L | 60.4999 | 2025-11-12 | L2 | 0.98 |  | MEN'S RESTROOM - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | D | DBP | 2950 | TOTAL THMS | 64.27 | UG/L | 80.4999 | 2025-11-12 | L2 | 0.44 |  | MEN'S RESTROOM - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3484416 | RINKER MATERIALS N. FLORIDA PIPE PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-12-10 | AAA |  | 0.5499 | POE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 38 | MG/L | 0 | 2025-04-23 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2025-04-23 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2025-04-23 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.2 | MG/L | 0 | 2025-04-23 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2025-04-23 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2025-04-23 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.9 | MG/L | 0 | 2025-04-23 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2025-04-23 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2025-04-23 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43 | MG/L | 0 | 2025-04-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2025-04-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2025-04-23 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.26 | UG/L | 60.4999 | 2025-05-01 | L1 | 2 |  | 1642 SILVER STAR RD - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 39.4 | UG/L | 80.4999 | 2025-05-01 | L1 | 0.13 |  | 1642 SILVER STAR RD - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.02 | UG/L | 60.4999 | 2025-05-01 | L2 | 2 |  | 2714 ILLINOIS ST - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 46.49 | UG/L | 80.4999 | 2025-05-01 | L2 | 0.13 |  | 2714 ILLINOIS ST - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.58 | UG/L | 60.4999 | 2025-05-01 | L3 | 2 |  | 758 DENNIS AVE - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 45.04 | UG/L | 80.4999 | 2025-05-01 | L3 | 0.13 |  | 758 DENNIS AVE - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.25 | UG/L | 60.4999 | 2025-05-01 | L4 | 2 |  | 10093 LAKE NONA BLVD - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 57.88 | UG/L | 80.4999 | 2025-05-01 | L4 | 0.13 |  | 10093 LAKE NONA BLVD - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.42 | UG/L | 60.4999 | 2025-05-01 | L5 | 2 |  | LANDSTAR RD / IOWA WOODS CIR - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 69.24 | UG/L | 80.4999 | 2025-05-01 | L5 | 0.13 |  | LANDSTAR RD / IOWA WOODS CIR - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.51 | UG/L | 60.4999 | 2025-05-01 | L6 | 2 |  | 5512 BAYSIDE DR - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 31.89 | UG/L | 80.4999 | 2025-05-01 | L6 | 0.13 |  | 5512 BAYSIDE DR - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.53 | UG/L | 60.4999 | 2025-05-01 | L8 | 2 |  | 7933 ARABIAN PLACE - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 28.77 | UG/L | 80.4999 | 2025-05-01 | L8 | 0.13 |  | 7933 ARABIAN PLACE - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.98 | UG/L | 60.4999 | 2025-05-01 | L9 | 2 |  | 14177 LAKE NONA BLVD - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 78.3 | UG/L | 80.4999 | 2025-05-01 | L9 | 0.13 |  | 14177 LAKE NONA BLVD - TTHM HAA5
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.43 | UG/L | 10.4999 | 2025-05-05 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.03 | UG/L | 10.4999 | 2025-05-05 | L7 | 0.59 |  | KIRMAN POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.94 | UG/L | 10.4999 | 2025-05-05 | L7 | 0.59 |  | PINE HILLS POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.07 | UG/L | 10.4999 | 2025-05-05 | L7 | 0.59 |  | HIGHLAND POINT POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.1 | UG/L | 10.4999 | 2025-05-05 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.03 | UG/L | 10.4999 | 2025-05-05 | L7 | 0.59 |  | SKY LAKE POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.8 | MG/L | 0 | 2025-05-07 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2025-05-07 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2025-05-07 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45.1 | MG/L | 0 | 2025-05-07 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2025-05-07 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2025-05-07 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2025-05-07 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2025-05-07 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2025-05-07 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.4 | MG/L | 0 | 2025-05-07 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2025-05-07 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2025-05-07 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.3 | MG/L | 0 | 2025-05-21 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2025-05-21 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-05-21 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 45 | MG/L | 0 | 2025-05-21 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2025-05-21 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2025-05-21 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.8 | MG/L | 0 | 2025-05-21 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2025-05-21 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2025-05-21 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2025-05-21 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2025-05-21 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2025-05-21 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.32 | UG/L | 10.4999 | 2025-06-02 | L7 | 0.59 |  | SOUTHWEST POE-BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.7 | UG/L | 10.4999 | 2025-06-02 | L7 | 0.59 |  | POE KIRKMAN BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.93 | UG/L | 10.4999 | 2025-06-02 | L7 | 0.59 |  | POE PINE HILLS BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 5.48 | UG/L | 10.4999 | 2025-06-02 | L7 | 0.59 |  | POE HIGHLAND BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.52 | UG/L | 10.4999 | 2025-06-02 | L7 | 0.59 |  | POE CONWAY- BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.02 | UG/L | 10.4999 | 2025-06-02 | L7 | 0.59 |  | POE SKY LAKE BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 37.8 | MG/L | 0 | 2025-06-04 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2025-06-04 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-06-04 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 44.9 | MG/L | 0 | 2025-06-04 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2025-06-04 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2025-06-04 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 35.3 | MG/L | 0 | 2025-06-04 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2025-06-04 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2025-06-04 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 42.6 | MG/L | 0 | 2025-06-04 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2025-06-04 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2025-06-04 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 36.8 | MG/L | 0 | 2025-06-18 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.51 | LN(10) |  | 2025-06-18 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2025-06-18 | WTP7 |  |  | KIRKMAN WP
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 43.7 | MG/L | 0 | 2025-06-18 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2025-06-18 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2025-06-18 | WTP10 |  |  | SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 34.9 | MG/L | 0 | 2025-06-18 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2025-06-18 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2025-06-18 | WTP11 |  |  | SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1919 | HARDNESS - CALCIUM | 41.7 | MG/L | 0 | 2025-06-18 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2025-06-18 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2025-06-18 | WTP6 |  |  | CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.86 | UG/L | 10.4999 | 2025-07-07 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.96 | UG/L | 10.4999 | 2025-07-07 | L7 | 0.59 |  | KIRKMAN POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.1 | UG/L | 10.4999 | 2025-07-07 | L7 | 0.59 |  | PINE HILLS POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 8.12 | UG/L | 10.4999 | 2025-07-07 | L7 | 0.59 |  | HIGHLAND POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.55 | UG/L | 10.4999 | 2025-07-07 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.49 | UG/L | 10.4999 | 2025-07-07 | L7 | 0.59 |  | SKY LAKE POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.91 | UG/L | 60.4999 | 2025-08-01 | L1 | 2 |  | 1642 SILVER STAR RD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 39.51 | UG/L | 80.4999 | 2025-08-01 | L1 | 0.13 |  | 1642 SILVER STAR RD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.61 | UG/L | 60.4999 | 2025-08-01 | L2 | 2 |  | 2714 ILLINOIS ST - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 37.5 | UG/L | 80.4999 | 2025-08-01 | L2 | 0.13 |  | 2714 ILLINOIS ST - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.86 | UG/L | 60.4999 | 2025-08-01 | L3 | 2 |  | 758 DENNIS AVE - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 43.61 | UG/L | 80.4999 | 2025-08-01 | L3 | 0.13 |  | 758 DENNIS AVE - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.79 | UG/L | 60.4999 | 2025-08-01 | L4 | 2 |  | 10093 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 55.18 | UG/L | 80.4999 | 2025-08-01 | L4 | 0.13 |  | 10093 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.66 | UG/L | 60.4999 | 2025-08-01 | L5 | 2 |  | LANDSTAR RD AND IOWA WOODS CIR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 75.61 | UG/L | 80.4999 | 2025-08-01 | L5 | 0.13 |  | LANDSTAR RD AND IOWA WOODS CIR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.14 | UG/L | 60.4999 | 2025-08-01 | L6 | 2 |  | 5512 BAYSIDE DR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 40.06 | UG/L | 80.4999 | 2025-08-01 | L6 | 0.13 |  | 5512 BAYSIDE DR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.64 | UG/L | 60.4999 | 2025-08-01 | L8 | 2 |  | 7933 ARABIAN PLACE - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 33.07 | UG/L | 80.4999 | 2025-08-01 | L8 | 0.13 |  | 7933 ARABIAN PLACE - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.08 | UG/L | 60.4999 | 2025-08-01 | L9 | 2 |  | 14177 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 73.66 | UG/L | 80.4999 | 2025-08-01 | L9 | 0.13 |  | 14177 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.97 | UG/L | 10.4999 | 2025-08-04 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.93 | UG/L | 10.4999 | 2025-08-04 | L7 | 0.59 |  | KIRKMAN POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.25 | UG/L | 10.4999 | 2025-08-04 | L7 | 0.59 |  | PINE HILLS POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 9.98 | UG/L | 10.4999 | 2025-08-04 | L7 | 0.59 |  | HIGHLAND POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.7 | UG/L | 10.4999 | 2025-08-04 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.69 | UG/L | 10.4999 | 2025-08-04 | L7 | 0.59 |  | SKY LAKE POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.73 | UG/L | 10.4999 | 2025-09-02 | L7 | 0.59 |  | POE SOUTHWEST
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.01 | UG/L | 10.4999 | 2025-09-02 | L7 | 0.59 |  | POE KIRKMAN
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.08 | UG/L | 10.4999 | 2025-09-02 | L7 | 0.59 |  | POE PINE HILLS
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 6.8 | UG/L | 10.4999 | 2025-09-02 | L7 | 0.59 |  | POE HIGHLAND
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.3 | UG/L | 10.4999 | 2025-09-02 | L7 | 0.59 |  | POE CONWAY
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.14 | UG/L | 10.4999 | 2025-09-02 | L7 | 0.59 |  | POE SKY LAKE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 0.59 | UG/L | 10.4999 | 2025-10-06 | L7 |  |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.24 | UG/L | 10.4999 | 2025-10-06 | L7 | 0.59 |  | HIGHLAND POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.89 | UG/L | 10.4999 | 2025-10-06 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.47 | UG/L | 10.4999 | 2025-10-06 | L7 | 0.59 |  | SKY LAKE POE - BROMATEW
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.71 | UG/L | 10.4999 | 2025-11-03 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.27 | UG/L | 10.4999 | 2025-11-03 | L7 | 0.59 |  | KIRKMAN POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.27 | UG/L | 10.4999 | 2025-11-03 | L7 | 0.59 |  | PINE HILLS POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 4.92 | UG/L | 10.4999 | 2025-11-03 | L7 | 0.59 |  | HIGHLAND POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.92 | UG/L | 10.4999 | 2025-11-03 | L7 | 0.59 |  | CONWAY POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.24 | UG/L | 10.4999 | 2025-11-03 | L7 | 0.59 |  | SKY LAKE POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.73 | UG/L | 60.4999 | 2025-11-03 | L1 | 2 |  | 1642 SILVER STAR RD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 60.61 | UG/L | 80.4999 | 2025-11-03 | L1 | 0.13 |  | 1642 SILVER STAR RD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.71 | UG/L | 60.4999 | 2025-11-03 | L2 | 2 |  | 2714 ILLINOIS ST - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 35.99 | UG/L | 80.4999 | 2025-11-03 | L2 | 0.13 |  | 2714 ILLINOIS ST - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.65 | UG/L | 60.4999 | 2025-11-03 | L3 | 2 |  | 758 DENNIS AVE - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 45.95 | UG/L | 80.4999 | 2025-11-03 | L3 | 0.13 |  | 758 DENNIS AVE - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.81 | UG/L | 60.4999 | 2025-11-03 | L4 | 2 |  | 10093 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 59.95 | UG/L | 80.4999 | 2025-11-03 | L4 | 0.13 |  | 10093 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.55 | UG/L | 60.4999 | 2025-11-03 | L5 | 2 |  | 124 LANDSTAR RD. & IOWA WOODS CIR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 72.12 | UG/L | 80.4999 | 2025-11-03 | L5 | 0.13 |  | 124 LANDSTAR RD. & IOWA WOODS CIR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.91 | UG/L | 60.4999 | 2025-11-03 | L6 | 2 |  | 5512 BAYSIDE DR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 38.83 | UG/L | 80.4999 | 2025-11-03 | L6 | 0.13 |  | 5512 BAYSIDE DR - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.69 | UG/L | 60.4999 | 2025-11-03 | L8 | 2 |  | 7933 ARABIAN PL - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 31.7 | UG/L | 80.4999 | 2025-11-03 | L8 | 0.13 |  | 7933 ARABIAN PL - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.6 | UG/L | 60.4999 | 2025-11-03 | L9 | 2 |  | 14177 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | D | DBP | 2950 | TOTAL THMS | 75.24 | UG/L | 80.4999 | 2025-11-03 | L9 | 0.13 |  | 14177 LAKE NONA BLVD - TTHM/HAA5
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.48 | UG/L | 10.4999 | 2025-12-01 | L7 | 0.59 |  | SW POE - BROMATE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.56 | UG/L | 10.4999 | 2025-12-01 | L7 | 0.59 |  | KIRKMAN POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 1.23 | UG/L | 10.4999 | 2025-12-01 | L7 | 0.59 |  | PINE HILLS POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 7.03 | UG/L | 10.4999 | 2025-12-01 | L7 | 0.59 |  | HIGHLAND POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 2.24 | UG/L | 10.4999 | 2025-12-01 | L7 | 0.59 |  | CONWAY POE
3480962 | ORLANDO UTILITIES COMMISSION | N | DBP | 1011 | BROMATE | 3.84 | UG/L | 10.4999 | 2025-12-01 | L7 | 0.59 |  | SKY LAKE POE
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-28 | AAA | 0.2
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-28 | AAA | 0.2
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-23 | AAA |  |  | WP- POE - ROUTINE COMP W/ 62-550
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-23 | AAA |  |  | WP- POE - ROUTINE COMP W/ 62-550
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-06-13 | AAA | 0.2 |  | ENTERED 09/06/2024 BY PHOTO FROM NATALIE PAVLIK
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-13 | AAA | 0.2 |  | ENTERED 09/06/2024 BY PHOTO FROM NATALIE PAVLIK
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-02 | AAA
3484408 | LOVING HIS PEOPLE ISRAEL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-02 | AAA
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1040 | NITRATE | 0.0265 | MG/L | 10.4999 | 2021-12-22 | AAA
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-22 | AAA
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-22 | AAA | 0.02
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-22 | AAA | 0.02
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1005 | ARSENIC | 0.0049 | MG/L | 0.0104 | 2022-04-22 | AAA | 0.001
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1010 | BARIUM | 0.0143 | MG/L | 2.4999 | 2022-04-22 | AAA | 0.002
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-04-22 | AAA | 0.001
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-04-22 | AAA | 0.001
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-04-22 | AAA | 0.005
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2022-04-22 | AAA | 0.2
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-04-22 | AAA | 0.001
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-04-22 | AAA | 0.0002
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1036 | NICKEL | 0.0011 | MG/L | 0.1499 | 2022-04-22 | AAA | 0.001
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-04-22 | AAA | 0.002
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1052 | SODIUM | 12.1 | MG/L | 160.4999 | 2022-04-22 | AAA | 0.5
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-04-22 | AAA | 0.001
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-04-22 | AAA | 0.0005
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-04-22 | AAA | 0.001
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0.96 | UG/L | 10499.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-04-22 | AAA | 0.5 | 0.5499 | VOC (XYLENES 0.96 UG/L DETECTION) HLKD 5/24/22
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-04-22 | AAA | 0.01 | 0.0149 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-04-22 | AAA | 0.01 | 0.0249 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-04-22 | AAA | 0.05 | 0.1499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-04-22 | AAA | 0.5 | 1.4999 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-04-22 | AAA | 0.1 | 1.4999 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-04-22 | AAA | 0.4 | 0.4499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-04-22 | AAA | 9 | 9.4999 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-04-22 | AAA | 6 | 6.4999 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-04-22 | AAA | 0.6 | 0.6499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-04-22 | AAA | 2 | 2.4999 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-04-22 | AAA | 0.07 | 0.0749 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-04-22 | AAA | 0.6 | 0.6499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-04-22 | AAA | 0.1 | 0.1499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-04-22 | AAA | 0.2 | 0.2499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-04-22 | AAA | 0.1 | 0.1499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-04-22 | AAA | 0.9 | 0.9499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-04-22 | AAA | 0.1 | 0.1499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-04-22 | AAA | 0.2 | 0.2499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-04-22 | AAA | 0.01 | 0.0449 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-04-22 | AAA | 0.01 | 0.0249 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-04-22 | AAA | 0.1 | 0.1499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-04-22 | AAA | 0.2 | 0.2499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-04-22 | AAA | 0.1 | 0.1499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-04-22 | AAA | 0.02 | 0.0249 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-04-22 | AAA | 0.04 | 0.0449 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-04-22 | AAA | 0.1 | 0.1499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-04-22 | AAA | 0.02 | 0.0249 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-04-22 | AAA | 0.01 | 0.0149 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-04-22 | AAA | 0.01 | 0.2499 | SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.2 | PCI/L | 15.4999 | 2022-04-22 | AAA | 1.2
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-04-22 | AAA | 0.7 | 1.4999
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-08-02 | AAA | 2.25
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-08-02 | AAA | 0.391 | 1.4999
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-08-02 | AAA | 0.01 | 0.0149 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-08-02 | AAA | 0.01 | 0.0249 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-08-02 | AAA | 0.05 | 0.1499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-08-02 | AAA | 0.5 | 1.4999 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484445 | CHURCH OF JESUS CHRIST OF LDS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-03 | A |  |  | POE
3484445 | CHURCH OF JESUS CHRIST OF LDS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-03 | A |  |  | POE
3484445 | CHURCH OF JESUS CHRIST OF LDS | N | INOR | 1040 | NITRATE | 0.73 | MG/L | 10.4999 | 2025-08-14 | A | 0.024
3484445 | CHURCH OF JESUS CHRIST OF LDS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-14 | A | 0.0034
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-08-02 | AAA | 0.4 | 0.4499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-08-02 | AAA | 9 | 9.4999 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-08-02 | AAA | 6 | 6.4999 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-08-02 | AAA | 2 | 2.4999 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-08-02 | AAA | 0.1 | 0.1499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-08-02 | AAA | 0.9 | 0.9499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-08-02 | AAA | 0.2 | 0.2499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-02 | AAA | 0.01 | 0.0449 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-02 | AAA | 0.01 | 0.0249 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-02 | AAA | 0.1 | 0.1499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-02 | AAA | 0.02 | 0.0249 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-02 | AAA | 0.1 | 0.1499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-02 | AAA | 0.02 | 0.0249 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-02 | AAA | 0.01 | 0.0149 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-02 | AAA | 0.01 | 0.2499 | 19 OF 29 SOC (Q QUALIFIERS: DAL, PIC, DIN, 2,4-D, 2,4,5-TP, PENTA-NOT ENTD. J QUALIFIERS: 2035, SIM, 2039, ATR-NOT ENTD)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-11-02 | AAA | 0.1 | 1.4999 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-11-02 | AAA | 0.6 | 0.0749 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-11-02 | AAA | 0.13 | 0.1499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-11-02 | AAA | 0.2 | 0.2499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.1 | 0.1499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-11-02 | AAA | 0.2 | 0.2499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-11-02 | AAA | 0.13 | 0.0449 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-11-02 | AAA | 0.02 | 0.0249 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0.788 | PCI/L | 2.4999 | 2022-11-02 | AAA | 0.592 | 1.4999
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-11-02 | AAA | 0.3 | 0.9499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-11-02 | AAA | 0.5 | 0.5499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-11-02 | AAA | 0.01 | 0.0149 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-11-02 | AAA | 0.1 | 0.0249 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-11-02 | AAA | 0.5 | 0.1499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.5 | 1.4999 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-11-02 | AAA | 0.4 | 0.4499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-11-02 | AAA | 9 | 9.4999 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-11-02 | AAA | 0.6 | 0.6499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-11-02 | AAA | 0.6 | 0.6499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-11-02 | AAA | 0.1 | 0.1499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-11-02 | AAA | 0.2 | 0.2499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-11-02 | AAA | 0.01 | 0.0449 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-11-02 | AAA | 0.1 | 0.0249 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-11-02 | AAA | 0.1 | 0.1499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-11-02 | AAA | 0.1 | 0.1499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-11-02 | AAA | 0.02 | 0.0249 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-11-02 | AAA | 0.1 | 0.1499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-11-02 | AAA | 0.01 | 0.0149 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-11-02 | AAA | 0.01 | 0.2499 | SOME CONTAMINANTS HAD J QUALIFIERS. SEE QA_CC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-11-02 | AAA | 3.4 | 6.4999
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-11-02 | AAA | 0.3 | 2.4999
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.6 | UG/L | 60.4999 | 2022-11-11 | L1 | 1.6 |  | LOCATION IS LISTED AS EDGE BUILDING IN REPORT_CC | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | M | DBP | 2950 | TOTAL THMS | 9.8 | UG/L | 80.4999 | 2022-11-11 | L1 | 0.5 |  | LOCATION IS LISTED AS EDGE BUILDING IN REPORT_CC | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | M | DBP | 2950 | TOTAL THMS | 14.1 | UG/L | 80.4999 | 2022-11-11 | L2 | 0.5 |  | LOCATION IS LISTED AS ADMIN BUILDING IN REPORT_CC | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.7 | UG/L | 60.4999 | 2022-11-11 | L2 | 1.6 |  | LOCATION IS LISTED AS ADMIN BUILDING IN REPORT_CC | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-12-15 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-15 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-01-23 | AAA | 0.0073 | 0.0149 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-01-23 | AAA | 0.0075 | 0.0249 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-01-23 | AAA | 0.0072 | 0.1499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-01-23 | AAA | 0.13 | 1.4999 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-01-23 | AAA | 0.9 | 1.4999 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-01-23 | AAA | 0.37 | 0.4499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-01-23 | AAA | 6 | 9.4999 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-01-23 | AAA | 5.9 | 6.4999 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-01-23 | AAA | 0.5 | 0.6499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-01-23 | AAA | 1.8 | 2.4999 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-01-23 | AAA | 0.06 | 0.0749 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-01-23 | AAA | 0.5 | 0.6499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-01-23 | AAA | 0.09 | 0.1499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-01-23 | AAA | 0.18 | 0.2499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-01-23 | AAA | 0.02 | 0.1499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-01-23 | AAA | 0.51 | 0.9499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-01-23 | AAA | 0.09 | 0.1499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-01-23 | AAA | 0.15 | 0.2499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-01-23 | AAA | 0.0063 | 0.0449 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-01-23 | AAA | 0.0055 | 0.0249 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-01-23 | AAA | 0.095 | 0.1499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-01-23 | AAA | 0.09 | 0.2499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-01-23 | AAA | 0.0066 | 0.1499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-01-23 | AAA | 0.015 | 0.0249 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-01-23 | AAA | 0.038 | 0.0449 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-01-23 | AAA | 0.098 | 0.1499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-01-23 | AAA | 0.0062 | 0.0249 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-01-23 | AAA | 0.0092 | 0.0149 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-01-23 | AAA | 0.056 | 0.2499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-01-23 | AAA | 0.28 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-01-23 | AAA | 0.32 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-01-23 | AAA | 0.28 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-01-23 | AAA | 0.44 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-01-23 | AAA | 0.46 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-01-23 | AAA | 0.26 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-01-23 | AAA | 0.2 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-01-23 | AAA | 0.18 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-01-23 | AAA | 0.28 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-01-23 | AAA | 0.36 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-01-23 | AAA | 0.39 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-01-23 | AAA | 0.23 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-01-23 | AAA | 0.26 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-23 | AAA | 0.28 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-01-23 | AAA | 0.12 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-23 | AAA | 0.24 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-01-23 | AAA | 0.12 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-01-23 | AAA | 0.17 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-01-23 | AAA | 0.22 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-01-23 | AAA | 0.17 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-01-23 | AAA | 0.39 | 0.5499 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4020 | RADIUM-226 | 0.5 | PCI/L | 3.4999 | 2023-01-25 | AAA | 0.4 | 1.4999 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-01-25 | AAA | 0.6 | 1.4999 | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0.8 | PCI/L | 15.4999 | 2023-01-25 | AAA | 0.6 |  | Q1 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-05-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4006 | COMBINED URANIUM | 0.81 | PCI/L | 20.4999 | 2023-05-09 | AAA | 0.2 | 0.667 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2023-05-10 | AAA | 0.8 |  | POE, Q2 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2023-05-10 | AAA | 0.2 | 1.4999 | POE, Q2 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-10 | AAA |  | 1.4999 | POE, Q2 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4006 | COMBINED URANIUM | 0.36 | PCI/L | 20.4999 | 2023-07-25 | AAA | 0.2 | 0.667 | POE, Q3 2023
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.1 | PCI/L | 15.4999 | 2023-07-25 | AAA | 1.2 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2023-07-25 | AAA | 0.4 | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-07-25 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-08-08 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-08 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.7 | UG/L | 60.4999 | 2023-08-15 | L1 | 0.98 |  | EDUCATION BUILDING HSBB | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2950 | TOTAL THMS | 31.78 | UG/L | 80.4999 | 2023-08-15 | L1 | 0.39 |  | EDUCATION BUILDING HSBB | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.76 | UG/L | 60.4999 | 2023-08-15 | L2 | 0.98 |  | ADMIN BUILDING HSBB | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2950 | TOTAL THMS | 32.27 | UG/L | 80.4999 | 2023-08-15 | L2 | 0.39 |  | ADMIN BUILDING HSBB | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.7 | UG/L | 60.4999 | 2023-08-15 | L1 | 0.98 |  | TTHMS SUBCONTRACTED TO LAB E82535 | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2950 | TOTAL THMS | 31.78 | UG/L | 80.4999 | 2023-08-15 | L1 | 0.39 |  | TTHMS SUBCONTRACTED TO LAB E82535 | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-08-23 | AAA | 0.0071 | 0.0149 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA | 0.0073 | 0.0249 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-08-23 | AAA | 0.007 | 0.1499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-08-23 | AAA | 0.12 | 1.4999 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-08-23 | AAA | 0.9 | 1.4999 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-08-23 | AAA | 0.37 | 0.4499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-08-23 | AAA | 6 | 9.4999 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-08-23 | AAA | 5.9 | 6.4999 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-08-23 | AAA | 0.5 | 0.6499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-08-23 | AAA | 1.8 | 2.4999 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-08-23 | AAA | 0.06 | 0.0749 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-08-23 | AAA | 0.5 | 0.6499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-08-23 | AAA | 0.09 | 0.1499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-08-23 | AAA | 0.18 | 0.2499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-08-23 | AAA | 0.02 | 0.1499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-08-23 | AAA | 0.51 | 0.9499 | Q3 SOC
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.7 | UG/L | 60.4999 | 2021-07-12 | L1 | 1 |  | 1315 DUSTY PINE DR. (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 36.7 | UG/L | 80.4999 | 2021-07-12 | L1 | 0.5 |  | 1315 DUSTY PINE DR. (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.9 | UG/L | 60.4999 | 2021-07-12 | L2 | 1 |  | 743 BIRCH HOLLOW (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 36.7 | UG/L | 80.4999 | 2021-07-12 | L2 | 0.5 |  | 743 BIRCH HOLLOW (HLKD) | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 69.3 | UG/L | 80.4999 | 2022-07-07 | L1 | 1 |  | 1315 DUSTY PINE (TOTAL HAA5 REPORT CORRECTED | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 31.81 | UG/L | 80.4999 | 2022-07-07 | L2 | 0.5 |  | 743 BIRCH HOLLOW (TOTAL HAA5 REPORT CORRECTED_AL | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.68 | UG/L | 60.4999 | 2022-07-07 | L2 | 1.5 |  | 743 BIRCH HOLLOW (TOTAL HAA5 REPORT CORRECTED_AL | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.5 | UG/L | 60.4999 | 2022-07-07 | L1 | 1.5 |  | 1315 DUSTY PINE (TOTAL HAA5 REPORT CORRECTED | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.82 | UG/L | 60.4999 | 2023-07-03 | L1 | 0.98 |  | 1315 DUSTY PINE DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 50.1 | UG/L | 80.4999 | 2023-07-03 | L1 | 0.39 |  | 1315 DUSTY PINE DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.04 | UG/L | 60.4999 | 2023-07-03 | L2 | 0.98 |  | 743 BIRCH HOLLOW DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2023-07-03 | L2 | 0.39 |  | 743 BIRCH HOLLOW DR | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 39.98 | UG/L | 80.4999 | 2024-07-03 | L2 | 0.39 |  | 743 BIRCH HOLLOW | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 41.42 | UG/L | 80.4999 | 2024-07-03 | L1 | 0.26 |  | 1315 DUSTY PINE | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.16 | UG/L | 60.4999 | 2024-07-03 | L1 | 0.98 |  | 1315 DUSTY PINE | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.9 | UG/L | 60.4999 | 2024-07-03 | L2 | 0.98 |  | 743 BIRCH HOLLOW | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.23 | UG/L | 60.4999 | 2025-07-02 | L1 | 0.98 |  | 13135 DUSTY PINES - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 39.18 | UG/L | 80.4999 | 2025-07-02 | L1 | 0.39 |  | 13135 DUSTY PINES - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.94 | UG/L | 60.4999 | 2025-07-02 | L2 | 0.98 |  | 743 BIRCH HOLLOW - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3484431 | OCOEE PINES (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 45.46 | UG/L | 80.4999 | 2025-07-02 | L2 | 0.39 |  | 743 BIRCH HOLLOW - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-08-23 | AAA | 0.09 | 0.1499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-08-23 | AAA | 0.15 | 0.2499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-08-23 | AAA | 0.0062 | 0.0449 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA | 0.0054 | 0.0249 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-08-23 | AAA | 0.095 | 0.1499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-08-23 | AAA | 0.09 | 0.2499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-08-23 | AAA | 0.0065 | 0.1499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA | 0.015 | 0.0249 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-08-23 | AAA | 0.038 | 0.0449 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-08-23 | AAA | 0.096 | 0.1499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA | 0.0061 | 0.0249 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-08-23 | AAA | 0.0091 | 0.0149 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-08-23 | AAA | 0.055 | 0.2499 | Q3 SOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-08-23 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-08-23 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-08-23 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-08-23 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-08-23 | AAA |  | 0.4499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-08-23 | AAA |  | 9.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-08-23 | AAA |  | 6.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-08-23 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-08-23 | AAA |  | 2.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-08-23 | AAA |  | 0.0749 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-08-23 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-08-23 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-08-23 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-08-23 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-08-23 | AAA |  | 0.9499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-08-23 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-08-23 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-08-23 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-08-23 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-08-23 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-08-23 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-08-23 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-08-23 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-08-23 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-08-23 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-08-23 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-26 | AAA |  | 0.0149 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-26 | AAA |  | 0.0249 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-26 | AAA |  | 0.1499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-26 | AAA |  | 1.4999 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-26 | AAA |  | 1.4999 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-26 | AAA |  | 0.4499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-26 | AAA |  | 9.4999 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-26 | AAA |  | 6.4999 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-26 | AAA |  | 0.6499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-26 | AAA |  | 2.4999 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-26 | AAA |  | 0.0749 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-26 | AAA |  | 0.6499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-26 | AAA |  | 0.1499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-26 | AAA |  | 0.2499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-26 | AAA |  | 0.1499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-26 | AAA |  | 0.9499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-26 | AAA |  | 0.1499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-26 | AAA |  | 0.2499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-26 | AAA |  | 0.0449 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-26 | AAA |  | 0.0249 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-26 | AAA |  | 0.1499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-26 | AAA |  | 0.2499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-26 | AAA |  | 0.1499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-26 | AAA |  | 0.0249 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-26 | AAA |  | 0.0449 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-26 | AAA |  | 0.1499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-26 | AAA |  | 0.0249 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-26 | AAA |  | 0.0149 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-26 | AAA |  | 0.2499 | Q4
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1 | PCI/L | 15.4999 | 2023-10-26 | AAA | 0.6 |  | Q4 (URANIUM RESULT WAS REPORTED IN UG/L - NOT ENT'D - RESULT MUST BE REPORTED IN PCI/L FOR DATA ENTRY IN PWS - CK'D & NOTE ADDED 12/4/23 BY BB PER REQUEST OF MR)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4020 | RADIUM-226 | 0.9 | PCI/L | 3.4999 | 2023-10-26 | AAA | 0.2 | 1.4999 | Q4 (URANIUM RESULT WAS REPORTED IN UG/L - NOT ENT'D - RESULT MUST BE REPORTED IN PCI/L FOR DATA ENTRY IN PWS - CK'D & NOTE ADDED 12/4/23 BY BB PER REQUEST OF MR)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-10-26 | AAA |  | 1.4999 | Q4 (URANIUM RESULT WAS REPORTED IN UG/L - NOT ENT'D - RESULT MUST BE REPORTED IN PCI/L FOR DATA ENTRY IN PWS - CK'D & NOTE ADDED 12/4/23 BY BB PER REQUEST OF MR)
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-01-23 | AAA |  | 0.5499 | ANNUAL VOC
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-02-05 | AAA |  | 6.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-02-05 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-02-05 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-02-05 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-02-05 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-02-05 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-02-05 | AAA |  | 0.4499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-02-05 | AAA |  | 9.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-02-05 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-02-05 | AAA |  | 0.0749 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-02-05 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-02-05 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-02-05 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-02-05 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-02-05 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-02-05 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-02-05 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-02-05 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-02-05 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-02-05 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-02-05 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-02-05 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-02-05 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-02-05 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-02-05 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-02-05 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-02-05 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4006 | COMBINED URANIUM | 0.35 | PCI/L | 20.4999 | 2024-02-20 | AAA | 0.2 | 0.667
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.1 | PCI/L | 15.4999 | 2024-02-20 | AAA | 0.8 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2024-02-20 | AAA | 0.3 | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-02-20 | AAA | 0.7 | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-03-06 | AAA | 0.67 | 0.9499
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-03-06 | AAA |  | 2.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-04-09 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-05-01 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-05-01 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-05-01 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-05-01 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-05-01 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-05-01 | AAA |  | 0.4499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-05-01 | AAA |  | 9.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-05-01 | AAA |  | 6.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-05-01 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-05-01 | AAA |  | 2.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-05-01 | AAA |  | 0.0749 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-05-01 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-05-01 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-05-01 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-05-01 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-05-01 | AAA |  | 0.9499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-05-01 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-05-01 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-05-01 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-05-01 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-05-01 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-05-01 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-05-01 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-05-01 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-05-01 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-05-01 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-05-01 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-05-01 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-05-01 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1040 | NITRATE | 0.066 | MG/L | 10.4999 | 2024-07-10 | AAA | 0.024 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-10 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.43 | UG/L | 60.4999 | 2024-08-12 | L2 | 0.98 |  | ADMIN BLDG AT FLO THRU | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2950 | TOTAL THMS | 21.02 | UG/L | 80.4999 | 2024-08-12 | L2 | 0.39 |  | ADMIN BLDG AT FLO THRU | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.63 | UG/L | 60.4999 | 2024-08-12 | L1 | 0.98 |  | ED BLDG AT FLO THRU | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2950 | TOTAL THMS | 29.41 | UG/L | 80.4999 | 2024-08-12 | L1 | 0.39 |  | ED BLDG AT FLO THRU | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1005 | ARSENIC | 0.0064 | MG/L | 0.0104 | 2025-04-07 | AAA | 0.00025 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2025-04-07 | AAA | 0.003 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1052 | SODIUM | 12 | MG/L | 160.4999 | 2025-04-07 | AAA | 0.8 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-04-07 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-04-07 | AAA |  | 0.5499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SEC | 1025 | FLUORIDE | 0.16 | MG/L | 2.0499 | 2025-04-23 | AAA | 0.0099 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1040 | NITRATE | 0.057 | MG/L | 10.4999 | 2025-04-23 | AAA | 0.024 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-23 | AAA |  |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2025-04-23 | AAA | 0.0099 |  | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-05-27 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-05-27 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-05-27 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-05-27 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-05-27 | AAA |  | 1.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-05-27 | AAA |  | 0.4499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-05-27 | AAA |  | 9.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-05-27 | AAA |  | 6.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-05-27 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-05-27 | AAA |  | 2.4999 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-05-27 | AAA |  | 0.0749 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-05-27 | AAA |  | 0.6499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-05-27 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-05-27 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-05-27 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-05-27 | AAA |  | 0.9499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-05-27 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-05-27 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-05-27 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-05-27 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-05-27 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-05-27 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-05-27 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-05-27 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-05-27 | AAA |  | 0.0449 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-05-27 | AAA |  | 0.1499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-05-27 | AAA |  | 0.0249 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-05-27 | AAA |  | 0.0149 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-05-27 | AAA |  | 0.2499 | POE
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-11 | L1 | 0.98 |  | EDUCATION BUILDING HSBB | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2950 | TOTAL THMS | 0.61 | UG/L | 80.4999 | 2025-08-11 | L1 | 0.44 |  | EDUCATION BUILDING HSBB | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-11 | L2 | 0.98 |  | ADMIN BUILDING HSBB | 3
3484417 | KOREAN PRESBYTERIAN CHURCH OF ORLANDO | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-08-11 | L2 | 0.44 |  | ADMIN BUILDING HSBB | 3
3484442 | LAKE MEADOW NATURALS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-28 | AAA | 0.2 |  | INITIAL NN
3484442 | LAKE MEADOW NATURALS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-28 | AAA | 0.2 |  | INITIAL NN
3484442 | LAKE MEADOW NATURALS | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-19 | AAA | 0.001 |  | NOT FOR COMPLIANCE. MONITORING LEAD FOR 4 QUARTERS DUE TO HISTORIC HIGH LEVELS FROM DOH. SMD 12/03/2021
3484442 | LAKE MEADOW NATURALS | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-01-05 | AAA |  |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-05-01 | AAA |  |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1030 | LEAD | 0.0056 | MG/L | 0.0154 | 2022-07-15 | AAA |  |  | POE. COMPLETED 4 QUARTERS OF SUPPLEMENTAL LEAD MONITORING WITH RESULTS BELOW THE ACTION LEVEL. NO FURTHER SAMPLING REQUIRED. SMD
3484442 | LAKE MEADOW NATURALS | N | INOR | 1040 | NITRATE | 0.21 | MG/L | 10.4999 | 2022-08-26 | AAA | 0.2 |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-26 | AAA |  |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1040 | NITRATE | 0.25 | MG/L | 10.4999 | 2023-08-23 | AAA | 0.024 |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-23 | AAA |  |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1040 | NITRATE | 0.064 | MG/L | 10.4999 | 2024-08-07 | AAA | 0.024 |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-07 | AAA |  |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1040 | NITRATE | 0.081 | MG/L | 10.4999 | 2025-09-15 | AAA | 0.024 |  | POE
3484442 | LAKE MEADOW NATURALS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-09-15 | AAA |  |  | POE
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.24 | UG/L | 60.4999 | 2021-08-16 | L1 |  |  | 13337 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 30.54 | UG/L | 80.4999 | 2021-08-16 | L1 |  |  | 13337 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.29 | UG/L | 60.4999 | 2021-08-16 | L2 |  |  | 1335 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 28.93 | UG/L | 80.4999 | 2021-08-16 | L2 |  |  | 1335 FLAMINGO | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.72 | UG/L | 60.4999 | 2022-08-16 | L2 | 1.42 |  | 13335 FLAMINGO CROSSING BLVD TTHM HAA5 | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 40.79 | UG/L | 80.4999 | 2022-08-16 | L2 | 0.84 |  | 13335 FLAMINGO CROSSING BLVD TTHM HAA5 | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.41 | UG/L | 60.4999 | 2022-08-16 | L1 | 1.43 |  | 13337 FLAMINGO CROSSING BLVD TTHM HAA5 | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 25.43 | UG/L | 80.4999 | 2022-08-16 | L1 | 0.84 |  | 13337 FLAMINGO CROSSING BLVD TTHM HAA5 | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.68 | UG/L | 60.4999 | 2023-08-15 | L1 | 1.43 |  | 13337 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 23.13 | UG/L | 80.4999 | 2023-08-15 | L1 | 0.84 |  | 13337 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.78 | UG/L | 60.4999 | 2023-08-15 | L2 | 1.43 |  | 13335 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 23.89 | UG/L | 80.4999 | 2023-08-15 | L2 | 0.84 |  | 13335 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.4 | UG/L | 60.4999 | 2024-08-15 | L1 | 1.43 |  | 1337 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 18.47 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.89 |  | 1337 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.86 | UG/L | 60.4999 | 2024-08-15 | L2 | 1.43 |  | 1335 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 19.38 | UG/L | 80.4999 | 2024-08-15 | L2 | 0.89 |  | 1335 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.64 | UG/L | 60.4999 | 2025-08-15 | L2 | 1.43 |  | 13335 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 22.04 | UG/L | 80.4999 | 2025-08-15 | L2 | 0.4 |  | 13335 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.67 | UG/L | 60.4999 | 2025-08-15 | L1 | 1.43 |  | 1337 FLAMINGO CROSSING BLVD | 3
3484437 | FLAMINGO CROSSING (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 20.9 | UG/L | 80.4999 | 2025-08-15 | L1 | 0.4 |  | 1337 FLAMINGO CROSSING BLVD | 3
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2021-10-26 | POE |  |  | WP
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1041 | NITRITE | 0.13 | MG/L | 1.4999 | 2021-10-26 | POE |  |  | WP
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-19 | POE |  |  | POE
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1041 | NITRITE | 0.11 | MG/L | 1.4999 | 2022-10-19 | POE | 0.0034 |  | POE
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1040 | NITRATE | 0.059 | MG/L | 10.4999 | 2023-10-11 | POE | 0.024 |  | POE
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-11 | POE |  |  | POE
3484435 | EAST ORANGE DISTRICT PARK | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-03 | POE |  |  | DIST
3484435 | EAST ORANGE DISTRICT PARK | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-03 | POE |  |  | DIST
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1040 | NITRATE | 0.083 | MG/L | 10.4999 | 2025-01-28 | POE | 0.024 |  | POE
3484435 | EAST ORANGE DISTRICT PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-28 | POE |  |  | POE
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.18 | UG/L | 60.4999 | 2021-08-16 | L2 |  |  | PIED PIPER CT HAA5 | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 61.65 | UG/L | 80.4999 | 2021-08-18 | L1 |  |  |  | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.44 | UG/L | 60.4999 | 2022-08-15 | L1 | 1.43 |  |  | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 61.51 | UG/L | 80.4999 | 2022-08-15 | L1 | 0.84 |  |  | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 58.32 | UG/L | 80.4999 | 2022-08-15 | L2 | 0.84 |  |  | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.28 | UG/L | 60.4999 | 2022-08-15 | L2 | 1.43 |  |  | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.64 | UG/L | 60.4999 | 2023-08-15 | L1 | 1.43 |  | 10246 SYMPHONY GROVE DR | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 55.25 | UG/L | 80.4999 | 2023-08-15 | L1 | 0.84 |  | 10246 SYMPHONY GROVE DR | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.66 | UG/L | 60.4999 | 2023-08-15 | L2 | 1.43 |  | 10015 PIED PIPER CT | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 57.49 | UG/L | 80.4999 | 2023-08-15 | L2 | 0.84 |  | 10015 PIED PIPER CT | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.41 | UG/L | 60.4999 | 2024-08-15 | L1 | 1.43 |  | 10246 SYMPHONY GROVE DR | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 51.12 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.89 |  | 10246 SYMPHONY GROVE DR | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.69 | UG/L | 60.4999 | 2024-08-15 | L2 | 1.43 |  | 10015 PIED PIPER CT | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 52.25 | UG/L | 80.4999 | 2024-08-15 | L2 | 0.89 |  | 10015 PIED PIPER CT | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21 | UG/L | 60.4999 | 2025-08-15 | L1 | 1.43 |  | 10246 SYMPHONY GROVE DR | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 59.7 | UG/L | 80.4999 | 2025-08-15 | L1 | 0.4 |  | 10246 SYMPHONY GROVE DR | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.86 | UG/L | 60.4999 | 2025-08-15 | L2 | 1.43 |  | 10015 PIED PIPER CT | 3
3484434 | ONE GOLDEN OAK (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 56.7 | UG/L | 80.4999 | 2025-08-15 | L2 | 0.4 |  | 10015 PIED PIPER CT | 3
3484443 | H&A FARMS, LLC | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-08-23 | AAA |  | 1.4999 | POE
3484443 | H&A FARMS, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1010 | BARIUM | 0 | MG/L | 2.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1052 | SODIUM | 73.9 | MG/L | 160.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1017 | CHLORIDE | 74.5 | MG/L | 250.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1022 | COPPER | 0.0043 | MG/L | 1.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1095 | ZINC | 0.0156 | MG/L | 5.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.43 | LN(10) |  | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 210 | MG/L | 500.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-08-23 | AAA |  | 0.0149 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-08-23 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 1.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-08-23 | AAA |  | 1.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-08-23 | AAA |  | 0.4499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 9.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-08-23 | AAA |  | 6.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-08-23 | AAA |  | 0.6499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-08-23 | AAA |  | 2.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-08-23 | AAA |  | 0.0749 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-08-23 | AAA |  | 0.6499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-08-23 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-08-23 | AAA |  | 0.2499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-08-23 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-08-23 | AAA |  | 0.9499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-08-23 | AAA |  | 0.2499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-08-23 | AAA |  | 0.0449 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-08-23 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-08-23 | AAA |  | 0.2499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.0449 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-08-23 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-08-23 | AAA |  | 0.0149 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-08-23 | AAA |  | 0.2499 | POE
3484443 | H&A FARMS, LLC | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-08-23 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1010 | BARIUM | 0 | MG/L | 2.4999 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1052 | SODIUM | 73.9 | MG/L | 160.4999 | 2021-08-23 | AAA | 0.5 |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-08-23 | AAA |  |  | PWS CODE - POE
3484443 | H&A FARMS, LLC | N | SEC | 1002 | ALUMINUM | 0.01 | MG/L | 0.2499 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1017 | CHLORIDE | 74.5 | MG/L | 250.4999 | 2021-08-23 | AAA | 0.4 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1022 | COPPER | 0.0043 | MG/L | 1.4999 | 2021-08-23 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1028 | IRON | 0.01 | MG/L | 0.3499 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1032 | MANGANESE | 0.01 | MG/L | 0.0549 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1050 | SILVER | 0.0005 | MG/L | 0.1499 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1055 | SULFATE | 1 | MG/L | 250.4999 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1095 | ZINC | 0.0156 | MG/L | 5.4999 | 2021-08-23 | AAA | 0.002 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.43 | LN(10) |  | 2021-08-23 | AAA | 0.01 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 210 | MG/L | 500.4999 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 2905 | FOAMING AGENTS | 0.2 |  | 0.5499 | 2021-08-23 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-08-23 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-08-23 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-08-23 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-08-23 | AAA |  | 0.4499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-08-23 | AAA |  | 9.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-08-23 | AAA |  | 6.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-08-23 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-08-23 | AAA |  | 2.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-08-23 | AAA |  | 0.0749 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-08-23 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-08-23 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-08-23 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-08-23 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-08-23 | AAA |  | 0.9499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-08-23 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-08-23 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-08-23 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-08-23 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-08-23 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-08-23 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-08-23 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-08-23 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-08-23 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-08-23 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.36 | UG/L | 60.4999 | 2021-09-21 | L1 | 1 |  | DOWNSTAIRS MENS BATHROOM SINK (HLKD) | 3
3484443 | H&A FARMS, LLC | D | DBP | 2950 | TOTAL THMS | 0.66 | UG/L | 80.4999 | 2021-09-21 | L1 | 0.5 |  | DOWNSTAIRS MENS BATHROOM SINK (HLKD) | 3
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-13 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-13 | AAA |  | 0.4499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 9.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-13 | AAA |  | 6.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-13 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 2.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-13 | AAA |  | 0.0749 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-13 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-13 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-13 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-13 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-13 | AAA |  | 0.9499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-13 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-13 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-13 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-13 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249 | PWS CODE
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-07 | AAA | 0.03 |  | CONFIRMED WITH THE OPERATOR THAT THE SAMPLE WAS COLLECTED AT THE POE. SMD
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-07 | AAA | 0.018 |  | CONFIRMED WITH THE OPERATOR THAT THE SAMPLE WAS COLLECTED AT THE POE. SMD
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-04-13 | AAA |  |  | POE
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-13 | AAA |  |  | POE
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-04-13 | AAA |  |  | POE
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-13 | AAA |  |  | POE
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-05-13 | AAA |  |  | POE
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-05-13 | AAA |  |  | POE
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2025-05-14 | AAA | 0.1 |  | 2025 N/N
3484444 | TIMBER CREEK PEDIATRICS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-05-14 | AAA | 0.1 |  | 2025 N/N
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-13 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-10-13 | AAA
3484443 | H&A FARMS, LLC | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-10-13 | AAA |  | 1.4999
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.0149
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 1.4999
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 1.4999
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-13 | AAA |  | 0.4499
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 9.4999
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-13 | AAA |  | 6.4999
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-13 | AAA |  | 0.6499
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 2.4999
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-13 | AAA |  | 0.0749
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-13 | AAA |  | 0.6499
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-13 | AAA |  | 0.9499
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-13 | AAA |  | 0.0449
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.0449
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-13 | AAA |  | 0.0149
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 0.5499
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.0149
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 1.4999
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 1.4999
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-13 | AAA |  | 0.4499
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-13 | AAA |  | 9.4999
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-13 | AAA |  | 6.4999
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-13 | AAA |  | 0.6499
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-13 | AAA |  | 2.4999
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-13 | AAA |  | 0.0749
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-13 | AAA |  | 0.6499
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-13 | AAA |  | 0.9499
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-13 | AAA |  | 0.0449
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-13 | AAA |  | 0.0449
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-13 | AAA |  | 0.1499
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-13 | AAA |  | 0.0249
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-13 | AAA |  | 0.0149
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-13 | AAA |  | 0.2499
3484443 | H&A FARMS, LLC | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-01-26 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-01-26 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-01-26 | AAA | 0.2 | 0.2499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-01-26 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-01-26 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-01-26 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-01-26 | AAA |  | 0.4499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-01-26 | AAA |  | 9.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-01-26 | AAA |  | 6.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-01-26 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-01-26 | AAA |  | 2.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-01-26 | AAA |  | 0.0749 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-01-26 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-01-26 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-01-26 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-01-26 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-01-26 | AAA |  | 0.9499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-01-26 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-01-26 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-01-26 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-01-26 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-01-26 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-01-26 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-01-26 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-01-26 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2022-01-26 | AAA |  |  | POE-HAF
3484443 | H&A FARMS, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-26 | AAA | 0.2 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-26 | AAA | 0.2 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-01-26 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1010 | BARIUM | 0 | MG/L | 2.4999 | 2022-01-26 | AAA | 0.002 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-01-26 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-01-26 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-01-26 | AAA | 0.005 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2022-01-26 | AAA | 0.2 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-01-26 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-01-26 | AAA | 0.0002 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-01-26 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-01-26 | AAA | 0.002 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1052 | SODIUM | 120 | MG/L | 160.4999 | 2022-01-26 | AAA | 0.5 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-01-26 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-01-26 | AAA | 0.0005 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-01-26 | AAA | 0.001 |  | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-01-26 | AAA | 0.01 | 0.0149 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.01 | 0.0249 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-01-26 | AAA | 0.05 | 0.1499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 1.4999 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-01-26 | AAA | 0.1 | 1.4999 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-01-26 | AAA | 0.4 | 0.4499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 9 | 9.4999 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-01-26 | AAA | 6 | 6.4999 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-01-26 | AAA | 0.6 | 0.6499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-01-26 | AAA | 2 | 2.4999 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-01-26 | AAA | 0.07 | 0.0749 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-01-26 | AAA | 0.6 | 0.6499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-01-26 | AAA | 0.1 | 0.1499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-01-26 | AAA | 0.1 | 0.1499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-01-26 | AAA | 0.9 | 0.9499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.1 | 0.1499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-01-26 | AAA | 0.2 | 0.2499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-01-26 | AAA | 0.01 | 0.0449 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.01 | 0.0249 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-01-26 | AAA | 0.1 | 0.1499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-01-26 | AAA | 0.2 | 0.2499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA | 0.1 | 0.1499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.02 | 0.0249 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-01-26 | AAA | 0.1 | 0.1499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.02 | 0.0249 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-01-26 | AAA | 0.01 | 0.0149 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-01-26 | AAA | 0.01 | 0.2499 | SOC (J QUALIFIERS: DINOSEB - OK, PENTACHLOROPHENOL- NOT ACCEPTABLE AND NOT ENTERED)
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-03-10 | AAA | 0.04 | 0.0449 | PENTACHLOROPHENOL (MARKED REVISED RESAMPLE) HLKD
3484443 | H&A FARMS, LLC | S | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-03-10 | AAA |  | 0.0449 | RECEIVED ACCEPTABLE PENTACHLOROPHENOLQA/QC 7/18/22 (ATR) )REVISED 7/7/22 REPORTING FORMAT WAS INCOMPLETE AND CONTAINED DISCREPANCIES - FILED IN OCULUS ALONG WITH 7/7/22 LETTER FROM EUOFIN (ATR)
3484443 | H&A FARMS, LLC | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-04-19 | AAA |  |  | PWS CODE
3484443 | H&A FARMS, LLC | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-04-19 | AAA |  | 1.4999 | PWS CODE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-15 | AAA |  |  | JOHN DEERE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-15 | AAA |  |  | JOHN DEERE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-09-08 | AAA |  |  | PWS CODE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-09-08 | AAA |  |  | PWS CODE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-11-08 | AAA |  |  | PWS CODE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-08 | AAA |  |  | PWS CODE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | N | INOR | 1030 | LEAD | 0.003 | MG/L | 0.0154 | 2023-11-08 | AAA | 0.0011 |  | PWS CODE
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-12 | AAA
3484439 | JOHN DEERE REGIONAL TRAINING FACILITY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-12 | AAA
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-04-07 | AAA |  |  | INITIAL NN OK
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-07 | AAA |  |  | INITIAL NN OK
3484441 | HIDDEN RIVER RV PARK | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-19 | AAA |  |  | PWS CODE
3484441 | HIDDEN RIVER RV PARK | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-19 | AAA |  |  | PWS CODE
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1040 | NITRATE | 0.31 | MG/L | 10.4999 | 2023-03-27 | AAA | 0.2
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-27 | AAA | 0.2
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-03-11 | AAA
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-11 | AAA
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-12 | AAA
3484441 | HIDDEN RIVER RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-12 | AAA
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 0.5499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-04-19 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-04-19 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-04-19 | AAA |  | 1.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-04-19 | AAA |  | 0.4499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-04-19 | AAA |  | 9.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-04-19 | AAA |  | 6.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-04-19 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-04-19 | AAA |  | 2.4999 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-04-19 | AAA |  | 0.0749 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-04-19 | AAA |  | 0.6499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-04-19 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-04-19 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-04-19 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-04-19 | AAA |  | 0.9499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-04-19 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-04-19 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-04-19 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-04-19 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-04-19 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-04-19 | AAA |  | 0.0449 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-04-19 | AAA |  | 0.1499 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-04-19 | AAA |  | 0.0249 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-04-19 | AAA |  | 0.0149 | PWS CODE
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-04-19 | AAA |  | 0.2499 | PWS CODE
3484443 | H&A FARMS, LLC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.7 | UG/L | 60.4999 | 2022-09-13 | L1 | 0.38 |  | DOWNSTAIRS MENS BATHROOM SINK (HLKD) | 3
3484443 | H&A FARMS, LLC | D | DBP | 2950 | TOTAL THMS | 0.91 | UG/L | 80.4999 | 2022-09-13 | L1 | 0.5 |  | DOWNSTAIRS MENS BATHROOM SINK (HLKD) | 3
3484443 | H&A FARMS, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-17 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-17 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-03-29 | AAA | 0.28 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-03-29 | AAA | 0.32 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-03-29 | AAA | 0.28 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-03-29 | AAA | 0.44 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-03-29 | AAA | 0.46 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-03-29 | AAA | 0.26 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-03-29 | AAA | 0.2 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-03-29 | AAA | 0.18 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-03-29 | AAA | 0.28 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-03-29 | AAA | 0.36 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-03-29 | AAA | 0.39 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-03-29 | AAA | 0.23 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-03-29 | AAA | 0.26 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-29 | AAA | 0.28 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-03-29 | AAA | 0.12 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-29 | AAA | 0.24 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-03-29 | AAA | 0.12 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-03-29 | AAA | 0.17 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-03-29 | AAA | 0.22 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-03-29 | AAA | 0.17 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-03-29 | AAA | 0.39 | 0.5499 | VOC
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-03-29 | AAA | 0.0069 | 0.0149 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-03-29 | AAA | 0.0071 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-03-29 | AAA | 0.0068 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-03-29 | AAA | 0.12 | 1.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-03-29 | AAA | 0.9 | 1.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-03-29 | AAA | 0.37 | 0.4499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-03-29 | AAA | 6 | 9.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-03-29 | AAA | 5.9 | 6.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-03-29 | AAA | 0.5 | 0.6499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-03-29 | AAA | 1.8 | 2.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-03-29 | AAA | 0.06 | 0.0749 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-03-29 | AAA | 0.5 | 0.6499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-03-29 | AAA | 0.09 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-03-29 | AAA | 0.18 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-03-29 | AAA | 0.019 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-03-29 | AAA | 0.51 | 0.9499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-03-29 | AAA | 0.09 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-03-29 | AAA | 0.15 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-03-29 | AAA | 0.006 | 0.0449 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-03-29 | AAA | 0.0052 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-03-29 | AAA | 0.095 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-03-29 | AAA | 0.09 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-03-29 | AAA | 0.0063 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-03-29 | AAA | 0.015 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-03-29 | AAA | 0.038 | 0.0449 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-03-29 | AAA | 0.093 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-03-29 | AAA | 0.0061 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-03-29 | AAA | 0.009 | 0.0149 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-03-29 | AAA | 0.053 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDOTHALL, 2042 HEX..., HEPTACHLOR, 2,4-D, BENZO, PENTA, PCBS, EDB, & CHLORDANE. - THEY SHOULD BE EXACTLY THE SAME)
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-02-19 | AAA |  | 0.1499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-02-19 | AAA |  | 0.2499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-02-19 | AAA |  | 0.1499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-02-19 | AAA |  | 0.0249 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-02-19 | AAA |  | 0.0449 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-02-19 | AAA |  | 0.1499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-02-19 | AAA |  | 0.0249 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-02-19 | AAA |  | 0.0149 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-02-19 | AAA |  | 0.2499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-19 | AAA |  | 0.5499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-02-19 | AAA |  | 0.0149 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-02-19 | AAA |  | 0.0249 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-02-19 | AAA |  | 0.1499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-02-19 | AAA |  | 1.4999 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-02-19 | AAA |  | 1.4999 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-02-19 | AAA |  | 0.4499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-02-19 | AAA |  | 9.4999 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-02-19 | AAA |  | 6.4999 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-02-19 | AAA |  | 0.6499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-02-19 | AAA |  | 0.0749 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-02-19 | AAA |  | 0.6499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-02-19 | AAA |  | 0.1499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-02-19 | AAA |  | 0.2499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-02-19 | AAA |  | 0.1499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-02-19 | AAA |  | 0.1499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-02-19 | AAA |  | 0.2499 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-02-19 | AAA |  | 0.0449 | POE HAF
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-02-19 | AAA |  | 0.0249 | POE HAF
3484443 | H&A FARMS, LLC | N | INOR | 1040 | NITRATE | 0.055 | MG/L | 10.4999 | 2024-03-11 | AAA | 0.02 |  | POE - H&A, NITRITE J QUALIFIER--SPIKE ACCEPTABLE_LIB
3484443 | H&A FARMS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-11 | AAA | 0.02 |  | POE - H&A, NITRITE J QUALIFIER--SPIKE ACCEPTABLE_LIB
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-03-25 | AAA | 1.8 | 2.4999 | OXAMYL AND CARBOFURAN
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-03-25 | AAA | 0.67 | 0.9499 | OXAMYL AND CARBOFURAN
3484443 | H&A FARMS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-05-13 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-09-24 | L1 | 0.2 |  | DOWNSTAIRS MENS BATHROOM SINK | 3
3484443 | H&A FARMS, LLC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-09-24 | L1 | 0.21 |  | DOWNSTAIRS MENS BATHROOM SINK | 3
3484443 | H&A FARMS, LLC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1010 | BARIUM | 0 | MG/L | 2.4999 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1020 | CHROMIUM | 0.002 | MG/L | 0.1499 | 2025-09-24 | AAA | 0.0004 |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1025 | FLUORIDE | 0.34 | MG/L | 4.0499 | 2025-09-24 | AAA | 0.1 |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1045 | SELENIUM | 0.006 | MG/L | 0.0549 | 2025-09-24 | AAA | 0.001 |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1052 | SODIUM | 67 | MG/L | 160.4999 | 2025-09-24 | AAA | 0.13 |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-09-24 | AAA |  |  | POE
3484443 | H&A FARMS, LLC | N | SEC | 1025 | FLUORIDE | 0.34 | MG/L | 2.0499 | 2025-09-24 | AAA | 0.1 |  | POE
3484443 | H&A FARMS, LLC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-09-24 | AAA |  | 0.5499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-09-24 | AAA |  | 0.0149 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-09-24 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-09-24 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-09-24 | AAA |  | 1.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-09-24 | AAA |  | 1.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-09-24 | AAA |  | 0.4499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-09-24 | AAA |  | 9.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-09-24 | AAA |  | 6.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-09-24 | AAA |  | 0.6499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-09-24 | AAA |  | 2.4999 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-09-24 | AAA |  | 0.0749 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-09-24 | AAA |  | 0.6499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-09-24 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-09-24 | AAA |  | 0.2499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-09-24 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-09-24 | AAA |  | 0.9499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-09-24 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-09-24 | AAA |  | 0.2499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-09-24 | AAA |  | 0.0449 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-09-24 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-09-24 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-09-24 | AAA |  | 0.2499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-09-24 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-09-24 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-09-24 | AAA |  | 0.0449 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-09-24 | AAA |  | 0.1499 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-09-24 | AAA |  | 0.0249 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-09-24 | AAA |  | 0.0149 | POE
3484443 | H&A FARMS, LLC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-09-24 | AAA |  | 0.2499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | S | INOR | 1030 | LEAD | 0.0008 | MG/L | 0.0154 | 2022-02-24 | DIST | 0.0005 |  | DISH SINK (NOT POE/D) NOT CLEARED STATUS CURRENTLY 4/21/22
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | W | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-24 | WELL | 0.0075 |  | WELL (NOT POE/D) NOT CLEARED STATUS CURRENTLY 4/21/22
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-12-12 | AAA |  | 0.5499 | Q4 2024 VOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-12-12 | AAA |  | 0.0149 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-12-12 | AAA |  | 0.0249 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-12-12 | AAA |  | 0.1499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-12-12 | AAA |  | 1.4999 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2031 | DALAPON | 1.1 | UG/L | 249.9999 | 2024-12-12 | AAA | 0.9 | 1.4999 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-12-12 | AAA |  | 0.4499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-12-12 | AAA |  | 9.4999 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-12-12 | AAA |  | 6.4999 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-12-12 | AAA |  | 0.6499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-12-12 | AAA |  | 2.4999 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-12-12 | AAA |  | 0.0749 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-12-12 | AAA |  | 0.6499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-12-12 | AAA |  | 0.1499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-12-12 | AAA |  | 0.2499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-12-12 | AAA |  | 0.1499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-12-12 | AAA |  | 0.9499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-12-12 | AAA |  | 0.1499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-12-12 | AAA |  | 0.2499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-12-12 | AAA |  | 0.0449 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-12-12 | AAA |  | 0.0249 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-12-12 | AAA |  | 0.1499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-12-12 | AAA |  | 0.2499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-12-12 | AAA |  | 0.1499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-12-12 | AAA |  | 0.0249 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-12-12 | AAA |  | 0.0449 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-12-12 | AAA |  | 0.1499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-12-12 | AAA |  | 0.0249 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-12-12 | AAA |  | 0.0149 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-12-12 | AAA |  | 0.2499 | Q4 2024 SOC
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-12 | AAA |  |  | 2024 NN
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-12 | AAA |  |  | 2024 NN
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-01-14 | AAA | 0.5 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-01-14 | AAA | 0.45 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-01-14 | AAA | 0.48 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-01-14 | AAA | 0.49 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-01-14 | AAA | 0.44 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-01-14 | AAA | 0.4 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-01-14 | AAA | 0.28 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-01-14 | AAA | 0.4 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-01-14 | AAA | 0.41 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-01-14 | AAA | 0.44 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-01-14 | AAA | 0.32 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-01-14 | AAA | 0.36 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-01-14 | AAA | 0.33 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-14 | AAA | 0.25 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-01-14 | AAA | 0.44 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-14 | AAA | 0.49 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-01-14 | AAA | 0.37 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-01-14 | AAA | 0.42 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-01-14 | AAA | 0.46 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-01-14 | AAA | 0.45 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-01-14 | AAA | 0.45 | 0.5499 | SUB E82535, E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-01-14 | AAA | 0.0069 | 0.0149
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-01-14 | AAA | 0.0071 | 0.0249
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-01-14 | AAA | 0.0068 | 0.1499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-01-14 | AAA | 0.12 | 1.4999
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-01-14 | AAA | 0.9 | 1.4999
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-01-14 | AAA | 0.37 | 0.4499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-01-14 | AAA | 3 | 9.4999
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-01-14 | AAA | 5.9 | 6.4999
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-01-14 | AAA | 0.05 | 0.6499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-01-14 | AAA | 1.8 | 2.4999
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-01-14 | AAA | 0.06 | 0.0749
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-01-14 | AAA | 0.05 | 0.6499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2040 | PICLORAM | 0.09 | UG/L | 549.9999 | 2025-01-14 | AAA | 0.09 | 0.1499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-01-14 | AAA | 0.18 | 0.2499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-01-14 | AAA | 0.1 | 0.1499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-01-14 | AAA | 0.67 | 0.9499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-01-14 | AAA | 0.09 | 0.1499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-01-14 | AAA | 0.15 | 0.2499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-01-14 | AAA | 0.006 | 0.0449
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-01-14 | AAA | 0.0052 | 0.0249
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-01-14 | AAA | 0.095 | 0.1499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-01-14 | AAA | 0.09 | 0.2499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-01-14 | AAA | 0.063 | 0.1499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-01-14 | AAA | 0.015 | 0.0249
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-01-14 | AAA | 0.038 | 0.0449
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-01-14 | AAA | 0.093 | 0.1499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-01-14 | AAA | 0.0061 | 0.0249
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-01-14 | AAA | 0.009 | 0.0149
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-01-14 | AAA | 0.053 | 0.2499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.4 | PCI/L | 15.4999 | 2025-01-16 | AAA | 3
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4020 | RADIUM-226 | 2.1 | PCI/L | 3.4999 | 2025-01-16 | AAA | 0.4 | 1.4999
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-01-16 | AAA | 0.8 | 1.4999
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 8.8 | PCI/L | 15.4999 | 2025-01-30 | AAA | 1.8 |  | SUB E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2025-01-30 | AAA | 0.2 | 0.667 | SUB E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4020 | RADIUM-226 | 2 | PCI/L | 3.4999 | 2025-01-30 | AAA | 0.1 | 1.4999 | SUB E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-01-30 | AAA | 0.6 | 1.4999 | SUB E82574
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-04-21 | AAA | 0.5 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-04-21 | AAA | 0.45 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2955 | TOT XYLENE | 4.3 | UG/L | 10499.9999 | 2025-04-21 | AAA | 0.48 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-04-21 | AAA | 0.49 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-04-21 | AAA | 0.44 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-04-21 | AAA | 0.4 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-04-21 | AAA | 0.28 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-04-21 | AAA | 0.4 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-04-21 | AAA | 0.41 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA | 0.44 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-04-21 | AAA | 0.32 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA | 0.36 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-04-21 | AAA | 0.33 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA | 0.25 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-04-21 | AAA | 0.44 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA | 0.49 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-04-21 | AAA | 0.37 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-04-21 | AAA | 0.42 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-04-21 | AAA | 0.46 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2992 | ETHYLBENZENE | 0.73 | UG/L | 749.9999 | 2025-04-21 | AAA | 0.45 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-04-21 | AAA | 0.45 | 0.5499 | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-04-21 | AAA | 0.0075 | 0.0149 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-04-21 | AAA | 0.0077 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-04-21 | AAA | 0.0074 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA | 0.13 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2031 | DALAPON | 7 | UG/L | 249.9999 | 2025-04-21 | AAA | 0.9 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-04-21 | AAA | 0.37 | 0.4499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-04-21 | AAA | 6 | 9.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-04-21 | AAA | 5.9 | 6.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-04-21 | AAA | 0.5 | 0.6499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-04-21 | AAA | 1.8 | 2.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-04-21 | AAA | 0.06 | 0.0749 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-04-21 | AAA | 0.5 | 0.6499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-04-21 | AAA | 0.09 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-04-21 | AAA | 0.18 | 0.2499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-04-21 | AAA | 0.021 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-04-21 | AAA | 0.67 | 0.9499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA | 0.09 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-04-21 | AAA | 0.15 | 0.2499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-04-21 | AAA | 0.0065 | 0.0449 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-04-21 | AAA | 0.0057 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-04-21 | AAA | 0.095 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-04-21 | AAA | 0.09 | 0.2499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-04-21 | AAA | 0.0068 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-04-21 | AAA | 0.015 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-04-21 | AAA | 0.038 | 0.0449 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-04-21 | AAA | 0.1 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-04-21 | AAA | 0.0062 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-04-21 | AAA | 0.0092 | 0.0149 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-04-21 | AAA | 0.058 | 0.2499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.5 | PCI/L | 15.4999 | 2025-04-21 | AAA | 2.4 |  | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4020 | RADIUM-226 | 1.8 | PCI/L | 3.4999 | 2025-04-21 | AAA | 0.2 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-04-21 | AAA | 0.6 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-08-12 | AAA |  | 0.2499
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-08-12 | AAA | 0.5 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-08-12 | AAA | 0.45 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-08-12 | AAA | 0.48 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-08-12 | AAA | 0.49 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-08-12 | AAA | 0.44 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-08-12 | AAA | 0.4 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-08-12 | AAA | 0.28 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-08-12 | AAA | 0.4 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-08-12 | AAA | 0.41 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-08-12 | AAA | 0.44 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-08-12 | AAA | 0.32 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-08-12 | AAA | 0.36 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-08-12 | AAA | 0.33 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-08-12 | AAA | 0.25 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-08-12 | AAA | 0.44 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-08-12 | AAA | 0.49 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-08-12 | AAA | 0.37 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-08-12 | AAA | 0.42 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-08-12 | AAA | 0.46 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-08-12 | AAA | 0.45 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-08-12 | AAA | 0.45 | 0.5499 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-08-12 | AAA | 0.0069 | 0.0149 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-08-12 | AAA | 0.0071 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-08-12 | AAA | 0.0068 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-08-12 | AAA | 0.12 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2031 | DALAPON | 1.6 | UG/L | 249.9999 | 2025-08-12 | AAA | 0.9 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-08-12 | AAA | 0.31 | 0.4499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-08-12 | AAA | 6 | 9.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-08-12 | AAA | 5.9 | 6.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-08-12 | AAA | 0.5 | 0.6499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-08-12 | AAA | 1.8 | 2.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-08-12 | AAA | 0.06 | 0.0749 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-08-12 | AAA | 0.5 | 0.6499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-08-12 | AAA | 0.09 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-08-12 | AAA | 0.18 | 0.2499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-08-12 | AAA | 0.019 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-08-12 | AAA | 0.67 | 0.9499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-08-12 | AAA | 0.09 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-08-12 | AAA | 0.15 | 0.2499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2025-08-12 | AAA | 0.006 | 0.0055 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-08-12 | AAA | 0.0052 | 0.0449 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-08-12 | AAA | 0.095 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-08-12 | AAA | 0.09 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-08-12 | AAA | 0.0063 | 0.2499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-08-12 | AAA | 0.015 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-08-12 | AAA | 0.038 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-08-12 | AAA | 0.093 | 0.0449 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-08-12 | AAA | 0.0062 | 0.1499 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-08-12 | AAA | 0.0092 | 0.0249 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-08-12 | AAA | 0.053 | 0.0149 | ENTRY POINT DESIGNATED BY WATER SYSTEM- 2031 DETECT
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 6.2 | PCI/L | 15.4999 | 2025-08-12 | AAA | 2.3 |  | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4020 | RADIUM-226 | 2.1 | PCI/L | 3.4999 | 2025-08-12 | AAA | 0.02 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-08-12 | AAA | 0.7 | 1.4999 | ENTRY POINT DESIGNATED BY WATER SYSTEM
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.96 | UG/L | 60.4999 | 2025-08-27 | L1 | 0.98 |  | OFFICE RESTROOM SINK | 3
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | D | DBP | 2950 | TOTAL THMS | 42.37 | UG/L | 80.4999 | 2025-08-27 | L1 | 0.44 |  | OFFICE RESTROOM SINK | 3
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.31 | UG/L | 60.4999 | 2025-08-27 | L2 | 0.98 |  | OUTSIDE CLEANING SINK | 3
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | D | DBP | 2950 | TOTAL THMS | 38.33 | UG/L | 80.4999 | 2025-08-27 | L2 | 0.44 |  | OUTSIDE CLEANING SINK | 3
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-09-10 | AAA | 0.003 |  | WELL
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1919 | HARDNESS - CALCIUM | 130 | MG/L | 0 | 2025-09-10 | AAA | 0.2 |  | WELL
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1022 | COPPER | 0 | MG/L | 1.5499 | 2025-09-10 | AAA | 0.005 |  | WELL
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1030 | LEAD | 0.0034 | MG/L | 0.0154 | 2025-09-10 | AAA | 0.003 |  | POE-EXCEEDANCES
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1022 | COPPER | 0.0088 | MG/L | 1.5499 | 2025-09-10 | AAA | 0.005 |  | POE-EXCEEDANCES
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1064 | CONDUCTIVITY | 1100 | MG/L | 0 | 2025-09-10 | AAA | 2 |  | POE-EXCEEDANCES
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1919 | HARDNESS - CALCIUM | 130 | MG/L | 0 | 2025-09-10 | AAA | 0 |  | POE-EXCEEDANCES
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1927 | TOTAL ALKALINITY | 300 | MG/L |  | 2025-09-10 | AAA | 5 |  | POE-EXCEEDANCES
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | D | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-09-10 | AAA | 0.003 |  | EDUCATION CENTER BLDG #2 KITCHENETTE SINK- EXCEEDANCE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | D | WQP | 1022 | COPPER | 0.6 | MG/L | 1.5499 | 2025-09-10 | AAA | 0.005 |  | EDUCATION CENTER BLDG #2 KITCHENETTE SINK- EXCEEDANCE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | D | WQP | 1919 | HARDNESS - CALCIUM | 130 | MG/L | 0 | 2025-09-10 | AAA | 0.2 |  | EDUCATION CENTER BLDG #2 KITCHENETTE SINK- EXCEEDANCE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1030 | LEAD | 0.001 | MG/L | 0.0154 | 2025-10-13 | AAA | 0.001 |  | POE-WELL
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1022 | COPPER | 0.025 | MG/L | 1.5499 | 2025-10-13 | AAA | 0.025 |  | POE-WELL
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1030 | LEAD | 0.001 | MG/L | 0.0154 | 2025-10-13 | AAA | 0.001 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | WQP | 1022 | COPPER | 0.025 | MG/L | 1.5499 | 2025-10-13 | AAA | 0.025 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1040 | NITRATE | 0.42 | MG/L | 10.4999 | 2025-10-30 | AAA | 0.024 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1005 | ARSENIC | 0.0003 | MG/L | 0.0104 | 2025-10-30 | AAA | 0.0003 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2025-10-30 | AAA | 0.003 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2025-10-30 | AAA | 0.0099 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1052 | SODIUM | 66 | MG/L | 160.4999 | 2025-10-30 | AAA | 0.8 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1074 | ANTIMONY | 0.004 | MG/L | 0.0065 | 2025-10-30 | AAA | 0.001 |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-10-30 | AAA |  |  | POE
3484436 | BACK TO NATURE WILDLIFE REFUGE CENTER | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-12-03 | AAA |  | 1.4999 | POE

## Osceola
PWS ID | Mailing Name | Sample Type | Contam Group | Contam Code | Contam Desc | Results | UOM | MCL | Sample Date | Loc Code | MDL | RDL | Remark | Max Qtr
3490631 | SECRETS HIDEAWAY | N | INOR | 1040 | NITRATE | 0.052 | MG/L | 10.4999 | 2021-05-10 | AAA
3490631 | SECRETS HIDEAWAY | N | INOR | 1041 | NITRITE | 0.063 | MG/L | 1.4999 | 2021-05-10 | AAA
3490631 | SECRETS HIDEAWAY | N | INOR | 1040 | NITRATE | 0.56 | MG/L | 10.4999 | 2022-02-22 | AAA | 0.03
3490631 | SECRETS HIDEAWAY | N | INOR | 1041 | NITRITE | 0.488 | MG/L | 1.4999 | 2022-02-22 | AAA | 0.036
3490631 | SECRETS HIDEAWAY | P | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-06-26 | AAA | 0.2 |  | POE
3490631 | SECRETS HIDEAWAY | P | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-26 | AAA | 0.2 |  | POE
3490631 | SECRETS HIDEAWAY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-27 | AAA |  |  | POE
3490631 | SECRETS HIDEAWAY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-27 | AAA |  |  | POE
3490631 | SECRETS HIDEAWAY | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2025-11-12 | AAA | 0.1 |  | 2025
3490631 | SECRETS HIDEAWAY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-12 | AAA | 0.1 |  | 2025
3490633 | TROPICAL PALMS RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.97 | UG/L | 60.4999 | 2022-08-02 | L1 | 0.98 |  | LOT 271 ( ) | 3
3490633 | TROPICAL PALMS RESORT | D | DBP | 2950 | TOTAL THMS | 38.25 | UG/L | 80.4999 | 2022-08-02 | L1 | 0.39 |  | LOT 271 ( ) | 3
3490633 | TROPICAL PALMS RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1005 | ARSENIC | 0.0029 | MG/L | 0.0104 | 2022-10-04 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2022-10-04 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1025 | FLUORIDE | 0.95 | MG/L | 4.0499 | 2022-10-04 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1052 | SODIUM | 4.9 | MG/L | 160.4999 | 2022-10-04 | AAA | 0.8 |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-10-04 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | RAD | 4006 | COMBINED URANIUM | 0.55 | PCI/L | 20.4999 | 2022-10-04 | AAA | 0.2 | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008 -POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-04 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-04 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-04 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-04 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-04 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-04 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-04 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-04 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-04 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-04 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-04 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-04 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-04 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-04 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-04 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-04 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-04 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-04 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-04 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-04 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-04 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-04 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-04 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-04 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-04 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-04 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-04 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-10-04 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | RAD | 4020 | RADIUM-226 | 2 | PCI/L | 3.4999 | 2022-10-04 | AAA | 0.05 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 -POE
3490633 | TROPICAL PALMS RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-10-04 | AAA | 0.06 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 -POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2023-10-16 | AAA | 0.024 |  | POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | POE
3490633 | TROPICAL PALMS RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-12-01 | AAA |  |  | POE
3490633 | TROPICAL PALMS RESORT | N | RAD | 4006 | COMBINED URANIUM | 1.67 | PCI/L | 20.4999 | 2024-12-01 | AAA | 0.323 | 0.667 | POE
3490633 | TROPICAL PALMS RESORT | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2024-12-01 | AAA |  | 1.4999 | POE
3490633 | TROPICAL PALMS RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-12-01 | AAA |  | 1.4999 | POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2025-12-10 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-10-04 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-04 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 - POE
3490633 | TROPICAL PALMS RESORT | N | INOR | 1040 | NITRATE | 0.08 | MG/L | 10.4999 | 2024-12-02 | AAA | 0.024 |  | 2024 NN
3490633 | TROPICAL PALMS RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-02 | AAA |  |  | 2024 NN
3490633 | TROPICAL PALMS RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-06 | L1 | 0.98 |  | LOT 271 | 3
3490633 | TROPICAL PALMS RESORT | D | DBP | 2950 | TOTAL THMS | 2.27 | UG/L | 80.4999 | 2025-08-06 | L1 | 0.44 |  | LOT 271 | 3
3490633 | TROPICAL PALMS RESORT | N | INOR | 1040 | NITRATE | 0.42 | MG/L | 10.4999 | 2025-12-10 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-12-10 | AAA | 0.0034 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1005 | ARSENIC | 0.0006 | MG/L | 0.0104 | 2025-12-10 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-12-10 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-12-10 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1025 | FLUORIDE | 0.12 | MG/L | 4.0499 | 2025-12-10 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-12-10 | AAA | 0.0005 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-12-10 | AAA | 3e-05 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-12-10 | AAA | 0.008 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-12-10 | AAA | 0.0012 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1052 | SODIUM | 6.2 | MG/L | 160.4999 | 2025-12-10 | AAA | 0.8 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-12-10 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-12-10 | AAA | 0.002 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-12-10 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008 1024 Q QUALIFIER
3490633 | TROPICAL PALMS RESORT | N | SEC | 1025 | FLUORIDE | 0.12 | MG/L | 2.0499 | 2025-12-10 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | RAD | 4006 | COMBINED URANIUM | 0.54 | PCI/L | 20.4999 | 2025-12-10 | AAA | 0.2 | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-12-10 | AAA | 0.5 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-12-10 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-12-10 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-12-10 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-12-10 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-12-10 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-12-10 | AAA | 0.28 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-12-10 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-12-10 | AAA | 0.41 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-12-10 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-12-10 | AAA | 0.32 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-12-10 | AAA | 0.36 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-12-10 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-12-10 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-12-10 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-12-10 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-12-10 | AAA | 0.37 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-12-10 | AAA | 0.42 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-12-10 | AAA | 0.46 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-12-10 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-12-10 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.8 | PCI/L | 15.4999 | 2025-12-10 | AAA | 1.2 |  | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2025-12-10 | AAA | 0.4 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490633 | TROPICAL PALMS RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-12-10 | AAA | 0.6 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-14 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-20 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.6 | UG/L | 60.4999 | 2021-01-26 | DBP-5 | 0.9 |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 58.9 | UG/L | 80.4999 | 2021-01-26 | DBP-5 | 0.47 |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.7 | UG/L | 60.4999 | 2021-01-26 | DBP-1 | 0.9 |  | SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 70.4 | UG/L | 80.4999 | 2021-01-26 | DBP-1 | 0.47 |  | SERALAGO BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.8 | UG/L | 60.4999 | 2021-01-26 | DBP-2 | 0.9 |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 71.9 | UG/L | 80.4999 | 2021-01-26 | DBP-2 | 0.47 |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.4 | UG/L | 60.4999 | 2021-01-26 | DBP-3 | 0.9 |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 45.9 | UG/L | 80.4999 | 2021-01-26 | DBP-3 | 0.47 |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.9 | UG/L | 60.4999 | 2021-01-26 | DBP-4 | 0.9 |  | EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 70.9 | UG/L | 80.4999 | 2021-01-26 | DBP-4 | 0.47 |  | EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.8 | UG/L | 60.4999 | 2021-01-26 | DBP-6 | 0.9 |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 70.1 | UG/L | 80.4999 | 2021-01-26 | DBP-6 | 0.47 |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP1 |  |  | POE NORTH BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP1 |  |  | POE NORTH BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP3 |  |  | POE PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP3 |  |  | POE PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP5 |  |  | POE CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP5 |  |  | POE CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-02-09 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-02-11 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-19 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-27 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-05 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-03-08 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-09 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-01-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-01-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-11 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-02-20 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-03-20 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-03-24 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-26 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-06 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-08 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.3 | UG/L | 60.4999 | 2021-04-22 | DBP-5 | 0.9 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 47 | UG/L | 80.4999 | 2021-04-22 | DBP-5 | 0.47 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.7 | UG/L | 60.4999 | 2021-04-22 | DBP-1 | 0.9 |  | 3200 SERALAGO BLVD. [2Q TTHM LRAA=51.775]
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 87.4 | UG/L | 80.4999 | 2021-04-22 | DBP-1 | 0.47 |  | 3200 SERALAGO BLVD. [2Q TTHM LRAA=51.775]
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.3 | UG/L | 60.4999 | 2021-04-22 | DBP-2 | 0.9 |  | 1400 RIVERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 78.5 | UG/L | 80.4999 | 2021-04-22 | DBP-2 | 0.47 |  | 1400 RIVERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.4 | UG/L | 60.4999 | 2021-04-22 | DBP-3 | 0.9 |  | 120 SIMPSON RD. [2Q TTHM LRAA=55.42]
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 96.9 | UG/L | 80.4999 | 2021-04-22 | DBP-3 | 0.47 |  | 120 SIMPSON RD. [2Q TTHM LRAA=55.42]
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.6 | UG/L | 60.4999 | 2021-04-22 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-23 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-01 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-13 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 78.4 | UG/L | 80.4999 | 2021-04-22 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.3 | UG/L | 60.4999 | 2021-04-22 | DBP-6 | 0.9 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 69.8 | UG/L | 80.4999 | 2021-04-22 | DBP-6 | 0.47 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-10 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-05-15 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-24 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-05-27 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-06-02 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-08 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-08 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-22 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-25 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-07-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-25 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-07 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-07-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-21 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.1 | UG/L | 60.4999 | 2021-07-23 | DBP-1 | 0.9 |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 51.1 | UG/L | 80.4999 | 2021-07-23 | DBP-1 | 0.47 |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.3 | UG/L | 60.4999 | 2021-07-23 | DBP-5 |  |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 67.8 | UG/L | 80.4999 | 2021-07-23 | DBP-5 |  |  | BRASSIE CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.6 | UG/L | 60.4999 | 2021-07-23 | DBP-2 |  |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 63.1 | UG/L | 80.4999 | 2021-07-23 | DBP-2 |  |  | RIVIERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.8 | UG/L | 60.4999 | 2021-07-23 | DBP-3 |  |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 41.1 | UG/L | 80.4999 | 2021-07-23 | DBP-3 |  |  | SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.6 | UG/L | 60.4999 | 2021-07-23 | DBP-4 |  |  | E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 59.9 | UG/L | 80.4999 | 2021-07-23 | DBP-4 |  |  | E LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.6 | UG/L | 60.4999 | 2021-07-23 | DBP-6 |  |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 72.6 | UG/L | 80.4999 | 2021-07-23 | DBP-6 |  |  | RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-08-04 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-11 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-08-11 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-18 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-08-24 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-08-27 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-01 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-04 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-06 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-19 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-21 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-09-22 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.2 | UG/L | 60.4999 | 2021-09-28 | DBP-7 |  |  | 2722 MATERA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 49.3 | UG/L | 80.4999 | 2021-09-28 | DBP-7 |  |  | 2722 MATERA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.7 | UG/L | 60.4999 | 2021-09-28 | DBP-8 |  |  | 5690 BARLETTA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 50.6 | UG/L | 80.4999 | 2021-09-28 | DBP-8 |  |  | 5690 BARLETTA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-10-06 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-10-06 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-11 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-20 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.3 | UG/L | 60.4999 | 2021-10-25 | DBP-5 | 0.9 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 59 | UG/L | 80.4999 | 2021-10-25 | DBP-5 | 0.47 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.4 | UG/L | 60.4999 | 2021-10-25 | DBP-1 | 0.9 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 34.5 | UG/L | 80.4999 | 2021-10-25 | DBP-1 | 0.47 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.1 | UG/L | 60.4999 | 2021-10-25 | DBP-2 | 0.9 |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 55 | UG/L | 80.4999 | 2021-10-25 | DBP-2 | 0.47 |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.4 | UG/L | 60.4999 | 2021-10-25 | DBP-3 | 0.9 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 41.4 | UG/L | 80.4999 | 2021-10-25 | DBP-3 | 0.47 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.4 | UG/L | 60.4999 | 2021-10-25 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 64.9 | UG/L | 80.4999 | 2021-10-25 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.3 | UG/L | 60.4999 | 2021-10-25 | DBP-6 | 0.9 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 66.1 | UG/L | 80.4999 | 2021-10-25 | DBP-6 | 0.47 |  | 2713 RISMEN CT. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-10-26 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-10-27 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-11-03 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-11-03 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-05 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-11-17 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-11-17 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-24 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-12-02 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-08 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-12-13 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-22 | WTP1 |  |  | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.3 | UG/L | 60.4999 | 2021-12-22 | DBP-7 | 0.9 |  | 2722 MATERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 79.9 | UG/L | 80.4999 | 2021-12-22 | DBP-7 | 0.47 |  | 2722 MATERA DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 46.6 | UG/L | 60.4999 | 2021-12-22 | DBP-8 | 0.9 |  | 5690 BARLETTA DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 85 | UG/L | 80.4999 | 2021-12-22 | DBP-8 | 0.47 |  | 5690 BARLETTA DR
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-12-23 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-29 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-21 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-01-04 | WTP5 |  |  | WTP 5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-01-19 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-06 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-12 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-17 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.5 | UG/L | 60.4999 | 2022-01-26 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 49.5 | UG/L | 80.4999 | 2022-01-26 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28 | UG/L | 60.4999 | 2022-01-26 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 37.2 | UG/L | 80.4999 | 2022-01-26 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.9 | UG/L | 60.4999 | 2022-01-26 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 41.3 | UG/L | 80.4999 | 2022-01-26 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.9 | UG/L | 60.4999 | 2022-01-26 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 35 | UG/L | 80.4999 | 2022-01-26 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.4 | UG/L | 60.4999 | 2022-01-26 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 52.8 | UG/L | 80.4999 | 2022-01-26 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.9 | UG/L | 60.4999 | 2022-01-26 | DBP-6 |  |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 46.4 | UG/L | 80.4999 | 2022-01-26 | DBP-6 |  |  | 2713 RISMEN CT
3490766 | LAKE MARIAN RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1017 | CHLORIDE | 58 | MG/L | 250.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1025 | FLUORIDE | 2 | MG/L | 2.0499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1055 | SULFATE | 7.6 | MG/L | 250.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1905 | COLOR | 7.7 | COLOR UNITS | 15.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.01 | LN(10) |  | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 300 | MG/L | 500.4999 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-02-21 | AAA |  |  | POE- DOH LAB CERTIFICATION E82535 - E82001
3490766 | LAKE MARIAN RESORT | N | INOR | 1040 | NITRATE | 0.011 | MG/L | 10.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 2 | MG/L | 4.0499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1052 | SODIUM | 36 | MG/L | 160.4999 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-02-22 | AAA |  |  | POE -DOH LAB CERTIFICATION E82574- E82535-E84589
3490766 | LAKE MARIAN RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-02-22 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-22 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-22 | AAA |  | 0.4499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-22 | AAA |  | 9.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-22 | AAA |  | 6.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-02-22 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-22 | AAA |  | 2.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-02-22 | AAA |  | 0.0749 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-02-22 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-22 | AAA |  | 0.9499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-02-22 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-22 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-22 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-22 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-22 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-22 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.6 | PCI/L | 15.4999 | 2021-03-01 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4020 | RADIUM-226 | 3.2 | PCI/L | 3.4999 | 2021-03-01 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-03-01 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 1.9 | MG/L | 4.0499 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | INOR | 1030 | LEAD | 0.0011 | MG/L | 0.0154 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | INOR | 1052 | SODIUM | 38.1 | MG/L | 160.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | SEC | 1017 | CHLORIDE | 60.7 | MG/L | 250.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | SEC | 1022 | COPPER | 0.025 | MG/L | 1.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | SEC | 1025 | FLUORIDE | 1.9 | MG/L | 2.0499 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | SEC | 1055 | SULFATE | 9 | MG/L | 250.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | SEC | 1095 | ZINC | 0.049 | MG/L | 5.4999 | 2021-03-23 | AAA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-02-02 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-02-08 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-02-15 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-17 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP5 | 0.025 |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP5 | 0.025 |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP1 | 0.025 |  | N. BERMUDA WP (NITRATE OK-ENT'D, NITRITE J QUALIFIER-NOT ENT'D PENDING EVALUATION)
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP3 | 0.025 |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP3 | 0.025 |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-22 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-02-24 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-03-04 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-07 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-03-08 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-14 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-22 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-03-22 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-03-24 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-04-05 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-07 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-12 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-18 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-04-20 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30 | UG/L | 60.4999 | 2022-04-22 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 46.9 | UG/L | 80.4999 | 2022-04-22 | DBP-5 |  |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.1 | UG/L | 60.4999 | 2022-04-22 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 40.8 | UG/L | 80.4999 | 2022-04-22 | DBP-1 |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.8 | UG/L | 60.4999 | 2022-04-22 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 52.7 | UG/L | 80.4999 | 2022-04-22 | DBP-2 |  |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.8 | UG/L | 60.4999 | 2022-04-22 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 26.2 | UG/L | 80.4999 | 2022-04-22 | DBP-3 |  |  | 120 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.7 | UG/L | 60.4999 | 2022-04-22 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 61.9 | UG/L | 80.4999 | 2022-04-22 | DBP-4 |  |  | 145 EAST LAKESHORE
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33 | UG/L | 60.4999 | 2022-04-22 | DBP-6 |  |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 53.8 | UG/L | 80.4999 | 2022-04-22 | DBP-6 |  |  | 2713 RISMEN CT
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-23 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-10 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-10 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-12 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-18 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-24 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-25 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-07 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-07 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-09 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-14 | WTP1 |  |  | WTP1 NORTH BERMUDA WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-27 | WTP5 |  |  | WTP5 CAMELOT WEST WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-28 | WTP3 |  |  | WTP3 PARKWAY WQP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-02 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-07-04 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-05 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-07-06 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-07-21 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-07-24 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.1 | UG/L | 60.4999 | 2022-07-25 | DBP-5 | 0.9 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 62.7 | UG/L | 80.4999 | 2022-07-25 | DBP-5 | 0.47 |  | 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.5 | UG/L | 60.4999 | 2022-07-25 | DBP-1 | 0.9 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 45 | UG/L | 80.4999 | 2022-07-25 | DBP-1 | 0.47 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.6 | UG/L | 60.4999 | 2022-07-25 | DBP-2 | 0.9 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 52.3 | UG/L | 80.4999 | 2022-07-25 | DBP-2 | 0.47 |  | 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.1 | UG/L | 60.4999 | 2022-07-25 | DBP-3 | 0.9 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 39.7 | UG/L | 80.4999 | 2022-07-25 | DBP-3 | 0.47 |  | 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 43.3 | UG/L | 60.4999 | 2022-07-25 | DBP-4 | 0.9 |  | 145 E. LAKESHORE BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 52.9 | UG/L | 80.4999 | 2022-07-25 | DBP-4 | 0.47 |  | 145 E. LAKESHORE BLVD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.3 | UG/L | 60.4999 | 2022-07-25 | DBP-6 | 0.9 |  | 2713 RISMEN CT., KISS. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 71 | UG/L | 80.4999 | 2022-07-25 | DBP-6 | 0.47 |  | 2713 RISMEN CT., KISS. (HLKD)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-07-26 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-28 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-08-03 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-08-05 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-08-07 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-08-08 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-08-22 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-08-22 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-08-23 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-08-30 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-09-05 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-09-06 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-09-07 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-09-08 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-09-21 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-09-21 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-09-22 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-09-23 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-10-01 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-10-06 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-10-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-10-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-10-20 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-10-21 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-10-25 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.4 | UG/L | 60.4999 | 2022-10-26 | DBP-5 |  |  | 1721 BRASSIE CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 51.3 | UG/L | 80.4999 | 2022-10-26 | DBP-5 |  |  | 1721 BRASSIE CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.4 | UG/L | 60.4999 | 2022-10-26 | DBP-1 |  |  | 3250 OWASSA CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 44.9 | UG/L | 80.4999 | 2022-10-26 | DBP-1 |  |  | 3250 OWASSA CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.2 | UG/L | 60.4999 | 2022-10-26 | DBP-2 |  |  | 1400 RIVIERA DR TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 53.6 | UG/L | 80.4999 | 2022-10-26 | DBP-2 |  |  | 1400 RIVIERA DR TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.5 | UG/L | 60.4999 | 2022-10-26 | DBP-3 |  |  | 120 SIMPSON RD TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 13.1 | UG/L | 80.4999 | 2022-10-26 | DBP-3 |  |  | 120 SIMPSON RD TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.9 | UG/L | 60.4999 | 2022-10-26 | DBP-4 |  |  | 145 E LAKESHORE TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 24.4 | UG/L | 80.4999 | 2022-10-26 | DBP-4 |  |  | 145 E LAKESHORE TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.6 | UG/L | 60.4999 | 2022-10-26 | DBP-6 |  |  | 2713 RISEMEN CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 32.9 | UG/L | 80.4999 | 2022-10-26 | DBP-6 |  |  | 2713 RISEMEN CT TTHM HAA5
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-10-27 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST- 230 INDIAN POINT CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-4603 OSCEOLA POINT TR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-4926 SAUSALITO LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-2749 POINCIANA BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-5324 MICCO ST
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-3132 PINTO DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-4831 WARRIOR LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-3230 SMOKE SIGNAL CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-3210 PEACE PIPE DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-5325 FLYING EAGLE LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-5690 W. 192
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-4445 GREAT HARBOR LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-2331 DYER BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-2007 HIDDEN DALE CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-2655 N JOHN YOUNG PKWY
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-343 COLUMBIA AVE
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-201 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-830 COUNTRY CROSSING CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-1319 ASTRO LAKE DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-1011 BILL BECK BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-2273 MALLARD CREEK CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-2645 HAWTHORNE LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-3929 COASTAL BREEZE
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-01 | DIST |  |  | DIST-1425 E. 192
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-03 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-11-05 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-11-06 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-11-10 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-11-24 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-11-24 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-11-25 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-26 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 2749 POINCIANA BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 4603 OSCEOLA POINT TR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 230 INDIAN POINT CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 4926 SAUSALITO LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 3132 PINTO DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 5324 MICCO ST
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 4831 WARRIOR LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 3230 SMOKE SIGNAL CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 5325 FLYING EAGLE LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 3210 PEACE PIPE DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 5690 W. 192
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 4445 GREAT HARBOR LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 2331 DYER BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 2007 HIDDEN DALE CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 2655 N JOHN YOUNG PKWY
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 343 COLUMBIA AVE
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 201 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 830 COUNTRY CROSSING CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 1319 ASTRO LAKE DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 1011 BILL BECK BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 2273 MALLARD CREEK CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 2645 HAWTHORNE LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 1425 E. 192
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-11-29 | DISTRIBUTION |  |  | 3929 COASTAL BREEZE
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-12-06 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-12-07 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-08 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-09 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-21 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-26 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-12-29 | WTP3 |  |  | PARKWAY WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-12-29 | WTP5 |  |  | CAMELOT WEST WP
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-01-06 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-06 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-10 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-17 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-01-21 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-23 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.1 | UG/L | 60.4999 | 2023-01-27 | DBP-5 | 0.9 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 46.6 | UG/L | 80.4999 | 2023-01-27 | DBP-5 | 0.47 |  | 1721 BRASSIE CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.6 | UG/L | 60.4999 | 2023-01-27 | DBP-1 | 0.9 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 46.4 | UG/L | 80.4999 | 2023-01-27 | DBP-1 | 0.47 |  | 3250 OWASSA CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16 | UG/L | 60.4999 | 2023-01-27 | DBP-2 | 0.9 |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 38.2 | UG/L | 80.4999 | 2023-01-27 | DBP-2 | 0.47 |  | 1400 RIVIERA DR.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.2 | UG/L | 60.4999 | 2023-01-27 | DBP-3 | 0.9 |  | 120 SIMPSON RD.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 13.5 | UG/L | 80.4999 | 2023-01-27 | DBP-3 | 0.47 |  | 120 SIMPSON RD.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.9 | UG/L | 60.4999 | 2023-01-27 | DBP-4 | 0.9 |  | 145 E. LAKESHORE (BLVD.)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 22.2 | UG/L | 80.4999 | 2023-01-27 | DBP-4 | 0.47 |  | 145 E. LAKESHORE (BLVD.)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.2 | UG/L | 60.4999 | 2023-01-27 | DBP-6 | 0.9 |  | 2713 RISMEN CT.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 29.7 | UG/L | 80.4999 | 2023-01-27 | DBP-6 | 0.47 |  | 2713 RISMEN CT.
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | WTP5 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP5 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | WTP3 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP3 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | WTP1 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP1 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-07 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-02-08 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-13 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-02-20 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-4603 OSCEOLA POINT TR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-230 INDIAN POINT CIRCLE
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-4926 SAUSALITO LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-2749 POINCIANA BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-3132 PINTO DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-5324 MICCO ST
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-4831 WARRIOR LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-3230 SMOKE SIGNAL CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-4445 GREAT HARBOR LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-5325 FLYING EAGLE LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-3210 PEACE PIPE DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-5690 W. 192
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-2331 DYER BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-2007 HIDDEN DALE CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-2655 N JOHN YOUNG PKWY
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-343 COLUMBIA AVE
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-201 SIMPSON RD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-830 COUNTRY CROSSING CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-1319 ASTRO LAKE DR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-1011 BILL BECK BLVD
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-2273 MALLARD CREEK CIR
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-2645 HAWTHORNE LN
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-3929 COASTAL BREEZE
3490751 | TOHO WATER AUTHORITY EASTERN | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-02-21 | DIST |  |  | DIST-1425 E. 192
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.2 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP5 | 0.2 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP3 | 0.33 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP3 | 0.2 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP1 | 0.4 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP1 | 0.23 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP3 | 0.35 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP3 | 0.11 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP3 | 0.44 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP3 | 0.3 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP3 | 0.12 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP3 | 0.29 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP3 | 0.27 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.3 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP3 | 0.27 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.28 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP3 | 0.44 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP3 | 0.28 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP3 | 0.4 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP3 | 0.28 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP3 | 0.23 | 0.5499 | PARKWAY STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP5 | 0.44 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP5 | 0.35 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP5 | 0.33 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP5 | 0.11 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP5 | 0.26 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP5 | 0.3 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP5 | 0.12 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP5 | 0.29 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP5 | 0.27 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP5 | 0.3 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP5 | 0.27 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP5 | 0.28 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP5 | 0.44 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP5 | 0.26 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP5 | 0.28 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP5 | 0.26 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP5 | 0.26 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP5 | 0.4 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP5 | 0.28 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP5 | 0.23 | 0.5499 | CAMELOT WEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP1 | 0.35 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP1 | 0.33 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP1 | 0.11 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.44 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP1 | 0.3 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP1 | 0.12 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP1 | 0.29 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.27 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.3 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP1 | 0.27 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.44 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | N. BERMUDA STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-24 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-27 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-04 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-03-07 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-07 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-21 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-22 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-03-23 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1010 | BARIUM | 0.017 | MG/L | 2.4999 | 2023-03-27 | WTP3 | 0.0024 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-03-27 | WTP3 | 0.025 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-27 | WTP3 | 0.025 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-27 | WTP3 | 0.0005 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-27 | WTP3 | 0.00067 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-27 | WTP3 | 0.0026 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1025 | FLUORIDE | 0.54 | MG/L | 4.0499 | 2023-03-27 | WTP3 | 0.015 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-27 | WTP3 | 0.00011 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-27 | WTP3 | 9e-05 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-27 | WTP3 | 0.002 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-27 | WTP3 | 0.00083 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1052 | SODIUM | 9.9 | MG/L | 160.4999 | 2023-03-27 | WTP3 | 0.59 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-27 | WTP3 | 0.00083 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-27 | WTP3 | 0.00019 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-27 | WTP3 | 0.00021 |  | PARKWAY 1024 Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-03-27 | WTP1 | 0.0072 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1017 | CHLORIDE | 11.5 | MG/L | 250.4999 | 2023-03-27 | WTP1 | 2.5 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-03-27 | WTP1 | 9e-05 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1025 | FLUORIDE | 0.12 | MG/L | 2.0499 | 2023-03-27 | WTP1 | 0.015 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-27 | WTP1 | 0.016 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-03-27 | WTP1 | 0.00093 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-27 | WTP1 | 0.0013 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1055 | SULFATE | 9.3 | MG/L | 250.4999 | 2023-03-27 | WTP1 | 2.5 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-27 | WTP1 | 0.0076 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2023-03-27 | WTP1 | 5 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-03-27 | WTP1 | 1 |  | PH Q
3490766 | LAKE MARIAN RESORT | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 305 | MG/L | 500.4999 | 2021-03-23 | AAA
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-03-23 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-03-23 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-08-09 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-08-09 | AAA |  | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-08-09 | AAA |  | 0.4499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 9.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-08-09 | AAA |  | 6.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-08-09 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-08-09 | AAA |  | 2.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-08-09 | AAA |  | 0.0749 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-08-09 | AAA |  | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-08-09 | AAA |  | 0.9499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-08-09 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-08-09 | AAA |  | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-08-09 | AAA |  | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-08-09 | AAA |  | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-08-09 | AAA |  | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.5 | PCI/L | 15.4999 | 2021-08-09 | AAA |  |  | POE (REVISED SMP DATE FROM 8/11/21 TO 8/9/21-BB)
3490766 | LAKE MARIAN RESORT | N | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2021-08-09 | AAA |  | 1.4999 | POE (REVISED SMP DATE FROM 8/11/21 TO 8/9/21-BB)
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-08-09 | AAA |  | 1.4999 | POE (REVISED SMP DATE FROM 8/11/21 TO 8/9/21-BB)
3490766 | LAKE MARIAN RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-09-01 | AAA | 1.2 |  | RCVD SAMPLER CERT 11/18/21
3490766 | LAKE MARIAN RESORT | N | RAD | 4020 | RADIUM-226 | 1.4 | PCI/L | 3.4999 | 2021-09-01 | AAA | 0.2 | 1.4999 | RCVD SAMPLER CERT 11/18/21
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-09-01 | AAA | 0.7 | 1.4999 | RCVD SAMPLER CERT 11/18/21
3490766 | LAKE MARIAN RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-09-01 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-09-01 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-09-01 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-09-01 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-09-01 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-09-01 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-09-01 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-09-01 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-09-01 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-09-01 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-09-01 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-09-01 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-09-01 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-09-01 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-09-07 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-09-07 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-03 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-03 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-03 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-03 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-03 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-03 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-03 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-03 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-03 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-03 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-03 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-03 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-03 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.3 | PCI/L | 15.4999 | 2021-11-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-11-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-11-03 | AAA | 1.5 | 3.4999 | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-11-03 | AAA | 1.5 |  | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-11-03 | AAA | 0.4 | 0.667 | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-11-03 | AAA | 0.6 | 1.4999 | FLOWERS LAB SMP 489022DW1/KNL SAMPLE 21.17412 (RADS ADDED 2/10/22)
3490766 | LAKE MARIAN RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1010 | BARIUM | 0.0131 | MG/L | 2.4999 | 2021-11-03 | AAA | 0.002 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1020 | CHROMIUM | 0.0013 | MG/L | 0.1499 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-11-03 | AAA | 0.005 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 2.05 | MG/L | 4.0499 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-11-03 | AAA | 0.0001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 160 | MG/L | 500.4999 | 2023-03-27 | WTP1 | 5 |  | PH Q
3490766 | LAKE MARIAN RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-08-09 | AAA |  | 0.5499 | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-03-27 | WTP1 | 0.099 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-03-27 | WTP5 | 0.0072 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1017 | CHLORIDE | 10.3 | MG/L | 250.4999 | 2023-03-27 | WTP5 | 2.5 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1022 | COPPER | 0.0012 | MG/L | 1.4999 | 2023-03-27 | WTP5 | 0.00093 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1025 | FLUORIDE | 0.073 | MG/L | 2.0499 | 2023-03-27 | WTP5 | 0.015 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-27 | WTP5 | 0.016 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1032 | MANGANESE | 0.0014 | MG/L | 0.0549 | 2023-03-27 | WTP5 | 0.00093 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-27 | WTP5 | 0.0013 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1055 | SULFATE | 10.8 | MG/L | 250.4999 | 2023-03-27 | WTP5 | 2.5 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-27 | WTP5 |  |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2023-03-27 | WTP5 | 5 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-03-27 | WTP5 | 1 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-03-27 | WTP5 | 0.099 |  | PH Q 1930 J
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-03-27 | WTP3 | 0.0072 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1017 | CHLORIDE | 14.1 | MG/L | 250.4999 | 2023-03-27 | WTP3 | 2.5 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1022 | COPPER | 0.046 | MG/L | 1.4999 | 2023-03-27 | WTP3 | 0.00093 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1025 | FLUORIDE | 0.54 | MG/L | 2.0499 | 2023-03-27 | WTP3 | 0.015 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-27 | WTP3 | 0.016 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-03-27 | WTP3 | 0.00093 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-27 | WTP3 | 0.0013 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1055 | SULFATE | 18 | MG/L | 250.4999 | 2023-03-27 | WTP3 | 2.5 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-27 | WTP3 |  |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-03-27 | WTP3 | 5 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-03-27 | WTP3 | 1 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 148 | MG/L | 500.4999 | 2023-03-27 | WTP3 | 5 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-03-27 | WTP3 | 0.099 |  | PH Q
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2023-03-27 | WTP1 | 0.0024 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-03-27 | WTP1 | 0.025 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-27 | WTP1 | 0.025 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-27 | WTP1 | 0.0005 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-27 | WTP1 | 0.00067 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-27 | WTP1 | 0.0026 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1025 | FLUORIDE | 0.12 | MG/L | 4.0499 | 2023-03-27 | WTP1 | 0.015 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-27 | WTP1 | 0.00022 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-27 | WTP1 | 9e-05 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-27 | WTP1 | 0.002 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-27 | WTP1 | 0.00083 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1052 | SODIUM | 9.1 | MG/L | 160.4999 | 2023-03-27 | WTP1 | 0.59 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-27 | WTP1 | 0.00083 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-27 | WTP1 | 0.00019 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-27 | WTP1 | 0.00021 |  | N. BERMUDA CYANIDE Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-03-27 | WTP5 | 0.025 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-27 | WTP5 | 0.025 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-27 | WTP5 | 0.0005 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2023-03-27 | WTP5 | 0.0024 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-27 | WTP5 | 0.00067 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-27 | WTP5 | 0.0026 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1025 | FLUORIDE | 0.073 | MG/L | 4.0499 | 2023-03-27 | WTP5 | 0.015 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-27 | WTP5 | 0.00022 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-27 | WTP5 | 9e-05 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-27 | WTP5 | 0.002 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-27 | WTP5 | 0.00083 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1052 | SODIUM | 5.8 | MG/L | 160.4999 | 2023-03-27 | WTP5 | 0.59 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-27 | WTP5 | 0.00083 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-27 | WTP5 | 0.00019 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-27 | WTP5 | 0.00021 |  | CAMELOT WEST 1024Q QUALIFIER
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-05 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-10 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-21 | WTP1 | 0.023 | 0.1499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-03 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-14 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-21 | WTP3 | 3.3 | 9.4999 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-21 | WTP1 | 0.0023 | 0.0149 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP1 | 0.0027 | 0.0249 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP1 | 0.25 | 1.4999 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-21 | WTP1 | 0.49 | 1.4999 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-21 | WTP1 | 0.16 | 0.4499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-21 | WTP1 | 3.3 | 9.4999 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-21 | WTP1 | 0.39 | 0.0749 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-21 | WTP1 | 4.2 | 6.4999 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-21 | WTP1 | 0.36 | 0.6499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-21 | WTP1 | 0.46 | 2.4999 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-21 | WTP1 | 0.46 | 0.6499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-21 | WTP1 | 0.04 | 0.1499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-21 | WTP1 | 0.16 | 0.2499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.056 | UG/L | 54.9999 | 2023-04-21 | WTP1 | 0.024 | 0.1499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-21 | WTP1 | 0.59 | 0.9499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP1 | 0.014 | 0.1499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-21 | WTP1 | 0.053 | 0.2499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-21 | WTP1 | 0.029 | 0.2499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-21 | WTP1 | 0.00088 | 0.0055 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-21 | WTP1 | 0.013 | 0.0449 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP1 | 0.003 | 0.0249 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-21 | WTP1 | 0.096 | 0.1499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-21 | WTP1 | 0.014 | 0.1499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP1 | 0.019 | 0.0249 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-21 | WTP1 | 0.014 | 0.0449 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-21 | WTP1 | 0.044 | 0.1499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP1 | 0.0064 | 0.0249 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-21 | WTP1 | 0.0075 | 0.0149 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-21 | WTP1 | 0.035 | 0.2499 | N. BERMUDA
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-21 | WTP5 | 0.0023 | 0.0149 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP5 | 0.0027 | 0.0249 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-21 | WTP5 | 0.023 | 0.1499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP5 | 0.25 | 1.4999 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-21 | WTP5 | 0.49 | 1.4999 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-21 | WTP5 | 0.16 | 0.4499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-21 | WTP5 | 3.3 | 9.4999 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-21 | WTP5 | 4.2 | 6.4999 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-21 | WTP5 | 0.36 | 0.6499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-21 | WTP5 | 0.46 | 2.4999 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-21 | WTP5 | 0.04 | 0.0749 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-21 | WTP5 | 0.46 | 0.6499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-21 | WTP5 | 0.04 | 0.1499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-21 | WTP5 | 0.16 | 0.2499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.053 | UG/L | 54.9999 | 2023-04-21 | WTP5 | 0.024 | 0.1499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-21 | WTP5 | 0.59 | 0.9499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP5 | 0.014 | 0.1499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-21 | WTP5 | 0.029 | 0.2499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-21 | WTP5 | 0.00072 | 0.0055 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-21 | WTP5 | 0.014 | 0.0449 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP5 | 0.003 | 0.0249 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-21 | WTP5 | 0.096 | 0.1499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-21 | WTP5 | 0.053 | 0.2499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-21 | WTP5 | 0.014 | 0.1499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP5 | 0.019 | 0.0249 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-21 | WTP5 | 0.014 | 0.0449 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-21 | WTP5 | 0.045 | 0.1499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP5 | 0.0064 | 0.0249 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-21 | WTP5 | 0.0075 | 0.0149 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-21 | WTP5 | 0.036 | 0.2499 | CAMELOT WEST WP- DETECT 2042
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-21 | WTP3 | 0.0023 | 0.0149 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP3 | 0.0027 | 0.0249 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-21 | WTP3 | 0.023 | 0.1499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP3 | 0.25 | 1.4999 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-21 | WTP3 | 0.49 | 1.4999 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-21 | WTP3 | 0.16 | 0.4499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-21 | WTP3 | 0.039 | 0.0749 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-21 | WTP3 | 4.2 | 6.4999 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-21 | WTP3 | 0.036 | 0.6499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-21 | WTP3 | 0.46 | 2.4999 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-21 | WTP3 | 0.46 | 0.6499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-21 | WTP3 | 0.04 | 0.1499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-21 | WTP3 | 0.16 | 0.2499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.055 | UG/L | 54.9999 | 2023-04-21 | WTP3 | 0.024 | 0.1499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-21 | WTP3 | 0.59 | 0.9499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP3 | 0.014 | 0.1499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-21 | WTP3 | 0.029 | 0.2499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-21 | WTP3 | 0.00095 | 0.0055 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-21 | WTP3 | 0.013 | 0.0449 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP3 | 0.003 | 0.0249 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-21 | WTP3 | 0.096 | 0.1499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-21 | WTP3 | 0.053 | 0.2499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-21 | WTP3 | 0.014 | 0.1499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP3 | 0.019 | 0.0249 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-21 | WTP3 | 0.014 | 0.0449 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-21 | WTP3 | 0.043 | 0.1499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP3 | 0.0064 | 0.0249 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-21 | WTP3 | 0.0075 | 0.0149 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-21 | WTP3 | 0.035 | 0.2499 | PARKWAY WP- 2033 J 2042 DETECT
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-22 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-23 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.2 | UG/L | 60.4999 | 2023-04-24 | DBP-5 | 0.9
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 61.5 | UG/L | 80.4999 | 2023-04-24 | DBP-5 | 0.47
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.3 | UG/L | 60.4999 | 2023-04-24 | DBP-1 | 0.9
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 44.7 | UG/L | 80.4999 | 2023-04-24 | DBP-1 | 0.47
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.3 | UG/L | 60.4999 | 2023-04-24 | DBP-2 | 0.9
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 61.8 | UG/L | 80.4999 | 2023-04-24 | DBP-2 | 0.47
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.6 | UG/L | 60.4999 | 2023-04-24 | DBP-3 | 0.9
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 58.2 | UG/L | 80.4999 | 2023-04-24 | DBP-3 | 0.47
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.5 | UG/L | 60.4999 | 2023-04-24 | DBP-4 | 0.9
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 63.7 | UG/L | 80.4999 | 2023-04-24 | DBP-4 | 0.47
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25 | UG/L | 60.4999 | 2023-04-24 | DBP-6 | 0.9
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 49.8 | UG/L | 80.4999 | 2023-04-24 | DBP-6 | 0.47
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-02 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-05-06 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-10 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-14 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-17 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-22 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-24 | WTP5 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP5 |  | 1.4999 | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-24 | WTP3 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP3 |  | 1.4999 | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-24 | WTP1 |  |  | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP1 |  | 1.4999 | POE
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-06 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-08 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-09 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-06-16 | WTP1 | 0.005 |  | N. BERMUDA CYNAIDE
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-06-16 | WTP3 | 0.005 |  | PARKWAY WP CYANIDE
3490751 | TOHO WATER AUTHORITY EASTERN | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 122 | MG/L | 500.4999 | 2023-06-16 | WTP5 | 5 |  | CAMELOT WEST WP TOTAL DISSOLVED SOLIDS
3490751 | TOHO WATER AUTHORITY EASTERN | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-06-16 | WTP5 | 0.005 |  | CAMELOT WEST WP- J QUALIFIER ACCEPTED BASED ON QA/QC
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-21 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-23 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-25 | WTP5 |  |  | CAMELOT WEST
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-06 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-06 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-20 | WTP3 |  |  | PARKWAY
3490751 | TOHO WATER AUTHORITY EASTERN | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-21 | WTP1 |  |  | RICHARD MCLAUGHLIN WP (N. BERMUDA)
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 48.2 | UG/L | 80.4999 | 2023-07-26 | DBP-1 | 0.47 |  | L1- 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.5 | UG/L | 60.4999 | 2023-07-26 | DBP-5 | 0.9 |  | L5- 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 61.3 | UG/L | 80.4999 | 2023-07-26 | DBP-5 | 0.47 |  | L5- 1721 BRASSIE CT., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34 | UG/L | 60.4999 | 2023-07-26 | DBP-1 | 0.9 |  | L1- 3250 OWASSA CT
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.5 | UG/L | 60.4999 | 2023-07-26 | DBP-2 | 0.9 |  | L2- 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 53.2 | UG/L | 80.4999 | 2023-07-26 | DBP-2 | 0.47 |  | L2- 1400 RIVIERA DR., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.3 | UG/L | 60.4999 | 2023-07-26 | DBP-3 | 0.9 |  | L3- 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 22.7 | UG/L | 80.4999 | 2023-07-26 | DBP-3 | 0.47 |  | L3- 120 SIMPSON RD., KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.3 | UG/L | 60.4999 | 2023-07-26 | DBP-4 | 0.9 |  | L4-145 EAST LAKESHORE, KISS.
3490751 | TOHO WATER AUTHORITY EASTERN | D | DBP | 2950 | TOTAL THMS | 67.5 | UG/L | 80.4999 | 2023-07-26 | DBP-4 | 0.47 |  | L4-145 EAST LAKESHORE, KISS.
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-01-08 | L5 | 0.64 |  | 1/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0.61 | MG/L | 10.4999 | 2021-01-27 | WTP1 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP1 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-02-05 | L5 |  |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-03-12 | L5 | 0.64 |  | 3/21 BROMATE - SW WP (HLKD) 3/21 BROMATE RAA RCVD SEPARATELY (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-04-02 | L5 | 0.64 |  | 4/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.9 | UG/L | 60.4999 | 2021-04-22 | L1 | 0.9 |  | 2600 EMERALD ISLAND BLVD. (HLKD) | 2
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 31.3 | UG/L | 80.4999 | 2021-04-22 | L1 | 0.47 |  | 2600 EMERALD ISLAND BLVD. (HLKD) | 2
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 1.4 | UG/L | 10.4999 | 2021-05-07 | L5 | 0.22 |  | 5/21 BROMATE - SW WP (HLKD) (6/21 QTR BROMATE RAA RCVD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-07-02 | L5 | 0.22 |  | 7/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.1 | UG/L | 60.4999 | 2021-07-23 | L2 | 0.9 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 28 | UG/L | 80.4999 | 2021-07-23 | L2 | 0.47 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-08-06 | L5 | 0.22 |  | 8/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-09-03 | L5 | 0.22 |  | 9/21 BROMATE - SW WP (HLKD) JQ RESULT ACCEPTED_MFC
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-10-01 | L5 | 0.22 |  | 10/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-12-03 | L5 | 0.22 |  | 12/21 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.94 | UG/L | 10.4999 | 2022-02-04 | L5 | 0.22 |  | 2/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP3 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP3 |  |  | SOUTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0.033 | MG/L | 10.4999 | 2022-02-21 | WTP1 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP1 |  |  | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.72 | UG/L | 10.4999 | 2022-03-04 | L5 | 0.22 |  | 3/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 2 | UG/L | 10.4999 | 2022-04-01 | L5 | 0.22 |  | 4/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.5 | UG/L | 60.4999 | 2022-04-22 | L1 |  |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 27.7 | UG/L | 80.4999 | 2022-04-22 | L1 |  |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-05-20 | L5 | 0.22 |  | 5/22 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-06-03 | L5 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-06-03 | L5 |  |  | 6/3/22 BROMATE - SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-07-01 | L5 |  |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.1 | UG/L | 60.4999 | 2022-07-25 | L2 | 0.9 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 26.9 | UG/L | 80.4999 | 2022-07-25 | L2 | 0.47 |  | 17627 BALI BLVD. (HLKD) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-08-05 | L5 | 0.22 |  | 8/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-10-07 | L5 | 0.22 |  | 10/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-11-09 | L5 | 0.22 |  | 11/22 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-12-02 | L5 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-01-06 | L5 | 0.22 |  | POE BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0.66 | MG/L | 10.4999 | 2023-01-31 | WTP1 | 0.025 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP1 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-02-10 | L5 | 0.22 |  | 2/23 BROMATE - SW WP (HLKD)
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP3 | 0.2 | 0.5499 | SOUTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.2 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP1 | 0.35 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP1 | 0.33 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP1 | 0.11 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.44 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP1 | 0.3 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP1 | 0.12 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP1 | 0.29 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.27 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.3 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP1 | 0.27 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.44 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP1 | 0.4 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP1 | 0.23 | 0.5499 | NORTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP3 | 0.36 | 0.5499 | SOUTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP3 | 0.33 | 0.5499 | SOUTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP3 | 0.11 | 0.5499 | SOUTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3491011 | TOHO WATER AUTHORITY WESTERN | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP3 | 0.44 | 0.5499 | SOUTHWEST STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3490766 | LAKE MARIAN RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-11-03 | AAA | 0.002 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1052 | SODIUM | 41 | MG/L | 160.4999 | 2021-11-03 | AAA | 0.5 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-11-03 | AAA | 0.0005 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1017 | CHLORIDE | 73.8 | MG/L | 250.4999 | 2021-11-03 | AAA | 0.4 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1022 | COPPER | 0.0029 | MG/L | 1.4999 | 2021-11-03 | AAA | 0.001 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1025 | FLUORIDE | 2.05 | MG/L | 2.0499 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1028 | IRON | 0.0601 | MG/L | 0.3499 | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1050 | SILVER | 0.0005 | MG/L | 0.1499 | 2021-11-03 | AAA | 0.0005 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1055 | SULFATE | 8.8 | MG/L | 250.4999 | 2021-11-03 | AAA | 1 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1095 | ZINC | 0.0373 | MG/L | 5.4999 | 2021-11-03 | AAA | 0.002 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-11-03 | AAA | 5 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-11-03 | AAA | 1 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.97 | LN(10) |  | 2021-11-03 | AAA | 0.01 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 374 | MG/L | 500.4999 | 2021-11-03 | AAA | 2.5 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-11-03 | AAA | 0.2 |  | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS" (FLUORIDE 2.05 MG/L, SECONDARY MCL IS 2.0) HLKD 2/1/22
3490766 | LAKE MARIAN RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.5 | 0.5499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA | 6 | 6.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-01-07 | L5 |  |  | SW POE BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-09-02 | L5 | 0.22 |  | 9/22 BROMATE - SW WP (HLKD)
3490766 | LAKE MARIAN RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-03 | AAA | 0.01 | 0.0149 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.01 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-03 | AAA | 0.05 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.5 | 1.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-03 | AAA | 0.1 | 1.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-03 | AAA | 0.4 | 0.4499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 9 | 9.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-03 | AAA | 0.6 | 0.6499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-03 | AAA | 2 | 2.4999 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-03 | AAA | 0.07 | 0.0749 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-03 | AAA | 0.6 | 0.6499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-03 | AAA | 0.2 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-03 | AAA | 0.9 | 0.9499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-03 | AAA | 0.2 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-03 | AAA | 0.01 | 0.0449 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.01 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-03 | AAA | 0.2 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.02 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.04 | 0.0449 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-03 | AAA | 0.1 | 0.1499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-03 | AAA | 0.02 | 0.0249 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-03 | AAA | 0.01 | 0.0149 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-03 | AAA | 0.01 | 0.2499 | FLOWERS LAB SAMPLE 489022DW1, MARKED "TRIENNIALS"
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19 | UG/L | 60.4999 | 2021-11-13 | L1 | 1 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 69.6 | UG/L | 80.4999 | 2021-11-13 | L1 | 0.5 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.8 | UG/L | 60.4999 | 2021-11-13 | L2 | 1 |  | LOT 107 TTHM MCL_NMS | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 82.1 | UG/L | 80.4999 | 2021-11-13 | L2 | 0.5 |  | LOT 107 TTHM MCL_NMS | 3
3490766 | LAKE MARIAN RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-11-09 | AAA |  | 0.0055 | DIOXIN - NOT REQUIRED
3490766 | LAKE MARIAN RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 0.5 | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-01-26 | AAA | 0.01 | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.01 | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-01-26 | AAA | 0.05 | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.5 | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-01-26 | AAA | 0.1 | 1.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-01-26 | AAA | 0.4 | 0.4499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-01-26 | AAA | 9 | 9.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-01-26 | AAA | 6 | 6.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-01-26 | AAA | 0.6 | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-01-26 | AAA | 2 | 2.4999 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-01-26 | AAA | 0.07 | 0.0749 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-01-26 | AAA | 0.6 | 0.6499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-01-26 | AAA | 0.1 | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-01-26 | AAA | 0.1 | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-01-26 | AAA | 0.9 | 0.9499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-01-26 | AAA | 0.1 | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-01-26 | AAA | 0.2 | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-01-26 | AAA | 0.01 | 0.0449 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.01 | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-01-26 | AAA | 0.1 | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-01-26 | AAA | 0.2 | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-01-26 | AAA | 0.1 | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.02 | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-01-26 | AAA | 0.1 | 0.1499 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-01-26 | AAA | 0.02 | 0.0249 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-01-26 | AAA | 0.01 | 0.0149 | POE
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-01-26 | AAA | 0.01 | 0.2499 | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.3 | PCI/L | 15.4999 | 2022-01-26 | AAA |  |  | 1ST QRTR (SAMPLE DATE REVISED FROM 2/1/22 TO 1/26/22 3/16/22, R228 REVISED FROM 0.5 TO -0- 3/16/22)
3490766 | LAKE MARIAN RESORT | N | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2022-01-26 | AAA |  | 1.4999 | 1ST QRTR (SAMPLE DATE REVISED FROM 2/1/22 TO 1/26/22 3/16/22, R228 REVISED FROM 0.5 TO -0- 3/16/22)
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-01-26 | AAA |  | 1.4999 | 1ST QRTR (SAMPLE DATE REVISED FROM 2/1/22 TO 1/26/22 3/16/22, R228 REVISED FROM 0.5 TO -0- 3/16/22)
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.6 | UG/L | 60.4999 | 2022-02-28 | L2 | 1 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 47.3 | UG/L | 80.4999 | 2022-02-28 | L2 | 0.5 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.7 | UG/L | 60.4999 | 2022-02-28 | L1 | 1 |  | LOT 134 (HLKD) | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 25.9 | UG/L | 80.4999 | 2022-02-28 | L1 | 0.5 |  | LOT 134 (HLKD) | 4
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 2.05 | MG/L | 4.0499 | 2022-05-31 | AAA | 0.2 |  | FLUORIDE 2.05 MG/L
3490766 | LAKE MARIAN RESORT | N | SEC | 1025 | FLUORIDE | 2.05 | MG/L | 2.0499 | 2022-05-31 | AAA | 0.2 |  | FLUORIDE 2.05 MG/L (HLKD). SYSTEM UNDER DRAFT CO. NEW WELL IS BEING DRILLED/PERMITTED AT THIS TIME_VPU
3490766 | LAKE MARIAN RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-07-12 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-07-12 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-07-12 | POE |  |  | 2022 ANNUAL N/N SAMPLES_LATE ENTRY_DJ
3490766 | LAKE MARIAN RESORT | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-07-12 | POE |  |  | 2022 ANNUAL N/N SAMPLES_LATE ENTRY_DJ
3490766 | LAKE MARIAN RESORT | S | INOR | 1025 | FLUORIDE | 1.9 | MG/L | 4.0499 | 2022-08-09 | AAA | 0.05 |  | (FL 1.9 MG/L) PAGE 2 OF LAB REPORT NOT SIGNED BY LAB REPRESENTATIVE TO VERIFY RESULTS (HLKD)
3490766 | LAKE MARIAN RESORT | S | SEC | 1025 | FLUORIDE | 1.9 | MG/L | 2.0499 | 2022-08-09 | AAA | 0.05 |  | (FL 1.9 MG/L) PAGE 2 OF LAB REPORT NOT SIGNED BY LAB REPRESENTATIVE TO VERIFY RESULTS (HLKD)
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20 | UG/L | 60.4999 | 2022-08-10 | L1 |  |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 0.5 | UG/L | 80.4999 | 2022-08-10 | L1 |  |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20 | UG/L | 60.4999 | 2022-08-10 | L2 |  |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 0.5 | UG/L | 80.4999 | 2022-08-10 | L2 |  |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-17 | AAA | 0.01 | 0.0449 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-17 | AAA | 0.01 | 0.0249 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-17 | AAA | 0.18 | 0.1499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-17 | AAA | 0.35 | 0.2499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-17 | AAA | 0.1 | 0.1499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-17 | AAA | 0.02 | 0.0249 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-17 | AAA | 0.07 | 0.0449 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-17 | AAA | 0.1 | 0.1499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-17 | AAA | 0.02 | 0.0249 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-17 | AAA | 0.01 | 0.0149 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-17 | AAA | 0.01 | 0.2499 | 26 OF 29 SOC ENT'D (J QUALIFIERS ON METHOXYCHLOR, ENDOTHALL, DINOSEB-NOT ENT'D)
3490766 | LAKE MARIAN RESORT | N | RAD | 4020 | RADIUM-226 | 1.12 | PCI/L | 3.4999 | 2022-08-17 | AAA | 0.328 | 1.4999 | 4002 GA LAB MDL, 4.32, EXCEEDS THE RDL OF 3(MDL MUST BE
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-20 | WTP1 | 0.0023 | 0.0149 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.0027 | 0.0249 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-20 | WTP1 | 0.023 | 0.1499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP1 | 0.26 | 1.4999 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-20 | WTP1 | 0.16 | 0.4499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-20 | WTP1 | 3.3 | 9.4999 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-20 | WTP1 | 4.2 | 6.4999 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-20 | WTP1 | 0.36 | 0.6499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-20 | WTP1 | 0.46 | 2.4999 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-20 | WTP1 | 0.04 | 0.0749 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-20 | WTP1 | 0.46 | 0.6499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-20 | WTP1 | 0.04 | 0.1499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-20 | WTP1 | 0.16 | 0.2499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-04-20 | WTP1 | 0.024 | 0.1499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-20 | WTP1 | 0.59 | 0.9499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP1 | 0.015 | 0.1499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-20 | WTP1 | 0.029 | 0.2499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-20 | WTP1 | 0.00063 | 0.0055 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-20 | WTP1 | 0.014 | 0.0449 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.003 | 0.0249 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-20 | WTP1 | 0.096 | 0.1499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-20 | WTP1 | 0.053 | 0.2499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-20 | WTP1 | 0.015 | 0.1499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.019 | 0.0249 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-20 | WTP1 | 0.014 | 0.0449 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-20 | WTP1 | 0.045 | 0.1499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.0064 | 0.0249 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-20 | WTP1 | 0.0075 | 0.0149 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-20 | WTP1 | 0.036 | 0.2499 | NORTHWEST WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-20 | WTP3 | 0.0023 | 0.0149 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.0027 | 0.0249 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-20 | WTP3 | 0.023 | 0.1499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP3 | 0.25 | 1.4999 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-20 | WTP3 | 0.49 | 1.4999 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-20 | WTP3 | 0.16 | 0.4499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-20 | WTP3 | 4.2 | 6.4999 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-20 | WTP3 | 0.35 | 0.6499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-20 | WTP3 | 0.46 | 2.4999 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-20 | WTP3 | 0.039 | 0.0749 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-20 | WTP3 | 0.46 | 0.6499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-20 | WTP3 | 0.04 | 0.1499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-20 | WTP3 | 0.16 | 0.2499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-04-20 | WTP3 | 0.024 | 0.1499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-20 | WTP3 | 0.59 | 0.9499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP3 | 0.014 | 0.1499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-20 | WTP3 | 0.029 | 0.2499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-20 | WTP3 | 0.0012 | 0.0055 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-20 | WTP3 | 0.013 | 0.0449 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.003 | 0.0249 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-20 | WTP3 | 0.096 | 0.1499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-20 | WTP3 | 0.014 | 0.0449 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-20 | WTP3 | 0.053 | 0.2499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-20 | WTP3 | 0.014 | 0.1499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.019 | 0.0249 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-20 | WTP3 | 0.045 | 0.1499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.0066 | 0.0249 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-20 | WTP3 | 0.0077 | 0.0149 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-20 | WTP3 | 0.036 | 0.2499 | SOUTHWEST WP (ENDOTHALL J QUALIFIER PER FORMAT PAGES-NOT ENT'D) SEE QC PAGE 33 OF 41 (25TH PAGE DOWN IN SCAN) REGARDING "MISSING PRESERVATIVES"- J QUALIFIER ACCEPTES_SG 6/6/2023
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.2 | UG/L | 60.4999 | 2023-04-24 | L1 | 0.9 |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 37.4 | UG/L | 80.4999 | 2023-04-24 | L1 | 0.47 |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-05-12 | L5 | 0.22 |  | 5-23 BROMATE - SW WP
3491011 | TOHO WATER AUTHORITY WESTERN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2023-05-24 | WTP3 | 2.57 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP3 |  | 1.4999 | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-24 | WTP1 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP1 |  | 1.4999 | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-06-09 | L5 | 0.22 |  | POE BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-06-16 | WTP1 | 0.005 |  | WOODLARK WP4 POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-07-07 | L5 | 0.22 |  | POE BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.3 | UG/L | 60.4999 | 2023-07-26 | L2 | 0.9 |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 33 | UG/L | 80.4999 | 2023-07-26 | L2 | 0.47 |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.68 | UG/L | 10.4999 | 2023-08-04 | L5 | 0.22 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.56 | UG/L | 10.4999 | 2023-09-08 | L5 | 0.22 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-27 | WTP1 | 0.26 | 1.4999 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-27 | WTP1 | 0.0023 | 0.0149 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP1 | 0.0026 | 0.0249 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-27 | WTP1 | 0.023 | 0.1499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-27 | WTP1 | 0.49 | 1.4999 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-27 | WTP1 | 0.16 | 0.4499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-27 | WTP1 | 3.3 | 9.4999 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-27 | WTP1 | 4.2 | 6.4999 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-27 | WTP1 | 0.35 | 0.6499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-27 | WTP1 | 0.46 | 2.4999 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-27 | WTP1 | 0.038 | 0.0749 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-27 | WTP1 | 0.45 | 0.6499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-27 | WTP1 | 0.04 | 0.1499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-27 | WTP1 | 0.16 | 0.2499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-27 | WTP1 | 0.023 | 0.1499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-27 | WTP1 | 0.59 | 0.9499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-27 | WTP1 | 0.014 | 0.1499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-27 | WTP1 | 0.028 | 0.2499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-27 | WTP1 | 0.013 | 0.0449 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP1 | 0.0029 | 0.0249 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-27 | WTP1 | 0.096 | 0.1499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-27 | WTP1 | 0.053 | 0.2499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-27 | WTP1 | 0.014 | 0.1499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP1 | 0.019 | 0.0249 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-27 | WTP1 | 0.014 | 0.0449 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-27 | WTP1 | 0.046 | 0.1499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP1 | 0.0066 | 0.0249 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-27 | WTP1 | 0.0078 | 0.0149 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-27 | WTP1 | 0.036 | 0.2499 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-27 | WTP3 | 0.0022 | 0.0149 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP3 | 0.0026 | 0.0249 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-27 | WTP3 | 0.022 | 0.1499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-27 | WTP3 | 0.25 | 1.4999 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-27 | WTP3 | 0.49 | 1.4999 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-27 | WTP3 | 0.16 | 0.4499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-27 | WTP3 | 3.3 | 9.4999 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-27 | WTP3 | 4.2 | 6.4999 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-27 | WTP3 | 0.35 | 0.6499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-27 | WTP3 | 0.46 | 2.4999 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-27 | WTP3 | 0.038 | 0.0749 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-27 | WTP3 | 0.45 | 0.6499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-27 | WTP3 | 0.04 | 0.1499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-27 | WTP3 | 0.16 | 0.2499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-27 | WTP3 | 0.023 | 0.1499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-27 | WTP3 | 0.59 | 0.9499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-27 | WTP3 | 0.014 | 0.1499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-27 | WTP3 | 0.028 | 0.2499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-27 | WTP3 | 0.0031 | 0.0055 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-27 | WTP3 | 0.013 | 0.0449 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP3 | 0.0029 | 0.0249 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-27 | WTP3 | 0.096 | 0.1499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-27 | WTP3 | 0.053 | 0.2499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-27 | WTP3 | 0.015 | 0.1499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP3 | 0.019 | 0.0249 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-27 | WTP3 | 0.014 | 0.0449 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-27 | WTP3 | 0.044 | 0.1499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-27 | WTP3 | 0.0065 | 0.0249 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-27 | WTP3 | 0.0076 | 0.0149 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-27 | WTP3 | 0.035 | 0.2499 | SW PLANT SECOND SET OF SOC, LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-27 | WTP1 | 0.0023 | 0.0055 | NW PLANT, SECOND SET OF SOC LMC
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-10-06 | L5 | 0.22 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-11-03 | L5 | 0.22 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-12-01 | L5 | 0.22 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-30 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP3 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0.047 | MG/L | 10.4999 | 2024-01-30 | WTP1 | 0.025 |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP1 |  |  | POE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-02-02 | L5 | 0.22 |  | POE-SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-03-01 | L5 | 0.22 |  | POE SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.96 | UG/L | 10.4999 | 2024-04-05 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2024-04-22 | L1 | 0.9 |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 42.1 | UG/L | 80.4999 | 2024-04-22 | L1 | 0.75 |  | 2600 EMERALD ISLAND | 2
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-05-03 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.77 | UG/L | 10.4999 | 2024-06-07 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-07-12 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.8 | UG/L | 60.4999 | 2024-07-23 | L2 | 0.9 |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 57.3 | UG/L | 80.4999 | 2024-07-23 | L2 | 0.75 |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-08-09 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-10-04 | L5 | 0.22 |  | SOUTHWEST - BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-11-01 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-12-06 | L5 | 0.22 |  | POE SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-01-03 | L5 | 0.22 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-02-14 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.69 | UG/L | 10.4999 | 2025-03-07 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-14 | WTP3 | 0 |  | SOUTHWEST WP SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP3 | 0 |  | SOUTHWEST WP SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1040 | NITRATE | 0.069 | MG/L | 10.4999 | 2025-03-14 | WTP1 | 0.025 |  | NORTHWEST WP NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP1 | 0 |  | NORTHWEST WP NORTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.9 | UG/L | 60.4999 | 2025-04-24 | L1 | 0.9 |  | 2600 EMERALD ISLAND BLVD | 2
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 39 | UG/L | 80.4999 | 2025-04-24 | L1 | 0.75 |  | 2600 EMERALD ISLAND BLVD | 2
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 1.4 | UG/L | 10.4999 | 2025-05-02 | L5 | 0.22 |  | POE-SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-06-06 | L5 | 0.22 |  | POE - SOUTHWEST - BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-07-03 | L5 | 0.22 |  | POE SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 5.7 | UG/L | 10.4999 | 2025-07-03 | L5 | 1.1 |  | POE SUNBRIDGE
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.3 | UG/L | 60.4999 | 2025-07-25 | L2 | 0.9 |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | D | DBP | 2950 | TOTAL THMS | 45.5 | UG/L | 80.4999 | 2025-07-25 | L2 | 0.75 |  | 17627 BALI BLVD. (TEST T/H 7/22/15-R.M) | 3
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-08-01 | L5 | 0.22 |  | SOUTHWEST- BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-09-05 | L5 | 0.22 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-10-03 | L5 | 0.22 |  | BROMATE
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-11-07 | L5 | 0.48 |  | POE BROMATE
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-01-26 | AAA | 0.041 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-01-26 | AAA | 0.48 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-01-26 | AAA | 0.04 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-01-26 | AAA | 0.16 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-01-26 | AAA | 0.025 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-01-26 | AAA | 0.59 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-01-26 | AAA | 0.015 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-01-26 | AAA | 0.03 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-01-26 | AAA | 0.014 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-01-26 | AAA | 0.0031 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-01-26 | AAA | 0.096 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-01-26 | AAA | 0.059 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-01-26 | AAA | 0.015 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-01-26 | AAA | 0.02 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-01-26 | AAA | 0.014 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-01-26 | AAA | 0.044 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-01-26 | AAA | 0.0067 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-01-26 | AAA | 0.0078 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-01-26 | AAA | 0.035 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-07 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-02-19 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2024-02-19 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-03-14 | AAA |  | 0.5499 | POE
3490766 | LAKE MARIAN RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-04-26 | AAA |  | 1.4999 | 2Q2024 RESULTS
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-09-06 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0.76 | UG/L | 10.4999 | 2025-04-04 | L5 | 0.22 |  | SOUTHWEST
3491011 | TOHO WATER AUTHORITY WESTERN | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-12-05 | L5 | 0.48 |  | BROMATE- SOUTHWEST
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.3 | UG/L | 60.4999 | 2024-02-16 | L1 | 0.9 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 1.2 | UG/L | 80.4999 | 2024-02-16 | L1 | 0.47 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.5 | UG/L | 60.4999 | 2024-02-16 | L2 | 0.9 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 25.1 | UG/L | 80.4999 | 2024-02-16 | L2 | 0.47 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 0.49 | MG/L | 4.0499 | 2024-03-06 | AAA | 0.015 |  | 2024 N/N, 1Q24 FLUORIDE
3490766 | LAKE MARIAN RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-03-06 | AAA | 0.38 |  | 2024 N/N, 1Q24 FLUORIDE
3490766 | LAKE MARIAN RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-06 | AAA | 0.38 |  | 2024 N/N, 1Q24 FLUORIDE
3490766 | LAKE MARIAN RESORT | N | SEC | 1025 | FLUORIDE | 0.49 | MG/L | 2.0499 | 2024-03-06 | AAA | 0.15 |  | 1Q24 FLUORIDE
3490766 | LAKE MARIAN RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-04-26 | AAA |  |  | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2024-04-26 | AAA |  | 1.4999 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-04-26 | AAA |  | 0.0149 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-04-26 | AAA |  | 0.0249 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-04-26 | AAA |  | 0.1499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-04-26 | AAA |  | 1.4999 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-04-26 | AAA |  | 1.4999 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-04-26 | AAA |  | 0.4499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-04-26 | AAA |  | 9.4999 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-04-26 | AAA |  | 6.4999 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-04-26 | AAA |  | 0.6499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-04-26 | AAA |  | 2.4999 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-04-26 | AAA |  | 0.0749 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-04-26 | AAA |  | 0.6499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-04-26 | AAA |  | 0.1499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-04-26 | AAA |  | 0.2499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-04-26 | AAA |  | 0.1499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-04-26 | AAA |  | 0.9499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-04-26 | AAA |  | 0.1499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-04-26 | AAA |  | 0.2499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-04-26 | AAA |  | 0.0449 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-04-26 | AAA |  | 0.0249 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-04-26 | AAA |  | 0.1499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-04-26 | AAA |  | 0.2499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-04-26 | AAA |  | 0.1499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-04-26 | AAA |  | 0.0249 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-04-26 | AAA |  | 0.0449 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-04-26 | AAA |  | 0.1499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-04-26 | AAA |  | 0.0249 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-04-26 | AAA |  | 0.0149 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-04-26 | AAA |  | 0.2499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-04-26 | AAA |  | 0.5499 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-04-26 | AAA |  | 0.667 | 2Q2024 RESULTS
3490766 | LAKE MARIAN RESORT | N | INOR | 1052 | SODIUM | 0 | MG/L | 160.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | SEC | 1002 | ALUMINUM | 0.021 | MG/L | 0.2499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1017 | CHLORIDE | 87.8 | MG/L | 250.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1022 | COPPER | 0.044 | MG/L | 1.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1025 | FLUORIDE | 0.5 | MG/L | 2.0499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1055 | SULFATE | 32.1 | MG/L | 250.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1095 | ZINC | 0.018 | MG/L | 5.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 264 | MG/L | 500.4999 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL SAMPLES (PH Q QUALIFIED, ACCEPTED) (FOAMING AGENTS J QUALIFIED, ACCEPTED)
3490766 | LAKE MARIAN RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1010 | BARIUM | 0.0034 | MG/L | 2.4999 | 2024-04-26 | AAA | 0.0024 |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-04-26 | AAA |  |  | 2024 TRIENNIAL INORGANIC RESULTS (CYANIDE J QUALIFIED, BIASED LOW NOT ACCEPTED) CYANIDE MAKEUP SAMPLE NEEDED
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.59 | UG/L | 60.4999 | 2024-05-20 | L1 | 0.98 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 6.33 | UG/L | 80.4999 | 2024-05-20 | L1 | 0.45 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.27 | UG/L | 60.4999 | 2024-05-20 | L2 | 0.98 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 21.67 | UG/L | 80.4999 | 2024-05-20 | L2 | 0.45 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | N | INOR | 1025 | FLUORIDE | 1.3 | MG/L | 4.0499 | 2024-05-31 | AAA | 0.1 |  | POE
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.44 | UG/L | 60.4999 | 2024-08-19 | L2 | 0.89 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 20.54 | UG/L | 80.4999 | 2024-08-19 | L2 | 0.45 |  | LOT 107 | 3
3490766 | LAKE MARIAN RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.69 | UG/L | 60.4999 | 2024-08-19 | L1 | 0.89 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | D | DBP | 2950 | TOTAL THMS | 20.32 | UG/L | 80.4999 | 2024-08-19 | L1 | 0.45 |  | LOT 134 | 4
3490766 | LAKE MARIAN RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-08-19 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-11-25 | AAA |  |  | POE
3490766 | LAKE MARIAN RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-25 | AAA |  |  | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.65 | UG/L | 60.4999 | 2021-08-27 | L1 |  |  |  | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 4.58 | UG/L | 80.4999 | 2021-08-27 | L1 |  |  |  | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0.094 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.0095 | MG/L | 2.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.22 | MG/L | 4.0499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 36 | MG/L | 160.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 47 | MG/L | 250.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.22 | MG/L | 2.0499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 13 | MG/L | 250.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1905 | COLOR | 11 | COLOR UNITS | 15.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.87 | LN(10) |  | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 286 | MG/L | 500.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0.05 |  | 0.5499 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-10-26 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1040 | NITRATE | 0.03 | MG/L | 10.4999 | 2021-01-19 | AAA | 0.03
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1041 | NITRITE | 0.018 | MG/L | 1.4999 | 2021-01-19 | AAA | 0.018
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2023-01-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1040 | NITRATE | 0.039 | MG/L | 10.4999 | 2024-01-09 | AAA | 0.024 |  | POE
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-09 | AAA |  |  | POE
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2025-01-06 | AAA | 0.024 |  | POE
3490775 | LAKEVIEW TERRACE TRAILER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-06 | AAA |  |  | POE
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2950 | TOTAL THMS | 21.8 | UG/L | 80.4999 | 2021-09-23 | L1 |  |  |  | 3
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.9 | UG/L | 60.4999 | 2021-09-23 | L1 |  |  |  | 3
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2015 | METHOXYCLOR | 0.05 | UG/L | 44.9999 | 2021-11-17 | AAA | 0.05 | 0.1499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2005 | ENDRIN | 0.01 | UG/L | 2.4999 | 2021-11-17 | AAA | 0.01 | 0.0149
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2010 | LINDANE | 0.01 | UG/L | 0.2499 | 2021-11-17 | AAA | 0.01 | 0.0249
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2005 | ENDRIN | 0.01 | UG/L | 2.4999 | 2021-11-17 | AAA | 0.01 | 0.0149
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2010 | LINDANE | 0.01 | UG/L | 0.2499 | 2021-11-17 | AAA | 0.01 | 0.0249
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2020 | TOXAPHENE | 0.5 | UG/L | 3.4999 | 2021-11-17 | AAA | 0.5 | 1.4999
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2031 | DALAPON | 0.1 | UG/L | 249.9999 | 2021-11-17 | AAA | 0.1 | 1.4999
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2032 | DIQUAT | 0.4 | UG/L | 24.9999 | 2021-11-17 | AAA | 0.4 | 0.4499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2033 | ENDOTHALL | 9 | UG/L | 149.9999 | 2021-11-17 | AAA | 9 | 9.4999
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2034 | GLYPHOSATE | 6 | UG/L | 749.9999 | 2021-11-17 | AAA | 6 | 6.4999
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0.6 | UG/L | 449.9999 | 2021-11-17 | AAA | 0.6 | 0.6499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 2 | UG/L | 249.9999 | 2021-11-17 | AAA | 2 | 2.4999
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2037 | SIMAZINE | 0.07 | UG/L | 4.4999 | 2021-11-17 | AAA | 0.07 | 0.0749
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0.6 | UG/L | 6.4999 | 2021-11-17 | AAA | 0.6 | 0.6499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2040 | PICLORAM | 0.1 | UG/L | 549.9999 | 2021-11-17 | AAA | 0.1 | 0.1499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2041 | DINOSEB | 0.2 | UG/L | 7.4999 | 2021-11-17 | AAA | 0.2 | 0.2499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.1 | UG/L | 54.9999 | 2021-11-17 | AAA | 0.1 | 0.1499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2046 | CARBOFURAN | 0.9 | UG/L | 44.9999 | 2021-11-17 | AAA | 0.9 | 0.9499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2050 | ATRAZINE | 0.1 | UG/L | 3.4999 | 2021-11-17 | AAA | 0.1 | 0.1499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0.2 | UG/L | 2.4999 | 2021-11-17 | AAA | 0.2 | 0.2499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2065 | HEPTACHLOR | 0.01 | UG/L | 0.4499 | 2021-11-17 | AAA | 0.01 | 0.0449
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0.01 | UG/L | 0.2499 | 2021-11-17 | AAA | 0.01 | 0.0249
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2105 | 2,4-D | 0.1 | UG/L | 74.9999 | 2021-11-17 | AAA | 0.1 | 0.1499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0.2 | UG/L | 54.9999 | 2021-11-17 | AAA | 0.2 | 0.2499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0.1 | UG/L | 1.4999 | 2021-11-17 | AAA | 0.1 | 0.1499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0.02 | UG/L | 0.2499 | 2021-11-17 | AAA | 0.02 | 0.0249
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0.04 | UG/L | 1.4999 | 2021-11-17 | AAA | 0.04 | 0.0449
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0.1 | UG/L | 0.5499 | 2021-11-17 | AAA | 0.1 | 0.1499
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0.02 | UG/L | 0.2499 | 2021-11-17 | AAA | 0.02 | 0.0249
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0.01 | UG/L | 0.0249 | 2021-11-17 | AAA | 0.01 | 0.0149
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2959 | CHLORDANE | 0.01 | UG/L | 2.4999 | 2021-11-17 | AAA | 0.01 | 0.2499
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1010 | BARIUM | 0.0098 | MG/L | 2.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1052 | SODIUM | 5 | MG/L | 160.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1017 | CHLORIDE | 7.75 | MG/L | 250.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1055 | SULFATE | 8.11 | MG/L | 250.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1095 | ZINC | 0.0041 | MG/L | 5.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.13 | LN(10) |  | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 132 | MG/L | 500.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1040 | NITRATE | 0.12 | MG/L | 10.4999 | 2023-01-03 | AAA | 0.024 |  | 2023 N/N RESULTS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-03 | AAA | 0.0034 |  | 2023 N/N RESULTS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1040 | NITRATE | 1.3 | MG/L | 10.4999 | 2022-05-04 | AAA | 0.03
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-05-04 | AAA | 0.018
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1030 | LEAD | 0.0006 | MG/L | 0.0154 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1052 | SODIUM | 8.8 | MG/L | 160.4999 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-30 | AAA |  |  | 2024 INORGS
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1017 | CHLORIDE | 11 | MG/L | 250.4999 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1022 | COPPER | 0.0073 | MG/L | 1.4999 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1055 | SULFATE | 8.9 | MG/L | 250.4999 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1905 | COLOR | 13 | COLOR UNITS | 15.4999 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1920 | ODOR THRESHOLD | 1.4 |  | 3.4999 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.19 | LN(10) |  | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 130 | MG/L | 500.4999 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SEC | 2905 | FOAMING AGENTS | 0.057 |  | 0.5499 | 2024-09-30 | AAA |  |  | 2024 SEC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-09-30 | AAA |  | 0.0149 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-09-30 | AAA |  | 0.0249 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-09-30 | AAA |  | 0.1499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-09-30 | AAA |  | 1.4999 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-09-30 | AAA |  | 1.4999 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-09-30 | AAA |  | 0.4499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-09-30 | AAA |  | 9.4999 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-09-30 | AAA |  | 6.4999 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-09-30 | AAA |  | 0.6499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-09-30 | AAA |  | 2.4999 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-09-30 | AAA |  | 0.0749 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-09-30 | AAA |  | 0.6499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-09-30 | AAA |  | 0.9499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-09-30 | AAA |  | 0.1499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-09-30 | AAA |  | 0.2499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-09-30 | AAA |  | 0.1499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-09-30 | AAA |  | 0.1499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-09-30 | AAA |  | 0.2499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-09-30 | AAA |  | 0.0055 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-09-30 | AAA |  | 0.0449 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-09-30 | AAA |  | 0.0249 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-09-30 | AAA |  | 0.1499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-09-30 | AAA |  | 0.2499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-09-30 | AAA |  | 0.1499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-09-30 | AAA |  | 0.0249 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-09-30 | AAA |  | 0.0449 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-09-30 | AAA |  | 0.1499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-09-30 | AAA |  | 0.0249 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-09-30 | AAA |  | 0.0149 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-09-30 | AAA |  | 0.2499 | 2024 SOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-30 | AAA |  | 0.5499 | 2024 VOC
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.95 | UG/L | 60.4999 | 2024-11-25 | L1 | 0.98 |  | 2024 MAKEUP SAMPLES | 3
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2950 | TOTAL THMS | 14.27 | UG/L | 80.4999 | 2024-11-25 | L1 | 0.44 |  | 2024 MAKEUP SAMPLES | 3
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.98 | UG/L | 60.4999 | 2024-11-25 | L2 | 0.98 |  | 2024 MAKEUP SAMPLES | 3
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2950 | TOTAL THMS | 14.08 | UG/L | 80.4999 | 2024-11-25 | L2 | 0.44 |  | 2024 MAKEUP SAMPLES | 3
3490816 | GREAT OAK R.V. RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-12-23 | AAA | 0.7 | 1.4999 | 2024 RADS
3490816 | GREAT OAK R.V. RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.2 | PCI/L | 15.4999 | 2024-12-23 | AAA | 1.1 |  | 2024 RADS
3490816 | GREAT OAK R.V. RESORT | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-12-23 | AAA | 0.2 | 0.667 | 2024 RADS
3490816 | GREAT OAK R.V. RESORT | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2024-12-23 | AAA | 0.2 | 1.4999 | 2024 RADS
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.2 | UG/L | 60.4999 | 2025-09-17 | L1 | 0.9 |  | LOT A-26 & LOT B25 | 3
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2950 | TOTAL THMS | 19.9 | UG/L | 80.4999 | 2025-09-17 | L1 | 0.75 |  | LOT A-26 & LOT B25 | 3
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.3 | UG/L | 60.4999 | 2025-09-17 | L2 |  |  | LOT A-26 & LOT B25 | 3
3490816 | GREAT OAK R.V. RESORT | D | DBP | 2950 | TOTAL THMS | 16.3 | UG/L | 80.4999 | 2025-09-17 | L2 |  |  | LOT A-26 & LOT B25 | 3
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-12-23 | AAA |  |  | 2025 N/N
3490816 | GREAT OAK R.V. RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-12-23 | AAA |  |  | 2025 N/N
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-26 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-26 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-26 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-26 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-26 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-26 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-26 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-26 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-26 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-26 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-26 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-26 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-26 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-26 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.7 | PCI/L | 15.4999 | 2021-10-26 | AAA | 1.6 |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0.0002 | PCI/L | 20.4999 | 2021-10-26 | AAA | 0.0002 | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2021-10-26 | AAA | 0.6 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0.7 | PCI/L | 2.4999 | 2021-10-26 | AAA | 0.7 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-02-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-06-07 | AAA |  | 1.4999 | IDENTIFIED AS SPECIAL
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0.9 | UG/L | 249.9999 | 2022-07-19 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.68 | UG/L | 60.4999 | 2022-08-10 | L1 | 0.98 |  | NORTH PAVILION (HLKD) **HIGH TTHMS 103.89 UG/L** | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 103.89 | UG/L | 80.4999 | 2022-08-10 | L1 | 0.39 |  | NORTH PAVILION (HLKD) **HIGH TTHMS 103.89 UG/L** | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 2.3 | UG/L | 249.9999 | 2022-11-07 | AAA | 0.9 | 1.4999
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.05 | UG/L | 60.4999 | 2022-11-21 | L1 | 0.98 |  | NORTH PAVILION TTHM HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 68.43 | UG/L | 80.4999 | 2022-11-21 | L1 | 0.39 |  | NORTH PAVILION TTHM HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.08 | UG/L | 60.4999 | 2022-11-21 | L2 | 0.98 |  | 1311 HASKER CIRCLE TTHM HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 67.95 | UG/L | 80.4999 | 2022-11-21 | L2 | 0.39 |  | 1311 HASKER CIRCLE TTHM HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.05 | UG/L | 60.4999 | 2023-05-17 | L1 | 0.98 |  |  | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 64.8 | UG/L | 80.4999 | 2023-05-17 | L1 | 0.39 |  |  | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.58 | UG/L | 60.4999 | 2023-05-17 | L2 | 0.98 |  |  | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 66.83 | UG/L | 80.4999 | 2023-05-17 | L2 | 0.39 |  |  | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.91 | UG/L | 60.4999 | 2023-08-19 | L1 |  |  | TTHM/HAA5 NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.47 | UG/L | 60.4999 | 2023-08-19 | L2 |  |  | TTHM/HAA5 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 41.6 | UG/L | 80.4999 | 2023-08-19 | L2 |  |  | TTHM/HAA5 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.17 | UG/L | 60.4999 | 2023-11-21 | L2 | 0.98 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 46.91 | UG/L | 80.4999 | 2023-11-21 | L2 | 0.39 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.95 | UG/L | 60.4999 | 2024-03-13 | L2 | 0.98 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | S | DBP | 2950 | TOTAL THMS | 33.37 | UG/L | 80.4999 | 2024-03-13 | L2 | 0.39 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-13 | AAA |  |  | DIST- POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-03-26 | AAA |  | 1.4999 | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-05-15 | AAA | 0.9 | 1.4999 | 2Q2024 DALAPON
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.7 | UG/L | 60.4999 | 2024-08-21 | L1 | 0.3 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 2.61 | UG/L | 80.4999 | 2024-08-21 | L1 | 0.5 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.6 | UG/L | 60.4999 | 2024-08-21 | L2 | 0.3 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 2.48 | UG/L | 80.4999 | 2024-08-21 | L2 | 0.5 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 39.97 | UG/L | 80.4999 | 2023-08-19 | L1 |  |  | TTHM AT L1 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.0095 | MG/L | 2.4999 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0.0012 | MG/L | 0.1499 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 39 | MG/L | 160.4999 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-24 | AAA |  |  | 2024 INORG RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 53 | MG/L | 250.4999 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0.0019 | MG/L | 1.4999 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0.0021 | MG/L | 0.0549 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 13 | MG/L | 250.4999 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0.0048 | MG/L | 5.4999 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 5 |  | 3.4999 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.1 | LN(10) |  | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 240 | MG/L | 500.4999 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-09-24 | AAA |  |  | 2024 SEC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-24 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-09-24 | AAA |  | 0.0149 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-09-24 | AAA |  | 0.0249 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-09-24 | AAA |  | 0.1499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-09-24 | AAA |  | 1.4999 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 1.8 | UG/L | 249.9999 | 2024-09-24 | AAA |  | 1.4999 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-09-24 | AAA |  | 0.4499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-09-24 | AAA |  | 9.4999 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-09-24 | AAA |  | 6.4999 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-09-24 | AAA |  | 0.6499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-09-24 | AAA |  | 2.4999 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-09-24 | AAA |  | 0.0749 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-09-24 | AAA |  | 0.6499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-09-24 | AAA |  | 0.1499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-09-24 | AAA |  | 0.2499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-09-24 | AAA |  | 0.1499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-09-24 | AAA |  | 0.9499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-09-24 | AAA |  | 0.1499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-09-24 | AAA |  | 0.2499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-09-24 | AAA |  | 0.0449 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-09-24 | AAA |  | 0.0249 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-09-24 | AAA |  | 0.1499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-09-24 | AAA |  | 0.2499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-09-24 | AAA |  | 0.1499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-09-24 | AAA |  | 0.0249 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-09-24 | AAA |  | 0.0449 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-09-24 | AAA |  | 0.1499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-09-24 | AAA |  | 0.0249 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-09-24 | AAA |  | 0.0149 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-09-24 | AAA |  | 0.2499 | 2024 SOC RESULTS
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.6 | UG/L | 60.4999 | 2025-02-14 | L1 | 0.2 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 9.6 | UG/L | 80.4999 | 2025-02-14 | L1 | 0.5 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.8 | UG/L | 60.4999 | 2025-02-14 | L2 | 0.2 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 11.26 | UG/L | 80.4999 | 2025-02-14 | L2 | 0.5 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0.062 | UG/L | 249.9999 | 2025-02-14 | AAA | 0.022 | 1.4999 | POE LRM - DETECT
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-05-15 | AAA |  |  | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-05-21 | AAA |  | 1.4999 | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.3 | UG/L | 60.4999 | 2025-05-21 | L1 | 0.2 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 14.95 | UG/L | 80.4999 | 2025-05-21 | L1 | 0.21 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.7 | UG/L | 60.4999 | 2025-05-21 | L2 | 0.2 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 14.87 | UG/L | 80.4999 | 2025-05-21 | L2 | 0.21 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-08-21 | AAA |  | 1.4999 | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29 | UG/L | 60.4999 | 2025-08-21 | L1 | 0.2 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 40.3 | UG/L | 80.4999 | 2025-08-21 | L1 | 0.21 |  | NORTH PAVILION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29 | UG/L | 60.4999 | 2025-08-21 | L2 | 0.2 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 38.8 | UG/L | 80.4999 | 2025-08-21 | L2 | 0.21 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.1 | UG/L | 60.4999 | 2025-11-18 | L1 |  |  | NORTH PAVILLION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 16.9 | UG/L | 80.4999 | 2025-11-18 | L1 |  |  | NORTH PAVILLION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-11-18 | AAA |  | 1.4999 | POE
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.9 | UG/L | 60.4999 | 2025-11-18 | L2 | 0.2 |  | 1311 HASKER CIRCLE | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 15.43 | UG/L | 80.4999 | 2025-11-18 | L2 | 0.21 |  | 1311 HASKER CIRCLE | 3
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-01-06 | AAA |  | 0.5499 | 1AM - TOTAL XYLENE. 2AM DUE 1Q2022_VPU
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-04-09 | AAA | 0.042
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1017 | CHLORIDE | 14.3 | MG/L | 250.4999 | 2021-04-09 | AAA | 2.5
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1022 | COPPER | 0.0028 | MG/L | 1.4999 | 2021-04-09 | AAA | 0.0026
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1025 | FLUORIDE | 0.25 | MG/L | 2.0499 | 2021-04-09 | AAA | 0.015
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1028 | IRON | 0.035 | MG/L | 0.3499 | 2021-04-09 | AAA | 0.016
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1032 | MANGANESE | 0.0037 | MG/L | 0.0549 | 2021-04-09 | AAA | 0.0012
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-04-09 | AAA | 0.0015
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1055 | SULFATE | 32.6 | MG/L | 250.4999 | 2021-04-09 | AAA | 2.5
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-04-09 | AAA | 0.0076
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-04-09 | AAA | 5
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-04-09 | AAA | 1
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.1 | LN(10) |  | 2021-04-09 | AAA | 0.1
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 246 | MG/L | 500.4999 | 2021-04-09 | AAA | 5
3490986 | PLEASANT HILL VILLAGE | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-04-09 | AAA | 0.099
3490986 | PLEASANT HILL VILLAGE | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-04-09 | AAA | 2.86
3490986 | PLEASANT HILL VILLAGE | N | RAD | 4020 | RADIUM-226 | 1.12 | PCI/L | 3.4999 | 2021-04-09 | AAA | 0.44 | 1.4999
3490986 | PLEASANT HILL VILLAGE | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-09 | AAA | 0.83 | 1.4999
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-09 | AAA | 0.0054 | 0.0149 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.0065 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-09 | AAA | 0.023 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.67 | 1.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2031 | DALAPON | 0.32 | UG/L | 249.9999 | 2021-04-09 | AAA | 0.23 | 1.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-04-09 | AAA | 0.16 | 0.4499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 3.3 | 9.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA | 4.2 | 6.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-04-09 | AAA | 0.36 | 0.6499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-04-09 | AAA | 0.46 | 2.4999 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-09 | AAA | 0.039 | 0.0749 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-09 | AAA | 0.46 | 0.6499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-04-09 | AAA | 0.04 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-04-09 | AAA | 0.16 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-09 | AAA | 0.024 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-04-09 | AAA | 0.59 | 0.9499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.014 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-09 | AAA | 0.029 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-09 | AAA | 0.013 | 0.0449 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.003 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-04-09 | AAA | 0.096 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-04-09 | AAA | 0.053 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.014 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.019 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.014 | 0.0449 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-04-09 | AAA | 0.043 | 0.1499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA | 0.0065 | 0.0249 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-04-09 | AAA | 0.0076 | 0.0149 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-04-09 | AAA | 0.035 | 0.2499 | SOC (DALAPON 0.32 UG/L, DOES NOT EXCEED RDL OF 1 UG/L)
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-04-09 | AAA | 0.025
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-09 | AAA | 0.025
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-04-09 | AAA | 0.0005
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1010 | BARIUM | 0.026 | MG/L | 2.4999 | 2021-04-09 | AAA | 0.0023
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-04-09 | AAA | 0.00024
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-04-09 | AAA | 0.00081
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-04-09 | AAA | 0.005
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1025 | FLUORIDE | 0.25 | MG/L | 4.0499 | 2021-04-09 | AAA | 0.015
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-04-09 | AAA | 0.00022
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-04-09 | AAA | 9e-05
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-04-09 | AAA | 0.002
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-04-09 | AAA | 0.00083
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1052 | SODIUM | 12.6 | MG/L | 160.4999 | 2021-04-09 | AAA | 0.59
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-04-09 | AAA | 0.00021
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-04-09 | AAA | 0.00021
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-04-09 | AAA | 0.0005
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA | 0.35 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA | 0.33 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-09 | AAA | 0.11 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA | 0.44 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-09 | AAA | 0.3 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.12 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-09 | AAA | 0.29 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 0.27 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.3 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-09 | AAA | 0.27 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.28 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA | 0.44 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA | 0.28 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 0.26 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA | 0.4 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-09 | AAA | 0.28 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA | 0.23 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA | 0.2 | 0.5499 | 3YR VOC (2AM/XY DUE 1Q'22 PER PREVIOUS SCREEN)
3490986 | PLEASANT HILL VILLAGE | S | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2021-08-20 | L2 | 0.47 |  | MOB. HOME 100 (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 1.9 | UG/L | 249.9999 | 2024-10-24 | AAA | 0.022 | 1.4999 | POE-LRM, DETECT
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.49 | UG/L | 60.4999 | 2024-11-21 | L1 | 0.3 |  | NORTH PAVILLION - TTHM & HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 20.2 | UG/L | 80.4999 | 2024-11-21 | L1 | 0.5 |  | NORTH PAVILLION - TTHM & HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.47 | UG/L | 60.4999 | 2024-11-21 | L2 | 0.3 |  | 1311 HASKER CIRCLE - TTHM & HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 19.3 | UG/L | 80.4999 | 2024-11-21 | L2 | 0.5 |  | 1311 HASKER CIRCLE - TTHM & HAA5 | 3
3490770 | LAKE RUNNYMEADE MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.053 | MG/L | 10.4999 | 2025-03-27 | AAA | 0.02 |  | POE-LRM, NITRITE J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.4 | UG/L | 60.4999 | 2021-08-20 | L1 | 0.9 |  | HOSEBIBB @ WWTP (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490986 | PLEASANT HILL VILLAGE | S | DBP | 2950 | TOTAL THMS | 24.9 | UG/L | 80.4999 | 2021-08-20 | L1 | 0.47 |  | HOSEBIBB @ WWTP (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490986 | PLEASANT HILL VILLAGE | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21 | UG/L | 60.4999 | 2021-08-20 | L2 | 0.9 |  | MOB. HOME 100 (J5 QUALIFIERS ON 2941 & 2943 & COLD STORAGE TEMPERATURE REQUIREMENT EXCEEDED BY 1.7 DEGREES FOR 78 HOURS FOR TTHMS) RESULTS ENT'D WITH "S" PENDING EVALUATION | 3
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-03-30 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.2 | UG/L | 60.4999 | 2022-08-19 | L2 | 0.9 |  | MH 100 TTHM HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 29.5 | UG/L | 80.4999 | 2022-08-19 | L2 | 0.47 |  | MH 100 TTHM HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2022-08-19 | L1 | 0.9 |  | BIBB @ WWTP TTHM HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 22.6 | UG/L | 80.4999 | 2022-08-19 | L1 | 0.47 |  | BIBB @ WWTP TTHM HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-27 | AAA |  |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-27 | AAA |  |  | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-03-15 | AAA | 0.11 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 29.5 | UG/L | 80.4999 | 2023-08-18 | L2 |  |  | MH 100 TTHM/HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1041 | NITRITE | 0.025 | MG/L | 1.4999 | 2022-10-27 | AAA |  |  | 2022 N/N
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1040 | NITRATE | 0.025 | MG/L | 10.4999 | 2022-10-27 | AAA |  |  | 2022 N/N
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.7 | UG/L | 60.4999 | 2023-08-18 | L1 |  |  | BIB @ WWTP TTHM/HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 28.4 | UG/L | 80.4999 | 2023-08-18 | L1 |  |  | BIB @ WWTP TTHM/HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20 | UG/L | 60.4999 | 2023-08-18 | L2 |  |  | MH 100 TTHM/HAA5 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.8 | UG/L | 60.4999 | 2024-08-21 | L1 | 0.9 |  | POE L1 BIB @ WWTP | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 30.2 | UG/L | 80.4999 | 2024-08-21 | L1 | 0.75 |  | POE L1 BIB @ WWTP | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.2 | UG/L | 60.4999 | 2024-08-21 | L2 | 0.9 |  | POE - L2 MH100 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 32.4 | UG/L | 80.4999 | 2024-08-21 | L2 | 0.75 |  | POE - L2 MH100 | 3
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-08-21 | AAA | 0.025 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-21 | AAA | 0.025 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-08-21 | AAA | 0.0005 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1010 | BARIUM | 0.033 | MG/L | 2.4999 | 2024-08-21 | AAA | 0.0024 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-08-21 | AAA | 0.00067 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-08-21 | AAA | 0.0048 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-08-21 | AAA | 0.005 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1025 | FLUORIDE | 0.29 | MG/L | 4.0499 | 2024-08-21 | AAA | 0.015 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-08-21 | AAA | 0.00025 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-08-21 | AAA | 0.00014 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-08-21 | AAA | 0.002 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-08-21 | AAA | 0.00083 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2024-08-21 | AAA | 0.59 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-08-21 | AAA | 0.00088 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-08-21 | AAA | 0.00019 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-08-21 | AAA | 0.00021 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-08-21 | AAA | 0.0086 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1017 | CHLORIDE | 14.5 | MG/L | 250.4999 | 2024-08-21 | AAA | 2.5 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1022 | COPPER | 0.0021 | MG/L | 1.4999 | 2024-08-21 | AAA | 0.00093 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1025 | FLUORIDE | 0.29 | MG/L | 2.0499 | 2024-08-21 | AAA | 0.015 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1028 | IRON | 0.11 | MG/L | 0.3499 | 2024-08-21 | AAA | 0.021 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1032 | MANGANESE | 0.0069 | MG/L | 0.0549 | 2024-08-21 | AAA | 0.0013 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-08-21 | AAA | 0.0022 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1055 | SULFATE | 36.1 | MG/L | 250.4999 | 2024-08-21 | AAA | 2.5 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1095 | ZINC | 0.017 | MG/L | 5.4999 | 2024-08-21 | AAA | 0.0077 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2024-08-21 | AAA | 1 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-08-21 | AAA | 1 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 | LN(10) |  | 2024-08-21 | AAA | 0.1 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 183 | MG/L | 500.4999 | 2024-08-21 | AAA | 5 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-08-21 | AAA | 2.68 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2024-08-21 | AAA | 0.96 | 1.4999 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-08-21 | AAA | 0.42 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | RAD | 4030 | RADIUM-228 | 0.859 | PCI/L | 2.4999 | 2024-08-21 | AAA | 0.758 | 1.4999 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-08-21 | AAA | 0.35 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-08-21 | AAA | 0.33 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-08-21 | AAA | 0.46 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-08-21 | AAA | 0.4 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-08-21 | AAA | 0.33 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-08-21 | AAA | 0.41 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-08-21 | AAA | 0.37 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA | 0.36 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-08-21 | AAA | 0.33 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA | 0.3 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-08-21 | AAA | 0.29 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-08-21 | AAA | 0.44 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA | 0.26 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-08-21 | AAA | 0.34 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA | 0.41 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-08-21 | AAA | 0.31 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-08-21 | AAA | 0.4 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-08-21 | AAA | 0.28 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-08-21 | AAA | 0.37 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-08-21 | AAA | 0.27 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-08-21 | AAA | 0.0051 | 0.0149 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA | 0.0027 | 0.0249 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-08-21 | AAA | 0.055 | 0.1499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA | 0.28 | 1.4999 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-08-21 | AAA | 0.49 | 1.4999 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-08-21 | AAA | 0.16 | 0.4499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-08-21 | AAA | 3.3 | 9.4999 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-08-21 | AAA | 4.2 | 6.4999 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-08-21 | AAA | 0.36 | 0.6499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-08-21 | AAA | 0.46 | 2.4999 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-08-21 | AAA | 0.04 | 0.0749 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-08-21 | AAA | 0.47 | 0.6499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-08-21 | AAA | 0.04 | 0.1499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-08-21 | AAA | 0.16 | 0.2499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-08-21 | AAA | 0.59 | 0.9499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA | 0.015 | 0.1499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-08-21 | AAA | 0.029 | 0.2499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-08-21 | AAA | 0.014 | 0.0449 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA | 0.003 | 0.0249 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-08-21 | AAA | 0.096 | 0.1499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-08-21 | AAA | 0.059 | 0.2499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-08-21 | AAA | 0.015 | 0.1499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA | 0.02 | 0.0249 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-08-21 | AAA | 0.014 | 0.0449 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-08-21 | AAA | 0.036 | 0.2499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-08-21 | AAA | 0.045 | 0.1499 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA | 0.0066 | 0.0249 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-08-21 | AAA | 0.0078 | 0.0149 | POE - 2042 DETECT
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.071 | UG/L | 54.9999 | 2024-10-23 | AAA | 0.025 | 0.1499 | HCCPD (CONTAM 2042) ONLY
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-01-14 | AAA | 0.024 | 0.1499 | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-14 | AAA | 0.025 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-14 | AAA | 0.025 |  | POE
3490986 | PLEASANT HILL VILLAGE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-01-14 | AAA | 0.42 | 0.5499 | POE
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-04-08 | AAA |  | 0.1499 | POE
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.025 | UG/L | 54.9999 | 2025-07-16 | AAA | 0.024 | 0.1499 | POE - DETECT
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2025-08-25 | L2 | 0.9 |  | MH 100 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 24.4 | UG/L | 80.4999 | 2025-08-25 | L2 | 0.75 |  | MH 100 | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.7 | UG/L | 60.4999 | 2025-08-25 | L1 | 0.9 |  | BIBB @ WWTP | 3
3490986 | PLEASANT HILL VILLAGE | D | DBP | 2950 | TOTAL THMS | 27.9 | UG/L | 80.4999 | 2025-08-25 | L1 | 0.75 |  | BIBB @ WWTP | 3
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-12-10 | AAA |  | 0.1499 | POE
3491002 | KISSIMMEE RV PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.9 | UG/L | 60.4999 | 2021-12-23 | L1 | 1 |  | COLLECTED DURING WRONG TIMEFRAME. MAKEUP SAMPLES | 3
3491002 | KISSIMMEE RV PARK | D | DBP | 2950 | TOTAL THMS | 27.8 | UG/L | 80.4999 | 2021-12-23 | L1 | 1 |  | COLLECTED DURING WRONG TIMEFRAME. MAKEUP SAMPLES | 3
3491002 | KISSIMMEE RV PARK | N | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3490986 | PLEASANT HILL VILLAGE | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-08-21 | AAA | 0.099 |  | POE - 2905 J QUALIFIER
3490986 | PLEASANT HILL VILLAGE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.094 | UG/L | 54.9999 | 2024-08-21 | AAA | 0.025 | 0.1499 | POE - 2042 DETECT
3491002 | KISSIMMEE RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-23 | AAA |  |  | LATE REPORTING VIOLATION
3491002 | KISSIMMEE RV PARK | N | SEC | 1002 | ALUMINUM | 0.0339 | MG/L | 0.2499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1017 | CHLORIDE | 13.6 | MG/L | 250.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1022 | COPPER | 0.0079 | MG/L | 1.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1028 | IRON | 0.0974 | MG/L | 0.3499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1055 | SULFATE | 3.16 | MG/L | 250.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1095 | ZINC | 0.0151 | MG/L | 5.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.23 | LN(10) |  | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 128 | MG/L | 500.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 0.5499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-23 | AAA |  | 0.0149 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-23 | AAA |  | 0.4499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-23 | AAA |  | 9.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-23 | AAA |  | 6.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-23 | AAA |  | 0.6499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-23 | AAA |  | 2.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-23 | AAA |  | 0.0749 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-23 | AAA |  | 0.6499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-23 | AAA |  | 0.9499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-23 | AAA |  | 0.0449 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-23 | AAA |  | 0.0449 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-23 | AAA |  | 0.1499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-23 | AAA |  | 0.0249 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-23 | AAA |  | 0.0149 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-23 | AAA |  | 0.2499 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 1.4 | PCI/L | 15.4999 | 2021-12-23 | AAA |  | 3.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.4 | PCI/L | 15.4999 | 2021-12-23 | AAA |  |  | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-23 | AAA |  | 0.667 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | RAD | 4020 | RADIUM-226 | 0.5 | PCI/L | 3.4999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-23 | AAA |  | 1.4999 | LATE REPORTING
3491002 | KISSIMMEE RV PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.8 | UG/L | 60.4999 | 2022-11-30 | L1 | 1.2 |  | WASTEWATER SINK (NO DISINFECTANT RESIDUAL REPORTED) HLKD (THIS REPORT RECEIVED & ENT'D 1/26/23) | 3
3491002 | KISSIMMEE RV PARK | D | DBP | 2950 | TOTAL THMS | 1.8 | UG/L | 80.4999 | 2022-11-30 | L1 | 0.5 |  | WASTEWATER SINK (NO DISINFECTANT RESIDUAL REPORTED) HLKD (THIS REPORT RECEIVED & ENT'D 1/26/23) | 3
3491002 | KISSIMMEE RV PARK | N | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2022-12-29 | AAA | 0.2 |  | POE
3491002 | KISSIMMEE RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-12-28 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-12-28 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 54.58 | UG/L | 60.4999 | 2024-09-30 | L1 | 0.98 |  | WWTF HOSE BIB | 3
3491002 | KISSIMMEE RV PARK | D | DBP | 2950 | TOTAL THMS | 77.88 | UG/L | 80.4999 | 2024-09-30 | L1 | 0.45 |  | WWTF HOSE BIB | 3
3491002 | KISSIMMEE RV PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-30 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-30 | AAA |  |  | POE
3491002 | KISSIMMEE RV PARK | N | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-12-30 | AAA |  | 3.4999 | 2024 RADS
3491002 | KISSIMMEE RV PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-12-30 | AAA |  |  | 2024 RADS
3491002 | KISSIMMEE RV PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-12-30 | AAA |  | 0.667 | 2024 RADS
3491002 | KISSIMMEE RV PARK | N | RAD | 4020 | RADIUM-226 | 0.7 | PCI/L | 3.4999 | 2024-12-30 | AAA |  | 1.4999 | 2024 RADS
3491002 | KISSIMMEE RV PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-12-30 | AAA |  | 1.4999 | 2024 RADS
3491002 | KISSIMMEE RV PARK | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2024-12-30 | AAA | 0.092 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-30 | AAA | 0.081 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-12-30 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2024-12-30 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-12-30 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-12-30 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-12-30 | AAA | 0.004 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-12-30 | AAA | 0.4 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-12-30 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-12-30 | AAA | 1e-05 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-12-30 | AAA | 0.008 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-12-30 | AAA | 0.0012 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1052 | SODIUM | 4.5 | MG/L | 160.4999 | 2024-12-30 | AAA | 0.8 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-12-30 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-12-30 | AAA | 0.002 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-12-30 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-12-30 | AAA | 0.021 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1017 | CHLORIDE | 8.8 | MG/L | 250.4999 | 2024-12-30 | AAA | 2 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1022 | COPPER | 0.0067 | MG/L | 1.4999 | 2024-12-30 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2024-12-30 | AAA | 0.4 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1055 | SULFATE | 7.1 | MG/L | 250.4999 | 2024-12-30 | AAA | 2 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.57 | UG/L | 60.4999 | 2023-09-29 | L1 | 0.98 |  | LOCATION GIVEN AS WATER SPICKET | 3
3491002 | KISSIMMEE RV PARK | D | DBP | 2950 | TOTAL THMS | 31.05 | UG/L | 80.4999 | 2023-09-29 | L1 | 0.45 |  | LOCATION GIVEN AS WATER SPICKET | 3
3491002 | KISSIMMEE RV PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-12-30 | AAA | 0.0067 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-12-30 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-12-30 | AAA | 0.008 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-12-30 | AAA | 0.05 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-12-30 | AAA | 4.3 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-12-30 | AAA | 1 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.24 | LN(10) |  | 2024-12-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 98 | MG/L | 500.4999 | 2024-12-30 | AAA | 10 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-12-30 | AAA | 0.04 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-12-30 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-12-30 | AAA | 0.27 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-12-30 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-12-30 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-12-30 | AAA | 0.39 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-12-30 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-12-30 | AAA | 0.29 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-12-30 | AAA | 0.22 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-12-30 | AAA | 0.21 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-12-30 | AAA | 0.24 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-12-30 | AAA | 0.29 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-12-30 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-12-30 | AAA | 0.26 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-12-30 | AAA | 0.14 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-12-30 | AAA | 0.27 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-12-30 | AAA | 0.42 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-12-30 | AAA | 0.36 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-12-30 | AAA | 0.26 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-12-30 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-12-30 | AAA | 0.31 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-12-30 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-12-30 | AAA | 0.0069 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-12-30 | AAA | 0.0071 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-12-30 | AAA | 0.0068 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-12-30 | AAA | 0.12 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-12-30 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-12-30 | AAA | 0.37 | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-12-30 | AAA | 6 | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-12-30 | AAA | 5.9 | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-12-30 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-12-30 | AAA | 1.8 | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-12-30 | AAA | 0.06 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-12-30 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-12-30 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-12-30 | AAA | 0.18 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-12-30 | AAA | 0.019 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-12-30 | AAA | 0.67 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-12-30 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-12-30 | AAA | 0.15 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-12-30 | AAA | 0.006 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-12-30 | AAA | 0.0052 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-12-30 | AAA | 0.015 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-12-30 | AAA | 0.095 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-12-30 | AAA | 0.09 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-12-30 | AAA | 0.0063 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-12-30 | AAA | 0.038 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-12-30 | AAA | 0.093 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-12-30 | AAA | 0.0049 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-12-30 | AAA | 0.0076 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-12-30 | AAA | 0.053 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491002 | KISSIMMEE RV PARK | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2025-12-29 | AAA | 0.1 |  | POE
3491002 | KISSIMMEE RV PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-12-29 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1044 | ORTHOPHOSPHATE | 0.03 | MG/L |  | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1064 | CONDUCTIVITY | 2.2 | MG/L | 0 | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1919 | HARDNESS - CALCIUM | 24 | MG/L | 0 | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1927 | TOTAL ALKALINITY | 85 | MG/L |  | 2021-02-23 | AAA |  |  | LOT # 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1044 | ORTHOPHOSPHATE | 0.04 | MG/L |  | 2021-02-23 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1064 | CONDUCTIVITY | 2.2 | MG/L | 0 | 2021-02-23 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1919 | HARDNESS - CALCIUM | 24 | MG/L | 0 | 2021-02-23 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-02-23 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1927 | TOTAL ALKALINITY | 86 | MG/L |  | 2021-02-23 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2021-04-21 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1064 | CONDUCTIVITY | 500 | MG/L | 0 | 2021-04-21 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1919 | HARDNESS - CALCIUM | 70 | MG/L | 0 | 2021-04-21 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1927 | TOTAL ALKALINITY | 230 | MG/L |  | 2021-04-21 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2021-04-21 | AAA |  |  | LOT 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1064 | CONDUCTIVITY | 510 | MG/L | 0 | 2021-04-21 | AAA |  |  | LOT 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1919 | HARDNESS - CALCIUM | 69 | MG/L | 0 | 2021-04-21 | AAA |  |  | LOT 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2021-04-21 | AAA |  |  | LOT 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | WQP | 1927 | TOTAL ALKALINITY | 240 | MG/L |  | 2021-04-21 | AAA |  |  | LOT 235
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-04-21 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-11 | L2
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-11 | L2
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1052 | SODIUM | 32 | MG/L | 160.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1017 | CHLORIDE | 42 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1028 | IRON | 0.025 | MG/L | 0.3499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1032 | MANGANESE | 0.0079 | MG/L | 0.0549 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1055 | SULFATE | 5 | MG/L | 250.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.06 | LN(10) |  | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 278 | MG/L | 500.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 2905 | FOAMING AGENTS | 0.1 |  | 0.5499 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-08 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4020 | RADIUM-226 | 0.7 | PCI/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-08 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-08 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-08 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-08 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-08 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-08 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-08 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-08 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-08 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-08 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-08 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-08 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/200 E84589, E82535, E82001, E82574, E84025
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.47 | UG/L | 60.4999 | 2022-05-09 | L2 | 0.98 |  | MANAGER'S RESIDENCE (HLKD) (LRAA: TTHM:38.78, HAA5-15.31)
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 73.44 | UG/L | 80.4999 | 2022-05-09 | L2 | 0.39 |  | MANAGER'S RESIDENCE (HLKD) (LRAA: TTHM:38.78, HAA5-15.31)
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2022-10-31 | AAA | 0.024 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-31 | AAA | 0.0034 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.9 | UG/L | 60.4999 | 2023-05-17 | L2 | 0.98
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 56.48 | UG/L | 80.4999 | 2023-05-17 | L2 | 0.39
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-10-16 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2024-08-12 | AAA | 0.5 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2024-08-12 | AAA | 0.003 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2024-08-12 | AAA | 0.1 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-08-12 | AAA | 0 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1052 | SODIUM | 28 | MG/L | 160.4999 | 2024-08-12 | AAA | 0.8 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-08-12 | AAA |  | 0.5499 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 2.2 | PCI/L | 15.4999 | 2024-08-12 | AAA | 2 | 3.4999 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.4 | PCI/L | 15.4999 | 2024-08-12 | AAA | 2 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4006 | COMBINED URANIUM | 0.2 | PCI/L | 20.4999 | 2024-08-12 | AAA | 0.2 | 0.667 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2024-08-12 | AAA | 0.4 | 1.4999 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-08-12 | AAA |  | 1.4999 | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1017 | CHLORIDE | 34 | MG/L | 250.4999 | 2024-08-12 | AAA | 4 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1022 | COPPER | 0.0021 | MG/L | 1.4999 | 2024-08-12 | AAA | 0.001 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1025 | FLUORIDE | 0.16 | MG/L | 2.0499 | 2024-08-12 | AAA | 0.1 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1032 | MANGANESE | 0.0026 | MG/L | 0.0549 | 2024-08-12 | AAA | 0.001 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1055 | SULFATE | 5 | MG/L | 250.4999 | 2024-08-12 | AAA | 2 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2024-08-12 | AAA | 5 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-08-12 | AAA |  |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.2 | LN(10) |  | 2024-08-12 | AAA | 7.2 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 310 | MG/L | 500.4999 | 2024-08-12 | AAA | 5 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | SEC | 2905 | FOAMING AGENTS | 0.061 |  | 0.5499 | 2024-08-12 | AAA | 0.04 |  | POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 72.07 | UG/L | 60.4999 | 2025-02-03 | L2 | 0.98 |  | MANAGER'S HOUSE-EXCEEDANCE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 127.84 | UG/L | 80.4999 | 2025-02-03 | L2 | 0.44 |  | MANAGER'S HOUSE-EXCEEDANCE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-24 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-24 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 78.8 | UG/L | 60.4999 | 2025-11-04 | L2 | 0.98 |  | MANAGER'S HOUSE - HAA5 & TTHM EXCEEDANCES
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 122.5 | UG/L | 80.4999 | 2025-11-04 | L2 | 0.44 |  | MANAGER'S HOUSE - HAA5 & TTHM EXCEEDANCES
3491188 | EL RANCHO CUCINA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA | 0.024
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 95 | UG/L | 60.4999 | 2024-08-07 | L2 | 0.98 |  | 2024 MAKE UP SAMPLES (MISSED ANNUAL MAY 2024 SAMPLES)
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 146.3 | UG/L | 80.4999 | 2024-08-07 | L2 | 0.44 |  | 2024 MAKE UP SAMPLES (MISSED ANNUAL MAY 2024 SAMPLES)
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.62 | UG/L | 60.4999 | 2024-11-04 | L2 | 0.98 |  | MANAGERS RESIDENCE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 52.86 | UG/L | 80.4999 | 2024-11-04 | L2 | 0.44 |  | MANAGERS RESIDENCE
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 50.99 | UG/L | 60.4999 | 2025-05-05 | L2 | 0.98 |  | 2Q25 DBP RESULTS
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 86.16 | UG/L | 80.4999 | 2025-05-05 | L2 | 0.44 |  | 2Q25 DBP RESULTS
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.07 | UG/L | 60.4999 | 2025-08-05 | L2 | 0.98 |  | MANAGER'S HOUSE - TTHM, HAA5
3491077 | EAST TOHO FKA BOGGY CREEK RESORT | D | DBP | 2950 | TOTAL THMS | 85.12 | UG/L | 80.4999 | 2025-08-05 | L2 | 0.44 |  | MANAGER'S HOUSE - TTHM, HAA5
3491188 | EL RANCHO CUCINA | N | INOR | 1041 | NITRITE | 0.24 | MG/L | 1.4999 | 2022-10-27 | AAA | 0.0034
3491188 | EL RANCHO CUCINA | D | INOR | 1040 | NITRATE | 0.099 | MG/L | 10.4999 | 2023-10-16 | AAA | 0.024 |  | DIST- LOCATION -POE
3491188 | EL RANCHO CUCINA | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | DIST- LOCATION -POE
3491188 | EL RANCHO CUCINA | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3491188 | EL RANCHO CUCINA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3491188 | EL RANCHO CUCINA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-21 | AAA | 0.024 |  | POE
3491188 | EL RANCHO CUCINA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA | 0.0034 |  | POE
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.87 | UG/L | 60.4999 | 2021-02-17 | L1 | 0.98 |  | 805 PARKWAY EAST (HLKD) [LRAA TTHM = 93.37., OEL= 95.48; HAA5=43.11]. TTHM MCL VIO, NEED PN AND OE REPORT_VPU | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 85.23 | UG/L | 80.4999 | 2021-02-17 | L1 | 0.39 |  | 805 PARKWAY EAST (HLKD) [LRAA TTHM = 93.37., OEL= 95.48; HAA5=43.11]. TTHM MCL VIO, NEED PN AND OE REPORT_VPU | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.83 | UG/L | 60.4999 | 2021-02-17 | L3 | 0.98 |  | 1315 PINE ISLAND (HLKD) [3 CONSEC QUARTERS AT THIS LOCATION, NO LRAA YET]_VPU
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 82.13 | UG/L | 80.4999 | 2021-02-17 | L3 | 0.39 |  | 1315 PINE ISLAND (HLKD) [3 CONSEC QUARTERS AT THIS LOCATION, NO LRAA YET]_VPU
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-17 | L1 | 0.39 |  | 805 PARKWAY EAST (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN) | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-17 | L3 | 0.39 |  | 1315 PINE ISLAND DR. (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN)
3491298 | SHELTER COVE RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-17 | L3 | 0.98 |  | 1315 PINE ISLAND DR. (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN)
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-17 | L1 | 0.98 |  | 805 PARKWAY EAST (VERY LOW HAA DETECTION REPORTED AS NON-DETECTION IN TOTAL HAA5) ENTERED TTHMS ONLY (IF YOU WANT TO ACCEPT THE TOTAL HAA5, PLS. ADD RESULT TO THIS SCREEN) | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.3 | UG/L | 60.4999 | 2021-08-20 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 43.15 | UG/L | 80.4999 | 2021-08-20 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.99 | UG/L | 60.4999 | 2021-08-20 | L1 |  |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 67.41 | UG/L | 80.4999 | 2021-08-20 | L1 |  |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | N | INOR | 1040 | NITRATE | 0.12 | MG/L | 10.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1010 | BARIUM | 0.0043 | MG/L | 2.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1025 | FLUORIDE | 0.26 | MG/L | 4.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1052 | SODIUM | 18 | MG/L | 160.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1017 | CHLORIDE | 18 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1025 | FLUORIDE | 0.26 | MG/L | 2.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1028 | IRON | 0.14 | MG/L | 0.3499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1055 | SULFATE | 2.2 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1905 | COLOR | 13 | COLOR UNITS | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 5.3 | LN(10) |  | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 304 | MG/L | 500.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-10-25 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-25 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-25 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.09 | UG/L | 60.4999 | 2021-11-17 | L1 |  |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 52.58 | UG/L | 80.4999 | 2021-11-17 | L1 |  |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.57 | UG/L | 60.4999 | 2021-11-17 | L3 |  |  | 1315 PINE ISLAND (LRAA, HAA5=21.43; TTHMS=43.83 -KAOB)
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 50.03 | UG/L | 80.4999 | 2021-11-17 | L3 |  |  | 1315 PINE ISLAND (LRAA, HAA5=21.43; TTHMS=43.83 -KAOB)
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.28 | UG/L | 60.4999 | 2022-02-16 | L1 |  |  | PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 79.67 | UG/L | 80.4999 | 2022-02-16 | L1 |  |  | PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.79 | UG/L | 60.4999 | 2022-02-16 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 78.17 | UG/L | 80.4999 | 2022-02-16 | L3 |  |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.1 | UG/L | 60.4999 | 2022-05-18 | L1 |  |  | 805 PARKWAY EAST TTHM LRAA 70.905 | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 84.06 | UG/L | 80.4999 | 2022-05-18 | L1 |  |  | 805 PARKWAY EAST TTHM LRAA 70.905 | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-05-18 | L3 |  |  | 1315 PINE ISLAND TTHM: 64.14
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 85.21 | UG/L | 80.4999 | 2022-05-18 | L3 |  |  | 1315 PINE ISLAND TTHM: 64.14
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 63.37 | UG/L | 60.4999 | 2022-08-16 | L1 | 0.98 |  | 805 PARKWAY EAST (**TTHM LRAA MCL VIOL**) HLKD | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 140.8 | UG/L | 80.4999 | 2022-08-16 | L1 | 0.39 |  | 805 PARKWAY EAST (**TTHM LRAA MCL VIOL**) HLKD | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 81.6 | UG/L | 60.4999 | 2022-08-16 | L3 | 0.98 |  | 1315 PINE ISLAND DR. (HLKD) **HIGH RESULTS** (**TTHM LRAA MCL VIOL**)
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 143.95 | UG/L | 80.4999 | 2022-08-16 | L3 | 0.39 |  | 1315 PINE ISLAND DR. (HLKD) **HIGH RESULTS** (**TTHM LRAA MCL VIOL**)
3491298 | SHELTER COVE RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3491298 | SHELTER COVE RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.46 | UG/L | 60.4999 | 2022-11-16 | L1 | 0.98 |  |  | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 65.38 | UG/L | 80.4999 | 2022-11-16 | L1 | 0.39 |  |  | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.15 | UG/L | 60.4999 | 2022-11-16 | L3 | 0.98
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 76.32 | UG/L | 80.4999 | 2022-11-16 | L3 | 0.39
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.25 | UG/L | 60.4999 | 2023-02-20 | L1 | 0.98 |  | 805 PARKWAY EAST TTHM HAA5 | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 50.28 | UG/L | 80.4999 | 2023-02-20 | L1 | 0.39 |  | 805 PARKWAY EAST TTHM HAA5 | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.49 | UG/L | 60.4999 | 2023-02-20 | L3 | 0.98 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 105.18 | UG/L | 80.4999 | 2023-02-20 | L3 | 0.39 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 95.3 | UG/L | 60.4999 | 2023-08-21 | L1 |  |  | TTHM/HAA5 AT L1 EXCEEDANCES FOR BOTH CONTAMINANTS | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 178.93 | UG/L | 80.4999 | 2023-08-21 | L1 |  |  | TTHM/HAA5 AT L1 EXCEEDANCES FOR BOTH CONTAMINANTS | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 94.75 | UG/L | 60.4999 | 2023-08-21 | L3 |  |  | TTHM/HAA5 AT L3 EXCEEDANCES FOR BOTH CONTAMINANTS
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 181.09 | UG/L | 80.4999 | 2023-08-21 | L3 |  |  | TTHM/HAA5 AT L3 EXCEEDANCES FOR BOTH CONTAMINANTS
3491298 | SHELTER COVE RESORT | D | INOR | 1040 | NITRATE | 0.079 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | DIST
3491298 | SHELTER COVE RESORT | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-17 | AAA |  |  | DIST
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 52.69 | UG/L | 60.4999 | 2023-11-17 | L1 | 0.98 |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 64.21 | UG/L | 80.4999 | 2023-11-17 | L1 | 0.39 |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 58.91 | UG/L | 60.4999 | 2023-11-17 | L3 | 0.98 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 55.33 | UG/L | 80.4999 | 2023-11-17 | L3 | 0.39 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.48 | UG/L | 60.4999 | 2024-02-16 | L1 | 0.98 |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 75.68 | UG/L | 80.4999 | 2024-02-16 | L1 | 0.39 |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.85 | UG/L | 60.4999 | 2024-02-16 | L3 | 0.98 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 57.51 | UG/L | 80.4999 | 2024-02-16 | L3 | 0.39 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.37 | UG/L | 60.4999 | 2024-05-15 | L1 | 0.98 |  | 2Q2024 TTHM/HAA5 RESULTS | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 49.13 | UG/L | 80.4999 | 2024-05-15 | L1 | 0.39 |  | 2Q2024 TTHM/HAA5 RESULTS | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.5 | UG/L | 60.4999 | 2024-05-15 | L3 | 0.98 |  | 2Q2024 TTHM/HAA5 RESULTS
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 70.24 | UG/L | 80.4999 | 2024-05-15 | L3 | 0.39 |  | 2Q2024 TTHM/HAA5 RESULTS
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-08-15 | L1 | 0.98 |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.39 |  | 805 PARKWAY EAST | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-08-15 | L3 | 0.98 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-08-15 | L3 | 0.39 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | N | SEC | 2905 | FOAMING AGENTS | 0.081 |  | 0.5499 | 2024-09-09 | AAA | 0.04 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.01 | UG/L | 60.4999 | 2023-05-16 | L3 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT L3 AND L1)
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 133.48 | UG/L | 80.4999 | 2023-05-16 | L3 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT L3 AND L1)
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.99 | UG/L | 60.4999 | 2023-05-16 | L1 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT L3 AND L1) | 3
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 121.54 | UG/L | 80.4999 | 2023-05-16 | L1 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT L3 AND L1) | 3
3491298 | SHELTER COVE RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.05 | LN(10) |  | 2024-09-09 | AAA |  |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 280 | MG/L | 500.4999 | 2024-09-09 | AAA | 10 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-09-09 | AAA | 0.2 | 0.667 | COMBINED URANIUM CONTRACTED TO E82574
3491298 | SHELTER COVE RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-09 | AAA | 0.5 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-09 | AAA | 0.24 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-09 | AAA | 0.48 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-09 | AAA | 0.49 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-09 | AAA | 0.44 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-09 | AAA | 0.4 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-09 | AAA | 0.28 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-09 | AAA | 0.4 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-09 | AAA | 0.41 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA | 0.44 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-09 | AAA | 0.32 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA | 0.36 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-09 | AAA | 0.33 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA | 0.25 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-09 | AAA | 0.44 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA | 0.49 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-09 | AAA | 0.37 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-09 | AAA | 0.16 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-09 | AAA | 0.2 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-09 | AAA | 0.33 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-09 | AAA | 0.26 | 0.5499 | POE
3491298 | SHELTER COVE RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-09-09 | AAA | 1.8 |  | COMBINED URANIUM CONTRACTED TO E82574
3491298 | SHELTER COVE RESORT | N | RAD | 4020 | RADIUM-226 | 0.7 | PCI/L | 3.4999 | 2024-09-09 | AAA | 0.3 | 1.4999 | COMBINED URANIUM CONTRACTED TO E82574
3491298 | SHELTER COVE RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-09 | AAA | 0.7 | 1.4999 | COMBINED URANIUM CONTRACTED TO E82574
3491298 | SHELTER COVE RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-09 | AAA | 0.024 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1017 | CHLORIDE | 18 | MG/L | 250.4999 | 2024-09-09 | AAA | 0.039 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-09 | AAA | 0.0034 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-09 | AAA | 0.00025 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1010 | BARIUM | 0.0045 | MG/L | 2.4999 | 2024-09-09 | AAA | 0.003 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-09 | AAA | 0.00025 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-09-09 | AAA | 0.005 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-09 | AAA | 0.004 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1025 | FLUORIDE | 0.22 | MG/L | 4.0499 | 2024-09-09 | AAA | 0.0099 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-09-09 | AAA | 0.0005 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-09 | AAA | 3e-05 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-09-09 | AAA | 0.008 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-09 | AAA | 0.0012 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1052 | SODIUM | 20 | MG/L | 160.4999 | 2024-09-09 | AAA | 0.8 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-09 | AAA | 0.001 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-09 | AAA | 0.002 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-09 | AAA | 0.00025 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-09-09 | AAA | 0.005 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1025 | FLUORIDE | 0.22 | MG/L | 2.0499 | 2024-09-09 | AAA | 0.0099 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1028 | IRON | 0.12 | MG/L | 0.3499 | 2024-09-09 | AAA | 0.038 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-09-09 | AAA | 0.005 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-09 | AAA | 0.0005 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1055 | SULFATE | 2.4 | MG/L | 250.4999 | 2024-09-09 | AAA | 0.034 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-09 | AAA | 0.05 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1905 | COLOR | 9.1 | COLOR UNITS | 15.4999 | 2024-09-09 | AAA | 5 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-09-09 | AAA | 1 |  | AL,CU,FE,MN,ZN SUBCONTRACTED TO E82535; AG SUBCONTRACTED TO E82574; FOAMING AGENTS SUBCONTRACTED TO E82001
3491298 | SHELTER COVE RESORT | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2025-01-14 | AAA | 0.024 |  | POE
3491298 | SHELTER COVE RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-14 | AAA |  |  | POE
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 62 | UG/L | 60.4999 | 2025-08-26 | L3 | 0.2 |  | 1315 PINE ISLAND - TTHM, HAA5
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 80.7 | UG/L | 80.4999 | 2025-08-26 | L3 | 0.21 |  | 1315 PINE ISLAND - TTHM, HAA5
3491397 | STUCKEY'S | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-09-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491397 | STUCKEY'S | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-09-07 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491397 | STUCKEY'S | N | INOR | 1040 | NITRATE | 0.025 | MG/L | 10.4999 | 2022-12-06 | AAA | 0.02 |  | POE
3491397 | STUCKEY'S | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-06 | AAA |  |  | POE
3491397 | STUCKEY'S | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-08-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3491397 | STUCKEY'S | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3491397 | STUCKEY'S | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-11-12 | AAA |  |  | POE
3491397 | STUCKEY'S | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-12 | AAA |  |  | POE
3491397 | STUCKEY'S | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-12-08 | AAA |  |  | POE
3491397 | STUCKEY'S | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-12-08 | AAA |  |  | POE
3491366 | SOUTHPORT PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - AS OF 8/31/2022, THIS IS DESIGNATED AS A MAKE-UP FOR 2021 NN'S - CJL
3491366 | SOUTHPORT PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - AS OF 8/31/2022, THIS IS DESIGNATED AS A MAKE-UP FOR 2021 NN'S - CJL
3491366 | SOUTHPORT PARK | N | INOR | 1040 | NITRATE | 0.043 | MG/L | 10.4999 | 2022-12-27 | AAA | 0.025 |  | POE
3491366 | SOUTHPORT PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-27 | AAA |  |  | POE
3491366 | SOUTHPORT PARK | N | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2023-06-16 | AAA | 0.025 |  | POE
3491366 | SOUTHPORT PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-16 | AAA |  |  | POE
3491366 | SOUTHPORT PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-19 | AAA |  |  | POE
3491366 | SOUTHPORT PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-19 | AAA |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-01-07 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-01-07 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-01-21 | WTP4
3491298 | SHELTER COVE RESORT | N | INOR | 1040 | NITRATE | 0.082 | MG/L | 10.4999 | 2024-09-09 | AAA | 0.024 |  | NO2-NO3 E53076; CYANIDE E84589; REMAINING SUBCONTRACTED TO E82574 AND E82535
3491298 | SHELTER COVE RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32 | UG/L | 60.4999 | 2025-11-24 | L3 | 0.2 |  | 1315 PINE ISLAND
3491298 | SHELTER COVE RESORT | D | DBP | 2950 | TOTAL THMS | 58.65 | UG/L | 80.4999 | 2025-11-24 | L3 | 0.21 |  | 1315 PINE ISLAND
3491366 | SOUTHPORT PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-04-15 | AAA
3491366 | SOUTHPORT PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-04-15 | AAA
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-01-07 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-01-07 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-01-07 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-01-07 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-01-21 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-01-22 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 139 | MG/L |  | 2021-01-22 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-01-22 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-01-22 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2021-02-04 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-02-04 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-02-04 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-02-04 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-02-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-02-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.3 | UG/L | 60.4999 | 2021-02-14 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.5 | UG/L | 80.4999 | 2021-02-14 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.4 | UG/L | 60.4999 | 2021-02-14 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 33.4 | UG/L | 80.4999 | 2021-02-14 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.5 | UG/L | 60.4999 | 2021-02-14 | L3 | 1 |  | LS 67 (FRIAR'S AND CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 32.1 | UG/L | 80.4999 | 2021-02-14 | L3 | 0.5 |  | LS 67 (FRIAR'S AND CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.6 | UG/L | 60.4999 | 2021-02-14 | L4 | 1 |  | 803 MASSACHUSSETTS AVE. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS-PGS 2 & 3 W/T RAA & H RAA DID NOT COPY) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 28.9 | UG/L | 80.4999 | 2021-02-14 | L4 | 0.5 |  | 803 MASSACHUSSETTS AVE. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS-PGS 2 & 3 W/T RAA & H RAA DID NOT COPY) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-02-18 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 137 | MG/L |  | 2021-02-18 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-02-18 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 145 | MG/L |  | 2021-02-18 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-02-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-02-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-03-04 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-03-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-03-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-03-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-03-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-03-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-03-18 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-25 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-03-25 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-03-25 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-03-25 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-01 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-04-01 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-01 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-04-01 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-04-01 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-04-01 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-04-15 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-04-15 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-04-15 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-04-15 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-04-15 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2021-04-15 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-04-29 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-04-29 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2021-04-29 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-04-29 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-13 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-05-13 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-13 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-05-13 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-05-13 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-04-29 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-04-29 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-05-13 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2021-05-18 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIRCLE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 36 | UG/L | 80.4999 | 2021-05-18 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIRCLE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.4 | UG/L | 60.4999 | 2021-05-18 | L2 | 1 |  | 4805 DOC DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 27.2 | UG/L | 80.4999 | 2021-05-18 | L2 | 0.5 |  | 4805 DOC DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.3 | UG/L | 60.4999 | 2021-05-18 | L3 | 1 |  | L.S. 67 FRIARS LN & (OLD) CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 24.3 | UG/L | 80.4999 | 2021-05-18 | L3 | 0.5 |  | L.S. 67 FRIARS LN & (OLD) CANOE CREEK RD.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.3 | UG/L | 60.4999 | 2021-05-18 | L4 | 1 |  | 803 MASSACHUSETTS AVE. (6/21 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 26.4 | UG/L | 80.4999 | 2021-05-18 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. (6/21 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-05-27 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-05-27 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-27 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-05-27 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-27 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2021-05-27 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-10 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-06-10 | WTP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2021-06-11 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-06-11 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-06-24 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-06-24 | WTP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-24 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2021-06-24 | WTP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-06-27 | WTP4 |  |  | 1/21 TO 6/21 DIST WQPS ALSO RCVD, TESTED APPROX. EV. 2 WEEKS AT 7 SITES (RCVD WITH THESE 1/21-6/21 POE WQPS BUT NOT ENTERED AT TIME OF RECEIPT ON 7/8/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-06-27 | WTP4 |  |  | 1/21 TO 6/21 DIST WQPS ALSO RCVD, TESTED APPROX. EV. 2 WEEKS AT 7 SITES (RCVD WITH THESE 1/21-6/21 POE WQPS BUT NOT ENTERED AT TIME OF RECEIPT ON 7/8/21)
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-08 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 137 | MG/L |  | 2021-07-08 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-08 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2021-07-08 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-07-08 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-07-08 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-07-22 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-07-22 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-22 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-07-22 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-22 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-07-22 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-08-05 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-05 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-08-05 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-08-05 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-08-05 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-08-05 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 63.1 | UG/L | 60.4999 | 2021-08-18 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIRCLE (SINGLE SAMPLE HAA5 EXCEEDANCE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 79 | UG/L | 80.4999 | 2021-08-18 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIRCLE (SINGLE SAMPLE HAA5 EXCEEDANCE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.5 | UG/L | 60.4999 | 2021-08-18 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 53.1 | UG/L | 80.4999 | 2021-08-18 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 57 | UG/L | 60.4999 | 2021-08-18 | L3 | 1 |  | LS 67 (FRIAR'S & OLD CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 33.8 | UG/L | 80.4999 | 2021-08-18 | L3 | 0.5 |  | LS 67 (FRIAR'S & OLD CANOE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.7 | UG/L | 60.4999 | 2021-08-18 | L4 | 1 |  | 803 MASSACHUSETTS AVE. (9/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.8 | UG/L | 80.4999 | 2021-08-18 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. (9/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-19 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-08-19 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-19 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2021-08-19 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-08-19 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-08-19 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-02 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2021-09-02 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-09-02 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-09-02 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-09-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-09-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-09-16 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 128 | MG/L |  | 2021-09-16 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-09-16 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-09-16 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-18 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2021-09-18 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-30 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-09-30 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-14 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-30 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-09-30 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-09-30 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-09-30 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-10-14 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-14 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-10-14 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-14 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-10-14 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-28 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-10-28 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-10-28 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-10-28 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-10-28 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2021-10-28 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-11-11 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-11-11 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-11-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-11-11 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-11-11 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-11-11 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.9 | UG/L | 60.4999 | 2021-11-15 | L1 | 1 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 48 | UG/L | 80.4999 | 2021-11-15 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13 | UG/L | 60.4999 | 2021-11-15 | L2 | 1 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 36.6 | UG/L | 80.4999 | 2021-11-15 | L2 | 0.5 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.5 | UG/L | 60.4999 | 2021-11-15 | L3 | 1 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 25.9 | UG/L | 80.4999 | 2021-11-15 | L3 | 0.5 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.5 | UG/L | 60.4999 | 2021-11-15 | L4 | 1 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 28.1 | UG/L | 80.4999 | 2021-11-15 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-11-25 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-11-25 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-11-25 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-11-25 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-11-25 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-11-25 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-09 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2021-12-09 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-09 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-12-09 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-12-09 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-12-09 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-12-23 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-12-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-12-23 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-12-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-12-23 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.1 | UG/L | 60.4999 | 2022-02-21 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.1 | UG/L | 80.4999 | 2022-02-21 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.5 | UG/L | 60.4999 | 2022-02-21 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 35.6 | UG/L | 80.4999 | 2022-02-21 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.4 | UG/L | 60.4999 | 2022-02-21 | L3 |  |  | LS 67
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 28.2 | UG/L | 80.4999 | 2022-02-21 | L3 |  |  | LS 67
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.7 | UG/L | 60.4999 | 2022-02-21 | L4 |  |  | 803 MASSACHUSETTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 27.5 | UG/L | 80.4999 | 2022-02-21 | L4 |  |  | 803 MASSACHUSETTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-13 | WTP4 |  |  | WTP 4 POE NN
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-13 | WTP4 |  |  | WTP 4 POE NN
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-13 | WTP1 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-13 | WTP1 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-04-13 | WTP2 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-04-13 | WTP2 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.5 | UG/L | 60.4999 | 2022-05-18 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 83.7 | UG/L | 80.4999 | 2022-05-18 | L1 |  |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.4 | UG/L | 60.4999 | 2022-05-18 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 54.8 | UG/L | 80.4999 | 2022-05-18 | L2 |  |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.8 | UG/L | 60.4999 | 2022-05-18 | L3 |  |  | FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 50.6 | UG/L | 80.4999 | 2022-05-18 | L3 |  |  | FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.8 | UG/L | 60.4999 | 2022-05-18 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 50.7 | UG/L | 80.4999 | 2022-05-18 | L4 |  |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-07-07 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-07-07 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 145 | MG/L |  | 2022-07-07 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-07-07 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-07-21 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2022-07-21 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-07-21 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 143 | MG/L |  | 2022-07-21 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-07-21 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-07-07 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-07-07 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2022-07-21 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-08-04 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 144 | MG/L |  | 2022-08-04 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-08-04 | WTP1 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 148 | MG/L |  | 2022-08-04 | WTP1 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7 | LN(10) |  | 2022-08-04 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-08-04 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 66.6 | UG/L | 80.4999 | 2022-08-17 | L1 | 0.5 |  | 5371 MAJESTIC ISLAND CIR. J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 46.2 | UG/L | 80.4999 | 2022-08-17 | L2 | 0.5 |  | 4805 DOC DR. J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 45.37 | UG/L | 80.4999 | 2022-08-17 | L3 | 0.5 |  | LS 67 (FRIAR'S & OLD CANOE) J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 44.54 | UG/L | 80.4999 | 2022-08-17 | L4 | 0.5 |  | 803 MASSACHUSETTS AVE. J QUALIFIERS ON 3 HAA CONSTITUENT ACIDS, NOT ACCEPTED FOR COMPLIANCE_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-08-18 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-08-18 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-08-18 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 152 | MG/L |  | 2022-08-18 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2022-08-18 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-08-18 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-09-01 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 74 | MG/L |  | 2022-09-01 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-09-01 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-09-01 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-09-01 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2022-09-15 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-09-15 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-09-15 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-09-15 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-09-29 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 145 | MG/L |  | 2022-09-29 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-09-29 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-09-29 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2022-09-29 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2022-09-01 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-09-15 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-09-15 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-09-29 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-10-13 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2022-10-13 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-10-13 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2022-10-13 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2022-10-13 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-10-13 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2022-10-27 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-10-27 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-10-27 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-10-27 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-10-27 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-10-27 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2022-11-10 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2022-11-10 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-10 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-11-10 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-11-10 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-11-10 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.3 | UG/L | 60.4999 | 2022-11-18 | L3 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 49.8 | UG/L | 80.4999 | 2022-11-18 | L3 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.7 | UG/L | 60.4999 | 2022-11-18 | L1 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 91 | UG/L | 80.4999 | 2022-11-18 | L1 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.5 | UG/L | 60.4999 | 2022-11-18 | L2 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 46.7 | UG/L | 80.4999 | 2022-11-18 | L2 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.9 | UG/L | 60.4999 | 2022-11-18 | L4 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.7 | UG/L | 80.4999 | 2022-11-18 | L4 |  |  | LATE DATA ENTRY_SMD
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2022-11-24 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-11-24 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-24 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2022-11-24 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-11-24 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-11-24 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2022-12-08 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2022-12-08 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-12-08 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2022-12-08 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-08 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-12-08 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.5 | LN(10) |  | 2022-12-22 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 155 | MG/L |  | 2022-12-22 | WTP1 |  |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-22 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2022-12-22 | WTP2 |  |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-12-22 | WTP4 |  |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-12-22 | WTP4 |  |  | WP4
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 83.6 | UG/L | 60.4999 | 2021-02-16 | L1 | 1 |  | BOAT RAMP [LRAA TTHM=106.28 ; HAA5=57.73 ]_VPU | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 152 | UG/L | 80.4999 | 2021-02-16 | L1 | 0.5 |  | BOAT RAMP [LRAA TTHM=106.28 ; HAA5=57.73 ]_VPU | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 91.5 | UG/L | 60.4999 | 2021-02-16 | L2 | 1 |  | A-15 (HLKD) [LRAA TTHM=107.43 ; HAA5=61.45] | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 157 | UG/L | 80.4999 | 2021-02-16 | L2 | 0.5 |  | A-15 (HLKD) [LRAA TTHM=107.43 ; HAA5=61.45] | 3
3491702 | FLORIDIAN RV RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1010 | BARIUM | 0.0085 | MG/L | 2.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1052 | SODIUM | 40.9 | MG/L | 160.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1017 | CHLORIDE | 68.9 | MG/L | 250.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1028 | IRON | 0.118 | MG/L | 0.3499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1055 | SULFATE | 73.8 | MG/L | 250.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1095 | ZINC | 0.0026 | MG/L | 5.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.05 | LN(10) |  | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 442 | MG/L | 500.4999 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-03-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-03-16 | AAA |  | 0.0149 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-03-16 | AAA |  | 1.4999 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 1.4999 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-03-16 | AAA |  | 0.4499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-03-16 | AAA |  | 9.4999 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-03-16 | AAA |  | 6.4999 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-03-16 | AAA |  | 0.6499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-03-16 | AAA |  | 2.4999 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-03-16 | AAA |  | 0.0749 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-03-16 | AAA |  | 0.6499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-03-16 | AAA |  | 0.9499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-03-16 | AAA |  | 0.0449 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-03-16 | AAA |  | 0.0449 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-03-16 | AAA |  | 0.1499 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-03-16 | AAA |  | 0.0249 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-03-16 | AAA |  | 0.0149 | POE
3491702 | FLORIDIAN RV RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-03-16 | AAA |  | 0.2499 | POE
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.6 | UG/L | 60.4999 | 2021-05-18 | L1 | 1 |  | BOAT RAMP LRAA TTHM=92.175 HAA5=49.925 (OEL: TTHM=79.75 HAA5=43.15)_NMS | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 30 | UG/L | 80.4999 | 2021-05-18 | L1 | 0.5 |  | BOAT RAMP LRAA TTHM=92.175 HAA5=49.925 (OEL: TTHM=79.75 HAA5=43.15)_NMS | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.87 | UG/L | 60.4999 | 2021-05-18 | L2 | 1 |  | A-15 LRAA TTHM=92.5 HAA5=50.5425 (OEL: TTHM = 79.8 HAA5=40.185)_NMS | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 30.1 | UG/L | 80.4999 | 2021-05-18 | L2 | 0.5 |  | A-15 LRAA TTHM=92.5 HAA5=50.5425 (OEL: TTHM = 79.8 HAA5=40.185)_NMS | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 56.3 | UG/L | 60.4999 | 2021-08-19 | L1 |  |  | BOAT RAMP. L1 TTHM LRAA = 96.15 AND OEL = 93.3. L1 HAA5 LRAA = 53.33 AND OEL = 52.95_AMF | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 95.6 | UG/L | 80.4999 | 2021-08-19 | L1 |  |  | BOAT RAMP. L1 TTHM LRAA = 96.15 AND OEL = 93.3. L1 HAA5 LRAA = 53.33 AND OEL = 52.95_AMF | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-08-19 | L2 |  |  | A-15. L2 TTHM LRAA = 96.68 AND OEL = 95.58. L2 HAA5 LRAA = 38.48 AND OEL = 24.59_AMF | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 97.6 | UG/L | 80.4999 | 2021-08-19 | L2 |  |  | A-15. L2 TTHM LRAA = 96.68 AND OEL = 95.58. L2 HAA5 LRAA = 38.48 AND OEL = 24.59_AMF | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.2 | UG/L | 60.4999 | 2021-11-15 | L1 | 1 |  | BOAT RAMP; L1 HAA5 LRAA = 39.93 AND OEL = 20.08; L1 TTHM LRAA = 70.74 AND OEL = 34.07_AMF | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 5.34 | UG/L | 80.4999 | 2021-11-15 | L1 | 0.5 |  | BOAT RAMP; L1 HAA5 LRAA = 39.93 AND OEL = 20.08; L1 TTHM LRAA = 70.74 AND OEL = 34.07_AMF | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.02 | UG/L | 60.4999 | 2021-11-15 | L2 | 1 |  | A-15; L2 HAA5 LRAA = 20.1 AND OEL = 4.73; L2 TTHM LRAA = 72.36 AND OEL = 34.3_AMF | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 4.75 | UG/L | 80.4999 | 2021-11-15 | L2 | 0.5 |  | A-15; L2 HAA5 LRAA = 20.1 AND OEL = 4.73; L2 TTHM LRAA = 72.36 AND OEL = 34.3_AMF | 3
3491702 | FLORIDIAN RV RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | N | SEC | 1022 | COPPER | 0.0014 | MG/L | 1.4999 | 2022-02-14 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.1 | UG/L | 60.4999 | 2022-05-17 | L1 |  |  | BOAT RAMP | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 2.98 | UG/L | 80.4999 | 2022-05-17 | L1 |  |  | BOAT RAMP | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.9 | UG/L | 60.4999 | 2022-05-17 | L2 |  |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 2.9 | UG/L | 80.4999 | 2022-05-17 | L2 |  |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 4.18 | UG/L | 80.4999 | 2022-08-15 | L2 | 0.39 |  | LOT A-15 OUTSIDE BIB | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.41 | UG/L | 60.4999 | 2022-08-15 | L1 | 0.98 |  | BOAT RAMP SINK BIB (HLKD) | 3
3491702 | FLORIDIAN RV RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 6.79 | LN(10) |  | 2022-11-08 | AAA |  |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1002 | ALUMINUM | 0.027 | MG/L | 0.2499 | 2022-11-08 | AAA | 0.024 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1017 | CHLORIDE | 66 | MG/L | 250.4999 | 2022-11-08 | AAA | 0.039 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2022-11-08 | AAA | 0.005 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2022-11-08 | AAA | 0.0099 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1028 | IRON | 0.05 | MG/L | 0.3499 | 2022-11-08 | AAA | 0.038 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-11-08 | AAA | 0.005 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-11-08 | AAA | 0.008 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1055 | SULFATE | 82 | MG/L | 250.4999 | 2022-11-08 | AAA | 0.034 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-11-08 | AAA | 0.05 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1905 | COLOR | 50 | COLOR UNITS | 15.4999 | 2022-11-08 | AAA | 5 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2022-11-08 | AAA | 1 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 450 | MG/L | 500.4999 | 2022-11-08 | AAA | 5 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-11-08 | AAA | 0.04 |  | SECONARIES PH Q QUALIFIER COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.87 | UG/L | 60.4999 | 2023-08-15 | L1 | 0.98 |  | BOAT RAMP | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 35.91 | UG/L | 80.4999 | 2023-08-15 | L2 | 0.39 |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | N | INOR | 1040 | NITRATE | 0.059 | MG/L | 10.4999 | 2023-10-16 | AAA | 0.024 |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2024-03-14 | AAA | 0.003 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1040 | NITRATE | 0.063 | MG/L | 10.4999 | 2024-03-14 | AAA | 0.024 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-14 | AAA | 0.0034 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-03-14 | AAA | 0.00025 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-03-14 | AAA | 0.00025 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-03-14 | AAA | 0.005 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1024 | CYANIDE | 0.0042 | MG/L | 0.2499 | 2024-03-14 | AAA | 0.004 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2024-03-14 | AAA | 0.0099 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-03-14 | AAA | 0.0005 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-03-14 | AAA | 0.008 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-03-14 | AAA | 0.0012 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1052 | SODIUM | 45 | MG/L | 160.4999 | 2024-03-14 | AAA | 0.8 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-03-14 | AAA | 0.001 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-03-14 | AAA | 0.002 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-03-14 | AAA | 0.00025 |  | POE - MERCURY Q QUALIFIER
3491702 | FLORIDIAN RV RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-03-14 | AAA | 0.024 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1017 | CHLORIDE | 65 | MG/L | 250.4999 | 2024-03-14 | AAA | 0.039 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-03-14 | AAA | 0.005 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1025 | FLUORIDE | 0.16 | MG/L | 2.0499 | 2024-03-14 | AAA | 0.0099 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1028 | IRON | 0.038 | MG/L | 0.3499 | 2024-03-14 | AAA | 0.038 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-03-14 | AAA | 0.005 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-03-14 | AAA | 0.008 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1055 | SULFATE | 89 | MG/L | 250.4999 | 2024-03-14 | AAA | 0.034 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-03-14 | AAA | 0.05 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1905 | COLOR | 44 | COLOR UNITS | 15.4999 | 2024-03-14 | AAA | 5 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-03-14 | AAA | 1 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.48 | LN(10) |  | 2024-03-14 | AAA | 0 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 440 | MG/L | 500.4999 | 2024-03-14 | AAA | 10 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | SEC | 2905 | FOAMING AGENTS | 0.057 |  | 0.5499 | 2024-03-14 | AAA | 0.04 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-03-14 | AAA | 0.5 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-03-14 | AAA | 0.24 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-03-14 | AAA | 0.48 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-03-14 | AAA | 0.49 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-03-14 | AAA | 0.44 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-03-14 | AAA | 0.4 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-03-14 | AAA | 0.28 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-03-14 | AAA | 0.4 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-03-14 | AAA | 0.41 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-03-14 | AAA | 0.44 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-03-14 | AAA | 0.32 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-03-14 | AAA | 0.36 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-03-14 | AAA | 0.33 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-03-14 | AAA | 0.25 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-03-14 | AAA | 0.44 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-03-14 | AAA | 0.49 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-03-14 | AAA | 0.37 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-03-14 | AAA | 0.16 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-03-14 | AAA | 0.2 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-03-14 | AAA | 0.33 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-03-14 | AAA | 0.26 | 0.5499 | POE
3491702 | FLORIDIAN RV RESORT | N | SEC | 1905 | COLOR | 16 | COLOR UNITS | 15.4999 | 2024-04-09 | AAA | 5 |  | POE - COLOR EXCEEDANCE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-04-22 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 65.76 | UG/L | 60.4999 | 2024-11-12 | L1 | 0.98 |  | HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535-EXCEEDANCE | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 133.51 | UG/L | 80.4999 | 2024-11-12 | L1 | 0.44 |  | HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535-EXCEEDANCE | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.35 | UG/L | 60.4999 | 2024-11-12 | L2 | 0.98 |  | HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 79.72 | UG/L | 80.4999 | 2024-11-12 | L2 | 0.44 |  | HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3491702 | FLORIDIAN RV RESORT | N | INOR | 1040 | NITRATE | 0.089 | MG/L | 10.4999 | 2025-01-14 | AAA | 0.024 |  | POE
3491702 | FLORIDIAN RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-14 | AAA |  |  | POE
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.45 | UG/L | 60.4999 | 2025-02-10 | L1 | 0.98 |  | BOAT RAMP - TTHM EXCEEDANCE | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 106.22 | UG/L | 80.4999 | 2025-02-10 | L1 | 0.44 |  | BOAT RAMP - TTHM EXCEEDANCE | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.1 | UG/L | 60.4999 | 2025-02-10 | L2 | 0.98 |  | A-15, TTHM EXCEEDANCE | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 111.16 | UG/L | 80.4999 | 2025-02-10 | L2 | 0.44 |  | A-15, TTHM EXCEEDANCE | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.6 | UG/L | 60.4999 | 2025-05-13 | L1 | 0.98 |  | SEWER PLANT TAP | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 6.3 | UG/L | 80.4999 | 2025-05-13 | L1 | 0.44 |  | SEWER PLANT TAP | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.02 | UG/L | 60.4999 | 2025-05-13 | L2 | 0.98 |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 6.28 | UG/L | 80.4999 | 2025-05-13 | L2 | 0.44 |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 18.78 | UG/L | 80.4999 | 2025-08-12 | L2 | 0.44 |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.26 | UG/L | 60.4999 | 2025-08-12 | L1 | 0.98 |  | WASTEWATER PLANT | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 17.17 | UG/L | 80.4999 | 2025-08-12 | L1 | 0.44 |  | WASTEWATER PLANT | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.58 | UG/L | 60.4999 | 2025-08-12 | L2 | 0.98 |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.7 | UG/L | 60.4999 | 2025-11-11 | L1 | 0.98 |  | SEWER PLANT TAP | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 9.91 | UG/L | 80.4999 | 2025-11-11 | L1 | 0.44 |  | SEWER PLANT TAP | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.25 | UG/L | 60.4999 | 2025-11-11 | L2 | 0.98 |  | A-15 | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 8.07 | UG/L | 80.4999 | 2025-11-11 | L2 | 0.44 |  | A-15 | 3
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-01-11 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-01-11 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-11 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-01-11 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-11 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-01-11 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-01-11 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491702 | FLORIDIAN RV RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.4 | PCI/L | 15.4999 | 2024-03-18 | AAA | 1.7 |  | 2024 RAD RESULTS
3491702 | FLORIDIAN RV RESORT | N | RAD | 4020 | RADIUM-226 | 2 | PCI/L | 3.4999 | 2024-03-18 | AAA | 0.5 | 1.4999 | 2024 RAD RESULTS
3491702 | FLORIDIAN RV RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-03-18 | AAA | 0.6 | 1.4999 | 2024 RAD RESULTS
3491702 | FLORIDIAN RV RESORT | D | DBP | 2950 | TOTAL THMS | 101.64 | UG/L | 80.4999 | 2024-08-19 | L2 | 0.39 |  | 2024 TTHM RESULTS (SINGLE SAMPLE EXCEEDANCE) | 3
3491702 | FLORIDIAN RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.22 | UG/L | 60.4999 | 2024-08-19 | L1 | 0.98 |  | 2024 HAA5 SAMPLE | 3
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-01-11 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-01-11 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-01-11 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-01-11 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2023-01-11 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-01-11 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-01-11 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-01-11 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-01-11 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-01-11 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-01-11 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-01-11 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-01-11 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-01-11 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-01-11 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-01-11 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-01-11 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-01-11 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-01-11 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-01-25 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-01-25 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-25 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-01-25 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-25 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-01-25 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-01-25 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-01-25 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-01-25 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-01-25 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-01-25 | 2234 EMPEROR DRIVE |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-01-25 | 2234 EMPEROR DRIVE |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-01-25 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-01-25 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-25 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-01-25 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-25 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-01-25 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-25 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-01-25 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-01-25 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-01-25 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-25 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-01-25 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-25 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-01-25 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-02-08 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-02-08 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-02-08 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-02-08 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-08 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 90 | MG/L |  | 2023-02-08 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-02-08 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 150 | MG/L |  | 2023-02-08 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-02-08 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-02-08 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-02-08 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-02-08 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-02-08 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-02-08 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-02-08 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-02-08 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-08 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-02-08 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-08 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-02-08 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-08 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-02-08 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-08 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-02-08 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-02-08 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-02-08 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.6 | UG/L | 60.4999 | 2023-02-15 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND (NO DISINF RESIDUAL REPORTED)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 71.1 | UG/L | 80.4999 | 2023-02-15 | L1 | 0.47 |  | 5371 MAJESTIC ISLAND (NO DISINF RESIDUAL REPORTED)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.4 | UG/L | 60.4999 | 2023-02-15 | L2 | 0.9 |  | 4805 DOC DR. (NO DISINF RESIDUAL REPORTED)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 47.7 | UG/L | 80.4999 | 2023-02-15 | L2 | 0.47 |  | 4805 DOC DR. (NO DISINF RESIDUAL REPORTED)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.8 | UG/L | 60.4999 | 2023-02-15 | L3 | 0.9 |  | L567 (FRIAR'S COVE) NO DISINF RESIDUAL REPORTED
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 60 | UG/L | 80.4999 | 2023-02-15 | L3 | 0.47 |  | L567 (FRIAR'S COVE) NO DISINF RESIDUAL REPORTED
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.2 | UG/L | 60.4999 | 2023-02-15 | L4 | 0.9 |  | 803 MASSACHUSETTS AVE. (NO DISINF RESIDUAL REPORTED)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 57.8 | UG/L | 80.4999 | 2023-02-15 | L4 | 0.47 |  | 803 MASSACHUSETTS AVE. (NO DISINF RESIDUAL REPORTED)
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-02-22 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-02-22 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-22 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-02-22 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 160 | MG/L |  | 2023-02-22 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-02-22 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-02-22 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-22 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-02-22 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-22 | LS 78 FRIAR COVE |  |  | LS 78 FRIAR COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-02-22 | LS 78 FRIAR COVE |  |  | LS 78 FRIAR COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-22 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-02-22 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-02-22 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-02-22 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-22 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-02-22 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-22 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2023-02-22 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-02-22 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-02-22 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-22 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-02-22 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-03-08 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-02-22 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-02-22 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-02-22 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-03-08 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-08 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-03-08 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-03-08 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-03-08 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-03-08 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-03-08 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-08 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-03-08 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-03-08 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-03-08 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-03-08 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-03-08 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-03-08 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-08 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-03-08 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-03-08 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-08 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-03-08 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-03-08 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-03-08 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-08 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-03-08 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-08 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-03-08 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-22 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-03-22 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-22 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2023-03-22 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-03-22 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-03-22 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-03-22 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 133 | MG/L |  | 2023-03-22 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-22 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-03-22 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-03-22 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-03-22 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-03-22 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-03-22 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-22 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-03-22 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-22 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-03-22 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-22 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-03-22 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-03-22 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-03-22 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-22 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-03-22 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-22 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-03-22 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-04-05 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2023-04-05 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-05 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-04-05 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-05 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-04-05 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-04-05 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-04-05 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-04-05 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 93 | MG/L |  | 2023-04-05 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-05 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-04-05 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-04-05 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2023-04-05 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-04-05 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-04-05 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-05 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-04-05 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-04-05 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-04-05 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-04-05 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-04-05 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-04-05 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-04-05 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-04-05 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-04-05 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.046 | MG/L | 10.4999 | 2023-04-11 | WTP4 | 0.025 |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-11 | WTP4 | 0.025 |  | WP4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2023-04-11 | WTP2 | 0.025 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-11 | WTP2 | 0.025 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-04-11 | WTP1 | 0.025 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-11 | WTP1 | 0.025 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-04-13 | WTP4 | 0.26 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-04-13 | WTP4 | 0.35 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-04-13 | WTP4 | 0.33 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-04-13 | WTP4 | 0.11 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP4 | 0.44 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-04-13 | WTP4 | 0.3 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP4 | 0.12 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-04-13 | WTP4 | 0.29 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP4 | 0.27 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP4 | 0.3 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-04-13 | WTP4 | 0.27 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP4 | 0.28 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP4 | 0.44 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP4 | 0.26 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP4 | 0.28 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP4 | 0.26 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP4 | 0.26 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP4 | 0.4 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-04-13 | WTP4 | 0.28 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-04-13 | WTP4 | 0.23 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP4 | 0.2 | 0.5499 | 2023 SAMPLES ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2023-04-13 | WTP1 | 0.025 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-13 | WTP1 | 0.025 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-04-13 | WTP1 | 0.0005 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1010 | BARIUM | 0.022 | MG/L | 2.4999 | 2023-04-13 | WTP1 | 0.0024 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-04-13 | WTP1 | 0.0067 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-04-13 | WTP1 | 0.0026 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-04-13 | WTP1 | 0.005 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1025 | FLUORIDE | 0.75 | MG/L | 4.0499 | 2023-04-13 | WTP1 | 0.015 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1030 | LEAD | 0.0002 | MG/L | 0.0154 | 2023-04-13 | WTP1 | 0.00022 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-04-13 | WTP1 | 9e-05 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-04-13 | WTP1 | 0.002 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-04-13 | WTP1 | 0.00083 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1052 | SODIUM | 46.3 | MG/L | 160.4999 | 2023-04-13 | WTP1 | 0.59 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-04-13 | WTP1 | 0.00083 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1017 | CHLORIDE | 90.3 | MG/L | 250.4999 | 2023-04-13 | WTP1 | 2.5 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-04-13 | WTP1 | 0.00019 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-04-13 | WTP1 | 0.00021 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-04-13 | WTP1 | 0.0072 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1022 | COPPER | 0.0016 | MG/L | 1.4999 | 2023-04-13 | WTP1 | 0.00093 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1025 | FLUORIDE | 0.75 | MG/L | 2.0499 | 2023-04-13 | WTP1 | 0.015 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-04-13 | WTP1 | 0.016 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1032 | MANGANESE | 0.0011 | MG/L | 0.0549 | 2023-04-13 | WTP1 | 0.00093 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-04-13 | WTP1 | 0.0013 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1055 | SULFATE | 71.9 | MG/L | 250.4999 | 2023-04-13 | WTP1 | 2.5 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-04-13 | WTP1 | 0.0076 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-04-13 | WTP1 | 5 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 374 | MG/L | 500.4999 | 2023-04-13 | WTP1 | 5 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-04-13 | WTP1 | 0.099 |  | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-04-13 | WTP1 | 0.35 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-04-13 | WTP1 | 0.33 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-04-13 | WTP1 | 0.11 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP1 | 0.44 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-04-13 | WTP1 | 0.26 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-04-13 | WTP1 | 0.3 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP1 | 0.12 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-04-13 | WTP1 | 0.29 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP1 | 0.27 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP1 | 0.3 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-04-13 | WTP1 | 0.27 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP1 | 0.28 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP1 | 0.44 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP1 | 0.26 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP1 | 0.28 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP1 | 0.26 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP1 | 0.26 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP1 | 0.4 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-04-13 | WTP1 | 0.28 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-04-13 | WTP1 | 0.23 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP1 | 0.2 | 0.5499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-13 | WTP1 | 0.0023 | 0.0149 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP1 | 0.0027 | 0.0249 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-13 | WTP1 | 0.023 | 0.1499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP1 | 0.25 | 1.4999 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-13 | WTP1 | 0.49 | 1.4999 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-13 | WTP1 | 0.16 | 0.4499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-13 | WTP1 | 3.3 | 9.4999 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-13 | WTP1 | 4.2 | 6.4999 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-13 | WTP1 | 0.35 | 0.6499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-13 | WTP1 | 0.46 | 2.4999 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-13 | WTP1 | 0.039 | 0.0749 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-13 | WTP1 | 0.46 | 0.6499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-13 | WTP1 | 0.04 | 0.1499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-13 | WTP1 | 0.16 | 0.2499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.084 | UG/L | 54.9999 | 2023-04-13 | WTP1 | 0.024 | 0.1499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-13 | WTP1 | 0.59 | 0.9499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP1 | 0.003 | 0.0249 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP1 | 0.014 | 0.1499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-13 | WTP1 | 0.029 | 0.2499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-13 | WTP1 | 0.013 | 0.0449 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0.11 | UG/L | 74.9999 | 2023-04-13 | WTP1 | 0.096 | 0.1499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-13 | WTP1 | 0.053 | 0.2499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP1 | 0.014 | 0.1499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP1 | 0.019 | 0.0249 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-13 | WTP1 | 0.014 | 0.0449 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-13 | WTP1 | 0.044 | 0.1499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP1 | 0.0065 | 0.0249 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-13 | WTP1 | 0.0076 | 0.0149 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-13 | WTP1 | 0.035 | 0.2499 | WP1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-13 | WTP2 | 0.0023 | 0.0149 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP2 | 0.0027 | 0.0249 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-13 | WTP2 | 0.023 | 0.1499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP2 | 0.25 | 1.4999 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0.64 | UG/L | 249.9999 | 2023-04-13 | WTP2 | 0.49 | 1.4999 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-13 | WTP2 | 0.16 | 0.4499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-13 | WTP2 | 3.3 | 9.4999 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-13 | WTP2 | 4.2 | 6.4999 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-13 | WTP2 | 0.35 | 0.6499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-13 | WTP2 | 0.46 | 2.4999 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-13 | WTP2 | 0.039 | 0.0749 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-13 | WTP2 | 0.46 | 0.6499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-13 | WTP2 | 0.04 | 0.1499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-13 | WTP2 | 0.16 | 0.2499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.089 | UG/L | 54.9999 | 2023-04-13 | WTP2 | 0.0024 | 0.1499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-13 | WTP2 | 0.59 | 0.9499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP2 | 0.014 | 0.1499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-13 | WTP2 | 0.029 | 0.2499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-13 | WTP2 | 0.013 | 0.0449 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP2 | 0.003 | 0.0249 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0.11 | UG/L | 74.9999 | 2023-04-13 | WTP2 | 0.096 | 0.1499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-13 | WTP2 | 0.053 | 0.2499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP2 | 0.014 | 0.1499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP2 | 0.019 | 0.0249 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-13 | WTP2 | 0.014 | 0.0449 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-13 | WTP2 | 0.044 | 0.1499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP2 | 0.0064 | 0.0249 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-13 | WTP2 | 0.0076 | 0.0149 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-13 | WTP2 | 0.035 | 0.2499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2023-04-13 | WTP2 | 0.0024 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.046 | MG/L | 10.4999 | 2023-04-13 | WTP2 | 0.025 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-13 | WTP2 | 0.025 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-04-13 | WTP2 | 0.0005 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-04-13 | WTP2 | 0.00067 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-04-13 | WTP2 | 0.0026 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1024 | CYANIDE | 0.006 | MG/L | 0.2499 | 2023-04-13 | WTP2 | 0.005 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1025 | FLUORIDE | 0.58 | MG/L | 4.0499 | 2023-04-13 | WTP2 | 0.015 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-04-13 | WTP2 | 0.00022 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-04-13 | WTP2 | 9e-05 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-04-13 | WTP2 | 0.002 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-04-13 | WTP2 | 0.00083 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1052 | SODIUM | 17.8 | MG/L | 160.4999 | 2023-04-13 | WTP2 | 0.59 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-04-13 | WTP2 | 0.00083 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-04-13 | WTP2 | 0.00019 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-04-13 | WTP2 | 0.00021 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-04-13 | WTP2 | 0.0072 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1017 | CHLORIDE | 35.6 | MG/L | 250.4999 | 2023-04-13 | WTP2 | 2.5 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1022 | COPPER | 0.0038 | MG/L | 1.4999 | 2023-04-13 | WTP2 | 0.00093 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1025 | FLUORIDE | 0.58 | MG/L | 2.0499 | 2023-04-13 | WTP2 | 0.015 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1028 | IRON | 0.028 | MG/L | 0.3499 | 2023-04-13 | WTP2 | 0.016 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-04-13 | WTP2 | 0.00093 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-04-13 | WTP2 | 0.0013 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1055 | SULFATE | 6.2 | MG/L | 250.4999 | 2023-04-13 | WTP2 | 2.5 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-04-13 | WTP2 | 0.0076 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-04-13 | WTP2 | 5 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 247 | MG/L | 500.4999 | 2023-04-13 | WTP2 | 5 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-04-13 | WTP2 | 0.099 |  | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-04-13 | WTP2 | 0.35 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-04-13 | WTP2 | 0.33 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-04-13 | WTP2 | 0.11 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP2 | 0.44 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-04-13 | WTP2 | 0.26 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-04-13 | WTP2 | 0.3 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP2 | 0.12 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-04-13 | WTP2 | 0.29 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP2 | 0.27 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP2 | 0.3 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-04-13 | WTP2 | 0.27 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP2 | 0.28 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP2 | 0.44 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP2 | 0.26 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-04-13 | WTP2 | 0.28 | 0.5499 | WP2
3491909 | LAKE TOHO RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-07-05 | AAA | 0.2 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-05 | AAA | 0.2 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1010 | BARIUM | 0.0114 | MG/L | 2.4999 | 2021-07-05 | AAA | 0.002 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-07-05 | AAA | 0.2 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1030 | LEAD | 0.0036 | MG/L | 0.0154 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1052 | SODIUM | 28.5 | MG/L | 160.4999 | 2021-07-05 | AAA | 0.5 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-07-05 | AAA | 2e-05 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-07-05 | AAA | 0.002 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-07-05 | AAA | 0.0005 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-07-05 | AAA | 0.001 |  | CYANIDE HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN (NN
3491909 | LAKE TOHO RESORT | N | SEC | 1017 | CHLORIDE | 36 | MG/L | 250.4999 | 2021-07-05 | AAA | 0.4 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1022 | COPPER | 0.02 | MG/L | 1.4999 | 2021-07-05 | AAA | 0.001 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-07-05 | AAA | 0.2 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1028 | IRON | 0.493 | MG/L | 0.3499 | 2021-07-05 | AAA | 0.01 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-07-05 | AAA | 0.001 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-07-05 | AAA | 0.0005 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1055 | SULFATE | 1.84 | MG/L | 250.4999 | 2021-07-05 | AAA | 1 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1095 | ZINC | 0.0072 | MG/L | 5.4999 | 2021-07-05 | AAA | 0.002 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-07-05 | AAA | 5 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.05 | LN(10) |  | 2021-07-05 | AAA | 0.01 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 176 | MG/L | 500.4999 | 2021-07-05 | AAA | 2.5 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-07-05 | AAA | 0.2 |  | ALUMINUM HAS J QUALIFIER-NOT ENT'D-NO EXPLANATION GIVEN, ODOR MISSING. IRON 0.493 MG/L (OVER MCL OF 0.3 MG/L)
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 0.5 | 0.5499 | 7/21 VOC
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-07-05 | AAA | 0.01 | 0.0149 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.01 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-07-05 | AAA | 0.05 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.5 | 1.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-07-05 | AAA | 0.1 | 1.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-07-05 | AAA | 0.4 | 0.4499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-07-05 | AAA | 9 | 9.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-07-05 | AAA | 6 | 6.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-07-05 | AAA | 0.6 | 0.6499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-07-05 | AAA | 2 | 2.4999 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-07-05 | AAA | 0.07 | 0.0749 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-07-05 | AAA | 0.6 | 0.6499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-07-05 | AAA | 0.9 | 0.9499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-07-05 | AAA | 0.2 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-07-05 | AAA | 0.2 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-07-05 | AAA | 0.01 | 0.0449 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.01 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-07-05 | AAA | 0.2 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.02 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-07-05 | AAA | 0.04 | 0.0449 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-07-05 | AAA | 0.1 | 0.1499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-07-05 | AAA | 0.02 | 0.0249 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-07-05 | AAA | 0.01 | 0.0149 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-07-05 | AAA | 0.01 | 0.2499 | 7/21 SOC (NO DETECTIONS)
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 0.5 | 0.5499 | 9/21 VOC
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-09-30 | AAA | 0.01 | 0.0149 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.01 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-09-30 | AAA | 0.05 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.5 | 1.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-09-30 | AAA | 0.1 | 1.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-09-30 | AAA | 0.4 | 0.4499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-09-30 | AAA | 9 | 9.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-09-30 | AAA | 6 | 6.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-09-30 | AAA | 0.6 | 0.6499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-09-30 | AAA | 2 | 2.4999 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-09-30 | AAA | 0.07 | 0.0749 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 2.08 | UG/L | 6.4999 | 2021-09-30 | AAA | 0.6 | 0.6499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-09-30 | AAA | 0.2 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-09-30 | AAA | 0.2 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-09-30 | AAA | 0.9 | 0.9499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-09-30 | AAA | 0.01 | 0.0449 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.01 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-09-30 | AAA | 0.2 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.02 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-09-30 | AAA | 0.04 | 0.0449 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-09-30 | AAA | 0.1 | 0.1499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-09-30 | AAA | 0.02 | 0.0249 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-09-30 | AAA | 0.01 | 0.0149 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-09-30 | AAA | 0.01 | 0.2499 | 9/21 SOC (DI(2-ETHYLHEXYL)PHTHALATE 2.08 UG/L (> RDL OF 0.6 UG/L BUT < MCL OF 6 UG/L, TRIGGERS QTRLY TESTING OF "PHTHALATE"
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2022-07-12 | AAA | 1.2 |  | RADS
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 0.7 | PCI/L | 3.4999 | 2022-07-12 | AAA | 0.3 | 1.4999 | RADS
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-07-12 | AAA | 0.7 | 1.4999 | RADS
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-07-29 | AAA | 0.44 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-07-29 | AAA | 0.27 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-07-29 | AAA | 0.44 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-07-29 | AAA | 0.44 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-07-29 | AAA | 0.39 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-07-29 | AAA | 0.33 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.29 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-07-29 | AAA | 0.22 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 0.21 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.24 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-07-29 | AAA | 0.29 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.25 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-07-29 | AAA | 0.26 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.14 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-07-29 | AAA | 0.27 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.42 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 0.36 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.26 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-07-29 | AAA | 0.33 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-07-29 | AAA | 0.31 | 0.5499 | POE VOC 2022
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 0.25 | 0.5499 | POE VOC 2022
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP2 | 0.26 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP2 | 0.26 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-04-13 | WTP2 | 0.4 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-04-13 | WTP2 | 0.28 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-04-13 | WTP2 | 0.23 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-04-13 | WTP2 | 0.2 | 0.5499 | WP2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-13 | WTP4 |  | 0.0149 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP4 |  | 0.0249 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-13 | WTP4 |  | 0.1499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP4 |  | 1.4999 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-13 | WTP4 |  | 1.4999 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-13 | WTP4 |  | 0.4499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-13 | WTP4 |  | 9.4999 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-13 | WTP4 |  | 6.4999 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-13 | WTP4 |  | 0.6499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-13 | WTP4 |  | 2.4999 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-13 | WTP4 |  | 0.0749 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-13 | WTP4 |  | 0.6499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-13 | WTP4 |  | 0.1499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-13 | WTP4 |  | 0.2499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-04-13 | WTP4 |  | 0.1499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-13 | WTP4 |  | 0.9499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-13 | WTP4 |  | 0.1499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-13 | WTP4 |  | 0.2499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-13 | WTP4 |  | 0.0449 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP4 |  | 0.0249 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-13 | WTP4 |  | 0.1499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-13 | WTP4 |  | 0.2499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0.085 | UG/L | 1.4999 | 2023-04-13 | WTP4 |  | 0.1499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP4 |  | 0.0249 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-13 | WTP4 |  | 0.0449 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-13 | WTP4 |  | 0.1499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-13 | WTP4 |  | 0.0249 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-13 | WTP4 |  | 0.0149 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-13 | WTP4 |  | 0.2499 | SET 1 OF SOC'S FOR WTP 2023 LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.95 | PCI/L | 15.4999 | 2023-04-13 | WTP1 | 2.56 |  | POE LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2023-04-13 | WTP1 | 0.19 | 0.667 | POE LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4020 | RADIUM-226 | 2.37 | PCI/L | 3.4999 | 2023-04-13 | WTP1 | 0.773 | 1.4999 | POE LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-04-13 | WTP1 | 0.724 | 1.4999 | POE LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-04-13 | WTP2 | 0.697 | 1.4999 | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-04-13 | WTP2 | 2.51 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2023-04-13 | WTP2 | 0.19 | 0.667 | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2023-04-13 | WTP2 | 0.791 | 1.4999 | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-04-13 | WTP4 | 2.68 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2023-04-13 | WTP4 | 0.19 | 0.667 | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4020 | RADIUM-226 | 0.9615 | PCI/L | 3.4999 | 2023-04-13 | WTP4 | 0.248 | 1.4999 | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | RAD | 4030 | RADIUM-228 | 0.714 | PCI/L | 2.4999 | 2023-04-13 | WTP4 | 0.714 | 1.4999 | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.052 | MG/L | 10.4999 | 2023-04-13 | WTP4 | 0.025 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-04-13 | WTP4 | 0.025 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-04-13 | WTP4 | 0.0005 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1010 | BARIUM | 0.015 | MG/L | 2.4999 | 2023-04-13 | WTP4 | 0.0024 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-04-13 | WTP4 | 0.00067 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-04-13 | WTP4 | 0.0026 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-04-13 | WTP4 | 0.005 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1025 | FLUORIDE | 0.59 | MG/L | 4.0499 | 2023-04-13 | WTP4 | 0.015 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-04-13 | WTP4 | 0.00022 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-04-13 | WTP4 | 9e-05 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-04-13 | WTP4 | 0.002 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-04-13 | WTP4 | 0.00083 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1052 | SODIUM | 19.4 | MG/L | 160.4999 | 2023-04-13 | WTP4 | 0.59 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-04-13 | WTP4 | 0.00083 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-04-13 | WTP4 | 0.00019 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-04-13 | WTP4 | 0.00021 |  | POE ALL OK LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-04-13 | WTP4 | 0.0072 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1017 | CHLORIDE | 39.3 | MG/L | 250.4999 | 2023-04-13 | WTP4 | 2.3 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-04-13 | WTP4 | 0.00093 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1025 | FLUORIDE | 0.59 | MG/L | 2.0499 | 2023-04-13 | WTP4 | 0.015 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1028 | IRON | 0.021 | MG/L | 0.3499 | 2023-04-13 | WTP4 | 0.016 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-04-13 | WTP4 | 0.00093 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-04-13 | WTP4 | 0.0013 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1055 | SULFATE | 5.5 | MG/L | 250.4999 | 2023-04-13 | WTP4 | 2.5 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-04-13 | WTP4 | 0.0076 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2023-04-13 | WTP4 | 5 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 248 | MG/L | 500.4999 | 2023-04-13 | WTP4 | 3 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-04-13 | WTP4 | 0.099 |  | PH AND TEMP Q QUALIFIED LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-04-19 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-04-19 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-19 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-04-19 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-04-19 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-04-19 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-19 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-04-19 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-19 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-04-19 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-19 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-04-19 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-04-19 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-04-19 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-04-19 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-04-19 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-04-19 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-04-19 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-19 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-04-19 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-19 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-04-19 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-19 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-04-19 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-19 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-04-19 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-03 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-05-03 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-03 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-05-03 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-03 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-05-03 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-03 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2023-05-03 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-03 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-03 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-05-03 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-05-03 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-03 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-05-03 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-03 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-05-03 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-03 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-05-03 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-03 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-05-03 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-03 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-05-03 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-05-03 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-05-03 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-03 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-03 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 45.2 | UG/L | 80.4999 | 2023-05-16 | L2 | 0.47 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33 | UG/L | 60.4999 | 2023-05-16 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 68.1 | UG/L | 80.4999 | 2023-05-16 | L1 | 0.47 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2023-05-16 | L2 | 0.9 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.1 | UG/L | 60.4999 | 2023-05-16 | L4 | 0.9 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 64.6 | UG/L | 80.4999 | 2023-05-16 | L4 | 0.47 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.4 | UG/L | 60.4999 | 2023-05-16 | L3 | 0.9 |  | LS67
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 64 | UG/L | 80.4999 | 2023-05-16 | L3 | 0.47 |  | LS67
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-05-17 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-05-17 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-17 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-05-17 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-17 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-05-17 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-05-17 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-17 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-17 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-17 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-17 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-05-17 | 2234 EMPERORS DR |  |  | 2234 EMPERORS DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-17 | 2234 EMPERORS DR |  |  | 2234 EMPERORS DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-17 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-17 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-05-17 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-17 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-05-17 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-17 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-17 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-05-17 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-17 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-17 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-17 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-17 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2023-05-17 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.6 | LN(10) |  | 2023-05-31 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-05-31 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.6 | LN(10) |  | 2023-05-31 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-05-31 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-31 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-05-31 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-05-31 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-05-31 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-05-31 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PL
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-05-31 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PL
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-31 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-05-31 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-05-31 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-05-31 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-05-31 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-05-31 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-05-31 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-05-31 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-07-29 | AAA | 0.0069 | 0.0149 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.0071 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-07-29 | AAA | 0.0068 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.12 | 1.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-07-29 | AAA | 0.37 | 0.4499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-07-29 | AAA | 6 | 9.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-07-29 | AAA | 5.9 | 6.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-07-29 | AAA | 0.5 | 0.6499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-07-29 | AAA | 1.8 | 2.4999 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-07-29 | AAA | 0.06 | 0.0749 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-07-29 | AAA | 0.5 | 0.6499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-07-29 | AAA | 0.09 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-07-29 | AAA | 0.18 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-07-29 | AAA | 0.019 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-07-29 | AAA | 0.51 | 0.9499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-07-29 | AAA | 0.09 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-07-29 | AAA | 0.15 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-07-29 | AAA | 0.006 | 0.0449 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.0056 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-07-29 | AAA | 0.095 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-07-29 | AAA | 0.09 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.0063 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.015 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-07-29 | AAA | 0.038 | 0.0449 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-07-29 | AAA | 0.093 | 0.1499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-07-29 | AAA | 0.0058 | 0.0249 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-07-29 | AAA | 0.0049 | 0.0149 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-07-29 | AAA | 0.053 | 0.2499 | POE SOC 2022 DALAPON HAD "J" QUALIFIER
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-30 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-05 | AAA | 0.024 |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-05 | AAA | 0.0034 |  | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA | 0.28 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA | 0.32 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-05 | AAA | 0.28 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.44 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-05 | AAA | 0.46 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-05 | AAA | 0.26 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA | 0.2 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-05 | AAA | 0.18 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.28 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.36 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-05 | AAA | 0.39 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.23 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.26 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.28 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.12 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.24 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.12 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA | 0.17 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-05 | AAA | 0.22 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-05 | AAA | 0.17 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.39 | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-05 | AAA |  | 0.4499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-05 | AAA |  | 9.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-05 | AAA |  | 6.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-05 | AAA |  | 2.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-05 | AAA |  | 0.0749 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-05 | AAA |  | 0.9499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-10-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2022-10-07 | AAA | 0.6 |  | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 1.2 | PCI/L | 3.4999 | 2022-10-07 | AAA | 0.4 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-10-07 | AAA | 0.6 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 57.15 | UG/L | 60.4999 | 2022-11-16 | L2 |  |  | LOT 64 TTHM/HAA5 TTHM EXCEEDANCE
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 106.24 | UG/L | 80.4999 | 2022-11-16 | L2 |  |  | LOT 64 TTHM/HAA5 TTHM EXCEEDANCE
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 55.54 | UG/L | 60.4999 | 2022-11-17 | L1 | 0.98 |  | TTHM EXCEEDANCE
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 96.53 | UG/L | 80.4999 | 2022-11-17 | L1 | 0.39 |  | TTHM EXCEEDANCE
3491909 | LAKE TOHO RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-12-15 | AAA | 0.024 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-15 | AAA | 0.0034 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-12-15 | AAA | 0.00025 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2022-12-15 | AAA | 0.003 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-12-15 | AAA | 0.00025 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-12-15 | AAA | 0.1 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-12-15 | AAA | 0.004 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2022-12-15 | AAA | 0.0099 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-12-15 | AAA | 0.0005 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-12-15 | AAA | 3e-05 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-12-15 | AAA | 0.008 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-12-15 | AAA | 0.0012 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1052 | SODIUM | 17 | MG/L | 160.4999 | 2022-12-15 | AAA | 0.8 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-12-15 | AAA | 0.001 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-12-15 | AAA | 0.002 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-12-15 | AAA | 0.00025 |  | POE PRIMARY
3491909 | LAKE TOHO RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-12-15 | AAA | 0.0024 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1017 | CHLORIDE | 23 | MG/L | 250.4999 | 2022-12-15 | AAA | 0.0039 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2022-12-15 | AAA | 0.005 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1025 | FLUORIDE | 0.17 | MG/L | 2.0499 | 2022-12-15 | AAA | 0.0099 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-12-15 | AAA | 0.038 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1032 | MANGANESE | 0.0071 | MG/L | 0.0549 | 2022-12-15 | AAA | 0.005 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-12-15 | AAA | 0.0005 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-12-15 | AAA | 0.05 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1905 | COLOR | 28 | COLOR UNITS | 15.4999 | 2022-12-15 | AAA | 5 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-12-15 | AAA | 1 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 200 | MG/L | 500.4999 | 2022-12-15 | AAA | 5 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | SEC | 2905 | FOAMING AGENTS | 0.059 |  | 0.5499 | 2022-12-15 | AAA | 0.04 |  | SECONARIES SULFATE J PH Q, COLOR EXCEED
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.69 | UG/L | 60.4999 | 2022-08-04 | L1 |  |  | LOT 19 AL
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 41.29 | UG/L | 80.4999 | 2022-08-04 | L1 |  |  | LOT 19 AL
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 56.6 | UG/L | 60.4999 | 2022-08-17 | L2 |  |  | LOT 64 AL
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 111.52 | UG/L | 80.4999 | 2022-08-17 | L2 |  |  | LOT 64 AL
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-01-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-01-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-01-05 | AAA |  | 0.4499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 9.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-01-05 | AAA |  | 6.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-01-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-01-05 | AAA |  | 2.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-01-05 | AAA |  | 0.0749 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-01-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-01-05 | AAA |  | 0.9499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-01-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-01-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.2 | PCI/L | 15.4999 | 2023-01-05 | AAA | 0.7 |  | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 1.3 | PCI/L | 3.4999 | 2023-01-05 | AAA | 0.4 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-01-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-01-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-01-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-01-05 | AAA |  | 0.4499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-01-05 | AAA |  | 9.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-01-05 | AAA |  | 6.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-01-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-01-05 | AAA |  | 2.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-01-05 | AAA |  | 0.0749 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-01-05 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-01-05 | AAA |  | 0.9499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-01-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-01-05 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-01-05 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-01-05 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-01-05 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-01-05 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.2 | PCI/L | 15.4999 | 2023-01-05 | AAA | 0.7 |  | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 1.3 | PCI/L | 3.4999 | 2023-01-05 | AAA | 0.5 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-01-05 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 77.94 | UG/L | 60.4999 | 2023-02-15 | L1 | 0.98 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 99.97 | UG/L | 80.4999 | 2023-02-15 | L1 | 0.39 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 62.01 | UG/L | 60.4999 | 2023-02-15 | L2 | 0.98 |  | LOT 64 (HLKD)
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 106.38 | UG/L | 80.4999 | 2023-02-15 | L2 | 0.39 |  | LOT 64 (HLKD)
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.5 | LN(10) |  | 2023-05-31 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-05-31 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-05-31 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-05-31 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.5 | LN(10) |  | 2023-05-31 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-05-31 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.5 | LN(10) |  | 2023-05-31 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-05-31 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-14 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-06-14 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-14 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-06-14 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-14 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-06-14 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-06-14 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-06-14 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-06-14 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-06-14 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-06-14 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-06-14 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-06-14 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-06-14 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-06-14 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-06-14 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-06-14 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-06-14 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-14 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-06-14 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-06-14 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-06-14 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-14 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-06-14 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-14 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-06-14 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-06-28 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2023-06-28 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-06-28 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-06-28 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-06-28 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-06-28 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2023-06-28 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-06-28 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-28 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-06-28 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-28 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2023-06-28 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-06-28 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-06-28 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-06-28 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-06-28 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-28 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-06-28 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-28 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-06-28 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-28 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-06-28 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-28 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-06-28 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-28 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-06-28 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-07-12 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-07-12 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-07-12 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-12 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-07-12 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-07-12 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-07-12 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-12 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2023-07-12 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-12 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-07-12 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-07-12 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-07-12 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-07-12 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-12 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-07-12 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-12 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-07-12 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-12 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2023-07-12 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-12 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-07-12 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-07-12 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-07-12 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-12 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-26 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-07-26 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-07-26 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-07-26 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-07-26 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-07-26 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-07-26 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-07-12 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-07-26 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2023-07-26 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-07-26 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-07-26 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-07-26 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-07-26 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-07-26 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-26 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-07-26 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-07-26 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-07-26 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-07-26 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-07-26 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-07-26 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-07-26 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-07-26 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-07-26 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-07-26 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-07-26 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-09 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 132 | MG/L |  | 2023-08-09 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-08-09 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-08-09 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-08-09 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-08-09 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-08-09 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-08-09 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-09 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-08-09 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-09 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-08-09 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-08-09 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-08-09 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-09 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-08-09 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-09 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-08-09 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-08-09 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-08-09 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-08-09 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-08-09 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-09 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 90 | MG/L |  | 2023-08-09 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-09 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-08-09 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.1 | UG/L | 60.4999 | 2023-08-18 | L2 | 0.9 |  | 4805 DOC DR. TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 40.2 | UG/L | 80.4999 | 2023-08-18 | L2 | 0.47 |  | 4805 DOC DR. TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2023-08-18 | L3 | 0.9 |  | LS67 FRIARS LN & CANOE CREEK RD TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 42.8 | UG/L | 80.4999 | 2023-08-18 | L3 | 0.47 |  | LS67 FRIARS LN & CANOE CREEK RD TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.1 | UG/L | 60.4999 | 2023-08-18 | L4 | 0.9 |  | 803 MASSACHUSETTS AVE. TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 40.8 | UG/L | 80.4999 | 2023-08-18 | L4 | 0.47 |  | 803 MASSACHUSETTS AVE. TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.3 | UG/L | 60.4999 | 2023-08-18 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR. TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43 | UG/L | 80.4999 | 2023-08-18 | L1 | 0.47 |  | 5371 MAJESTIC ISLAND CIR. TTHM HAA5
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-23 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-08-23 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-23 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-08-23 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-23 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-08-23 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-08-23 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-08-23 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-23 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-08-23 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-08-23 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-08-23 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-08-23 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-08-23 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-23 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2023-08-23 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-08-23 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-08-23 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-08-23 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-08-23 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-08-23 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-08-23 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-08-23 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-08-23 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-23 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-08-23 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-09-06 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-09-06 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-06 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-09-06 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-09-06 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-09-06 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-09-06 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-09-06 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-09-06 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-06 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-06 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-09-06 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-09-06 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-09-06 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-06 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-09-06 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-06 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-09-06 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-09-06 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-09-06 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-09-06 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-09-06 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-06 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-15 | WTP1 | 0.52 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-09-06 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-06 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-09-06 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-15 | WTP1 | 0.01 | 0.0149 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP1 | 0.016 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-15 | WTP1 | 0.25 | 0.6499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-15 | WTP1 | 0.035 | 0.0749 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-15 | WTP1 | 0.5 | 0.6499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-15 | WTP1 | 0.078 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-15 | WTP1 | 0.1 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-15 | WTP1 | 0.2 | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-15 | WTP1 | 0.0042 | 0.0055 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-15 | WTP1 | 0.014 | 0.0449 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP1 | 0.018 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-15 | WTP1 | 0.054 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP1 | 0.01 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-15 | WTP2 | 0.01 | 0.0149 | POE, J QUALIFIED ENDRIN LMC
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-04-06 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-06 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-06 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-06 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-06 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-06 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-06 | AAA |  | 0.4499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-06 | AAA |  | 9.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-06 | AAA |  | 6.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-06 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-06 | AAA |  | 2.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-06 | AAA |  | 0.0749 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-06 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-06 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-06 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-04-06 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-06 | AAA |  | 0.9499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-06 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-06 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-06 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-06 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-06 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-06 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-06 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-06 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-06 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-06 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-06 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-06 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-06 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2 | PCI/L | 15.4999 | 2023-04-13 | AAA | 0.8 |  | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2023-04-13 | AAA | 0.4 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0.9 | PCI/L | 2.4999 | 2023-04-13 | AAA | 0.6 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.15 | UG/L | 60.4999 | 2023-05-16 | L1 | 0.98
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 51.55 | UG/L | 80.4999 | 2023-05-16 | L1 | 0.39
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.92 | UG/L | 60.4999 | 2023-05-16 | L2 | 0.98
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 44.36 | UG/L | 80.4999 | 2023-05-16 | L2 | 0.39
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-07-24 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-07-24 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-07-24 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-07-24 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-07-24 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-07-24 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-07-24 | AAA |  | 0.4499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-07-24 | AAA |  | 9.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-07-24 | AAA |  | 6.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-07-24 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-07-24 | AAA |  | 2.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-07-24 | AAA |  | 0.0749 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-07-24 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-07-24 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-07-24 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-07-24 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-07-24 | AAA |  | 0.9499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-07-24 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-07-24 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-07-24 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-07-24 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-07-24 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-07-24 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-07-24 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-07-24 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-07-24 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-07-24 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-24 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-24 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-07-24 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.8 | PCI/L | 15.4999 | 2023-07-24 | AAA | 1.4 |  | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2023-07-24 | AAA | 0.5 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-07-24 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 67.25 | UG/L | 60.4999 | 2023-08-16 | L1 | 0.98 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 108.63 | UG/L | 80.4999 | 2023-08-16 | L1 | 0.39 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 69.39 | UG/L | 60.4999 | 2023-08-16 | L2 | 0.98 |  | LOT 64
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 110.38 | UG/L | 80.4999 | 2023-08-16 | L2 | 0.39 |  | LOT 64
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-10-18 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2023-10-18 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | INOR | 1041 | NITRITE | 0.065 | MG/L | 1.4999 | 2023-10-18 | AAA | 0.0034 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-10-18 | AAA | 0.5 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-10-18 | AAA | 0.24 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-10-18 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-10-18 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-10-18 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-10-18 | AAA | 0.28 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-10-18 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-10-18 | AAA | 0.41 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-10-18 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-10-18 | AAA | 0.32 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-10-18 | AAA | 0.36 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-10-18 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-10-18 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-10-18 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-10-18 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-10-18 | AAA | 0.37 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-10-18 | AAA | 0.16 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-10-18 | AAA | 0.2 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-10-18 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-10-18 | AAA | 0.26 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-18 | AAA | 0.0069 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-18 | AAA | 0.0071 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-18 | AAA | 0.0068 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-18 | AAA | 0.12 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-18 | AAA | 0.37 | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-18 | AAA | 6 | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-18 | AAA | 5.9 | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-18 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-18 | AAA | 1.8 | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-18 | AAA | 0.06 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-18 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-18 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-18 | AAA | 0.18 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-18 | AAA | 0.019 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-18 | AAA | 0.51 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-18 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-18 | AAA | 0.15 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-18 | AAA | 0.006 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-18 | AAA | 0.0052 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-18 | AAA | 0.095 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-18 | AAA | 0.09 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-18 | AAA | 0.0063 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-18 | AAA | 0.015 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-18 | AAA | 0.038 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-18 | AAA | 0.093 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-18 | AAA | 0.0062 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-18 | AAA | 0.0092 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-18 | AAA | 0.053 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 1.2 | UG/L | 249.9999 | 2023-10-18 | AAA | 0.9 | 1.4999 | 4Q23 DALAPON DETECT
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.28 | UG/L | 60.4999 | 2023-11-16 | L1 | 0.98 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 14.56 | UG/L | 80.4999 | 2023-11-16 | L1 | 0.39 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.68 | UG/L | 60.4999 | 2023-11-16 | L2 | 0.98 |  | LOT 64
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 15.21 | UG/L | 80.4999 | 2023-11-16 | L2 | 0.39 |  | LOT 64
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-11-16 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP2 | 0.016 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-15 | WTP2 | 0.052 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-15 | WTP2 | 0.25 | 0.6499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-15 | WTP2 | 0.035 | 0.0749 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-15 | WTP2 | 0.5 | 0.6499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-15 | WTP2 | 0.078 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-15 | WTP2 | 0.1 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-15 | WTP2 | 0.2 | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-15 | WTP2 | 0.0021 | 0.0055 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-15 | WTP2 | 0.0014 | 0.0449 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP2 | 0.018 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-15 | WTP2 | 0.054 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP2 | 0.014 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-15 | WTP4 | 0.01 | 0.0149 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP4 | 0.016 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-15 | WTP4 | 0.052 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-15 | WTP4 | 0.25 | 0.6499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-15 | WTP4 | 0.035 | 0.0749 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-15 | WTP4 | 0.5 | 0.6499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-15 | WTP4 | 0.078 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-15 | WTP4 | 0.1 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-15 | WTP4 | 0.2 | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-15 | WTP4 | 0.054 | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.1 | PCI/L | 15.4999 | 2023-10-23 | AAA | 0.7 |  | 4Q2023 RESULTS
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 0.5 | PCI/L | 3.4999 | 2023-10-23 | AAA | 0.4 | 1.4999 | 4Q2023 RESULTS
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-10-23 | AAA | 0.7 | 1.4999 | 4Q2023 RESULTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-15 | WTP4 | 0.0042 | 0.0055 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-15 | WTP4 | 0.014 | 0.0449 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP4 | 0.018 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP4 | 0.01 | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-15 | WTP1 |  | 1.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-15 | WTP1 |  | 1.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-15 | WTP1 |  | 0.4499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-15 | WTP1 |  | 9.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-15 | WTP1 |  | 6.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-15 | WTP1 |  | 2.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-15 | WTP1 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-15 | WTP1 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-15 | WTP1 |  | 0.9499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-15 | WTP1 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-15 | WTP1 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-15 | WTP1 |  | 0.0449 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-15 | WTP1 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP1 |  | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-15 | WTP1 |  | 0.0149 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-15 | WTP1 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-15 | WTP2 |  | 1.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-15 | WTP2 |  | 1.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-15 | WTP2 |  | 0.4499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-15 | WTP2 |  | 9.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-15 | WTP2 |  | 6.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-15 | WTP2 |  | 2.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-15 | WTP2 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-15 | WTP2 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-15 | WTP2 |  | 0.9499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-15 | WTP2 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-15 | WTP2 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-15 | WTP2 |  | 0.0449 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-15 | WTP2 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP2 |  | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-15 | WTP2 |  | 0.0149 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-15 | WTP2 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-15 | WTP4 |  | 1.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-15 | WTP4 |  | 1.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-15 | WTP4 |  | 0.4499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-15 | WTP4 |  | 9.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-15 | WTP4 |  | 6.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-15 | WTP4 |  | 2.4999 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-15 | WTP4 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-15 | WTP4 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-15 | WTP4 |  | 0.9499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-15 | WTP4 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-15 | WTP4 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-15 | WTP4 |  | 0.0449 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-15 | WTP4 |  | 0.1499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-15 | WTP4 |  | 0.0249 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-15 | WTP4 |  | 0.0149 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-15 | WTP4 |  | 0.2499 | POE, J QUALIFIED ENDRIN LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-20 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-09-20 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-09-20 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-09-20 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-20 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-09-20 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-09-20 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-09-20 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-20 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-09-20 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-20 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-09-20 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-20 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-09-20 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-09-20 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-09-20 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-09-20 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-09-20 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-20 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-09-20 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-09-20 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-09-20 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-09-20 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-09-20 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-20 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2023-09-20 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-10-04 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 135 | MG/L |  | 2023-10-04 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-10-04 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2023-10-04 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-04 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-10-04 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-10-04 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-10-04 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-04 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-10-04 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-10-04 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-10-04 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-04 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-10-04 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-04 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-10-04 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-04 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-10-04 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-04 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-10-04 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-10-04 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-10-04 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-04 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 145 | MG/L |  | 2023-10-04 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-04 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-10-04 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-18 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2023-10-18 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-18 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-10-18 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-10-18 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-10-18 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-18 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-10-18 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-18 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-10-18 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-10-18 | 2234 EMPEROR DRIVE |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-10-18 | 2234 EMPEROR DRIVE |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-10-18 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-18 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-10-18 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-18 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-10-18 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-10-18 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-18 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 94 | MG/L |  | 2023-10-18 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-10-18 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-10-18 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-18 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-10-18 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-10-18 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 91 | MG/L |  | 2023-10-18 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-01 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-11-01 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-01 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-11-01 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-11-01 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-11-01 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-01 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-11-01 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-01 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-11-01 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-01 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2023-11-01 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-11-01 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-01 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2023-11-01 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-11-01 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2023-11-01 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-11-01 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-11-01 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-11-01 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-01 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-11-01 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-01 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-11-01 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-01 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-11-01 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-01-16 | AAA |  | 0.5499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-01-16 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-01-16 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-01-16 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-01-16 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-01-16 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-01-16 | AAA |  | 0.4499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-01-16 | AAA |  | 9.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-01-16 | AAA |  | 6.4999 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-01-16 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-01-16 | AAA |  | 0.0749 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-01-16 | AAA |  | 0.6499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-01-16 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-01-16 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-01-16 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-01-16 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-01-16 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-01-16 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-01-16 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-01-16 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-01-16 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-01-16 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-01-16 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-01-16 | AAA |  | 0.0449 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-01-16 | AAA |  | 0.1499 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-01-16 | AAA |  | 0.0249 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-01-16 | AAA |  | 0.0149 | POE
3491909 | LAKE TOHO RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-01-16 | AAA |  | 0.2499 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4020 | RADIUM-226 | 1.6 | PCI/L | 3.4999 | 2024-01-16 | AAA | 0.5 | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-01-16 | AAA |  | 1.4999 | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.1 | PCI/L | 15.4999 | 2024-01-16 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-01-17 | AAA | 1.1 |  | LOCATION CODE SET BY PWS - 03/10/2008
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 64.8 | UG/L | 60.4999 | 2024-02-15 | L1 | 0.98 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 43.37 | UG/L | 80.4999 | 2024-02-15 | L1 | 0.39 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.16 | UG/L | 60.4999 | 2024-02-15 | L2 | 0.98 |  | LOT 64
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 44.58 | UG/L | 80.4999 | 2024-02-15 | L2 | 0.39 |  | LOT 64
3491909 | LAKE TOHO RESORT | N | SEC | 1032 | MANGANESE | 0.0066 | MG/L | 0.0549 | 2024-03-07 | AAA | 0.005 |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1025 | FLUORIDE | 0.18 | MG/L | 2.0499 | 2024-03-07 | AAA | 0.0099 |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1055 | SULFATE | 2.6 | MG/L | 250.4999 | 2024-03-07 | AAA | 0.034 |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1905 | COLOR | 26 | COLOR UNITS | 15.4999 | 2024-03-07 | AAA | 5 |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.49 | LN(10) |  | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 240 | MG/L | 500.4999 | 2024-03-07 | AAA | 10 |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2024-03-07 | AAA | 0.024 |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1010 | BARIUM | 0.013 | MG/L | 2.4999 | 2024-03-07 | AAA | 0.003 |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2024-03-07 | AAA | 0.0099 |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1052 | SODIUM | 24 | MG/L | 160.4999 | 2024-03-07 | AAA | 0.8 |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-03-07 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1017 | CHLORIDE | 32 | MG/L | 250.4999 | 2024-03-07 | AAA | 0.039 |  | POE
3491909 | LAKE TOHO RESORT | N | SEC | 1905 | COLOR | 13 | COLOR UNITS | 15.4999 | 2024-03-26 | AAA | 5 |  | COLOR MAKEUP SAMPLE
3491909 | LAKE TOHO RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-03-26 | AAA | 0.67 | 0.9499
3491909 | LAKE TOHO RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-03-26 | AAA | 1.8 | 2.4999
3491909 | LAKE TOHO RESORT | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 72.1 | UG/L | 60.4999 | 2024-03-28 | L2 | 0.98 |  | LOT 64 - HAA5 EXCEEDANCE
3491909 | LAKE TOHO RESORT | S | DBP | 2950 | TOTAL THMS | 54.9 | UG/L | 80.4999 | 2024-03-28 | L2 | 0.39 |  | LOT 64 - HAA5 EXCEEDANCE
3491909 | LAKE TOHO RESORT | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 75.36 | UG/L | 60.4999 | 2024-03-28 | L1 | 0.98 |  | LOT 19 - HAA5 EXCEEDANCE
3491909 | LAKE TOHO RESORT | S | DBP | 2950 | TOTAL THMS | 55.59 | UG/L | 80.4999 | 2024-03-28 | L1 | 0.39 |  | LOT 19 - HAA5 EXCEEDANCE
3491909 | LAKE TOHO RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-04-24 | AAA |  | 1.4999 | 2Q2024 DALAPON RESULTS
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 70 | UG/L | 60.4999 | 2024-05-20 | L1 | 0.4 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 43 | UG/L | 80.4999 | 2024-05-20 | L1 | 0.5 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44 | UG/L | 60.4999 | 2024-05-20 | L2 | 0.28 |  | LOT 64
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 73 | UG/L | 80.4999 | 2024-05-20 | L2 | 0.5 |  | LOT 64
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 120 | UG/L | 80.4999 | 2024-08-20 | L2 | 0.5 |  | LOT 64 - TTHM & HAA5 EXCEEDED
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 79 | UG/L | 60.4999 | 2024-08-20 | L1 | 0.28 |  | LOT 19 - TTHM & HAA5 EXCEEDED
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 130 | UG/L | 80.4999 | 2024-08-20 | L1 | 0.5 |  | LOT 19 - TTHM & HAA5 EXCEEDED
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 79 | UG/L | 60.4999 | 2024-08-20 | L2 | 0.28 |  | LOT 64 - TTHM & HAA5 EXCEEDED
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 73 | UG/L | 60.4999 | 2024-11-19 | L1 | 0.28 |  | LOT 19 4TH QT- EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 120 | UG/L | 80.4999 | 2024-11-19 | L1 | 0.5 |  | LOT 19 4TH QT- EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 73 | UG/L | 60.4999 | 2024-11-19 | L2 | 0.28 |  | LOT 64 4TH QT - EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 110 | UG/L | 80.4999 | 2024-11-19 | L2 | 0.5 |  | LOT 64 4TH QT - EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.5 | UG/L | 60.4999 | 2025-02-20 | L1 | 0.28 |  | LOT 19 - TTHM/HAA5
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 8.1 | UG/L | 80.4999 | 2025-02-20 | L1 | 0.5 |  | LOT 19 - TTHM/HAA5
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.2 | UG/L | 60.4999 | 2025-02-20 | L2 | 0.28 |  | LOT 64 - TTHM/HAA5
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 7.8 | UG/L | 80.4999 | 2025-02-20 | L2 | 0.5 |  | LOT 64 - TTHM/HAA5
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 67.2 | UG/L | 60.4999 | 2025-05-19 | L1 | 0.765 |  | LOT 19 - EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 150 | UG/L | 80.4999 | 2025-05-19 | L1 | 0.21 |  | LOT 19 - EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 67.4 | UG/L | 60.4999 | 2025-05-19 | L2 | 0.765 |  | LOT 64 - EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 130 | UG/L | 80.4999 | 2025-05-19 | L2 | 0.21 |  | LOT 64 - EXCEEDANCES
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2025-08-21 | L1 | 0.765 |  | LOT 19 3RD QT
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 34 | UG/L | 80.4999 | 2025-08-21 | L1 | 0.21 |  | LOT 19 3RD QT
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.72 | UG/L | 60.4999 | 2025-08-21 | L2 | 0.765 |  | LOT 64 3RD QT
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 32 | UG/L | 80.4999 | 2025-08-21 | L2 | 0.21 |  | LOT 64 3RD QT
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 49.2 | UG/L | 60.4999 | 2025-11-20 | L1 | 0.765 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 97 | UG/L | 80.4999 | 2025-11-20 | L1 | 0.21 |  | LOT 19
3491909 | LAKE TOHO RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 51.1 | UG/L | 60.4999 | 2025-11-20 | L2 | 0.765 |  | LOT 64
3491909 | LAKE TOHO RESORT | D | DBP | 2950 | TOTAL THMS | 95 | UG/L | 80.4999 | 2025-11-20 | L2 | 0.21 |  | LOT 64
3491909 | LAKE TOHO RESORT | N | INOR | 1040 | NITRATE | 0.025 | MG/L | 10.4999 | 2025-11-20 | AAA | 0.02 |  | POE
3491909 | LAKE TOHO RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-20 | AAA |  |  | POE
3491909 | LAKE TOHO RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491909 | LAKE TOHO RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-11-21 | AAA |  | 0.5499 | 2025 VOCS
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-15 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2023-11-15 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-15 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-11-15 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-11-15 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 80 | MG/L |  | 2023-11-15 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-11-15 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-15 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-15 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 90 | MG/L |  | 2023-11-15 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-15 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-11-15 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-15 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-15 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-15 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-11-15 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-11-15 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-11-15 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-11-15 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 89 | MG/L |  | 2023-11-15 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-15 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-15 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-11-15 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 90 | MG/L |  | 2023-11-15 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-15 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2023-11-15 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.6 | UG/L | 60.4999 | 2023-11-17 | L3 | 0.9 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 22.6 | UG/L | 80.4999 | 2023-11-17 | L3 | 0.47 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.1 | UG/L | 60.4999 | 2023-11-17 | L4 | 0.9 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 42.4 | UG/L | 80.4999 | 2023-11-17 | L4 | 0.47 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.2 | UG/L | 60.4999 | 2023-11-17 | L2 | 0.9 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 30.4 | UG/L | 80.4999 | 2023-11-17 | L2 | 0.47 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.6 | UG/L | 60.4999 | 2023-11-17 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 50.6 | UG/L | 80.4999 | 2023-11-17 | L1 | 0.47 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-11-29 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2023-11-29 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-11-29 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-11-29 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-11-29 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-11-29 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-29 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-11-29 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-29 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-29 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-11-29 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-29 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-29 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-11-29 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-29 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-11-29 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-11-29 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-29 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-29 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-11-29 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-11-29 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-11-29 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-29 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-11-29 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-29 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-11-29 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-12-13 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-12-13 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-12-13 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-13 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-12-13 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-12-13 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-12-13 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-12-13 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-12-13 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-12-13 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-12-13 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-12-13 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2023-12-13 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-13 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2023-12-13 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-13 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-12-13 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-12-13 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2023-12-13 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2023-12-13 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-13 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-12-13 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-13 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-12-13 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-12-13 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-12-13 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-27 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-12-27 | 3269 MAJESTIC OAK DR |  |  | 3269 MAJESTIC OAK DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-12-27 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 80 | MG/L |  | 2023-12-27 | 1848 ASHTON PARK PL |  |  | 1848 ASHTON PARK PLACE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-12-27 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-12-27 | 2234 EMPEROR DR |  |  | 2234 EMPEROR DRIVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-12-27 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-12-27 | LS 78 FRIARS COVE |  |  | LS 78 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-12-27 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-12-27 | LS 64 SOUTHERN PINES |  |  | LS 64 SOUTHERN PINES
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-12-27 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-12-27 | LS 24 KINCAID |  |  | LS 24 KINCAID
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-27 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-12-27 | 17 JERSEY AVE |  |  | 17 JERSEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-27 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 94 | MG/L |  | 2023-12-27 | 2660 SHIRLEY AVE |  |  | 2660 SHIRLEY AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-12-27 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-12-27 | 907 MARYLAND AVE |  |  | 907 MARYLAND AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-12-27 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-12-27 | 607 WISCONSIN AVE |  |  | 607 WISCONSIN AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-12-27 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-12-27 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-12-27 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-12-27 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-12-27 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-12-27 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.5 | LN(10) |  | 2024-01-08 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-01-08 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-01-08 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2024-01-22 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-01-22 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-01-22 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.051 | MG/L | 10.4999 | 2024-01-30 | WTP1 | 0.025 |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP1 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.047 | MG/L | 10.4999 | 2024-01-30 | WTP2 | 0.025 |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP2 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-30 | WTP4 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP4 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2024-02-05 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-02-05 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-02-05 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2024-02-16 | L3 | 0.9 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 33.2 | UG/L | 80.4999 | 2024-02-16 | L3 | 0.47 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.4 | UG/L | 60.4999 | 2024-02-16 | L4 | 0.9 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 33 | UG/L | 80.4999 | 2024-02-16 | L4 | 0.47 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.7 | UG/L | 60.4999 | 2024-02-16 | L2 | 0.9 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 38 | UG/L | 80.4999 | 2024-02-16 | L2 | 0.47 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.5 | UG/L | 60.4999 | 2024-02-16 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 31.2 | UG/L | 80.4999 | 2024-02-16 | L1 | 0.47 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2024-02-19 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-02-19 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-02-19 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-03-04 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-03-04 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-03-04 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-03-18 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-03-18 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-03-18 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-04-01 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-04-01 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-04-01 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2024-04-15 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-04-15 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-04-15 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-04-29 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-04-29 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-04-29 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-05-13 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-05-13 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-05-13 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.1 | UG/L | 60.4999 | 2024-05-17 | L3 | 0.9 |  | LS 67 (FRIARS COVE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 28.4 | UG/L | 80.4999 | 2024-05-17 | L3 | 0.75 |  | LS 67 (FRIARS COVE)
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.2 | UG/L | 60.4999 | 2024-05-17 | L4 | 0.9 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 36.3 | UG/L | 80.4999 | 2024-05-17 | L4 | 0.75 |  | 803 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.7 | UG/L | 60.4999 | 2024-05-17 | L2 | 0.9 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2024-05-17 | L2 | 0.75 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.7 | UG/L | 60.4999 | 2024-05-17 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 30.6 | UG/L | 80.4999 | 2024-05-17 | L1 | 0.75 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2024-05-27 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-05-27 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-05-27 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2024-06-10 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-06-10 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-06-10 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-06-24 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-06-24 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-06-24 | WTP1 |  |  | WTP 1
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-29 | AAA |  |  | POE
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-29 | AAA |  |  | POE
3491703 | CANOE CREEK SERVICE PLAZA | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-08-10 | AAA | 2.68
3491703 | CANOE CREEK SERVICE PLAZA | N | RAD | 4020 | RADIUM-226 | 1.07 | PCI/L | 3.4999 | 2022-08-10 | AAA | 0.585 | 1.4999
3491703 | CANOE CREEK SERVICE PLAZA | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-08-10 | AAA | 0.554 | 1.4999
3491703 | CANOE CREEK SERVICE PLAZA | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 66.1 | UG/L | 60.4999 | 2022-08-10 | L1 | 0.9 |  | C STORE HAND SINK TTHM HAA5 EXCEEDANCES
3491703 | CANOE CREEK SERVICE PLAZA | S | DBP | 2950 | TOTAL THMS | 93.4 | UG/L | 80.4999 | 2022-08-10 | L1 | 0.47 |  | C STORE HAND SINK TTHM HAA5 EXCEEDANCES
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-24 | AAA | 0.2 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-08-24 | AAA | 0.0023 | 0.0149 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-08-24 | AAA | 0.0027 | 0.0249 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-08-24 | AAA | 0.023 | 0.1499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-08-24 | AAA | 0.68 | 1.4999 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 3.6 | UG/L | 249.9999 | 2022-08-24 | AAA | 0.49 | 1.4999 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-08-24 | AAA | 0.16 | 0.4499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-08-24 | AAA | 3.3 | 9.4999 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-08-24 | AAA | 4.2 | 6.4999 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-08-24 | AAA | 0.36 | 0.6499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-08-24 | AAA | 0.46 | 2.4999 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-08-24 | AAA | 0.04 | 0.0749 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-08-24 | AAA | 0.47 | 0.6499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-08-24 | AAA | 0.04 | 0.1499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-08-24 | AAA | 0.16 | 0.2499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.15 | UG/L | 54.9999 | 2022-08-24 | AAA | 0.024 | 0.1499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-08-24 | AAA | 0.59 | 0.9499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-08-24 | AAA | 0.015 | 0.1499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-08-24 | AAA | 0.029 | 0.2499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-24 | AAA | 0.014 | 0.0449 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-24 | AAA | 0.003 | 0.0249 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-24 | AAA | 0.096 | 0.1499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-24 | AAA | 0.053 | 0.2499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-24 | AAA | 0.015 | 0.1499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-24 | AAA | 0.019 | 0.0249 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-24 | AAA | 0.014 | 0.0449 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-24 | AAA | 0.044 | 0.1499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-24 | AAA | 0.0064 | 0.0249 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-24 | AAA | 0.0075 | 0.0149 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-24 | AAA | 0.035 | 0.2499 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2063 | DIOXIN (NG/L) | 0.03 | NG/L | 0.0349 | 2022-08-24 | AAA | 0.0014 | 0.0055 | SOC (2031 DALAPON 3.6, 2042 HEXACHLOROCYCLOPENTADIENE 0.15) NOTE: DIOXIN REPORTED ON LAST PAGE OF REPORT ON NON-FORMAT (NOT ENT'D)
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1010 | BARIUM | 0.0096 | MG/L | 2.4999 | 2022-08-24 | AAA | 0.0024
3491373 | ST. CLOUD, CITY OF (3 WPS) | S | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-02-13 | WTP1 | 1 |  | 2023 MAKE UP ODOR SAMPLES LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | S | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-02-13 | WTP2 | 1 |  | 2023 MAKE UP ODOR SAMPLES LMC
3491373 | ST. CLOUD, CITY OF (3 WPS) | S | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-02-13 | WTP4 | 1 |  | 2023 MAKE UP ODOR SAMPLES LMC
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-08-24 | AAA | 0.025
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-24 | AAA | 0.025
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-08-24 | AAA | 0.0005
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-08-24 | AAA | 0.00067
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-08-24 | AAA | 0.0026
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-08-24 | AAA | 0.005
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1025 | FLUORIDE | 0.27 | MG/L | 4.0499 | 2022-08-24 | AAA | 0.015
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1030 | LEAD | 0.0012 | MG/L | 0.0154 | 2022-08-24 | AAA | 0.00022
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1035 | MERCURY | 0.0001 | MG/L | 0.0024 | 2022-08-24 | AAA | 9e-05
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-08-24 | AAA | 0.002
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-08-24 | AAA | 0.00083
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1052 | SODIUM | 12.3 | MG/L | 160.4999 | 2022-08-24 | AAA | 0.59
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-08-24 | AAA | 0.00083
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-08-24 | AAA | 0.00019
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-08-24 | AAA | 0.00021
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-08-24 | AAA | 0.0072 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1017 | CHLORIDE | 35.7 | MG/L | 250.4999 | 2022-08-24 | AAA | 2.5 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1022 | COPPER | 0.02 | MG/L | 1.4999 | 2022-08-24 | AAA | 0.00093 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1025 | FLUORIDE | 0.27 | MG/L | 2.0499 | 2022-08-24 | AAA | 0.015 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1028 | IRON | 0.069 | MG/L | 0.3499 | 2022-08-24 | AAA | 0.016 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1032 | MANGANESE | 0.0027 | MG/L | 0.0549 | 2022-08-24 | AAA | 0.00093 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-08-24 | AAA | 0.0013 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1055 | SULFATE | 9.8 | MG/L | 250.4999 | 2022-08-24 | AAA | 2.5 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1095 | ZINC | 0.3 | MG/L | 5.4999 | 2022-08-24 | AAA | 0.0076 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2022-08-24 | AAA | 5 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2022-08-24 | AAA | 1 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.2 | LN(10) |  | 2022-08-24 | AAA | 0.1 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 218 | MG/L | 500.4999 | 2022-08-24 | AAA | 5 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 2905 | FOAMING AGENTS | 0.1 |  | 0.5499 | 2022-08-24 | AAA | 0.099 |  | SECONDARIES NOT RQRD FOR NTNC SYSTEMS BUT VOLUNTARILY TESTED HERE
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-24 | AAA | 0.35 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-24 | AAA | 0.33 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-24 | AAA | 0.11 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-24 | AAA | 0.44 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-24 | AAA | 0.26 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-24 | AAA | 0.3 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-24 | AAA | 0.12 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-24 | AAA | 0.29 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-24 | AAA | 0.27 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-24 | AAA | 0.3 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-24 | AAA | 0.27 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-24 | AAA | 0.28 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-24 | AAA | 0.44 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-24 | AAA | 0.26 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-24 | AAA | 0.28 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-24 | AAA | 0.26 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-24 | AAA | 0.26 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-24 | AAA | 0.4 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-08-24 | AAA | 0.28 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-24 | AAA | 0.23 | 0.5499 | VOC
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1920 | ODOR THRESHOLD | 8 |  | 3.4999 | 2022-09-19 | AAA | 1 |  | SECONDARIES NOT REQUIRED FOR NTNC THEREFORE NO ACTION TAKEN FOR RESULT ANALYSIS_CC
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 250 | UG/L | 60.4999 | 2022-10-13 | L1 | 9 |  | "C" STORE HAND SINK (HLKD 11/7/22)
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 188 | UG/L | 80.4999 | 2022-10-13 | L1 | 0.47 |  | "C" STORE HAND SINK (HLKD 11/7/22)
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1030 | LEAD | 0.015 | MG/L | 0.0154 | 2022-12-21 | AAA | 0.0022 |  | WQP SET #1 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 3.7 | UG/L | 249.9999 | 2022-10-26 | AAA | 0.49 | 1.4999
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.16 | UG/L | 54.9999 | 2022-10-26 | AAA | 0.024 | 0.1499
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-12-21 | AAA |  |  | WQP SET #1 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1016 | CALCIUM | 49.7 | MG/L |  | 2022-12-21 | AAA | 0.5 |  | WQP SET #1 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1022 | COPPER | 0.095 | MG/L | 1.5499 | 2022-12-21 | AAA | 0.00093 |  | WQP SET #1 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1927 | TOTAL ALKALINITY | 156 | MG/L |  | 2022-12-21 | AAA | 5 |  | WQP SET #1 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1064 | CONDUCTIVITY | 388 | MG/L | 0 | 2022-12-21 | AAA | 2 |  | WQP SET #1 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-12-21 | AAA |  |  | ALE WQP SET #1 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1016 | CALCIUM | 49.1 | MG/L |  | 2022-12-21 | AAA | 0.5 |  | ALE WQP SET #1 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1022 | COPPER | 0.052 | MG/L | 1.5499 | 2022-12-21 | AAA | 0.00093 |  | ALE WQP SET #1 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1030 | LEAD | 0.0035 | MG/L | 0.0154 | 2022-12-21 | AAA | 0.00022 |  | ALE WQP SET #1 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1927 | TOTAL ALKALINITY | 159 | MG/L |  | 2022-12-21 | AAA | 5 |  | ALE WQP SET #1 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1064 | CONDUCTIVITY | 395 | MG/L | 0 | 2022-12-21 | AAA | 2 |  | ALE WQP SET #1 POE
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-09 | AAA |  |  | ALE WQP SET #2 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1016 | CALCIUM | 80.2 | MG/L |  | 2023-02-09 | AAA | 0.5 |  | ALE WQP SET #2 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1022 | COPPER | 0.011 | MG/L | 1.5499 | 2023-02-09 | AAA | 0.00093 |  | ALE WQP SET #2 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-09 | AAA | 0.00022 |  | ALE WQP SET #2 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1927 | TOTAL ALKALINITY | 15 | MG/L |  | 2023-02-09 | AAA | 5 |  | ALE WQP SET #2 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | D | WQP | 1064 | CONDUCTIVITY | 1280 | MG/L | 0 | 2023-02-09 | AAA | 2 |  | ALE WQP SET #2 DISTRIBUTION
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-09 | AAA |  |  | ALE WQP SET #2 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1016 | CALCIUM | 80.9 | MG/L |  | 2023-02-09 | AAA | 0.5 |  | ALE WQP SET #2 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-02-09 | AAA | 0.0022 |  | ALE WQP SET #2 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1022 | COPPER | 0.013 | MG/L | 1.5499 | 2023-02-09 | AAA | 0.00093 |  | ALE WQP SET #2 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1927 | TOTAL ALKALINITY | 188 | MG/L |  | 2023-02-09 | AAA | 5 |  | ALE WQP SET #2 POE
3491703 | CANOE CREEK SERVICE PLAZA | N | WQP | 1064 | CONDUCTIVITY | 1290 | MG/L | 0 | 2023-02-09 | AAA | 2 |  | ALE WQP SET #2 POE
3491703 | CANOE CREEK SERVICE PLAZA | S | DBP | 2950 | TOTAL THMS | 202 | UG/L | 80.4999 | 2023-03-14 | L1 | 0.47 |  | 2023 Q1
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1040 | NITRATE | 0.039 | MG/L | 10.4999 | 2023-02-08 | AAA | 0.025 |  | LATE DATA ENTRY_ALP
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-08 | AAA | 0.025 |  | LATE DATA ENTRY_ALP
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 2.5 | UG/L | 249.9999 | 2023-03-02 | AAA | 0.49 | 1.4999 | Q1 RESULTS
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.089 | UG/L | 54.9999 | 2023-03-02 | AAA | 0.025 | 0.1499 | Q1 RESULTS
3491703 | CANOE CREEK SERVICE PLAZA | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 144 | UG/L | 60.4999 | 2023-03-14 | L1 | 45 |  | 2023 Q1
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 2.8 | UG/L | 249.9999 | 2023-06-16 | AAA | 0.49 | 1.4999 | Q2 RESULTS
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.16 | UG/L | 54.9999 | 2023-06-16 | AAA | 0.0024 | 0.1499 | Q2 RESULTS
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-07-08 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-07-08 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-07-08 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-07-08 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-07-08 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2024-07-08 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-07-22 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 122 | MG/L |  | 2024-07-22 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-07-22 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-07-22 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-07-22 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-07-22 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-08-05 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-08-05 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-08-05 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-08-05 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-08-05 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-08-05 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.9 | UG/L | 60.4999 | 2024-08-16 | L3 | 0.9 |  | LS 67 FRIERS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 39.1 | UG/L | 80.4999 | 2024-08-16 | L3 | 0.75 |  | LS 67 FRIERS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.8 | UG/L | 60.4999 | 2024-08-16 | L4 | 0.9 |  | 803 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 38.4 | UG/L | 80.4999 | 2024-08-16 | L4 | 0.75 |  | 803 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.3 | UG/L | 60.4999 | 2024-08-16 | L2 | 0.9 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 49.3 | UG/L | 80.4999 | 2024-08-16 | L2 | 0.75 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.8 | UG/L | 60.4999 | 2024-08-16 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 57.4 | UG/L | 80.4999 | 2024-08-16 | L1 | 0.75 |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-08-19 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 150 | MG/L |  | 2024-08-19 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-08-19 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-08-19 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-08-19 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-08-19 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-09-02 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 150 | MG/L |  | 2024-09-02 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-09-02 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2024-09-02 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-09-02 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2024-09-02 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2024-09-16 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2024-09-16 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-09-16 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-09-16 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-09-16 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2024-09-16 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-09-30 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 140 | MG/L |  | 2024-09-30 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-09-30 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2024-09-30 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-09-30 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-09-30 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | W | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-10-14 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | W | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-10-14 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-10-14 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2024-10-14 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-10-14 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-10-14 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-10-28 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2024-10-28 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-10-28 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-10-28 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-10-28 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2024-10-28 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-11-04 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 130 | MG/L |  | 2024-11-04 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-11-04 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-11-04 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-11-04 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-11-04 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.1 | UG/L | 60.4999 | 2024-11-15 | L3 | 0.9 |  | LS67 FRIARS LN AND CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 36.6 | UG/L | 80.4999 | 2024-11-15 | L3 | 0.75 |  | LS67 FRIARS LN AND CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.4 | UG/L | 60.4999 | 2024-11-15 | L5 | 0.9 |  | 1014 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 45.5 | UG/L | 80.4999 | 2024-11-15 | L5 | 0.75 |  | 1014 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.6 | UG/L | 60.4999 | 2024-11-15 | L2 | 0.9 |  | 4805 DOC RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 36.4 | UG/L | 80.4999 | 2024-11-15 | L2 | 0.75 |  | 4805 DOC RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.8 | UG/L | 60.4999 | 2024-11-15 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIRCLE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.6 | UG/L | 80.4999 | 2024-11-15 | L1 | 0.75 |  | 5371 MAJESTIC ISLAND CIRCLE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-11-18 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 123 | MG/L |  | 2024-11-18 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-11-18 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2024-11-18 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-11-18 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-11-18 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2024-12-09 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 138 | MG/L |  | 2024-12-09 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-12-09 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-12-09 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-12-09 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-12-09 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-12-23 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2024-12-23 | WTP1 |  |  | WTP 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-12-23 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2024-12-23 | WTP2 |  |  | WTP 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-12-23 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-12-23 | WTP4 |  |  | WTP 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.1 | UG/L | 60.4999 | 2025-02-20 | L3 | 0.9 |  | LS67 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 25.1 | UG/L | 80.4999 | 2025-02-20 | L3 | 0.75 |  | LS67 FRIARS COVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.3 | UG/L | 60.4999 | 2025-02-20 | L5 | 0.9 |  | 1014 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 24.9 | UG/L | 80.4999 | 2025-02-20 | L5 | 0.75 |  | 1014 MASSACHUSETTS AVE
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.1 | UG/L | 60.4999 | 2025-02-20 | L2 | 0.9 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 42.7 | UG/L | 80.4999 | 2025-02-20 | L2 | 0.75 |  | 4805 DOC DR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.1 | UG/L | 60.4999 | 2025-02-20 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 69.6 | UG/L | 80.4999 | 2025-02-20 | L1 | 0.75 |  | 5371 MAJESTIC ISLAND CIR
3491373 | ST. CLOUD, CITY OF (3 WPS) | C | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2025-03-14 | WTP1 | 0.025 |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | C | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP1 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.05 | MG/L | 10.4999 | 2025-03-14 | WTP2 | 0.025 |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP2 |  |  | POE
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2025-03-14 | WTP1 | 0.025 |  | WP1 PLANT 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP1 | 0 |  | WP1 PLANT 1
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.05 | MG/L | 10.4999 | 2025-03-14 | WTP2 | 0.025 |  | WP2 PLANT 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP2 | 0 |  | WP2 PLANT 2
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.054 | MG/L | 10.4999 | 2025-03-14 | WTP4 | 0.025 |  | WP4 PLANT 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP4 | 0 |  | WP4 PLANT 4
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10 | UG/L | 60.4999 | 2025-05-16 | L2 | 0.9 |  | 4805 DOC DR.
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 185 | UG/L | 60.4999 | 2023-04-12 | L1 | 9 |  | Q2 TTHM&HAA5 EXCEEDANCE.
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 286 | UG/L | 80.4999 | 2023-04-12 | L1 | 4.7 |  | Q2 TTHM&HAA5 EXCEEDANCE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.3 | UG/L | 60.4999 | 2025-05-16 | L3 | 0.9 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 30.5 | UG/L | 80.4999 | 2025-05-16 | L3 | 0.75 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.5 | UG/L | 60.4999 | 2025-05-16 | L5 | 0.9 |  | 1014 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 15.7 | UG/L | 80.4999 | 2025-05-16 | L5 | 0.75 |  | 1014 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 34.1 | UG/L | 80.4999 | 2025-05-16 | L2 | 0.75 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 46.5 | UG/L | 60.4999 | 2025-05-16 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 38.7 | UG/L | 80.4999 | 2025-05-16 | L1 | 0.75 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.9 | UG/L | 60.4999 | 2025-08-15 | L3 | 0.9 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 26.4 | UG/L | 80.4999 | 2025-08-15 | L3 | 0.75 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.7 | UG/L | 60.4999 | 2025-08-15 | L5 | 0.9 |  | 1014 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 35.1 | UG/L | 80.4999 | 2025-08-15 | L5 | 0.75 |  | 1014 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.6 | UG/L | 60.4999 | 2025-08-15 | L2 | 0.9 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 36.8 | UG/L | 80.4999 | 2025-08-15 | L2 | 0.75 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.5 | UG/L | 60.4999 | 2025-08-15 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 54.5 | UG/L | 80.4999 | 2025-08-15 | L1 | 0.75 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.9 | UG/L | 60.4999 | 2025-11-20 | L3 | 0.9 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 22.5 | UG/L | 80.4999 | 2025-11-20 | L3 | 0.75 |  | LS67 FRIARS LN & CANOE CREEK RD
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.9 | UG/L | 60.4999 | 2025-11-20 | L5 | 0.9 |  | 1014 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 23.7 | UG/L | 80.4999 | 2025-11-20 | L5 | 0.75 |  | 1014 MASSACHUSETTS AVE.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.9 | UG/L | 60.4999 | 2025-11-20 | L2 | 0.9 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 31.9 | UG/L | 80.4999 | 2025-11-20 | L2 | 0.75 |  | 4805 DOC DR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36 | UG/L | 60.4999 | 2025-11-20 | L1 | 0.9 |  | 5371 MAJESTIC ISLAND CIR.
3491373 | ST. CLOUD, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 37.6 | UG/L | 80.4999 | 2025-11-20 | L1 | 0.75 |  | 5371 MAJESTIC ISLAND CIR.
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 149 | UG/L | 60.4999 | 2023-07-12 | L1 | 4.5 |  | Q3 EXCEEDANCE LRAA TTHM 266.5 HAA5 158
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 260 | UG/L | 80.4999 | 2023-07-12 | L1 | 4.7 |  | Q3 EXCEEDANCE LRAA TTHM 266.5 HAA5 158
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 2.6 | UG/L | 249.9999 | 2023-09-30 | AAA | 0.49 | 1.4999 | Q3
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.078 | UG/L | 54.9999 | 2023-09-30 | AAA | 0.024 | 0.1499 | Q3
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 211 | UG/L | 60.4999 | 2023-10-13 | L1 | 9 |  | Q4 EXCEEDANCE, LRAA TTHM 275.5 HAA5 189, CHLORITE AND BROMATE ALSO TESTED
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 278 | UG/L | 80.4999 | 2023-10-13 | L1 | 4.7 |  | Q4 EXCEEDANCE, LRAA TTHM 275.5 HAA5 189, CHLORITE AND BROMATE ALSO TESTED
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 1009 | CHLORITE | 5.7 | UG/L | 1000.4999 | 2023-10-13 | L1 | 2.8 |  | Q4 EXCEEDANCE, LRAA TTHM 275.5 HAA5 189, CHLORITE AND BROMATE ALSO TESTED
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-10-13 | L1 | 1.1 |  | Q4 EXCEEDANCE, LRAA TTHM 275.5 HAA5 189, CHLORITE AND BROMATE ALSO TESTED
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.1 | UG/L | 54.9999 | 2023-12-28 | AAA | 0.024 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 144 | UG/L | 60.4999 | 2024-01-13 | L1 | 4.5 |  | "C" STORE HAND SINK
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 214 | UG/L | 80.4999 | 2024-01-13 | L1 | 0.47 |  | "C" STORE HAND SINK
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-03-21 | AAA |  |  | POE
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-21 | AAA |  |  | POE
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 195 | UG/L | 60.4999 | 2024-04-11 | L1 | 4.5 |  | C STORE HS LRAA: TTHM 322.25 HAA5 174.75
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 537 | UG/L | 80.4999 | 2024-04-11 | L1 | 7.5 |  | C STORE HS LRAA: TTHM 322.25 HAA5 174.75
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 2.9 | UG/L | 249.9999 | 2024-04-11 | AAA | 0.49 | 1.4999 | POE - DALAPON DETECT
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-04-11 | AAA | 0.025 | 0.1499 | POE - DALAPON DETECT
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 2.9 | UG/L | 249.9999 | 2024-07-09 | AAA | 0.49 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.3 | UG/L | 54.9999 | 2024-07-09 | AAA | 0.024 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-07-09 | AAA | 0.00086 | 0.0055 | LOCATION CODE SET BY PWS - 03/10/2008
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 227 | UG/L | 60.4999 | 2024-07-11 | L1 | 4.5 |  | "C" STORE HAND SINK-EXCEEDANCE LRAA TTHM 320.25 HAA5 194.25
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 252 | UG/L | 80.4999 | 2024-07-11 | L1 | 7.5 |  | "C" STORE HAND SINK-EXCEEDANCE LRAA TTHM 320.25 HAA5 194.25
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-07-11 | L1 | 1.1 |  | "C" STORE HAND SINK-EXCEEDANCE LRAA TTHM 320.25 HAA5 194.25
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 1009 | CHLORITE | 5.7 | UG/L | 1000.4999 | 2024-07-11 | L1 | 2.8 |  | "C" STORE HAND SINK-EXCEEDANCE LRAA TTHM 320.25 HAA5 194.25
3491703 | CANOE CREEK SERVICE PLAZA | S | SOC | 2031 | DALAPON | 4.3 | UG/L | 249.9999 | 2024-10-23 | AAA | 0.49 | 1.4999 | POE - 2031, 2042 DETECT - TAKEN OUTSIDE OF MONITORING QUARTER
3491703 | CANOE CREEK SERVICE PLAZA | S | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.19 | UG/L | 54.9999 | 2024-10-23 | AAA | 0.024 | 0.1499 | POE - 2031, 2042 DETECT - TAKEN OUTSIDE OF MONITORING QUARTER
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-04 | AAA |  |  | POE
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-04 | AAA |  |  | POE
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1010 | BARIUM | 0.0075 | MG/L | 2.4999 | 2025-03-20 | AAA | 0.00033 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 2.4 | UG/L | 249.9999 | 2023-12-28 | AAA | 0.49 | 1.4999 | DETECT
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 3 | UG/L | 249.9999 | 2024-03-21 | AAA | 0.49 | 1.4999 | Q1 2024
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.11 | UG/L | 54.9999 | 2024-03-21 | AAA | 0.025 | 0.1499 | Q1 2024
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-03-21 | AAA |  | 0.0055 | Q1 2024
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 244 | UG/L | 60.4999 | 2024-10-08 | L1 | 9 |  | C STORE HAND SINK - TTHM AND HAA5 EXCEEDED MCL LRAA TTHM: 325 HAA5: 202.5
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 297 | UG/L | 80.4999 | 2024-10-08 | L1 | 7.5 |  | C STORE HAND SINK - TTHM AND HAA5 EXCEEDED MCL LRAA TTHM: 325 HAA5: 202.5
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 152 | UG/L | 60.4999 | 2025-01-14 | L1 | 4 |  | C STORE HAND SINK - EXCEEDANCE
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 103.98 | UG/L | 80.4999 | 2025-01-14 | L1 | 0.5 |  | C STORE HAND SINK - EXCEEDANCE
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-20 | AAA | 0.2 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-20 | AAA | 0.2 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-03-20 | AAA | 0.00035 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-03-20 | AAA | 0.00022 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1020 | CHROMIUM | 0.0008 | MG/L | 0.1499 | 2025-03-20 | AAA | 0.00035 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1024 | CYANIDE | 0.0055 | MG/L | 0.2499 | 2025-03-20 | AAA | 0.005 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1025 | FLUORIDE | 0.33 | MG/L | 4.0499 | 2025-03-20 | AAA | 0.2 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-03-20 | AAA | 0.00022 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-03-20 | AAA | 0.0002 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-03-20 | AAA | 0.00082 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-03-20 | AAA | 0.0009 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1052 | SODIUM | 30 | MG/L | 160.4999 | 2025-03-20 | AAA | 0.12 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-03-20 | AAA | 0.00037 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-03-20 | AAA | 0.00029 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-03-20 | AAA | 0.00031 |  | ALL EXCEPT ASBESTOS
3491703 | CANOE CREEK SERVICE PLAZA | N | SEC | 1025 | FLUORIDE | 0.33 | MG/L | 2.0499 | 2025-03-20 | AAA | 0.2 |  | FLUORIDE ONLY
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-03-20 | AAA | 0.29 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-03-20 | AAA | 0.19 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-03-20 | AAA | 0.27 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-03-20 | AAA | 0.5 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-03-20 | AAA | 0.5 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-03-20 | AAA | 0.32 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-03-20 | AAA | 0.4 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-03-20 | AAA | 0.39 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-03-20 | AAA | 0.33 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-03-20 | AAA | 0.23 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-03-20 | AAA | 0.16 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-03-20 | AAA | 0.28 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-03-20 | AAA | 0.43 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-03-20 | AAA | 0.34 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-03-20 | AAA | 0.39 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-03-20 | AAA | 0.37 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-03-20 | AAA | 0.3 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-03-20 | AAA | 0.17 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-03-20 | AAA | 0.23 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-03-20 | AAA | 0.24 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-03-20 | AAA | 0.1 | 0.1499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-03-20 | AAA | 0.24 | 0.5499 | ALL 21
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-03-20 | AAA | 0.01 | 0.0149 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-03-20 | AAA | 0.02 | 0.0249 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-03-20 | AAA | 1 | 1.4999 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2031 | DALAPON | 2.2 | UG/L | 249.9999 | 2025-03-20 | AAA | 0.022 | 1.4999 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-03-20 | AAA | 9 | 9.4999 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-03-20 | AAA | 6 | 6.4999 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-03-20 | AAA | 0.6 | 0.6499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-03-20 | AAA | 0.4 | 2.4999 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-03-20 | AAA | 0.07 | 0.0749 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-03-20 | AAA | 0.6 | 0.6499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-03-20 | AAA | 0.019 | 0.1499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-03-20 | AAA | 0.028 | 0.2499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.1 | UG/L | 54.9999 | 2025-03-20 | AAA | 0.1 | 0.1499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-03-20 | AAA | 0.4 | 0.9499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-03-20 | AAA | 0.1 | 0.1499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-03-20 | AAA | 0.2 | 0.2499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-03-20 | AAA | 0.01 | 0.0449 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-03-20 | AAA | 0.01 | 0.0249 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2105 | 2,4-D | 0.55 | UG/L | 74.9999 | 2025-03-20 | AAA | 0.022 | 0.1499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-03-20 | AAA | 0.035 | 0.2499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-03-20 | AAA | 0.1 | 0.1499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-03-20 | AAA | 0.02 | 0.0249 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-03-20 | AAA | 0.017 | 0.0449 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-03-20 | AAA | 0.1 | 0.1499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-03-20 | AAA | 0.02 | 0.0249 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-03-20 | AAA | 0.01 | 0.0149 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-03-20 | AAA | 0.01 | 0.2499 | DETECT - 2031, 2042, 2105; J3 QUALIFIED - 2032 (NOT ENTERED)
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.52 | UG/L | 60.4999 | 2025-07-09 | L1 | 0.2 |  | "C" STORE HAND SINK-TTHM EXCEEDANCE
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 198.6 | UG/L | 80.4999 | 2025-07-09 | L1 | 0.21 |  | "C" STORE HAND SINK-TTHM EXCEEDANCE
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-08-07 | AAA | 0 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 HYDROTANK
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 202.95 | UG/L | 60.4999 | 2025-10-14 | L1 | 0.2 |  | "C" STORE HAND SINK-
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 255.5 | UG/L | 80.4999 | 2025-10-14 | L1 | 0.21 |  | "C" STORE HAND SINK-
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-10-14 | AAA |  | 0.1499 | POE
3491705 | GATE PRECAST | N | INOR | 1040 | NITRATE | 0.096 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.12 | UG/L | 60.4999 | 2022-08-04 | L1 | 0.98 |  | WEST BUILDING (HLKD) | 3
3491705 | GATE PRECAST | D | DBP | 2950 | TOTAL THMS | 5.71 | UG/L | 80.4999 | 2022-08-04 | L1 | 0.39 |  | WEST BUILDING (HLKD) | 3
3491705 | GATE PRECAST | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491703 | CANOE CREEK SERVICE PLAZA | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-03-20 | AAA |  | 0.4499 | J3 QUALIFIED - ACCEPTED
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 99 | UG/L | 60.4999 | 2025-04-10 | L1 |  |  | Q2 2025
3491703 | CANOE CREEK SERVICE PLAZA | D | DBP | 2950 | TOTAL THMS | 205.4 | UG/L | 80.4999 | 2025-04-10 | L1 |  |  | Q2 2025
3491705 | GATE PRECAST | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2022-10-06 | AAA | 0.001 |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1025 | FLUORIDE | 0.13 | MG/L | 4.0499 | 2022-10-06 | AAA | 0.0099 |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1052 | SODIUM | 20 | MG/L | 160.4999 | 2022-10-06 | AAA | 0.8 |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2022-10-06 | AAA |  |  | POE-LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-06 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-06 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-06 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-06 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-06 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-06 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-06 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-06 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-06 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-06 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-06 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-06 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-06 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-06 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-06 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-06 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-06 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-06 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-06 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-06 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-06 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-06 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-06 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-06 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-06 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-06 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-06 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-10-06 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-10-06 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-06 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491705 | GATE PRECAST | N | INOR | 1040 | NITRATE | 0.058 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | POE
3491705 | GATE PRECAST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-08 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-08 | AAA |  |  | POE
3491705 | GATE PRECAST | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.8 | UG/L | 60.4999 | 2025-08-05 | L1 | 0.98 |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2950 | TOTAL THMS | 13.42 | UG/L | 80.4999 | 2025-08-05 | L1 | 0.44 |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2450 | MONOCHLORACETIC ACID | 0 | UG/L |  | 2025-08-05 | L1 |  |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2451 | DICHLOROACETIC ACID | 2.72 | UG/L |  | 2025-08-05 | L1 | 0.42 |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2452 | TRICHLOROACETIC ACID | 2.08 | UG/L |  | 2025-08-05 | L1 | 0.94 |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2453 | MONOBROMACETIC ACID | 0 | UG/L |  | 2025-08-05 | L1 |  |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2454 | DIBROMOACETIC ACID | 0 | UG/L |  | 2025-08-05 | L1 |  |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2941 | CHLOROFORM | 7.2 | UG/L | 100 | 2025-08-05 | L1 | 0.39 |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2942 | BROMOFORM | 0 | UG/L | 100 | 2025-08-05 | L1 |  |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2943 | BROMODICHLOROMETHANE | 4.1 | UG/L | 100 | 2025-08-05 | L1 | 0.44 |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | D | DBP | 2944 | DIBROMOCHLOROMETHANE | 2.12 | UG/L | 100 | 2025-08-05 | L1 | 0.32 |  | DIST - WEST BUILDING | 3
3491705 | GATE PRECAST | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1005 | ARSENIC | 0.0003 | MG/L | 0.0104 | 2025-10-17 | AAA | 0.0003 |  | POE
3491705 | GATE PRECAST | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2025-10-17 | AAA | 0.003 |  | POE
3491705 | GATE PRECAST | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1024 | CYANIDE | 0.014 | MG/L | 0.2499 | 2025-10-17 | AAA | 0.002 |  | POE
3491705 | GATE PRECAST | N | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2025-10-17 | AAA | 0.0099 |  | POE
3491705 | GATE PRECAST | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1052 | SODIUM | 100 | MG/L | 160.4999 | 2025-10-17 | AAA | 0.8 |  | POE
3491705 | GATE PRECAST | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-10-17 | AAA |  |  | POE
3491705 | GATE PRECAST | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3491705 | GATE PRECAST | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2025-10-17 | AAA | 1.7 |  | POE
3491705 | GATE PRECAST | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2025-10-17 | AAA | 0.2 | 1.4999 | POE
3491705 | GATE PRECAST | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-10-17 | AAA |  | 1.4999 | POE
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.04 | UG/L | 60.4999 | 2021-08-31 | L1 | 0.98 |  | LOT #47 (HLKD) | 3
3491705 | GATE PRECAST | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.4 | PCI/L | 15.4999 | 2022-10-20 | AAA | 0.8 |  | RADS (RADS WERE ADDED AT BACK OF RE-SUBMITTAL OF TRIENNIALS)
3491705 | GATE PRECAST | N | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2022-10-20 | AAA | 0.6 | 1.4999 | RADS (RADS WERE ADDED AT BACK OF RE-SUBMITTAL OF TRIENNIALS)
3491705 | GATE PRECAST | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-10-20 | AAA | 0.5 | 1.4999 | RADS (RADS WERE ADDED AT BACK OF RE-SUBMITTAL OF TRIENNIALS)
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 28.37 | UG/L | 80.4999 | 2021-08-31 | L1 | 0.39 |  | LOT #47 (HLKD) | 3
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.095 | MG/L | 10.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.0091 | MG/L | 2.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 30 | MG/L | 160.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 32 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 1.7 | MG/L | 250.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.01 | LN(10) |  | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 376 | MG/L | 500.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-10-25 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 2.3 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-25 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-25 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-25 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-25 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-25 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-25 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-25 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-25 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-25 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-25 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-25 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-25 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.2 | PCI/L | 15.4999 | 2021-10-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-10-25 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0.99 | UG/L | 249.9999 | 2022-02-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 1.4 | UG/L | 249.9999 | 2022-06-23 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008, ROUTINE COMP W/ 62-550
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 1.5 | UG/L | 249.9999 | 2022-08-31 | AAA | 0.9 | 1.4999 | DALAPON 1.50 UG/L (HLKD 9/20/22)
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 2 | UG/L | 249.9999 | 2023-01-16 | AAA | 0.9 | 1.4999 | DALAPON DETECT
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 2.8 | UG/L | 249.9999 | 2023-06-28 | AAA | 0.9 | 1.4999 | DALAPON DETECT
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-08 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- DALAPON I QUALIFIER
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-08 | AAA | 0.18 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- DALAPON I QUALIFIER
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-08 | AAA | 0.095 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- DALAPON I QUALIFIER
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-08 | AAA | 0.09 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- DALAPON I QUALIFIER
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-08 | AAA | 0.038 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008- DALAPON I QUALIFIER
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-19 | AAA |  | 1.4999 | POE
3491726 | SHARP'S MOBILE HOME PARK | D | INOR | 1040 | NITRATE | 0.075 | MG/L | 10.4999 | 2023-11-15 | AAA | 0.024 |  | DIST- POE
3491726 | SHARP'S MOBILE HOME PARK | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-15 | AAA |  |  | DIST- POE
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-01-12 | AAA |  | 1.4999 | POE
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-06-26 | AAA | 0.289 | 1.4999 | 2Q24 DALAPON RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0.001 | MG/L | 0.1499 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 2.9 | UG/L | 249.9999 | 2023-08-25 | AAA | 0.9 | 1.4999 | DALAPON - DETECT
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.009 | MG/L | 2.4999 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.103 | MG/L | 4.0499 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0.0002 | MG/L | 0.0154 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 28.5 | MG/L | 160.4999 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2024-08-08 | AAA |  |  | 2024 INORG RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1028 | IRON | 0.0047 | MG/L | 0.3499 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 34.4 | MG/L | 250.4999 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0.005 | MG/L | 1.4999 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.103 | MG/L | 2.0499 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0.0028 | MG/L | 0.0549 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 1.02 | MG/L | 250.4999 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0.0065 | MG/L | 5.4999 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.5 | LN(10) |  | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 362 | MG/L | 500.4999 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0.019 |  | 0.5499 | 2024-08-08 | AAA |  |  | 2024 SECONDARY
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-08-08 | AAA | 2.3 |  | 2024 RADS
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-08-08 | AAA | 0.0014 | 0.667 | 2024 RADS
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0.9 | PCI/L | 3.4999 | 2024-08-08 | AAA | 0.5 | 1.4999 | 2024 RADS
3491726 | SHARP'S MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-08-08 | AAA | 0 | 1.4999 | 2024 RADS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-08-08 | AAA |  | 0.0149 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA |  | 0.0249 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-08-08 | AAA |  | 0.1499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-08-08 | AAA |  | 1.4999 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-08-08 | AAA |  | 1.4999 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-08-08 | AAA |  | 0.4499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-08-08 | AAA |  | 9.4999 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-08-08 | AAA |  | 6.4999 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-08-08 | AAA |  | 0.6499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-08-08 | AAA |  | 2.4999 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-08-08 | AAA |  | 0.0749 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-08-08 | AAA |  | 0.6499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-08-08 | AAA |  | 0.1499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-08-08 | AAA |  | 0.2499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-08-08 | AAA |  | 0.1499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-08-08 | AAA |  | 0.9499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-08-08 | AAA |  | 0.1499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-08-08 | AAA |  | 0.2499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-08-08 | AAA |  | 0.0055 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-08-08 | AAA |  | 0.0449 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA |  | 0.0249 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-08-08 | AAA |  | 0.1499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-08-08 | AAA |  | 0.2499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-08-08 | AAA |  | 0.1499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA |  | 0.0249 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-08-08 | AAA |  | 0.0449 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-08-08 | AAA |  | 0.1499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA |  | 0.0249 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-08-08 | AAA |  | 0.0149 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-08-08 | AAA |  | 0.2499 | 2024 SOC RESULTS
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-09-18 | AAA | 0.289 | 1.4999 | 3Q2024 DALAPON RESULT
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 1.5 | UG/L | 10499.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC (DETECT-2955)
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.1 | UG/L | 60.4999 | 2024-10-22 | L1 |  |  | 2024 MAKEUP SAMPLES FOR MISSED AUGUST SAMPLING EVENT_SYSTEM MUST RETURN TO ROUTINE, ANNUAL DBP SAMPLING DURING AUGUST AND ADD A SECOND LOCATION_DJ | 3
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 49.1 | UG/L | 80.4999 | 2024-10-22 | L1 |  |  | 2024 MAKEUP SAMPLES FOR MISSED AUGUST SAMPLING EVENT_SYSTEM MUST RETURN TO ROUTINE, ANNUAL DBP SAMPLING DURING AUGUST AND ADD A SECOND LOCATION_DJ | 3
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0.9 | UG/L | 249.9999 | 2024-11-08 | AAA | 0.49 | 1.4999 | DIST-POE
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-02-17 | AAA |  | 0.5499 | POE-TRIP BLANK
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-02-17 | AAA |  | 1.4999 | POE
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-04-08 | AAA | 0.1 |  | POE - NN
3491726 | SHARP'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-08 | AAA | 0.1 |  | POE - NN
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0.89 | UG/L | 10499.9999 | 2025-05-22 | AAA | 0.5 | 0.5499 | POE - Q2 XYLENE
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 1.4 | UG/L | 249.9999 | 2025-05-22 | AAA | 0.022 | 1.4999 | POE - Q2 DALAPON
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-07-15 | AAA | 0.5 | 0.5499 | POE
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0.53 | UG/L | 249.9999 | 2025-07-15 | AAA | 0.022 | 1.4999 | POE - 2031 DETECT
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 50.63 | UG/L | 60.4999 | 2025-08-26 | L1 | 0.2 |  | LOT 47 - TTHM, HAA5 | 3
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 38 | UG/L | 80.4999 | 2025-08-26 | L1 | 0.21 |  | LOT 47 - TTHM, HAA5 | 3
3491726 | SHARP'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-28 | AAA |  | 0.5499 | POE
3491726 | SHARP'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-10-28 | AAA |  | 1.4999 | POE
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-18 | AAA |  |  | FIRST POINT OF ENTRY- DOH LAB E83182- E87610
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-18 | AAA |  |  | FIRST POINT OF ENTRY- DOH LAB E83182- E87610
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1030 | LEAD | 0.0003 | MG/L | 0.0154 | 2021-05-18 | AAA |  |  | FIRST POINT OF ENTRY- DOH LAB E83182- E87610
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-07-19 | AAA | 0.03
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-19 | AAA | 0.018
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1040 | NITRATE | 0.32 | MG/L | 10.4999 | 2022-06-01 | AAA | 0.03 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-06-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1040 | NITRATE | 0.95 | MG/L | 10.4999 | 2023-05-23 | AAA | 0.024 |  | UPDATED FIESTA VILLAGE (FL0039829)
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-05-23 | AAA | 0.0034 |  | UPDATED FIESTA VILLAGE (FL0039829)
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-05-23 | AAA | 0.005 |  | UPDATED FIESTA VILLAGE (FL0039829)
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1040 | NITRATE | 0.53 | MG/L | 10.4999 | 2024-05-28 | AAA | 0.024 |  | POE-WELL
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-05-28 | AAA |  |  | POE-WELL
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1040 | NITRATE | 0.053 | MG/L | 10.4999 | 2024-05-28 | AAA | 0.024 |  | POE- WELL, RAW
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-05-28 | AAA |  |  | POE- WELL, RAW
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1030 | LEAD | 0.0006 | MG/L | 0.0154 | 2024-05-28 | AAA | 0.005 |  | POE- WELL, RAW
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-06-04 | AAA |  |  | FIRST POE
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-06-04 | AAA |  |  | FIRST POE
3494290 | RICHARDSON'S FISH CAMP | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-06-04 | AAA |  |  | FIRST POE
3491904 | KING'S MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.47 | UG/L | 60.4999 | 2021-08-17 | L1 |  |  |  | 3
3491904 | KING'S MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 8.18 | UG/L | 80.4999 | 2021-08-17 | L1 |  |  |  | 3
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.1 | MG/L | 4.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 9.8 | MG/L | 160.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 14 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.1 | MG/L | 2.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 9 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.81 | LN(10) |  | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 222 | MG/L | 500.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0.06 |  | 0.5499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-02 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.6 | UG/L | 60.4999 | 2025-11-24 | L1 |  |  | Q4 2025DBP RESULTS | 3
3491726 | SHARP'S MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2025-11-24 | L1 |  |  | Q4 2025DBP RESULTS | 3
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-02 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-02 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-04 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-04 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.059 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | POE
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-17 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.95 | UG/L | 60.4999 | 2024-08-13 | L1 | 0.98 |  | LOT #18 | 3
3491904 | KING'S MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 11.46 | UG/L | 80.4999 | 2024-08-13 | L1 | 0.39 |  | LOT #18 | 3
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.085 | MG/L | 10.4999 | 2024-11-14 | AAA | 0.024 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-14 | AAA | 0.0034 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0.0003 | MG/L | 0.0104 | 2024-11-14 | AAA | 0.00025 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.019 | MG/L | 2.4999 | 2024-11-14 | AAA | 0.003 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-11-14 | AAA | 0.00025 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-11-14 | AAA | 0.005 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-11-14 | AAA | 0.004 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.13 | MG/L | 4.0499 | 2024-11-14 | AAA | 0.0099 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-11-14 | AAA | 0.0005 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-11-14 | AAA | 3e-05 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-11-14 | AAA | 0.008 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-11-14 | AAA | 0.0012 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 15 | MG/L | 160.4999 | 2024-11-14 | AAA | 0.8 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-11-14 | AAA | 0.001 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-11-14 | AAA | 0.002 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-11-14 | AAA | 0.00025 |  | SUB E84589, E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-11-14 | AAA | 0.024 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 19 | MG/L | 250.4999 | 2024-11-14 | AAA | 0.039 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0.0096 | MG/L | 1.4999 | 2024-11-14 | AAA | 0.005 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.13 | MG/L | 2.0499 | 2024-11-14 | AAA | 0.0099 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1028 | IRON | 0.043 | MG/L | 0.3499 | 2024-11-14 | AAA | 0.038 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-11-14 | AAA | 0.005 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-11-14 | AAA | 0.0005 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 8.7 | MG/L | 250.4999 | 2024-11-14 | AAA | 0.034 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-11-14 | AAA | 0.05 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-11-14 | AAA | 5 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-11-14 | AAA | 1 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.45 | LN(10) |  | 2024-11-14 | AAA |  |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 150 | MG/L | 500.4999 | 2024-11-14 | AAA | 10 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0.1 |  | 0.5499 | 2024-11-14 | AAA | 0.04 |  | SUB E82535, E82001, E82574
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-11-14 | AAA | 0.134 | 0.667
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.6 | PCI/L | 15.4999 | 2024-11-14 | AAA | 1.1
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-11-14 | AAA |  | 0.5499 | 2024 VOC
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2024-11-19 | AAA | 0.3 | 1.4999 | POE
3491904 | KING'S MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-11-19 | AAA | 0.6 | 1.4999 | POE
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-03 | AAA | 0.024 |  | POE
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-03 | AAA | 0.0034 |  | POE
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-20 | AAA |  |  | POE
3491904 | KING'S MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-20 | AAA |  |  | POE
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-09-07 | AAA |  |  | POE
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-09-07 | AAA |  |  | POE
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-07-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-07-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-07-17 | AAA | 0.025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-07-17 | AAA | 0.025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-04-27 | AAA |  |  | POE
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-04-27 | AAA |  |  | POE
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-04-21 | AAA |  |  | POE
3494310 | PILOT TRAVEL CENTER 096 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-21 | AAA |  |  | POE
3494313 | WHISPERING PINES MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.36 | UG/L | 60.4999 | 2021-08-16 | L1 |  |  | 1729 GRAND CYPRESS | 3
3494313 | WHISPERING PINES MHP | D | DBP | 2950 | TOTAL THMS | 14.46 | UG/L | 80.4999 | 2021-08-16 | L1 |  |  | 1729 GRAND CYPRESS | 3
3494313 | WHISPERING PINES MHP | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1052 | SODIUM | 8.3 | MG/L | 160.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.14 | MG/L | 4.0499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0.0003 | MG/L | 0.0154 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 11.2 | MG/L | 160.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 12.5 | MG/L | 250.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0.0033 | MG/L | 1.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.14 | MG/L | 2.0499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1041 | NITRITE | 0.093 | MG/L | 1.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA |  |  | POE
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-27 | AAA |  |  | POE
3494353 | JIFFY FOOD STORE #2483 | D | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2023-10-18 | AAA | 0.024 |  | DIST -
3494353 | JIFFY FOOD STORE #2483 | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-18 | AAA |  |  | DIST -
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1040 | NITRATE | 0.086 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-21 | AAA |  |  | POE
3494353 | JIFFY FOOD STORE #2483 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA |  |  | POE
3494313 | WHISPERING PINES MHP | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1017 | CHLORIDE | 8 | MG/L | 250.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1028 | IRON | 0.059 | MG/L | 0.3499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1055 | SULFATE | 46 | MG/L | 250.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.77 | LN(10) |  | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 192 | MG/L | 500.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SEC | 2905 | FOAMING AGENTS | 0.05 |  | 0.5499 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-22 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-22 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-22 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-22 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-22 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-22 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-22 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-22 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-22 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-22 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-22 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-22 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-22 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-22 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-22 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.6 | PCI/L | 15.4999 | 2021-11-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-11-22 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494313 | WHISPERING PINES MHP | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-05 | AAA |  |  | POE
3494313 | WHISPERING PINES MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-05 | AAA |  |  | POE
3494313 | WHISPERING PINES MHP | N | INOR | 1040 | NITRATE | 0.058 | MG/L | 10.4999 | 2023-10-16 | AAA | 0.024 |  | POE
3494313 | WHISPERING PINES MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | POE
3494313 | WHISPERING PINES MHP | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.74 | UG/L | 60.4999 | 2024-08-13 | L1 | 0.98 |  | 1729 GRAND CYPRESS AVE. | 3
3494313 | WHISPERING PINES MHP | D | DBP | 2950 | TOTAL THMS | 11.04 | UG/L | 80.4999 | 2024-08-13 | L1 | 0.39 |  | 1729 GRAND CYPRESS AVE. | 3
3494313 | WHISPERING PINES MHP | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1040 | NITRATE | 0.072 | MG/L | 10.4999 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1052 | SODIUM | 6.8 | MG/L | 160.4999 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-10 | AAA |  |  | 2024 INORG RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1017 | CHLORIDE | 8.3 | MG/L | 250.4999 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1025 | FLUORIDE | 0.19 | MG/L | 2.0499 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1055 | SULFATE | 43 | MG/L | 250.4999 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.75 | LN(10) |  | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 210 | MG/L | 500.4999 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-10 | AAA | 0.7 | 1.4999 | 2024 RAD RESULTS
3494313 | WHISPERING PINES MHP | N | SEC | 2905 | FOAMING AGENTS | 0.053 |  | 0.5499 | 2024-09-10 | AAA |  |  | 2024 SEC RESULTS
3494313 | WHISPERING PINES MHP | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.5 | PCI/L | 15.4999 | 2024-09-10 | AAA | 1.1 |  | 2024 RAD RESULTS
3494313 | WHISPERING PINES MHP | N | RAD | 4020 | RADIUM-226 | 1.4 | PCI/L | 3.4999 | 2024-09-10 | AAA | 0.4 | 1.4999 | 2024 RAD RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-10 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494313 | WHISPERING PINES MHP | N | INOR | 1040 | NITRATE | 0.083 | MG/L | 10.4999 | 2025-01-14 | AAA | 0.024 |  | POE
3494313 | WHISPERING PINES MHP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-14 | AAA |  |  | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1028 | IRON | 0.069 | MG/L | 0.3499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0.0024 | MG/L | 0.0549 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 3.9 | MG/L | 250.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0.01 | MG/L | 5.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.2 | LN(10) |  | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 128 | MG/L | 500.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-04-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-04-09 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-09 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-04-09 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-04-09 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-04-09 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-04-09 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-04-09 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-04-09 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-09 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-09 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-04-09 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-09 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-04-09 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-04-09 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-04-09 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-04-09 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-04-09 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494316 | BERMUDA MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9 | UG/L | 60.4999 | 2021-09-24 | L1 |  |  | 2021 TTHM/HAA5 RESULTS | 3
3494316 | BERMUDA MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 12.1 | UG/L | 80.4999 | 2021-09-24 | L1 |  |  | 2021 TTHM/HAA5 RESULTS | 3
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA |  |  | 2022 N/N SAMPLES
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-27 | AAA |  |  | 2022 N/N SAMPLES
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-27 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-27 | AAA |  |  | POE
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-27 | AAA |  |  | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-11-21 | AAA |  | 0.5499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-08-21 | AAA |  |  | 2024 RAD RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-08-21 | AAA |  | 0.667 | 2024 RAD RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2024-08-21 | AAA |  | 1.4999 | 2024 RAD RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-08-21 | AAA |  | 1.4999 | 2024 RAD RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-08-21 | AAA |  | 0.5499 | 2024 VOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-08-21 | AAA |  | 0.0149 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA |  | 0.0249 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-08-21 | AAA |  | 0.1499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA |  | 1.4999 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-08-21 | AAA |  | 1.4999 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-08-21 | AAA |  | 0.4499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-08-21 | AAA |  | 9.4999 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-08-21 | AAA |  | 6.4999 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-08-21 | AAA |  | 0.6499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-08-21 | AAA |  | 2.4999 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-08-21 | AAA |  | 0.0749 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-08-21 | AAA |  | 0.6499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-08-21 | AAA |  | 0.1499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-08-21 | AAA |  | 0.2499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-08-21 | AAA |  | 0.1499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-08-21 | AAA |  | 0.9499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-08-21 | AAA |  | 0.1499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-08-21 | AAA |  | 0.2499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-08-21 | AAA |  | 0.0449 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA |  | 0.0249 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-08-21 | AAA |  | 0.1499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-08-21 | AAA |  | 0.2499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-08-21 | AAA |  | 0.1499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA |  | 0.0249 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0.21 | UG/L | 1.4999 | 2024-08-21 | AAA | 0.014 | 0.0449 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-08-21 | AAA |  | 0.1499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-08-21 | AAA |  | 0.0249 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-08-21 | AAA |  | 0.0149 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-08-21 | AAA |  | 0.2499 | 2024 SOC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.13 | MG/L | 4.0499 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0.0036 | MG/L | 0.0154 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 16.3 | MG/L | 160.4999 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-08-21 | AAA |  |  | 2024 INORG RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 17.7 | MG/L | 250.4999 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0.0079 | MG/L | 1.4999 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.13 | MG/L | 2.0499 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1028 | IRON | 0.48 | MG/L | 0.3499 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0.0061 | MG/L | 0.0549 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 4.3 | MG/L | 250.4999 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0.045 | MG/L | 5.4999 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.2 | LN(10) |  | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 141 | MG/L | 500.4999 | 2024-08-21 | AAA |  |  | 2024 SEC RESULTS
3494316 | BERMUDA MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.5 | UG/L | 60.4999 | 2024-09-23 | L1 | 0.9 |  | L-1 (TRAILER #1) | 3
3494316 | BERMUDA MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 18.1 | UG/L | 80.4999 | 2024-09-23 | L1 | 0.75 |  | L-1 (TRAILER #1) | 3
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-10-30 | AAA |  | 1.4999 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-10-30 | AAA |  | 0.1499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-10-30 | AAA |  | 0.2499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-10-30 | AAA |  | 0.1499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-10-30 | AAA |  | 0.2499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-10-30 | AAA |  | 0.0449 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-01-07 | AAA | 0.014 | 0.0449 | POE-PENTACHLROPHENOL
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-19 | AAA |  |  | POE
3494316 | BERMUDA MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-19 | AAA |  |  | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-04-09 | AAA |  | 0.0449 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-09-26 | AAA |  | 1.4999 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-09-26 | AAA |  | 0.1499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-09-26 | AAA |  | 0.2499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-09-26 | AAA |  | 0.1499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-09-26 | AAA |  | 0.2499 | POE
3494316 | BERMUDA MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-09-26 | AAA |  | 0.0449 | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-06 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-06 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2021-01-13 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2021-01-13 | AAA |  |  | POE...FLUORIDE MCL
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.24 | UG/L | 60.4999 | 2021-02-17 | L1 |  |  | BREEZEWAY | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 13.72 | UG/L | 80.4999 | 2021-02-17 | L1 |  |  | BREEZEWAY | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.4 | UG/L | 60.4999 | 2021-02-17 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 13.74 | UG/L | 80.4999 | 2021-02-17 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | N | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 1.7 |  |  | 2021-03-01 | AAA | 0.5 |  | TOC
3494318 | LAKE MARIAN SHORES | N | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2 |  |  | 2021-04-01 | AAA | 0.5 |  | POE TOC 2.0 MG/L (PRIOR TO FILTER 2.3 MG/L) SPECIAL MONITORING TO CHECK TOC LEVEL FOR DBPS
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2021-04-22 | AAA | 0.0065 |  | FLUORIDE 2.5 MG/L
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2021-04-22 | AAA | 0.0065 |  | FLUORIDE 2.5 MG/L (OVER THE SECONDARY MCL OF 2.0 MG/L)
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-19 | L2 |  |  | LOT 46, LRAA TTHM=42.4825 HAA5=21.1325_NMS
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.19 | UG/L | 60.4999 | 2021-05-19 | L1 |  |  | LOT 64, LRAA TTHM= 45.185 HAA5=22.1325_NMS | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-05-19 | L1 |  |  | LOT 64, LRAA TTHM= 45.185 HAA5=22.1325_NMS | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-05-19 | L2 |  |  | LOT 46, LRAA TTHM=42.4825 HAA5=21.1325_NMS
3494318 | LAKE MARIAN SHORES | D | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2021-07-15 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2021-07-15 | AAA |  |  | POE...FLUORIDE MCL
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-07-31 | AAA |  | 1.4999 | 1Q RESTART DUE TO MISSED SAMPLING. - NEED 4Q 2021 & 1Q, 2Q, 3Q 2022 - MISSED 1Q & 2Q 2021_NMS
3494320 | 21 PALMS RV RESORT | N | INOR | 1040 | NITRATE | 0.095 | MG/L | 10.4999 | 2021-11-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494320 | 21 PALMS RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-22 | AAA |  | 1.4999 | 2Q RESTART DUE TO MISSED SAMPLING DALAPON - NEED 1Q, 2Q, 3Q 2022 - MISSED 1Q & 2Q 2021_NMS
3494320 | 21 PALMS RV RESORT | N | INOR | 1040 | NITRATE | 0.47 | MG/L | 10.4999 | 2022-03-09 | AAA |  |  | 2022 ANNUAL N/N
3494320 | 21 PALMS RV RESORT | N | INOR | 1041 | NITRITE | 0.018 | MG/L | 1.4999 | 2022-03-09 | AAA |  |  | 2022 ANNUAL N/N
3494320 | 21 PALMS RV RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-03-09 | AAA | 0.089 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-03-09 | AAA | 0.079 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-03-09 | AAA | 0.16 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-03-09 | AAA | 0.15 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-03-09 | AAA | 0.065 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-03-09 | AAA | 0.071 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-03-09 | AAA | 0.12 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-03-09 | AAA | 0.13 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-03-09 | AAA | 0.26 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.12 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-03-09 | AAA | 0.091 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.16 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-03-09 | AAA | 0.21 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.1 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-03-09 | AAA | 0.23 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.14 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-03-09 | AAA | 0.12 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-03-09 | AAA | 0.066 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-03-09 | AAA | 0.11 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-03-09 | AAA | 0.067 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-03-09 | AAA | 0.049 | 0.5499 | 2022 ANNUAL VOC
3494320 | 21 PALMS RV RESORT | N | INOR | 1040 | NITRATE | 0.47 | MG/L | 10.4999 | 2022-03-09 | AAA | 0.03 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-09 | AAA | 0.018 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-03-09 | AAA | 0.0049 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-03-09 | AAA | 0.00047 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1010 | BARIUM | 0.0131 | MG/L | 2.4999 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-03-09 | AAA | 0.00045 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1025 | FLUORIDE | 0.09 | MG/L | 4.0499 | 2022-03-09 | AAA | 0.034 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-03-09 | AAA | 0.0013 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-03-09 | AAA | 0.00015 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1036 | NICKEL | 0.0014 | MG/L | 0.1499 | 2022-03-09 | AAA | 1e-05 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-03-09 | AAA | 0.00091 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1052 | SODIUM | 8.79 | MG/L | 160.4999 | 2022-03-09 | AAA | 0.4 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-03-09 | AAA | 0.00037 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-03-09 | AAA | 0.00011 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-03-09 | AAA | 0.013 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1017 | CHLORIDE | 15 | MG/L | 250.4999 | 2022-03-09 | AAA | 0.047 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1022 | COPPER | 0.0017 | MG/L | 1.4999 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1025 | FLUORIDE | 0.09 | MG/L | 2.0499 | 2022-03-09 | AAA | 0.034 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1028 | IRON | 0.0952 | MG/L | 0.3499 | 2022-03-09 | AAA | 0.022 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1032 | MANGANESE | 0.0058 | MG/L | 0.0549 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-03-09 | AAA | 0.0001 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1055 | SULFATE | 1.3 | MG/L | 250.4999 | 2022-03-09 | AAA | 0.08 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1095 | ZINC | 0.0032 | MG/L | 5.4999 | 2022-03-09 | AAA | 0.0011 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2022-03-09 | AAA | 5 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2022-03-09 | AAA | 1 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2022-03-09 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 200 | MG/L | 500.4999 | 2022-03-09 | AAA | 10 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-03-09 | AAA | 0.026 |  | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-03-09 | AAA | 0.003 | 0.0149 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA | 0.0031 | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-03-09 | AAA | 0.024 | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.22 | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-03-09 | AAA | 0.22 | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-03-09 | AAA | 0.16 | 0.4499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-03-09 | AAA | 3.3 | 9.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-03-09 | AAA | 4.2 | 6.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-03-09 | AAA | 0.19 | 0.6499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-03-09 | AAA | 0.15 | 2.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-03-09 | AAA | 0.059 | 0.0749 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-03-09 | AAA | 0.31 | 0.6499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-03-09 | AAA | 0.1 | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-03-09 | AAA | 0.028 | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-03-09 | AAA | 0.0043 | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-03-09 | AAA | 0.082 | 0.9499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.044 | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-03-09 | AAA | 0.025 | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-03-09 | AAA | 0.0056 | 0.0449 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA | 0.012 | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-03-09 | AAA | 0.099 | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-03-09 | AAA | 0.05 | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-03-09 | AAA | 0.0015 | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA | 0.02 | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-03-09 | AAA | 0.039 | 0.0449 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-03-09 | AAA | 0.029 | 0.1499 | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2021-08-23 | AAA | 0.0065 |  | FLUORIDE 2.4
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2021-08-23 | AAA | 0.0065 |  | FLUORIDE 2.4 (OVER THE SECONDARY MCL OF 2.0 MG/L) HLKD
3494318 | LAKE MARIAN SHORES | N | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2.2 |  |  | 2021-08-23 | AAA | 0.5 |  | POST FILTER TOC 2.2 MG/L (PRE FILTER 2.2 MG/L) SPECIAL MONITORING TO CHECK TOC LEVEL FOR DBPS
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.71 | UG/L | 60.4999 | 2021-08-25 | L2 | 0.98 |  | (BREEZEWAY CT.) LOT 46 (HLKD)
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 13.22 | UG/L | 80.4999 | 2021-08-25 | L2 | 0.39 |  | (BREEZEWAY CT.) LOT 46 (HLKD)
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.83 | UG/L | 60.4999 | 2021-08-25 | L1 | 0.98 |  | (BREEZEWAY COURT) LOT 64 (HLKD) | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 9.75 | UG/L | 80.4999 | 2021-08-25 | L1 | 0.39 |  | (BREEZEWAY COURT) LOT 64 (HLKD) | 4
3494318 | LAKE MARIAN SHORES | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1052 | SODIUM | 24 | MG/L | 160.4999 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-10-26 | AAA |  |  | FLUORIDE SMCL EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1017 | CHLORIDE | 34 | MG/L | 250.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1055 | SULFATE | 2.9 | MG/L | 250.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.92 | LN(10) |  | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 259 | MG/L | 500.4999 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-10-26 | AAA |  |  | SMCL FLUORIDE EXCEEDANCE_NMS
3494318 | LAKE MARIAN SHORES | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-10-26 | AAA |  | 0.667
3494318 | LAKE MARIAN SHORES | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 0.5499
3494318 | LAKE MARIAN SHORES | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.0149
3494318 | LAKE MARIAN SHORES | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-10-26 | AAA |  | 0.4499
3494318 | LAKE MARIAN SHORES | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-10-26 | AAA |  | 9.4999
3494318 | LAKE MARIAN SHORES | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-10-26 | AAA |  | 6.4999
3494318 | LAKE MARIAN SHORES | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-10-26 | AAA |  | 0.6499
3494318 | LAKE MARIAN SHORES | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-10-26 | AAA |  | 2.4999
3494318 | LAKE MARIAN SHORES | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-10-26 | AAA |  | 0.0749
3494318 | LAKE MARIAN SHORES | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-10-26 | AAA |  | 0.6499
3494318 | LAKE MARIAN SHORES | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-10-26 | AAA |  | 0.9499
3494318 | LAKE MARIAN SHORES | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-10-26 | AAA |  | 0.0449
3494318 | LAKE MARIAN SHORES | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-10-26 | AAA |  | 0.0449
3494318 | LAKE MARIAN SHORES | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-10-26 | AAA |  | 0.1499
3494318 | LAKE MARIAN SHORES | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-10-26 | AAA |  | 0.0249
3494318 | LAKE MARIAN SHORES | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-10-26 | AAA |  | 0.0149
3494318 | LAKE MARIAN SHORES | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-10-26 | AAA |  | 0.2499
3494318 | LAKE MARIAN SHORES | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 5.4 | PCI/L | 15.4999 | 2021-10-26 | AAA
3494318 | LAKE MARIAN SHORES | N | RAD | 4020 | RADIUM-226 | 2.6 | PCI/L | 3.4999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-10-26 | AAA |  | 1.4999
3494318 | LAKE MARIAN SHORES | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-09 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2022-02-09 | AAA |  |  | ENTERED LATE_AL
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.3 | MG/L | 2.0499 | 2022-06-23 | AAA |  |  | RECIEVED LATE_AL
3494318 | LAKE MARIAN SHORES | S | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2 |  |  | 2022-06-23 | AAA | 0.5 |  | POE TOC 2.0 MG/L
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.3 | MG/L | 4.0499 | 2022-06-23 | AAA |  |  | FLUORIDE 2.30 MG/L (NEED FLUORIDE REPORTED FOR SECONDARIES)
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2022-08-02 | AAA | 0.0099 |  | RECIEVED CORRECTED REPORT_AL
3494318 | LAKE MARIAN SHORES | S | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2022-08-02 | AAA | 0.0099 |  | FLUORIDE 2.50 MG/L (NEED LAB REPORT DATED NEXT TO LAB MANAGER'S SIGNATURE ON EACH PAGE 2 IN SUBMITTAL, DATE WILL BE 9/8/22 OR EARLIER MOST LIKELY GOING BY OTHER REPORTS)
3494318 | LAKE MARIAN SHORES | S | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3 |  |  | 2022-08-02 | AAA | 0.5 |  | PRE-FILTER TOCS 3 MG/L (NEED LAB REPORT DATED NEXT TO LAB MANAGER'S SIGNATURE ON EACH PAGE 2 IN SUBMITTAL, DATE WILL BE 9/8/22 OR EARLIER MOST LIKELY GOING BY OTHER REPORTS)
3494318 | LAKE MARIAN SHORES | N | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2 |  |  | 2022-08-02 | AAA | 0.5 |  | RECIEVED CORRECTED REPORT_AL
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.64 | UG/L | 60.4999 | 2022-08-16 | L1 |  |  | LOT 64 | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 146.03 | UG/L | 80.4999 | 2022-08-16 | L1 |  |  | LOT 64 | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 55.54 | UG/L | 60.4999 | 2022-08-16 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 191.62 | UG/L | 80.4999 | 2022-08-16 | L2 |  |  | LOT 46
3494318 | LAKE MARIAN SHORES | N | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2022-10-26 | AAA | 0.024 |  | SAMPLE TYPE- ENTRY POINT - POE AND DISTRIBUTION
3494318 | LAKE MARIAN SHORES | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | SAMPLE TYPE- ENTRY POINT - POE AND DISTRIBUTION
3494318 | LAKE MARIAN SHORES | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-11-08 | AAA |  | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.24 | UG/L | 60.4999 | 2022-11-16 | L1 |  |  | Q422 TTHM HAA5 LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 64.77 | UG/L | 80.4999 | 2022-11-16 | L1 |  |  | Q422 TTHM HAA5 LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.44 | UG/L | 60.4999 | 2022-11-16 | L2 |  |  | 4Q22 TTHM HAA5 LOT46
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 58.22 | UG/L | 80.4999 | 2022-11-16 | L2 |  |  | 4Q22 TTHM HAA5 LOT46
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.8 | MG/L | 4.0499 | 2023-01-24 | AAA | 0.18 |  | FLUORIDE 2.80 MG/L
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.8 | MG/L | 2.0499 | 2023-01-24 | AAA | 0.18 |  | FLUORIDE 2.80 MG/L (EXCEEDS SECONDARY MCL OF 2.0 MG/L)
3494318 | LAKE MARIAN SHORES | S | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3.5 |  |  | 2023-01-24 | AAA | 0.5 |  | PRE-FILTER TOC 3.50 MG/L
3494318 | LAKE MARIAN SHORES | S | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 2.1 |  |  | 2023-01-24 | AAA | 0.5 |  | POST FILTER TOC 2.10 MG/L
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.72 | UG/L | 60.4999 | 2023-02-20 | L2 | 0.98 |  | LOT 46 (LAB REPORT HAS PWSID# & STREET ADDRESS OF LAKE MARIAN PARADISE 3490766, 901 ARNOLD RD.) ***PLS. VERIFY TESTING SITE WITH US WATER OPR/SAMPLER***
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 20.91 | UG/L | 80.4999 | 2023-02-20 | L2 | 0.39 |  | LOT 46 (LAB REPORT HAS PWSID# & STREET ADDRESS OF LAKE MARIAN PARADISE 3490766, 901 ARNOLD RD.) ***PLS. VERIFY TESTING SITE WITH US WATER OPR/SAMPLER***
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.43 | UG/L | 60.4999 | 2023-02-20 | L1 | 0.98 |  | LOT 64, BREEZEWAY COURT (LAB REPORT HAS PWSID# & STREET ADDRESS OF LAKE MARIAN PARADISE 3490766, 901 ARNOLD RD.) ***PLS. VERIFY TESTING SITE WITH US WATER OPR/SAMPLER*** | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 21.09 | UG/L | 80.4999 | 2023-02-20 | L1 | 0.39 |  | LOT 64, BREEZEWAY COURT (LAB REPORT HAS PWSID# & STREET ADDRESS OF LAKE MARIAN PARADISE 3490766, 901 ARNOLD RD.) ***PLS. VERIFY TESTING SITE WITH US WATER OPR/SAMPLER*** | 4
3494318 | LAKE MARIAN SHORES | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.25 | UG/L | 60.4999 | 2023-05-19 | L2 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT LOT 64 AND LOT 46)
3494318 | LAKE MARIAN SHORES | N | DBP | 2950 | TOTAL THMS | 86.73 | UG/L | 80.4999 | 2023-05-19 | L2 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT LOT 64 AND LOT 46)
3494318 | LAKE MARIAN SHORES | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 45.2 | UG/L | 60.4999 | 2023-05-19 | L1 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT LOT 64 AND LOT 46) | 4
3494318 | LAKE MARIAN SHORES | N | DBP | 2950 | TOTAL THMS | 112.98 | UG/L | 80.4999 | 2023-05-19 | L1 |  |  | 2Q23 TTHM AND HAA5 RESULTS (TTHM LRAA > MCL VIOLATION AT LOT 64 AND LOT 46) | 4
3494318 | LAKE MARIAN SHORES | D | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2023-06-27 | AAA | 0.0099 |  | DIST.
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2023-06-27 | AAA | 0.0099 |  | DIST.
3494318 | LAKE MARIAN SHORES | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-27 | AAA |  | 1.4999 | DIST.
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.48 | UG/L | 60.4999 | 2023-08-21 | L2 | 0.98 |  | LOT46
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2023-08-21 | L2 | 0.39 |  | LOT46
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.41 | UG/L | 60.4999 | 2023-08-21 | L1 | 0.98 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2023-08-21 | L1 | 0.39 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.3 | MG/L | 4.0499 | 2023-09-08 | AAA | 0.0099 |  | DIST - POE
3494318 | LAKE MARIAN SHORES | D | SEC | 1025 | FLUORIDE | 2.3 | MG/L | 2.0499 | 2023-09-08 | AAA | 0.0099 |  | DIST -POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1040 | NITRATE | 0.098 | MG/L | 10.4999 | 2023-10-16 | AAA | 0.024 |  | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-10-19 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.3 | MG/L | 4.0499 | 2023-11-17 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.3 | MG/L | 2.0499 | 2023-11-17 | AAA | 0.0099 |  | 4Q2023 FLUORIDE
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 59.94 | UG/L | 60.4999 | 2023-11-23 | L2 |  |  | TTHM HAA5 MCL EXCEEDANCE TTHM AND HAA5 @L1 TTHM @L2 4Q23 SAMPLES_DJ
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2022-02-09 | AAA |  |  | ENTERED LATE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2022-11-07 | AAA | 0.0099 |  | FLUORIDE 2.50 MG/L (RCVD 1-23-23)
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2022-11-07 | AAA | 0.0099 |  | FLUORIDE 2.50 MG/L (RCVD 1-23-23)
3494318 | LAKE MARIAN SHORES | S | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 3 |  |  | 2022-11-07 | AAA | 0.5 |  | PRE-FILTER TOCS 3 MG/L
3494318 | LAKE MARIAN SHORES | S | SEC | 2920 | TOTAL ORGANIC CARBON (TOC) | 1.8 |  |  | 2022-11-07 | AAA | 0.5 |  | POST FILTER TOCS 1.80 MG/L
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 65.84 | UG/L | 60.4999 | 2023-11-21 | L1 |  |  | TTHM HAA5 MCL EXCEEDANCE TTHM AND HAA5 @L1 AND TTHM @L2 4Q23 SAMPLES_DJ | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 144.54 | UG/L | 80.4999 | 2023-11-21 | L1 |  |  | TTHM HAA5 MCL EXCEEDANCE TTHM AND HAA5 @L1 AND TTHM @L2 4Q23 SAMPLES_DJ | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 143.98 | UG/L | 80.4999 | 2023-11-23 | L2 |  |  | TTHM HAA5 MCL EXCEEDANCE TTHM AND HAA5 @L1 TTHM @L2 4Q23 SAMPLES_DJ
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2024-01-12 | AAA | 0.0099 |  | POE
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-02-16 | L1 | 0.98 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-02-16 | L1 | 0.39 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-02-16 | L2 | 0.98 |  | LOT46
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-02-16 | L2 | 0.39 |  | LOT46
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2024-04-16 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2024-04-17 | AAA | 0.0099 |  | 2Q24 FLUORIDE
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.29 | UG/L | 60.4999 | 2024-05-15 | L1 | 0.98 |  | 2Q2024 TTHM/HAA5 RESULTS | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 60.87 | UG/L | 80.4999 | 2024-05-15 | L1 | 0.39 |  | 2Q2024 TTHM/HAA5 RESULTS | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.42 | UG/L | 60.4999 | 2024-05-15 | L2 | 0.98 |  | 2Q2024 TTHM/HAA5 RESULTS
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 61.26 | UG/L | 80.4999 | 2024-05-15 | L2 | 0.39 |  | 2Q2024 TTHM/HAA5 RESULTS
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2024-07-15 | AAA | 0.0099 |  | POE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2024-07-15 | AAA | 0.0099 |  | POE - 1025 EXCEEDANCE
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-08-15 | L1 | 0.98 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.39 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-08-15 | L2 | 0.98 |  | LOT 64, 46
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-08-15 | L2 | 0.39 |  | LOT 64, 46
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.4 | MG/L | 4.0499 | 2024-08-19 | AAA | 0.0099 |  | POE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2024-08-19 | AAA | 0.0099 |  | POE - 1025 EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1015 | CADMIUM | 0.0003 | MG/L | 0.0055 | 2024-10-21 | AAA | 0.00025 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.4 | MG/L | 2.0499 | 2024-01-12 | AAA | 2 |  | 1Q24 FLOURIDE_DJ
3494318 | LAKE MARIAN SHORES | N | INOR | 1040 | NITRATE | 0.32 | MG/L | 10.4999 | 2024-10-21 | AAA | 0.024 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-21 | AAA | 0.0034 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-10-21 | AAA | 0.00025 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1010 | BARIUM | 0.0038 | MG/L | 2.4999 | 2024-10-21 | AAA | 0.003 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-10-21 | AAA | 0.005 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-10-21 | AAA | 0.004 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.3 | MG/L | 4.0499 | 2024-10-21 | AAA | 0.0099 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1030 | LEAD | 0.026 | MG/L | 0.0154 | 2024-10-21 | AAA | 0.0005 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-10-21 | AAA | 3e-05 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-10-21 | AAA | 0.008 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-10-21 | AAA | 0.0012 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1052 | SODIUM | 29 | MG/L | 160.4999 | 2024-10-21 | AAA | 0.8 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-10-21 | AAA | 0.001 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-10-21 | AAA | 0.002 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-10-21 | AAA | 0.00025 |  | POE - LEAD EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-10-21 | AAA | 0.024 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1017 | CHLORIDE | 40 | MG/L | 250.4999 | 2024-10-21 | AAA | 0.039 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1022 | COPPER | 0.15 | MG/L | 1.4999 | 2024-10-21 | AAA | 0.005 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.3 | MG/L | 2.0499 | 2024-10-21 | AAA | 0.0099 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1028 | IRON | 0.04 | MG/L | 0.3499 | 2024-10-21 | AAA | 0.038 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-10-21 | AAA | 0.005 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-10-21 | AAA | 0.0005 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2024-10-21 | AAA | 2.6 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1095 | ZINC | 0.41 | MG/L | 5.4999 | 2024-10-21 | AAA | 0.05 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-10-21 | AAA | 5 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2024-10-21 | AAA | 1 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.21 | LN(10) |  | 2024-10-21 | AAA |  |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 270 | MG/L | 500.4999 | 2024-10-21 | AAA | 10 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | SEC | 2905 | FOAMING AGENTS | 0.049 |  | 0.5499 | 2024-10-21 | AAA | 0.04 |  | POE - FLUORIDE EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-10-21 | AAA | 0.2 | 0.667 | POE - CONTAM 4006 SUBCONTRACTED TO E82574 BY E53076
3494318 | LAKE MARIAN SHORES | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.2 | PCI/L | 15.4999 | 2024-10-21 | AAA | 1.6 |  | POE - CONTAM 4006 SUBCONTRACTED TO E82574 BY E53076
3494318 | LAKE MARIAN SHORES | N | RAD | 4020 | RADIUM-226 | 1.4 | PCI/L | 3.4999 | 2024-10-21 | AAA | 0.4 | 1.4999 | POE - CONTAM 4006 SUBCONTRACTED TO E82574 BY E53076
3494318 | LAKE MARIAN SHORES | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-10-21 | AAA | 0.8 | 1.4999 | POE - CONTAM 4006 SUBCONTRACTED TO E82574 BY E53076
3494318 | LAKE MARIAN SHORES | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-10-21 | AAA | 0.5 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-10-21 | AAA | 0.24 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-10-21 | AAA | 0.48 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-10-21 | AAA | 0.49 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-10-21 | AAA | 0.44 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-10-21 | AAA | 0.4 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-10-21 | AAA | 0.28 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-21 | AAA | 0.4 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-10-21 | AAA | 0.4 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-10-21 | AAA | 0.44 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-10-21 | AAA | 0.32 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-10-21 | AAA | 0.36 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-10-21 | AAA | 0.33 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-21 | AAA | 0.25 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-10-21 | AAA | 0.44 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-21 | AAA | 0.49 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-10-21 | AAA | 0.37 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-10-21 | AAA | 0.26 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-10-21 | AAA | 0.16 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-10-21 | AAA | 0.2 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-10-21 | AAA | 0.33 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.31 | UG/L | 60.4999 | 2024-11-20 | L1 | 0.98 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 62.72 | UG/L | 80.4999 | 2024-11-20 | L1 | 0.44 |  | LOT 64, BREEZEWAY COURT | 4
3494318 | LAKE MARIAN SHORES | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18 | UG/L | 60.4999 | 2024-11-20 | L2 | 0.98 |  | LOT46
3494318 | LAKE MARIAN SHORES | D | DBP | 2950 | TOTAL THMS | 51.64 | UG/L | 80.4999 | 2024-11-20 | L2 | 0.44 |  | LOT46
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.3 | MG/L | 4.0499 | 2025-01-14 | AAA | 0.0099 |  | POE FLUORIDE AND LEAD
3494318 | LAKE MARIAN SHORES | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-01-14 | AAA | 0.003 |  | POE FLUORIDE AND LEAD
3494318 | LAKE MARIAN SHORES | N | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2025-01-29 | AAA | 0.024 |  | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-29 | AAA |  |  | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1030 | LEAD | 0.0045 | MG/L | 0.0154 | 2025-07-08 | AAA | 0.003
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2025-07-08 | AAA | 0.0099 |  | FLUORIDE
3494318 | LAKE MARIAN SHORES | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-10-13 | AAA | 0.5 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-11-13 | AAA | 0.0005 |  | 2024 LEAD INORG CONFIRMATION SAMPLE_DJ
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2025-04-23 | AAA | 0.0099 |  | POE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2025-04-23 | AAA | 0.0099 |  | POE - 1025 EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-04-23 | AAA | 0.001 |  | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1025 | FLUORIDE | 2.5 | MG/L | 4.0499 | 2025-10-13 | AAA | 0.0099 |  | POE
3494318 | LAKE MARIAN SHORES | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-10-13 | AAA | 0.0005 |  | POE
3494318 | LAKE MARIAN SHORES | N | SEC | 1025 | FLUORIDE | 2.5 | MG/L | 2.0499 | 2025-10-13 | AAA | 0.0099 |  | POE, 1025 EXCEEDANCE
3494318 | LAKE MARIAN SHORES | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-10-13 | AAA | 0.45 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-13 | AAA | 0.48 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-10-13 | AAA | 0.49 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-10-13 | AAA | 0.44 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-10-13 | AAA | 0.4 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-10-13 | AAA | 0.28 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-10-13 | AAA | 0.4 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-10-13 | AAA | 0.41 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-10-13 | AAA | 0.44 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-10-13 | AAA | 0.32 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-10-13 | AAA | 0.36 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-10-13 | AAA | 0.33 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-13 | AAA | 0.25 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-10-13 | AAA | 0.44 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-10-13 | AAA | 0.46 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-13 | AAA | 0.49 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-10-13 | AAA | 0.37 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-10-13 | AAA | 0.42 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-10-13 | AAA | 0.45 | 0.5499 | POE
3494318 | LAKE MARIAN SHORES | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-10-13 | AAA | 0.45 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-03-09 | AAA | 0.9 | 1.4999
3494320 | 21 PALMS RV RESORT | D | DBP | 2950 | TOTAL THMS | 46.2 | UG/L | 80.4999 | 2022-08-01 | L1 | 1 |  | ADDRESS GIVEN AS 6951 OSCEOLA POLK LINE RD., WHICH IS ADDRESS OF 21 PALMS RV RESORT (STAGE 2 SITE IS LOT 20 - ?) PG1 NOT SIGNED&SMP TYPE MISSING(PARTIAL REVISION RCVD 9/19/22 BUT LOT 20 STILL MISSING) | 3
3494320 | 21 PALMS RV RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-03-09 | AAA | 0.0019 | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-03-09 | AAA | 0.002 | 0.0149 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-03-09 | AAA | 0.2 | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-01 | AAA | 0.31 | 1.4999 | DALAPON
3494320 | 21 PALMS RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2022-08-01 | L1 | 2 |  | ADDRESS GIVEN AS 6951 OSCEOLA POLK LINE RD., WHICH IS ADDRESS OF 21 PALMS RV RESORT (STAGE 2 SITE IS LOT 20 - ?) PG1 NOT SIGNED&SMP TYPE MISSING(PARTIAL REVISION RCVD 9/19/22 BUT LOT 20 STILL MISSING) | 3
3494320 | 21 PALMS RV RESORT | D | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-18 | AAA |  | 1.4999 | POE-LOCATION CODE SET BY PWS - 03/10/2008 - DIST
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-08-21 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494320 | 21 PALMS RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.4 | UG/L | 60.4999 | 2023-11-21 | L1 | 0.98 |  | LOT 20 | 3
3494320 | 21 PALMS RV RESORT | D | DBP | 2950 | TOTAL THMS | 49.71 | UG/L | 80.4999 | 2023-11-21 | L1 | 0.39 |  | LOT 20 | 3
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-11-21 | AAA | 0.9 | 1.4999 | POE LOT 20
3494320 | 21 PALMS RV RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-02-27 | AAA | 0.024
3494320 | 21 PALMS RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-02-27 | AAA | 0.0034
3494320 | 21 PALMS RV RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-27 | AAA | 0.28 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-27 | AAA | 0.32 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-27 | AAA | 0.26 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA | 0.44 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-27 | AAA | 0.46 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-27 | AAA | 0.26 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-27 | AAA | 0.39 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-27 | AAA | 0.2 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-27 | AAA | 0.18 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA | 0.28 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA | 0.36 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA | 0.23 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA | 0.26 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA | 0.26 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA | 0.12 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA | 0.24 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA | 0.12 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-27 | AAA | 0.17 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-27 | AAA | 0.22 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-27 | AAA | 0.17 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA | 0.39 | 0.5499 | 2023 VOC MAKEUP SAMPLES_DJ
3494320 | 21 PALMS RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.5 | UG/L | 60.4999 | 2024-02-27 | L1 | 0.98 |  | LOT 20 (OUTSIDE SAMPLING PLAN) | 3
3494320 | 21 PALMS RV RESORT | D | DBP | 2950 | TOTAL THMS | 37.03 | UG/L | 80.4999 | 2024-02-27 | L1 | 0.39 |  | LOT 20 (OUTSIDE SAMPLING PLAN) | 3
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-03-26 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.39 | UG/L | 60.4999 | 2024-05-15 | L1 | 0.98 |  | LOT 20 - OUTSIDE OF APPROVAL PLAN, MUST SAMPLE IN SEPTEMBER 2024 | 3
3494320 | 21 PALMS RV RESORT | S | DBP | 2950 | TOTAL THMS | 55.21 | UG/L | 80.4999 | 2024-05-15 | L1 | 0.39 |  | LOT 20 - OUTSIDE OF APPROVAL PLAN, MUST SAMPLE IN SEPTEMBER 2024 | 3
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-05-15 | AAA | 0.9 | 1.4999 | 2Q2024 DALAPON
3494320 | 21 PALMS RV RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-09-04 | AAA |  | 0.0149 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-09-04 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-09-04 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-09-04 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-09-04 | AAA |  | 0.4499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-09-04 | AAA |  | 9.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-09-04 | AAA |  | 6.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-09-04 | AAA |  | 0.6499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-09-04 | AAA |  | 0.6499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-09-04 | AAA |  | 2.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-09-04 | AAA |  | 0.0749 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-09-04 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-09-04 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-09-04 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-09-04 | AAA |  | 0.9499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-09-04 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-09-04 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-09-04 | AAA |  | 0.0449 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-09-04 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-09-04 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-09-04 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-09-04 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-09-04 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-09-04 | AAA |  | 0.0449 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-09-04 | AAA |  | 0.1499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-09-04 | AAA |  | 0.0249 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-09-04 | AAA |  | 0.0149 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-09-04 | AAA |  | 0.2499 | POE
3494320 | 21 PALMS RV RESORT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0.8 | PCI/L | 15.4999 | 2024-09-04 | AAA | 0.7 |  | POE
3494320 | 21 PALMS RV RESORT | N | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2024-09-04 | AAA | 0.4 | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-04 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1017 | CHLORIDE | 12 | MG/L | 250.4999 | 2024-09-04 | AAA | 0.039 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1025 | FLUORIDE | 0.013 | MG/L | 2.0499 | 2024-09-04 | AAA | 0.0099 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1055 | SULFATE | 10 | MG/L | 250.4999 | 2024-09-04 | AAA | 0.034 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1905 | COLOR | 5.1 | COLOR UNITS | 15.4999 | 2024-09-04 | AAA | 5 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.7 | LN(10) |  | 2024-09-04 | AAA |  |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 160 | MG/L | 500.4999 | 2024-09-04 | AAA | 10 |  | POE
3494320 | 21 PALMS RV RESORT | N | SEC | 2905 | FOAMING AGENTS | 0.098 |  | 0.5499 | 2024-09-04 | AAA | 0.04 |  | POE
3494320 | 21 PALMS RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.19 | UG/L | 60.4999 | 2024-09-30 | L1 | 0.98 |  | LOT 20 | 3
3494320 | 21 PALMS RV RESORT | D | DBP | 2950 | TOTAL THMS | 62.47 | UG/L | 80.4999 | 2024-09-30 | L1 | 0.39 |  | LOT 20 | 3
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-11-26 | AAA |  | 1.4999 | POE
3494320 | 21 PALMS RV RESORT | N | INOR | 1040 | NITRATE | 0.084 | MG/L | 10.4999 | 2025-02-11 | AAA | 0.024 |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2025-02-11 | AAA | 0.003 |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1025 | FLUORIDE | 0.27 | MG/L | 4.0499 | 2025-02-11 | AAA | 0.0099 |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1052 | SODIUM | 9.1 | MG/L | 160.4999 | 2025-02-11 | AAA | 0.8 |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-02-11 | AAA |  |  | 2024 MAKEUP SAMPLES + 2025 N/N SAMPLES
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-08-05 | AAA | 9 | 1.4999
3494320 | 21 PALMS RV RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-10-01 | AAA | 0.44 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-02-03 | AAA | 0.9 | 1.4999 | POE - DALAPON ONLY
3494320 | 21 PALMS RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.72 | UG/L | 60.4999 | 2025-09-04 | L1 | 0.98 |  | LOT 20 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3494320 | 21 PALMS RV RESORT | D | DBP | 2950 | TOTAL THMS | 62.69 | UG/L | 80.4999 | 2025-09-04 | L1 | 0.39 |  | LOT 20 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3494320 | 21 PALMS RV RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-10-01 | AAA | 0.5 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-10-01 | AAA | 0.45 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-01 | AAA | 0.48 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-10-01 | AAA | 0.49 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-10-01 | AAA | 0.4 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-10-01 | AAA | 0.28 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-10-01 | AAA | 0.4 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-10-01 | AAA | 0.41 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-10-01 | AAA | 0.44 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-10-01 | AAA | 0.32 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-10-01 | AAA | 0.36 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-10-01 | AAA | 0.33 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-01 | AAA | 0.25 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-10-01 | AAA | 0.44 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-01 | AAA | 0.49 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-10-01 | AAA | 0.37 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-10-01 | AAA | 0.42 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-10-01 | AAA | 0.46 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-10-01 | AAA | 0.45 | 0.5499 | POE
3494320 | 21 PALMS RV RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-10-01 | AAA | 0.45 | 0.5499 | POE
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-18 | AAA |  |  | POE
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-18 | AAA |  |  | POE
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | POE
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-17 | AAA |  |  | POE
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1040 | NITRATE | 0.085 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-21 | AAA | 0.024 |  | POE - NN
3494325 | WILD FLORIDA AIRBOATS, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA | 0.0034 |  | POE - NN
3494333 | PAPS FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-12-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494333 | PAPS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494333 | PAPS FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-12-30 | AAA | 0.2 |  | POE
3494333 | PAPS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-30 | AAA | 0.2 |  | POE
3494333 | PAPS FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-27 | AAA | 0.2 |  | 2025
3494333 | PAPS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-27 | AAA | 0.2 |  | 2025
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1040 | NITRATE | 0.096 | MG/L | 10.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-26 | AAA | 0.0034 |  | POE
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | D | INOR | 1040 | NITRATE | 0.055 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | DIST
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | D | INOR | 1041 | NITRITE | 0.11 | MG/L | 1.4999 | 2023-10-17 | AAA | 0.0034 |  | DIST
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-23 | AAA |  |  | POE
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-23 | AAA |  |  | POE
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-21 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494334 | NARAYAN FOOD MART (SHELL FOOD MART) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA | 0.0034 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494354 | COZY COVE INN | N | INOR | 1040 | NITRATE | 0.088 | MG/L | 10.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494354 | COZY COVE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494354 | COZY COVE INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA | 0.024 |  | NITRITE J QUALIFIER
3494354 | COZY COVE INN | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-27 | AAA | 0.0034 |  | NITRITE J QUALIFIER - J QUAL ACCEPTED FOLLOWING LCS QC REPORT - FW 12/28/22
3494354 | COZY COVE INN | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-27 | AAA | 0.0034 |  | NITRITE J QUALIFIER
3494354 | COZY COVE INN | N | INOR | 1040 | NITRATE | 0.062 | MG/L | 10.4999 | 2023-10-18 | AAA | 0.024 |  | POE
3494354 | COZY COVE INN | N | INOR | 1041 | NITRITE | 0.0034 | MG/L | 1.4999 | 2023-10-18 | AAA | 0.0034 |  | POE
3494354 | COZY COVE INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-22 | AAA |  |  | POE
3494354 | COZY COVE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494354 | COZY COVE INN | N | INOR | 1040 | NITRATE | 0.083 | MG/L | 10.4999 | 2025-01-21 | AAA | 0.024 |  | POE
3494354 | COZY COVE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA | 0.0034 |  | POE
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-12-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494333 | PAPS FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-29 | AAA | 0.2
3494333 | PAPS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-29 | AAA | 0.2
3494333 | PAPS FOOD MART | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2023-12-29 | AAA | 0.024 |  | POE
3494333 | PAPS FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-12-29 | AAA |  |  | POE
3494354 | COZY COVE INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA |  |  | NITRITE J QUALIFIER - J QUAL ACCEPTED FOLLOWING LCS QC REPORT - FW 12/28/22
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-26 | AAA | 0.0034 |  | POE
3494360 | KENANSVILLE COUNTRY STORE | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-10-16 | AAA |  |  | DIST POE
3494360 | KENANSVILLE COUNTRY STORE | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | DIST POE
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2025-01-21 | AAA | 0.024 |  | POE
3494360 | KENANSVILLE COUNTRY STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA |  |  | POE
3494372 | AMVETS POST 33 | N | INOR | 1040 | NITRATE | 0.72 | MG/L | 10.4999 | 2022-01-31 | AAA | 0.03 |  | 2021 NN SAMPLES, SAMPLED AND SUBMITTED LATE
3494372 | AMVETS POST 33 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-31 | AAA | 0.018 |  | 2021 NN SAMPLES, SAMPLED AND SUBMITTED LATE
3494372 | AMVETS POST 33 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-06 | AAA | 0.03 |  | POE
3494372 | AMVETS POST 33 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA | 0.018 |  | POE
3494372 | AMVETS POST 33 | N | INOR | 1040 | NITRATE | 0.08 | MG/L | 10.4999 | 2023-06-14 | AAA | 0.024 |  | POE - NO2/NO3; SUBCONTRACTED TO LAB #E53076
3494372 | AMVETS POST 33 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-14 | AAA | 0.0034 |  | POE - NO2/NO3; SUBCONTRACTED TO LAB #E53076
3494372 | AMVETS POST 33 | N | INOR | 1040 | NITRATE | 0.051 | MG/L | 10.4999 | 2024-06-17 | AAA | 0.024 |  | POE
3494372 | AMVETS POST 33 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-06-17 | AAA |  |  | POE
3494372 | AMVETS POST 33 | N | INOR | 1040 | NITRATE | 0.067 | MG/L | 10.4999 | 2025-06-23 | AAA | 0.024 |  | POE
3494372 | AMVETS POST 33 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-06-23 | AAA |  |  | POE
3494375 | HITCHING POST | S | INOR | 1040 | NITRATE | 0.44 | MG/L | 10.4999 | 2022-01-31 | AAA | 0.03 |  | MAKE UP SAMPLES FOR 2021
3494375 | HITCHING POST | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-31 | AAA | 0.018 |  | MAKE UP SAMPLES FOR 2021
3494375 | HITCHING POST | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2023-06-14 | AAA | 0.024 |  | POE - NO2/NO3; SUBCONTRACTED TO LAB #E53076
3494375 | HITCHING POST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-14 | AAA | 0.0034 |  | POE - NO2/NO3; SUBCONTRACTED TO LAB #E53076
3494375 | HITCHING POST | N | INOR | 1040 | NITRATE | 0.064 | MG/L | 10.4999 | 2024-06-17 | AAA | 0.024 |  | POE
3494375 | HITCHING POST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-06-17 | AAA |  |  | POE
3494375 | HITCHING POST | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-06-23 | AAA |  |  | POE
3494375 | HITCHING POST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-06-23 | AAA |  |  | POE
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | N | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-12-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | N | INOR | 1040 | NITRATE | 0.0821 | MG/L | 10.4999 | 2022-10-03 | AAA | 0.024 |  | POE
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | N | INOR | 1041 | NITRITE | 0.087 | MG/L | 1.4999 | 2022-10-03 | AAA | 0.0034 |  | POE
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-22 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-22 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | INOR | 1025 | FLUORIDE | 0.24 | MG/L | 4.0499 | 2024-01-22 | AAA | 0.0099 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-02-14 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1017 | CHLORIDE | 20 | MG/L | 250.4999 | 2024-02-14 | AAA | 0.039 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-02-14 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1025 | FLUORIDE | 0.24 | MG/L | 2.0499 | 2024-02-14 | AAA | 0.0099 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-02-14 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-02-14 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-02-14 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1055 | SULFATE | 24 | MG/L | 250.4999 | 2024-02-14 | AAA | 0.034 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1095 | ZINC | 1.5 | MG/L | 5.4999 | 2024-02-14 | AAA | 0.05 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1905 | COLOR | 30 | COLOR UNITS | 15.4999 | 2024-02-14 | AAA | 5 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1920 | ODOR THRESHOLD | 2.9 |  | 3.4999 | 2024-02-14 | AAA | 1 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 6.25 | LN(10) |  | 2024-02-14 | AAA |  |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 180 | MG/L | 500.4999 | 2024-02-14 | AAA | 5 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 2905 | FOAMING AGENTS | 0.065 |  | 0.5499 | 2024-02-14 | AAA | 0.04 |  | RAW
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | P | INOR | 1040 | NITRATE | 0.087 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | P | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | N | INOR | 1040 | NITRATE | 0.059 | MG/L | 10.4999 | 2025-08-05 | AAA | 0.024 |  | POE
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-05 | AAA |  |  | POE
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1040 | NITRATE | 0.09 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (NITRITE CORRECTED 1/31/22 FROM -0- TO 0.091 - BB)
3494375 | HITCHING POST | N | INOR | 1040 | NITRATE | 0.31 | MG/L | 10.4999 | 2022-06-06 | AAA | 0.03
3494375 | HITCHING POST | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-06 | AAA | 0.018
3494377 | PARTIN TRIANGLE PK OF OSCEOLA COUNTY | R | SEC | 1905 | COLOR | 37 | COLOR UNITS | 15.4999 | 2024-02-14 | AAA | 5 |  | RAW
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1041 | NITRITE | 0.091 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (NITRITE CORRECTED 1/31/22 FROM -0- TO 0.091 - BB)
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3494392 | CIRCLE K #7466/KISSIMMEE | D | INOR | 1040 | NITRATE | 0.073 | MG/L | 10.4999 | 2023-10-18 | AAA | 0.024 |  | DIST
3494392 | CIRCLE K #7466/KISSIMMEE | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-18 | AAA |  |  | DIST
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-05 | AAA |  |  | POE
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-05 | AAA |  |  | POE
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1040 | NITRATE | 0.083 | MG/L | 10.4999 | 2025-01-14 | AAA | 0.024 |  | POE
3494392 | CIRCLE K #7466/KISSIMMEE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-14 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-01-26 | L2 |  |  | DEERFIELD ST [LRAA TTHM=16.53; HAA5=6.34]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-01-26 | L2 |  |  | DEERFIELD ST [LRAA TTHM=16.53; HAA5=6.34]
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-01-26 | L1 |  |  | HAMMOCK POINTE [LRAA TTHM=14.55 ; HAA5=6.31] CONTINUE SAMPLING Q. NEED 4 CONSEC QUARTERS DUE TO AMENDED CO EXECUTED 8/2020
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-01-26 | L1 |  |  | HAMMOCK POINTE [LRAA TTHM=14.55 ; HAA5=6.31] CONTINUE SAMPLING Q. NEED 4 CONSEC QUARTERS DUE TO AMENDED CO EXECUTED 8/2020
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.28 | UG/L | 60.4999 | 2021-07-26 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 103.33 | UG/L | 80.4999 | 2021-07-26 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.81 | UG/L | 60.4999 | 2021-07-26 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 110.89 | UG/L | 80.4999 | 2021-07-26 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.48 | UG/L | 60.4999 | 2021-10-22 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 22.69 | UG/L | 80.4999 | 2021-10-22 | L1 |  |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.59 | UG/L | 60.4999 | 2021-10-22 | L2 |  |  | 2801 DEERFIELD ST.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 23.29 | UG/L | 80.4999 | 2021-10-22 | L2 |  |  | 2801 DEERFIELD ST.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1010 | BARIUM | 0.0064 | MG/L | 2.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-04-22 | L2 |  |  | 2801 DEERFIELD LRAA - TTHMA=7.21 HAA5=3.07_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-04-22 | L2 |  |  | 2801 DEERFIELD LRAA - TTHMA=7.21 HAA5=3.07_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-04-22 | L1 |  |  | 5221 HAMMOCK POINT CT LRAA TTHMS= 6.96 HAA5 3.39_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2021-04-22 | L1 |  |  | 5221 HAMMOCK POINT CT LRAA TTHMS= 6.96 HAA5 3.39_NMS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1052 | SODIUM | 27 | MG/L | 160.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1017 | CHLORIDE | 41 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1055 | SULFATE | 6 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1905 | COLOR | 8 | COLOR UNITS | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.03 | LN(10) |  | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 75 | MG/L | 500.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 2905 | FOAMING AGENTS | 0.09 |  | 0.5499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-02 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494416 | HIDDEN GLEN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, ACCEPTED)_VPU
3494416 | HIDDEN GLEN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | AAA | 0.025 |  | NITRATE ENTD (NITRITE HAS J QUALIFIER, ACCEPTED)_VPU
3494416 | HIDDEN GLEN | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA |  | 1.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 1.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-25 | AAA |  | 0.4499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-25 | AAA |  | 9.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-25 | AAA |  | 6.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 2.4999 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-25 | AAA |  | 0.1499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-25 | AAA |  | 0.2499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-25 | AAA |  | 0.9499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-02-25 | AAA |  | 0.0055 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-25 | AAA |  | 0.1499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-25 | AAA |  | 0.2499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-25 | AAA |  | 0.0449 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-25 | AAA |  | 0.1499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-25 | AAA |  | 0.0149 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.2499 | HIDDEN GLENN- POE
3494416 | HIDDEN GLEN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-03-19 | AAA |  | 0.0149 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-03-19 | AAA |  | 0.0249 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-03-19 | AAA |  | 0.6499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-03-19 | AAA |  | 0.0749 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-03-19 | AAA |  | 0.6499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-03-19 | AAA |  | 0.2499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-03-19 | AAA |  | 0.0449 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-03-19 | AAA |  | 0.0249 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-03-19 | AAA |  | 0.1499 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-03-19 | AAA |  | 0.0249 | HIDDEN GLENN-POE
3494416 | HIDDEN GLEN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-27 | AAA | 0.025
3494416 | HIDDEN GLEN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.025
3494416 | HIDDEN GLEN | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-27 | AAA | 0.0005
3494416 | HIDDEN GLEN | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2021-05-27 | AAA | 0.0062
3494416 | HIDDEN GLEN | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-27 | AAA | 0.00067
3494416 | HIDDEN GLEN | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0026
3494416 | HIDDEN GLEN | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.005
3494416 | HIDDEN GLEN | N | INOR | 1025 | FLUORIDE | 0.076 | MG/L | 4.0499 | 2021-05-27 | AAA | 0.015
3494416 | HIDDEN GLEN | N | INOR | 1030 | LEAD | 0.0012 | MG/L | 0.0154 | 2021-05-27 | AAA | 0.00022
3494416 | HIDDEN GLEN | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-27 | AAA | 9e-05
3494416 | HIDDEN GLEN | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.002
3494416 | HIDDEN GLEN | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.00083
3494416 | HIDDEN GLEN | N | INOR | 1052 | SODIUM | 5.8 | MG/L | 160.4999 | 2021-05-27 | AAA | 0.59
3494416 | HIDDEN GLEN | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-27 | AAA | 0.00021
3494416 | HIDDEN GLEN | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-27 | AAA | 0.00058
3494416 | HIDDEN GLEN | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-27 | AAA | 0.0005
3494416 | HIDDEN GLEN | S | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2021-05-27 | AAA | 0.2 |  | POE/D ASBESTOS (NOT TESTED OUT IN THE DISTRIBUTION SYSTEM)
3494416 | HIDDEN GLEN | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.0072
3494416 | HIDDEN GLEN | N | SEC | 1017 | CHLORIDE | 8.2 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5
3494416 | HIDDEN GLEN | N | SEC | 1022 | COPPER | 0.0071 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.00093
3494416 | HIDDEN GLEN | N | SEC | 1025 | FLUORIDE | 0.076 | MG/L | 2.0499 | 2021-05-27 | AAA | 0.015
3494416 | HIDDEN GLEN | N | SEC | 1028 | IRON | 0.083 | MG/L | 0.3499 | 2021-05-27 | AAA | 0.016
3494416 | HIDDEN GLEN | N | SEC | 1032 | MANGANESE | 0.0039 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.0027
3494416 | HIDDEN GLEN | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0033
3494416 | HIDDEN GLEN | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2021-05-27 | AAA | 2.5
3494416 | HIDDEN GLEN | N | SEC | 1095 | ZINC | 0.022 | MG/L | 5.4999 | 2021-05-27 | AAA | 0.0076
3494416 | HIDDEN GLEN | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-05-27 | AAA | 5
3494416 | HIDDEN GLEN | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-05-27 | AAA | 1
3494416 | HIDDEN GLEN | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.7 | LN(10) |  | 2021-05-27 | AAA | 0.1
3494416 | HIDDEN GLEN | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 145 | MG/L | 500.4999 | 2021-05-27 | AAA | 5
3494416 | HIDDEN GLEN | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-27 | AAA | 0.099
3494416 | HIDDEN GLEN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-06-28 | AAA |  |  | HIDDEN GLENN
3494416 | HIDDEN GLEN | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-28 | AAA |  | 1.4999 | HIDDEN GLENN
3494416 | HIDDEN GLEN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.4 | UG/L | 60.4999 | 2022-07-25 | L1 | 0.9 |  | 6624 IVY MIST LN (HLKD) | 3
3494416 | HIDDEN GLEN | D | DBP | 2950 | TOTAL THMS | 28.1 | UG/L | 80.4999 | 2022-07-25 | L1 | 0.47 |  | 6624 IVY MIST LN (HLKD) | 3
3494416 | HIDDEN GLEN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | AAA |  |  | POE
3494416 | HIDDEN GLEN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | AAA |  |  | POE
3494416 | HIDDEN GLEN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21 | UG/L | 60.4999 | 2023-07-26 | L1 | 0.9 |  | 6624 IVY MIST | 3
3494416 | HIDDEN GLEN | D | DBP | 2950 | TOTAL THMS | 22.6 | UG/L | 80.4999 | 2023-07-26 | L1 | 0.47 |  | 6624 IVY MIST | 3
3494416 | HIDDEN GLEN | P | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-30 | AAA |  |  | POE
3494416 | HIDDEN GLEN | P | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | AAA |  |  | POE
3494416 | HIDDEN GLEN | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | AAA | 0.025
3494416 | HIDDEN GLEN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | AAA | 0.025
3494416 | HIDDEN GLEN | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494416 | HIDDEN GLEN | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-03-29 | AAA | 0.0086 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2024-03-29 | AAA | 0.0024 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-03-29 | AAA | 0.025 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-29 | AAA | 0.025 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-03-29 | AAA | 0.0005 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-03-29 | AAA | 0.00067 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-03-29 | AAA | 0.0048 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-03-29 | AAA | 0.005 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1025 | FLUORIDE | 0.053 | MG/L | 4.0499 | 2024-03-29 | AAA | 0.015 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-03-29 | AAA | 0.00025 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-03-29 | AAA | 0.00014 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-03-29 | AAA | 0.002 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-03-29 | AAA | 0.00083 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1052 | SODIUM | 6.3 | MG/L | 160.4999 | 2024-03-29 | AAA | 0.59 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-03-29 | AAA | 0.00088 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-03-29 | AAA | 0.00019 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-03-29 | AAA | 0.00021 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2024-03-29 | AAA | 0.19 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1017 | CHLORIDE | 8.3 | MG/L | 250.4999 | 2024-03-29 | AAA | 2.5 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1022 | COPPER | 0.0025 | MG/L | 1.4999 | 2024-03-29 | AAA | 0.00093 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1025 | FLUORIDE | 0.053 | MG/L | 2.0499 | 2024-03-29 | AAA | 0.015 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1028 | IRON | 0.088 | MG/L | 0.3499 | 2024-03-29 | AAA | 0.021 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1032 | MANGANESE | 0.0038 | MG/L | 0.0549 | 2024-03-29 | AAA | 0.0013 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-03-29 | AAA | 0.0022 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2024-03-29 | AAA | 2.5 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-03-29 | AAA | 0.0077 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-03-29 | AAA | 5 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-03-29 | AAA | 1 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2024-03-29 | AAA | 0.1 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 146 | MG/L | 500.4999 | 2024-03-29 | AAA | 5 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-03-29 | AAA | 0.099 |  | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-04-30 | AAA | 0.0023 | 0.0149 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.0027 | 0.0249 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-04-30 | AAA | 0.023 | 0.1499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-04-30 | AAA | 0.27 | 1.4999 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-04-30 | AAA | 0.49 | 1.4999 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-04-30 | AAA | 0.16 | 0.4499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-04-30 | AAA | 3.3 | 9.4999 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-04-30 | AAA | 4.2 | 6.4999 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-04-30 | AAA | 0.36 | 0.6499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-04-30 | AAA | 0.46 | 2.4999 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-04-30 | AAA | 0.04 | 0.0749 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-04-30 | AAA | 0.47 | 0.6499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-04-30 | AAA | 0.04 | 0.1499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-04-30 | AAA | 0.16 | 0.2499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-04-30 | AAA | 0.59 | 0.9499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-04-30 | AAA | 0.015 | 0.1499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-04-30 | AAA | 0.029 | 0.2499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-04-30 | AAA | 0.0014 | 0.0055 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-04-30 | AAA | 0.014 | 0.0449 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-04-30 | AAA | 0.015 | 0.1499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.003 | 0.0249 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-04-30 | AAA | 0.096 | 0.1499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-04-30 | AAA | 0.059 | 0.2499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.02 | 0.0249 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-04-30 | AAA | 0.014 | 0.0449 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-04-30 | AAA | 0.045 | 0.1499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.0063 | 0.0249 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-04-30 | AAA | 0.0074 | 0.0149 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-04-30 | AAA | 0.036 | 0.2499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.075 | UG/L | 54.9999 | 2024-04-30 | AAA | 0.024 | 0.1499 | POE- 2042 DETECT
3494416 | HIDDEN GLEN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-05-21 | AAA |  |  | POE
3494416 | HIDDEN GLEN | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-05-21 | AAA |  | 1.4999 | POE
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.0911 | UG/L | 54.9999 | 2024-07-12 | AAA | 0.024 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494416 | HIDDEN GLEN | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.3 | UG/L | 60.4999 | 2024-07-23 | L1 | 0.9 |  | 6624 IVY MIST - TTHM/HAA5 | 3
3494416 | HIDDEN GLEN | D | DBP | 2950 | TOTAL THMS | 27.7 | UG/L | 80.4999 | 2024-07-23 | L1 | 0.75 |  | 6624 IVY MIST - TTHM/HAA5 | 3
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-10-08 | AAA | 0.024 | 0.1499 | 4Q2024 CONTAM ID 2042 RESULT (J QUALIFIED)
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-11-15 | AAA | 0.024 | 0.1499 | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-01-10 | AAA | 0.024 | 0.1499 | HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-14 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 HIDDEN GLEN
3494416 | HIDDEN GLEN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 HIDDEN GLEN
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-04-04 | AAA |  | 0.1499 | POE
3494416 | HIDDEN GLEN | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-07-18 | AAA | 0 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-02 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494416 | HIDDEN GLEN | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-05-21 | AAA | 1.14 |  | 6701 S OBT POE; SUBCONTRACTED TO E87683
3494416 | HIDDEN GLEN | N | RAD | 4030 | RADIUM-228 | 0.805 | PCI/L | 2.4999 | 2024-05-21 | AAA | 0.766 | 1.4999 | 6701 S OBT POE; SUBCONTRACTED TO E87683
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-02 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 45.08 | UG/L | 80.4999 | 2022-01-27 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.31 | UG/L | 60.4999 | 2022-01-27 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 69.31 | UG/L | 80.4999 | 2022-01-27 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.1 | UG/L | 60.4999 | 2022-01-27 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 68.54 | UG/L | 60.4999 | 2022-07-20 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 116.05 | UG/L | 80.4999 | 2022-07-20 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 70.47 | UG/L | 60.4999 | 2022-07-20 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 114.52 | UG/L | 80.4999 | 2022-07-20 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT. (HLKD/HIGH RESULTS)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.88 | UG/L | 60.4999 | 2022-10-11 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 101.77 | UG/L | 80.4999 | 2022-10-11 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-10-11 | L2 | 0.98 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 6.69 | UG/L | 80.4999 | 2022-10-11 | L2 | 0.39 |  | 2801 DEERFIELD ST. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1040 | NITRATE | 0.15 | MG/L | 10.4999 | 2022-10-26 | AAA | 0.024 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-26 | AAA | 0.0034 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.08 | UG/L | 60.4999 | 2023-01-11 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 49.18 | UG/L | 80.4999 | 2023-01-11 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT. (HLKD)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2023-01-11 | L2 | 0.98 |  | 2801 DEERFIELD ST HAA5 TTHM RESULTS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 1.79 | UG/L | 80.4999 | 2023-01-11 | L2 | 0.39 |  | 2801 DEERFIELD ST HAA5 TTHM RESULTS
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 62.42 | UG/L | 60.4999 | 2023-04-21 | L2 | 0.98 |  | 2831 DEERFIELD-WRONG SITE (STG2 SITE IS 2801 DEERFIELD ST.) RESULTS EXCEED MCLS & MAY BE BETTER SITES FOR STG2. SITES WERE TESTED APRIL 3RD WEEK INSTEAD OF APRIL 2ND WEEK. MATRIX IS WW (?) ON CHAIN
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2950 | TOTAL THMS | 108.96 | UG/L | 80.4999 | 2023-04-21 | L2 | 0.39 |  | 2831 DEERFIELD-WRONG SITE (STG2 SITE IS 2801 DEERFIELD ST.) RESULTS EXCEED MCLS & MAY BE BETTER SITES FOR STG2. SITES WERE TESTED APRIL 3RD WEEK INSTEAD OF APRIL 2ND WEEK. MATRIX IS WW (?) ON CHAIN
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 74.19 | UG/L | 60.4999 | 2023-04-21 | L1 | 0.98 |  | 5211 HAMMOCK CIRCLE-OUTSIDE APPROVED TIMEFRAME
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2950 | TOTAL THMS | 127.86 | UG/L | 80.4999 | 2023-04-21 | L1 | 0.39 |  | 5211 HAMMOCK CIRCLE-OUTSIDE APPROVED TIMEFRAME
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.61 | UG/L | 60.4999 | 2023-07-10 | L1 | 0.98 |  | 5221 HAMMOCK POINTE CT.-Q QUALIFIER TTHM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.22 | UG/L | 60.4999 | 2023-07-10 | L2 | 0.98 |  | 2801 DEERFIELD ST. (PHASE 3 EOL)-Q QUALIFIER TTHM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2950 | TOTAL THMS | 74.26 | UG/L | 80.4999 | 2023-07-10 | L2 | 0.39 |  | 2801 DEERFIELD ST. (PHASE 3 EOL)-Q QUALIFIER TTHM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2950 | TOTAL THMS | 42.78 | UG/L | 80.4999 | 2023-07-10 | L1 | 0.39 |  | 5221 HAMMOCK POINTE CT.-Q QUALIFIER TTHM
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.43 | UG/L | 60.4999 | 2023-08-17 | L1 | 0.98 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2950 | TOTAL THMS | 76.28 | UG/L | 80.4999 | 2023-08-17 | L1 | 0.39 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.12 | UG/L | 60.4999 | 2023-08-17 | L2 | 0.98 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | S | DBP | 2950 | TOTAL THMS | 74.58 | UG/L | 80.4999 | 2023-08-17 | L2 | 0.39 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.28 | UG/L | 60.4999 | 2023-10-11 | L1 | 0.98 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 7.76 | UG/L | 80.4999 | 2023-10-11 | L1 | 0.39 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.76 | UG/L | 60.4999 | 2023-10-11 | L2 | 0.98 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 78.45 | UG/L | 80.4999 | 2023-10-11 | L2 | 0.39 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2023-10-18 | AAA | 0.024 |  | DIST
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-18 | AAA |  |  | DIST
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.75 | UG/L | 60.4999 | 2024-01-10 | L1 | 0.98 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 44.73 | UG/L | 80.4999 | 2024-01-10 | L1 | 0.39 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.59 | UG/L | 60.4999 | 2024-01-10 | L2 | 0.98 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-01-10 | L2 | 0.39 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.63 | UG/L | 60.4999 | 2024-04-10 | L1 | 0.98 |  | 5211 HAMMOCK CIRCLE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 52.94 | UG/L | 80.4999 | 2024-04-10 | L1 | 0.39 |  | 5211 HAMMOCK CIRCLE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.92 | UG/L | 60.4999 | 2024-04-10 | L2 | 0.98 |  | 2831 DEERFIELD ST
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 33.1 | UG/L | 80.4999 | 2024-04-10 | L2 | 0.39 |  | 2831 DEERFIELD ST
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.14 | UG/L | 60.4999 | 2024-07-10 | L1 | 0.98 |  | 5211 HAMMOCK POINTE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-07-10 | L1 | 0.39 |  | 5211 HAMMOCK POINTE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.77 | UG/L | 60.4999 | 2024-07-10 | L2 | 0.98 |  | 2831 DEERFIELD ST
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-07-10 | L2 | 0.39 |  | 2831 DEERFIELD ST
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1017 | CHLORIDE | 39 | MG/L | 250.4999 | 2024-09-09 | AAA | 0.039 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2024-09-09 | AAA | 0.4 | 1.4999
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-09 | AAA |  | 1.4999
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1022 | COPPER | 0.035 | MG/L | 1.4999 | 2024-09-09 | AAA | 0.005 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1025 | FLUORIDE | 0.16 | MG/L | 2.0499 | 2024-09-09 | AAA | 0.0099 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1055 | SULFATE | 6.3 | MG/L | 250.4999 | 2024-09-09 | AAA | 0.034 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1905 | COLOR | 9.1 | COLOR UNITS | 15.4999 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.26 | LN(10) |  | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 290 | MG/L | 500.4999 | 2024-09-09 | AAA | 10 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1010 | BARIUM | 0.0071 | MG/L | 2.4999 | 2024-09-09 | AAA | 0.03 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2024-09-09 | AAA | 24 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2024-09-09 | AAA | 0.0099 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1036 | NICKEL | 0.017 | MG/L | 0.1499 | 2024-09-09 | AAA | 0.008 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1052 | SODIUM | 29 | MG/L | 160.4999 | 2024-09-09 | AAA | 0.8 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-09 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-09-09 | AAA |  | 0.667 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-09 | AAA |  | 0.5499 | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.1 | PCI/L | 15.4999 | 2024-09-09 | AAA | 1.4
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.37 | UG/L | 60.4999 | 2024-10-08 | L1 | 0.89 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 53.57 | UG/L | 80.4999 | 2024-10-08 | L1 | 0.39 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 48.11 | UG/L | 60.4999 | 2024-10-08 | L2 | 0.89 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 91.37 | UG/L | 80.4999 | 2024-10-08 | L2 | 0.39 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.89 | UG/L | 60.4999 | 2025-01-07 | L1 | 0.98 |  | 5211 HAMMOCK POINTE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 77.48 | UG/L | 80.4999 | 2025-01-07 | L1 | 0.39 |  | 5211 HAMMOCK POINTE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 52.95 | UG/L | 60.4999 | 2025-01-07 | L2 | 0.98 |  | 2831 DEERFIELD ST.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 89.36 | UG/L | 80.4999 | 2025-01-07 | L2 | 0.39 |  | 2831 DEERFIELD ST.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2025-01-14 | AAA | 0.024 |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-14 | AAA |  |  | POE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.95 | UG/L | 60.4999 | 2025-04-07 | L1 | 0.98 |  | 5211 HAMMOCK POINTE CT.-TTHM EXCEEDANCE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 105.24 | UG/L | 80.4999 | 2025-04-07 | L1 | 0.44 |  | 5211 HAMMOCK POINTE CT.-TTHM EXCEEDANCE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 50.24 | UG/L | 60.4999 | 2025-04-07 | L2 | 0.98 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)-TTHM EXCEEDANCE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 101.37 | UG/L | 80.4999 | 2025-04-07 | L2 | 0.44 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)-TTHM EXCEEDANCE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.14 | UG/L | 60.4999 | 2025-07-08 | L1 | 0.98 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 58.77 | UG/L | 80.4999 | 2025-07-08 | L1 | 0.44 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 53.21 | UG/L | 60.4999 | 2025-07-08 | L2 | 0.98 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)-2950 EXCEEDANCE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 97 | UG/L | 80.4999 | 2025-07-08 | L2 | 0.44 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)-2950 EXCEEDANCE
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.08 | UG/L | 60.4999 | 2025-10-14 | L2 | 0.98 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 70.13 | UG/L | 80.4999 | 2025-10-14 | L2 | 0.44 |  | 2831 DEERFIELD ST. (PHASE 3 EOL)
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.28 | UG/L | 60.4999 | 2025-10-14 | L1 | 0.98 |  | 5211 HAMMOCK POINTE CT.
3494400 | HAMMOCK POINTE UTILITY ASSOCIATION INC | D | DBP | 2950 | TOTAL THMS | 61.71 | UG/L | 80.4999 | 2025-10-14 | L1 | 0.44 |  | 5211 HAMMOCK POINTE CT.
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0.094 | MG/L | 1.4999 | 2021-10-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3494407 | NARCOOSSEE COMMUNITY PARK | D | INOR | 1040 | NITRATE | 0.061 | MG/L | 10.4999 | 2023-10-18 | AAA | 0.024 |  | POE- DIST
3494407 | NARCOOSSEE COMMUNITY PARK | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-18 | AAA |  |  | POE- DIST
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.085 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1040 | NITRATE | 0.087 | MG/L | 10.4999 | 2025-08-05 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494407 | NARCOOSSEE COMMUNITY PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-05 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494409 | CANE ISLAND POWER PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-07-29 | AAA |  |  | POE
3494409 | CANE ISLAND POWER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-29 | AAA |  |  | POE
3494409 | CANE ISLAND POWER PARK | S | VOC | 2955 | TOT XYLENE | 1.6 | UG/L | 10499.9999 | 2022-06-16 | AAA |  | 0.5499 | 2ND ANNUAL TOT XYLENE CANNOT BE USED TO DEMONSTATE COMPLIANCE - WRONG METHOD USED AND MDL EXCEEDS RDL (ATR)
3494409 | CANE ISLAND POWER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11 | UG/L | 60.4999 | 2022-07-08 | L1 | 1.5 |  | REMOTE RECIRC (TOTAL HAA5 INCORRECTLY REPORTED ON "OTHER" CONTAM. FORMAT, MISSING REG. MRL COLUMN) HLKD 8/18/22 | 3
3494409 | CANE ISLAND POWER PARK | D | DBP | 2950 | TOTAL THMS | 33.17 | UG/L | 80.4999 | 2022-07-08 | L1 | 0.2 |  | REMOTE RECIRC (TOTAL HAA5 INCORRECTLY REPORTED ON "OTHER" CONTAM. FORMAT, MISSING REG. MRL COLUMN) HLKD 8/18/22 | 3
3494409 | CANE ISLAND POWER PARK | S | VOC | 2955 | TOT XYLENE | 3 | UG/L | 10499.9999 | 2022-07-12 | AAA | 0.5 | 0.5499 | MAKE-UP FOR 2022 2ND ANNUAL (ATR)
3494409 | CANE ISLAND POWER PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-08-11 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-11 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-08-11 | AAA | 0.01 | 0.0149 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-08-11 | AAA | 0.01 | 0.0249 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-08-11 | AAA | 0.05 | 0.1499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-08-11 | AAA | 0.5 | 1.4999 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-11 | AAA | 0.18 | 1.4999 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-08-11 | AAA | 0.4 | 0.4499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-08-11 | AAA | 9 | 9.4999 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-08-11 | AAA | 6 | 6.4999 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-08-11 | AAA | 0.6 | 0.6499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-08-11 | AAA | 2 | 2.4999 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 1.3 | UG/L | 6.4999 | 2022-08-11 | AAA | 0.6 | 0.6499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-08-11 | AAA | 0.18 | 0.1499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-08-11 | AAA | 0.35 | 0.2499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-08-11 | AAA | 0.1 | 0.1499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-08-11 | AAA | 0.9 | 0.9499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-08-11 | AAA | 0.2 | 0.2499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-11 | AAA | 0.001 | 0.0449 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-11 | AAA | 0.001 | 0.0249 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-11 | AAA | 0.18 | 0.1499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-11 | AAA | 0.35 | 0.2499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-11 | AAA | 0.1 | 0.1499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-11 | AAA | 0.07 | 0.0449 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-11 | AAA | 0.02 | 0.0249 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-11 | AAA | 0.001 | 0.0149 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-11 | AAA | 0.01 | 0.2499 | SIMAZINE, ATRAZINE, BENZO(A)PYRENE ARE J QUALIFIED AND NOT ACCEPTABLE BASED ON QA REPORT. NOT ENTERED. CC
3494409 | CANE ISLAND POWER PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-11 | AAA | 0.5 | 0.5499
3494409 | CANE ISLAND POWER PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-09-30 | AAA | 0.02
3494409 | CANE ISLAND POWER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-09-30 | AAA | 0.02
3494409 | CANE ISLAND POWER PARK | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2022-09-30 | AAA | 0.2
3494409 | CANE ISLAND POWER PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-09-30 | AAA | 0.002
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0.057 | UG/L | 10499.9999 | 2021-02-24 | AAA | 0.5 | 0.5499 | "I" QUALIFIER (ATR)
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-27 | AAA |  | 0.5499 | 2021 ANNUAL SAMPLE - (ATR)
3494409 | CANE ISLAND POWER PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-09-30 | AAA | 0.002
3494409 | CANE ISLAND POWER PARK | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2022-09-30 | AAA | 0.002
3494409 | CANE ISLAND POWER PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-09-30 | AAA | 0.001
3494409 | CANE ISLAND POWER PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-09-30 | AAA | 0.001
3494409 | CANE ISLAND POWER PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-09-30 | AAA | 0.002
3494409 | CANE ISLAND POWER PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-09-30 | AAA | 0
3494409 | CANE ISLAND POWER PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-09-30 | AAA | 0.0005
3494409 | CANE ISLAND POWER PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-09-30 | AAA | 0.0005
3494409 | CANE ISLAND POWER PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-12-22 | AAA | 0.01 | 0.1499 | RESAMPLED SOCS_CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-12-22 | AAA | 0.02 | 0.6499 | RESAMPLED SOCS_CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-12-22 | AAA | 0.03 | 0.0749 | RESAMPLED SOCS_CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-12-22 | AAA | 0.1 | 0.6499 | RESAMPLED SOCS_CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-12-22 | AAA | 0.01 | 0.2499 | RESAMPLED SOCS_CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-12-22 | AAA | 0.012 | 0.0249 | RESAMPLED SOCS_CC
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-03-06 | AAA |  | 0.6499 | POE
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-04-13 | AAA |  | 0.5499 | POE
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-13 | AAA |  | 0.6499 | POE
3494409 | CANE ISLAND POWER PARK | N | INOR | 1040 | NITRATE | 0.031 | MG/L | 10.4999 | 2023-08-25 | AAA | 0.02 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494409 | CANE ISLAND POWER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-25 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-08-25 | AAA | 0.6 | 0.6499 | POE
3494409 | CANE ISLAND POWER PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-28 | AAA | 0.01 | 0.0149 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-28 | AAA | 0.4 | 0.4499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-28 | AAA | 0.01 | 0.0249 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-28 | AAA | 0.05 | 0.1499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-28 | AAA | 0.5 | 1.4999 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2031 | DALAPON | 0.35 | UG/L | 249.9999 | 2023-09-28 | AAA | 0.022 | 1.4999 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-28 | AAA | 9 | 9.4999 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-28 | AAA | 6 | 6.4999 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-28 | AAA | 0.6 | 0.6499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-28 | AAA | 0.4 | 2.4999 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-28 | AAA | 0.07 | 0.0749 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-28 | AAA | 0.6 | 0.6499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-28 | AAA | 0.019 | 0.1499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-28 | AAA | 0.028 | 0.2499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-28 | AAA | 0.1 | 0.1499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-28 | AAA | 0.4 | 0.9499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-28 | AAA | 0.1 | 0.1499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-28 | AAA | 0.2 | 0.2499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-28 | AAA | 0.01 | 0.0449 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-28 | AAA | 0.01 | 0.0249 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-28 | AAA | 0.022 | 0.1499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-28 | AAA | 0.035 | 0.2499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-28 | AAA | 0.1 | 0.1499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-28 | AAA | 0.02 | 0.0249 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-28 | AAA | 0.017 | 0.0449 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-28 | AAA | 0.02 | 0.0249 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-28 | AAA | 0.01 | 0.0149 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-28 | AAA | 0.01 | 0.2499 | 2031 DETECT
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-12-08 | AAA |  | 0.5499 | POE
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-12-08 | AAA |  | 0.6499 | POE
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-03-08 | AAA |  | 0.5499 | POE
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-03-08 | AAA |  | 0.6499 | POE
3494409 | CANE ISLAND POWER PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-08-29 | AAA |  |  | POE
3494409 | CANE ISLAND POWER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-29 | AAA |  |  | POE
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-05-02 | AAA |  | 0.5499 | POE
3494409 | CANE ISLAND POWER PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-06-13 | AAA |  | 0.2499
3494409 | CANE ISLAND POWER PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-06-13 | AAA | 0.1 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-06-13 | AAA | 0.1 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-06-13 | AAA | 0.00035 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2025-06-13 | AAA | 0.00033 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-06-13 | AAA | 0.00022 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1020 | CHROMIUM | 0.0005 | MG/L | 0.1499 | 2025-06-13 | AAA | 0.00035 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-06-13 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2025-06-13 | AAA | 0.1 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-06-13 | AAA | 0.00022 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-06-13 | AAA | 0.0002 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-06-13 | AAA | 0.00082 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-06-13 | AAA | 0.0009 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1052 | SODIUM | 5.6 | MG/L | 160.4999 | 2025-06-13 | AAA | 0.12 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-06-13 | AAA | 0.00037 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-06-13 | AAA | 0.00029 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-06-13 | AAA | 0.00031 |  | LOCATION CODE SET BY PWS - 03/10/2008-
3494409 | CANE ISLAND POWER PARK | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2025-06-13 | AAA | 0.1 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-06-13 | AAA | 0.29 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-06-13 | AAA | 0.19 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-06-13 | AAA | 0.5 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-06-13 | AAA | 0.5 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-06-13 | AAA | 0.32 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-06-13 | AAA | 0.27 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-06-13 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-06-13 | AAA | 0.39 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-06-13 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-06-13 | AAA | 0.23 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-06-13 | AAA | 0.16 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-06-13 | AAA | 0.28 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-06-13 | AAA | 0.43 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-13 | AAA | 0.34 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-06-13 | AAA | 0.39 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-06-13 | AAA | 0.37 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-06-13 | AAA | 0.3 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-06-13 | AAA | 0.17 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-06-13 | AAA | 0.23 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-06-13 | AAA | 0.24 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-06-13 | AAA | 0.24 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494409 | CANE ISLAND POWER PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-06-13 | AAA | 0.01 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-06-13 | AAA | 0.01 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-06-13 | AAA | 0.05 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-06-13 | AAA | 0.5 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2031 | DALAPON | 0.45 | UG/L | 249.9999 | 2025-06-13 | AAA | 0.022 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-06-13 | AAA | 0.4 | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-06-13 | AAA | 9 | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-06-13 | AAA | 6 | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-06-13 | AAA | 0.6 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-06-13 | AAA | 0.4 | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-06-13 | AAA | 0.07 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-06-13 | AAA | 0.1 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-06-14 | AAA |  | 0.5499 | POE
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-08-29 | AAA | 0.6 | 0.6499 | Q3
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-06-13 | AAA | 0.6 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-06-13 | AAA | 0.019 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-06-13 | AAA | 0.028 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-06-13 | AAA | 0.1 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-06-13 | AAA | 0.4 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-06-13 | AAA | 0.2 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-06-13 | AAA | 0.01 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-06-13 | AAA | 0.01 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-06-13 | AAA | 0.022 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-06-13 | AAA | 0.035 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-06-13 | AAA | 0.1 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-06-13 | AAA | 0.02 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-06-13 | AAA | 0.017 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-06-13 | AAA | 0.02 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-06-13 | AAA | 0.01 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-06-13 | AAA | 0.01 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008-DALAPON DETECT
3494409 | CANE ISLAND POWER PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.45 | UG/L | 60.4999 | 2025-07-29 | L1 |  |  |  | 3
3494409 | CANE ISLAND POWER PARK | D | DBP | 2950 | TOTAL THMS | 25.701 | UG/L | 80.4999 | 2025-07-29 | L1 |  |  |  | 3
3494409 | CANE ISLAND POWER PARK | N | INOR | 1010 | BARIUM | 0.019 | MG/L | 2.4999 | 2025-08-08 | AAA | 0.00037
3494409 | CANE ISLAND POWER PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-09-05 | AAA |  | 0.6499 | POE
3494409 | CANE ISLAND POWER PARK | N | RAD | 4020 | RADIUM-226 | 1.7 | PCI/L | 3.4999 | 2025-12-22 | AAA |  | 1.4999 | 2025 RADS
3494409 | CANE ISLAND POWER PARK | N | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 4.7 | PCI/L | 15.4999 | 2025-12-22 | AAA |  | 3.4999 | 2025 RADS
3494409 | CANE ISLAND POWER PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 4.7 | PCI/L | 15.4999 | 2025-12-22 | AAA |  |  | 2025 RADS
3494409 | CANE ISLAND POWER PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2025-12-22 | AAA |  | 0.667 | 2025 RADS
3494409 | CANE ISLAND POWER PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-12-22 | AAA |  | 1.4999 | 2025 RADS
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.92 | UG/L | 60.4999 | 2021-03-19 | L1 | 0.89 |  | CAR WASH HOSEBIB (HLKD) | 3
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 57.35 | UG/L | 80.4999 | 2021-03-19 | L1 | 0.39 |  | CAR WASH HOSEBIB (HLKD) | 3
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.008 | MG/L | 2.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.2 | MG/L | 4.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 27 | MG/L | 160.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 33 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.2 | MG/L | 2.0499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1028 | IRON | 0.17 | MG/L | 0.3499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0.0065 | MG/L | 0.0549 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 3 | MG/L | 250.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0.06 |  | 0.5499 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.78 | LN(10) |  | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 446 | MG/L | 500.4999 | 2021-12-02 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 (MANGANESE RESULT REVISED FROM -0- TO 0.0065 ON 2/3/22-BB)
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-02 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-02 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-02 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-02 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-02 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-02 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-02 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-02 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-02 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-02 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-02 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-02 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.42 | UG/L | 60.4999 | 2022-03-15 | L1 |  |  | CAR WASH | 3
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 5.13 | UG/L | 80.4999 | 2022-03-15 | L1 |  |  | CAR WASH | 3
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-04-26 | AAA |  | 1.4999 | MAKEUP SAMPLES FOR MISSED MONITORING 2021_AL
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.6 | PCI/L | 15.4999 | 2022-04-26 | AAA |  |  | MAKEUP SAMPLES FOR MISSED MONITORING 2021_AL
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2022-04-26 | AAA |  | 0.667 | MAKEUP SAMPLES FOR MISSED MONITORING 2021_AL
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2022-04-26 | AAA |  | 1.4999 | MAKEUP SAMPLES FOR MISSED MONITORING 2021_AL
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA |  |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-27 | AAA |  |  | POE
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.39 | UG/L | 60.4999 | 2023-03-16 | L1 | 0.98 |  | CAR WASH AREA | 3
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 27.84 | UG/L | 80.4999 | 2023-03-16 | L1 | 0.39 |  | CAR WASH AREA | 3
3490265 | COLONIAL MOBILE HOME PARK | D | INOR | 1040 | NITRATE | 0.055 | MG/L | 10.4999 | 2023-10-17 | AAA | 0.024 |  | DIST
3490265 | COLONIAL MOBILE HOME PARK | D | INOR | 1041 | NITRITE | 0.065 | MG/L | 1.4999 | 2023-10-17 | AAA | 0.0034 |  | DIST
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.97 | UG/L | 60.4999 | 2024-03-11 | L1 | 0.98 |  | CAR WASH HOSEBIB | 3
3490265 | COLONIAL MOBILE HOME PARK | D | DBP | 2950 | TOTAL THMS | 23.36 | UG/L | 80.4999 | 2024-03-11 | L1 | 0.39 |  | CAR WASH HOSEBIB | 3
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2024-08-08 | AAA | 0.3 | 1.4999 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.0643 | MG/L | 2.4999 | 2024-08-08 | AAA | 4e-05 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.476 | MG/L | 10.4999 | 2024-08-08 | AAA | 0.0196 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-08 | AAA | 0.0275 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0.0011 | MG/L | 0.0104 | 2024-08-08 | AAA | 8e-05 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-08-08 | AAA | 1e-05 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0.0004 | MG/L | 0.1499 | 2024-08-08 | AAA | 0.00015 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-08-08 | AAA | 0.0021 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.101 | MG/L | 4.0499 | 2024-08-08 | AAA | 0.0079 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0.0005 | MG/L | 0.0154 | 2024-08-08 | AAA | 3e-05 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-08-08 | AAA | 0.00012 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0.0013 | MG/L | 0.1499 | 2024-08-08 | AAA | 0.00017 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-08-08 | AAA | 0.00041 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 5.42 | MG/L | 160.4999 | 2024-08-08 | AAA | 0.16 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-08-08 | AAA | 4e-05 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-08-08 | AAA | 2e-05 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-08-08 | AAA | 0 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-08-08 | AAA | 0.0041 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 10.6 | MG/L | 250.4999 | 2024-08-08 | AAA | 0.153 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0.017 | MG/L | 1.4999 | 2024-08-08 | AAA | 0.002 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.101 | MG/L | 2.0499 | 2024-08-08 | AAA | 0.0079 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1028 | IRON | 0.007 | MG/L | 0.3499 | 2024-08-08 | AAA | 0.0015 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0.0006 | MG/L | 0.0549 | 2024-08-08 | AAA | 0.0001 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-08-08 | AAA | 0.0005 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 62.1 | MG/L | 250.4999 | 2024-08-08 | AAA | 0.182 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0.0055 | MG/L | 5.4999 | 2024-08-08 | AAA | 0.0013 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-08-08 | AAA | 5 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-08-08 | AAA | 1 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 222 | MG/L | 500.4999 | 2024-08-08 | AAA | 20 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0.011 |  | 0.5499 | 2024-08-08 | AAA | 0.01 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 2.1 | PCI/L | 15.4999 | 2024-08-08 | AAA | 1.1 |  | POE
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0.364 | PCI/L | 20.4999 | 2024-08-08 | AAA | 0.0014 | 0.667 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-08-08 | AAA | 0.9 | 1.4999 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-08-08 | AAA | 0.0019 | 0.0149 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA | 0.0016 | 0.0249 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-08-08 | AAA | 0.0039 | 0.1499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-08-08 | AAA | 0.23 | 1.4999 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-08-08 | AAA | 0.289 | 1.4999 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-08-08 | AAA | 0.328 | 0.4499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-08-08 | AAA | 1.41 | 9.4999 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-08-08 | AAA | 3.71 | 6.4999 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-08-08 | AAA | 0.0125 | 0.6499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-08-08 | AAA | 0.258 | 2.4999 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-08-08 | AAA | 0.0111 | 0.0749 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-08-08 | AAA | 0.0248 | 0.6499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-08-08 | AAA | 0.0727 | 0.1499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-08-08 | AAA | 0.167 | 0.2499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-08-08 | AAA | 0.0051 | 0.1499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-08-08 | AAA | 0.438 | 0.9499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-08-08 | AAA | 0.0127 | 0.1499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-08-08 | AAA | 0.0156 | 0.2499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-08-08 | AAA | 0.0016 | 0.0449 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA | 0.0014 | 0.0249 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-08-08 | AAA | 0.0761 | 0.1499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-08-08 | AAA | 0.0742 | 0.2499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-08-08 | AAA | 0.0016 | 0.1499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA | 0.0041 | 0.0249 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-08-08 | AAA | 0.0154 | 0.0449 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-08-08 | AAA | 0.0468 | 0.1499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-08-08 | AAA | 0.0045 | 0.0249 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-08-08 | AAA | 0.0051 | 0.0149 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-08-08 | AAA | 0.02 | 0.2499 | POE
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-10-22 | AAA |  | 0.5499 | 2024 VOC RESULTS
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-04-08 | AAA | 0.1 |  | POE - NN
3490265 | COLONIAL MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-08 | AAA | 0.1 |  | POE - NN
3494423 | HOLOPAW MINI MART | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494423 | HOLOPAW MINI MART | N | INOR | 1041 | NITRITE | 0.09 | MG/L | 1.4999 | 2021-12-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494423 | HOLOPAW MINI MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-26 | AAA |  |  | POE
3494423 | HOLOPAW MINI MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-26 | AAA |  |  | POE
3494423 | HOLOPAW MINI MART | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-10-16 | AAA |  |  | DIST - LOCATION POE
3494423 | HOLOPAW MINI MART | D | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2023-10-16 | AAA | 0.0034 |  | DIST - LOCATION POE
3494423 | HOLOPAW MINI MART | N | INOR | 1040 | NITRATE | 0.081 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494423 | HOLOPAW MINI MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494423 | HOLOPAW MINI MART | N | INOR | 1040 | NITRATE | 0.083 | MG/L | 10.4999 | 2025-02-03 | AAA | 0.024 |  | POE
3494423 | HOLOPAW MINI MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-03 | AAA |  |  | POE
3494424 | THE NATURE CONSERVANCY | N | INOR | 1040 | NITRATE | 0.4 | MG/L | 10.4999 | 2022-02-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494424 | THE NATURE CONSERVANCY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494424 | THE NATURE CONSERVANCY | N | INOR | 1040 | NITRATE | 0.035 | MG/L | 10.4999 | 2024-01-05 | AAA | 0.024 |  | POE
3494424 | THE NATURE CONSERVANCY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-05 | AAA |  |  | POE
3494424 | THE NATURE CONSERVANCY | N | INOR | 1040 | NITRATE | 1.7 | MG/L | 10.4999 | 2025-10-09 | AAA | 0.1 |  | 2025 N/N
3494424 | THE NATURE CONSERVANCY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-09 | AAA | 0.1 |  | 2025 N/N
3494424 | THE NATURE CONSERVANCY | E | INOR | 1040 | NITRATE | 1.7 | MG/L | 10.4999 | 2025-10-09 | AAA | 0.1 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE-NC
3494424 | THE NATURE CONSERVANCY | E | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-09 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE-NC
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1040 | NITRATE | 0.094 | MG/L | 10.4999 | 2021-12-15 | AAA | 0.0075
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-15 | AAA | 0.048
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA |  |  | POE
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-27 | AAA |  |  | POE
3490190 | SMITTY'S BAR-B-Q, LLC | D | INOR | 1040 | NITRATE | 0.091 | MG/L | 10.4999 | 2023-11-15 | AAA | 0.024 |  | DIST --POE
3490190 | SMITTY'S BAR-B-Q, LLC | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-15 | AAA |  |  | DIST --POE
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1040 | NITRATE | 0.085 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2025-01-21 | AAA | 0.024 |  | POE
3490190 | SMITTY'S BAR-B-Q, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA |  |  | POE
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-03-31 | AAA |  |  | POE
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-31 | AAA |  |  | POE
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-17 | AAA | 0.024 |  | NITRATE J QUALIFIED, ACCEPTED. NITRITE J QUALIFIED NOT ACCEPTED. RESAMPLE SCHEDULED - FW 2/23
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-20 | AAA |  |  | POE
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-03-21 | AAA | 0.02 |  | POE CACR - NITRITE J QUALIFIER
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-10 | AAA |  |  | POE
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1040 | NITRATE | 0.023 | MG/L | 10.4999 | 2025-03-27 | AAA | 0.02 |  | POE
3490207 | CANOE CREEK RV RESORT, LLC | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-27 | AAA |  |  | POE
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-06 | AAA | 0.03 |  | SUBMITTED 9/20/2022 - CJL
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-06 | AAA | 0.018 |  | SUBMITTED 9/20/2022 - CJL
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1030 | LEAD | 0.001 | MG/L | 0.0154 | 2021-01-06 | AAA | 0.0001 |  | SUBMITTED 9/20/2022 - CJL
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1040 | NITRATE | 0.46 | MG/L | 10.4999 | 2022-01-11 | AAA | 0.03 |  | INCOMPLETE-RSLTS ENT'D WITH SMPL TYPE "S" (HLKD 2/11/22)
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-11 | AAA | 0.018 |  | INCOMPLETE-RSLTS ENT'D WITH SMPL TYPE "S" (HLKD 2/11/22)
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1030 | LEAD | 0.0002 | MG/L | 0.0154 | 2022-01-11 | AAA | 0.00013 |  | INCOMPLETE-RSLTS ENT'D WITH SMPL TYPE "S" (HLKD 2/11/22)
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2023-01-17 | AAA | 0.024 |  | SIGNATURE RCVD 2/23 FW INCOMPLETE-PG1 NOT SIGNED-RSLTS ENT'D WITH SMPL TYPE "S" (HLKD 2/24/23) LEAD NOT ENTERED-DISCREPANCY BETWEEN LAB MDL IN LAB MDL COLUMN & THE LAB MDL USED IN THE ANALYSIS RESULT.
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-17 | AAA | 0.0034 |  | SIGNATURE RCVD 2/23 FW INCOMPLETE-PG1 NOT SIGNED-RSLTS ENT'D WITH SMPL TYPE "S" (HLKD 2/24/23) LEAD NOT ENTERED-DISCREPANCY BETWEEN LAB MDL IN LAB MDL COLUMN & THE LAB MDL USED IN THE ANALYSIS RESULT.
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-02-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SOURCE
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-02-12 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SOURCE
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-26 | AAA | 0.024 |  | 2025
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-26 | AAA | 0.0034 |  | 2025
3490208 | FRIENDLY VILLAGE INN | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-02-26 | AAA | 0.005 |  | 2025
3494433 | CENTRAL FLORIDA YOUTH AND FAMILY CAMP | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-03 | AAA |  |  | C.F.Y.F.C
3494433 | CENTRAL FLORIDA YOUTH AND FAMILY CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-03 | AAA |  |  | C.F.Y.F.C
3494433 | CENTRAL FLORIDA YOUTH AND FAMILY CAMP | S | INOR | 1038 | TOTAL NITRATE+NITRITE | 0.46 | MG/L | 10.4999 | 2022-09-06 | AAA | 0.02 |  | (RECEIVED 2-10-23) 1038 TOTAL N-N WITH J QUALIFIER (UNACCEPTABLE FOR COMPLIANCE PURPOSES) ENT'D W/SMP TYPE "S" FOR INFO.PURPOSES ONLY. NEED SEPARATE 2022 1040 NITRATE & 1041 NITRITE REPORTED W/IN HOLD
3494433 | CENTRAL FLORIDA YOUTH AND FAMILY CAMP | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-03-08 | AAA | 0.2 |  | 2022 MAKE-UP SAMPLING RCVD 3-16-23 FW
3494433 | CENTRAL FLORIDA YOUTH AND FAMILY CAMP | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-08 | AAA | 0.2 |  | 2022 MAKE-UP SAMPLING RCVD 3-16-23 FW
3494424 | THE NATURE CONSERVANCY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-04 | AAA |  |  | POE
3494424 | THE NATURE CONSERVANCY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-04 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1010 | BARIUM | 0.0055 | MG/L | 2.4999 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1052 | SODIUM | 18.4 | MG/L | 160.4999 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-17 | AAA
3490293 | MILL CREEK RV RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1022 | COPPER | 0.0021 | MG/L | 1.4999 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1028 | IRON | 0.295 | MG/L | 0.3499 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1040 | NITRATE | 3.7 | MG/L | 10.4999 | 2021-07-13 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-13 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-07-13 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-07-05 | AAA | 0.0051 | 0.0249 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-07-05 | AAA | 0.053 | 0.0149 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.95 | UG/L | 60.4999 | 2022-07-05 | L1 | 0.98 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2950 | TOTAL THMS | 26.61 | UG/L | 80.4999 | 2022-07-05 | L1 | 0.44 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2450 | MONOCHLORACETIC ACID | 1.72 | UG/L |  | 2022-07-05 | L1 | 0.98 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2451 | DICHLOROACETIC ACID | 3.97 | UG/L |  | 2022-07-05 | L1 | 0.42 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2452 | TRICHLOROACETIC ACID | 2.07 | UG/L |  | 2022-07-05 | L1 | 0.94 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.95 | UG/L | 60.4999 | 2022-07-05 | L1 | 0.98 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2950 | TOTAL THMS | 26.61 | UG/L | 80.4999 | 2022-07-05 | L1 | 0.44 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2450 | MONOCHLORACETIC ACID | 1.72 | UG/L |  | 2022-07-05 | L1 | 0.98 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2451 | DICHLOROACETIC ACID | 3.97 | UG/L |  | 2022-07-05 | L1 | 0.42 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2452 | TRICHLOROACETIC ACID | 2.07 | UG/L |  | 2022-07-05 | L1 | 0.94 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2453 | MONOBROMACETIC ACID | 2.08 | UG/L |  | 2022-07-05 | L1 | 0.41 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2454 | DIBROMOACETIC ACID | 1.11 | UG/L |  | 2022-07-05 | L1 | 0.74 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2941 | CHLOROFORM | 17.96 | UG/L | 100 | 2022-07-05 | L1 | 0.32 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2942 | BROMOFORM | 1.41 | UG/L | 100 | 2022-07-05 | L1 | 0.44 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2943 | BROMODICHLOROMETHANE | 3.64 | UG/L | 100 | 2022-07-05 | L1 | 0.42 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | DBP | 2944 | DIBROMOCHLOROMETHANE | 3.6 | UG/L | 100 | 2022-07-05 | L1 | 0.37 |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.95 | UG/L | 60.4999 | 2022-07-05 | L1 |  |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | D | DBP | 2950 | TOTAL THMS | 26.61 | UG/L | 80.4999 | 2022-07-05 | L1 |  |  | L1 NE SIDE OF BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-07-05 | AAA | 0.0069 | 0.0149 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-07-05 | AAA | 0.0071 | 0.0249 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-07-05 | AAA | 0.0068 | 0.1499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-07-05 | AAA | 0.12 | 1.4999 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-07-05 | AAA | 0.9 | 1.4999 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-07-05 | AAA | 0.37 | 0.4499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-07-05 | AAA | 6 | 9.4999 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-07-05 | AAA | 5.9 | 6.4999 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-07-05 | AAA | 0.5 | 0.6499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-07-05 | AAA | 1.8 | 2.4999 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-07-05 | AAA | 0.06 | 0.0749 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-07-05 | AAA | 0.5 | 0.6499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-07-05 | AAA | 0.09 | 0.1499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-07-05 | AAA | 0.18 | 0.2499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-07-05 | AAA | 0.019 | 0.1499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-07-05 | AAA | 0.51 | 0.9499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-07-05 | AAA | 0.09 | 0.1499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-07-05 | AAA | 0.15 | 0.2499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-07-05 | AAA | 0.006 | 0.0449 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-07-05 | AAA | 0.0052 | 0.0249 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-07-05 | AAA | 0.095 | 0.1499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-07-05 | AAA | 0.09 | 0.2499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-07-05 | AAA | 0.0063 | 0.1499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-07-05 | AAA | 0.015 | 0.0249 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-07-05 | AAA | 0.038 | 0.0449 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-07-05 | AAA | 0.093 | 0.1499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-07-05 | AAA | 0.053 | 0.2499 | 27 OF 29 SOC (THE FAKE RESULTS FOR 2931 DBCP & EDB NEED TO BE REMOVED OR AUTHENTIC RESULTS PUT IN THEIR PLACE) HLKD 8/5/22
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1040 | NITRATE | 3 | MG/L | 10.4999 | 2022-07-05 | AAA | 0.092 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-07-05 | AAA | 0.081 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-07-05 | AAA | 0.00025 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1010 | BARIUM | 0.034 | MG/L | 2.4999 | 2022-07-05 | AAA | 0.003 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-07-05 | AAA | 0.001 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-07-05 | AAA | 0.005 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-07-05 | AAA | 0.004 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2022-07-05 | AAA | 0.4 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-07-05 | AAA | 0.003 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1035 | MERCURY | 0.0001 | MG/L | 0.0024 | 2022-07-05 | AAA | 1e-05 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-07-05 | AAA | 0.008 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-07-05 | AAA | 0.04 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1052 | SODIUM | 47 | MG/L | 160.4999 | 2022-07-05 | AAA | 0.8 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-07-05 | AAA | 0.001 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-07-05 | AAA | 0.002 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-07-05 | AAA | 0.00025 |  | E82574/ARS, ANT,THAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-07-05 | AAA | 0.44 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-07-05 | AAA | 0.27 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-07-05 | AAA | 0.44 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-07-05 | AAA | 0.44 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-07-05 | AAA | 0.22 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-07-05 | AAA | 0.39 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-07-05 | AAA | 0.33 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-07-05 | AAA | 0.29 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-07-05 | AAA | 0.21 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-07-05 | AAA | 0.24 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-07-05 | AAA | 0.29 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-07-05 | AAA | 0.25 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-07-05 | AAA | 0.26 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-05 | AAA | 0.14 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-07-05 | AAA | 0.27 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-05 | AAA | 0.42 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-07-05 | AAA | 0.36 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-07-05 | AAA | 0.26 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-07-05 | AAA | 0.33 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-07-05 | AAA | 0.31 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-07-05 | AAA | 0.25 | 0.5499 | VOC
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-11-14 | AAA | 0.44 | 0.5499 | BEGIN - Q4 XYLENES - ALP
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-01-08 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-04-10 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-07-10 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1040 | NITRATE | 4.2 | MG/L | 10.4999 | 2024-07-10 | AAA | 0.092 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-10 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1040 | NITRATE | 3.7 | MG/L | 10.4999 | 2025-04-21 | AAA | 0.9 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1010 | BARIUM | 0.033 | MG/L | 2.4999 | 2025-04-21 | AAA | 0.003 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1052 | SODIUM | 40 | MG/L | 160.4999 | 2025-04-21 | AAA | 0.8 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1040 | NITRATE | 3.9 | MG/L | 10.4999 | 2023-07-19 | AAA | 0.092 |  | 9120 TEACHER LANE - PARTIAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-07-19 | AAA | 0.081 |  | 9120 TEACHER LANE - PARTIAL
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1017 | CHLORIDE | 58 | MG/L | 250.4999 | 2025-04-21 | AAA | 2 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1028 | IRON | 0.33 | MG/L | 0.3499 | 2025-04-21 | AAA | 0.007 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1055 | SULFATE | 39 | MG/L | 250.4999 | 2025-04-21 | AAA | 2 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1095 | ZINC | 0.05 | MG/L | 5.4999 | 2025-04-21 | AAA | 0.05 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 0 | LN(10) |  | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 270 | MG/L | 500.4999 | 2025-04-21 | AAA | 10 |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2025-04-21 | AAA |  |  | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | RAD | 4006 | COMBINED URANIUM | 0.83 | PCI/L | 20.4999 | 2025-04-21 | AAA | 0.2 | 0.667 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-04-21 | AAA |  | 0.5499 | POE
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.84 | UG/L | 60.4999 | 2025-07-07 | L1 | 0.98 |  | L-1 NE SIDE BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | D | DBP | 2950 | TOTAL THMS | 32.99 | UG/L | 80.4999 | 2025-07-07 | L1 | 0.44 |  | L-1 NE SIDE BLDG | 3
3494435 | COMMUNITY OF FAITH UNITED METHODIST CH | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-17 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.88 | LN(10) |  | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 250 | MG/L | 500.4999 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-05-17 | AAA |  | 0.1499
3490293 | MILL CREEK RV RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-05-17 | AAA |  | 0.5499
3490293 | MILL CREEK RV RESORT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-05-17 | AAA |  | 0.0149
3490293 | MILL CREEK RV RESORT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-05-17 | AAA |  | 0.0249
3490293 | MILL CREEK RV RESORT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-05-17 | AAA |  | 1.4999
3490293 | MILL CREEK RV RESORT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-05-17 | AAA |  | 1.4999
3490293 | MILL CREEK RV RESORT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-05-17 | AAA |  | 0.4499
3490293 | MILL CREEK RV RESORT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-05-17 | AAA |  | 9.4999
3490293 | MILL CREEK RV RESORT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-05-17 | AAA |  | 6.4999
3490293 | MILL CREEK RV RESORT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-05-17 | AAA |  | 0.6499
3490293 | MILL CREEK RV RESORT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-05-17 | AAA |  | 2.4999
3490293 | MILL CREEK RV RESORT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-05-17 | AAA |  | 0.0749
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 10.7 | UG/L | 6.4999 | 2021-05-17 | AAA |  | 0.6499
3490293 | MILL CREEK RV RESORT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-05-17 | AAA |  | 0.1499
3490293 | MILL CREEK RV RESORT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-05-17 | AAA |  | 0.2499
3490293 | MILL CREEK RV RESORT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-05-17 | AAA |  | 0.1499
3490293 | MILL CREEK RV RESORT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-05-17 | AAA |  | 0.9499
3490293 | MILL CREEK RV RESORT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-05-17 | AAA |  | 0.1499
3490293 | MILL CREEK RV RESORT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-05-17 | AAA |  | 0.2499
3490293 | MILL CREEK RV RESORT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-05-17 | AAA |  | 0.0055
3490293 | MILL CREEK RV RESORT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-05-17 | AAA |  | 0.0449
3490293 | MILL CREEK RV RESORT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-05-17 | AAA |  | 0.0249
3490293 | MILL CREEK RV RESORT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-05-17 | AAA |  | 0.1499
3490293 | MILL CREEK RV RESORT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-05-17 | AAA |  | 0.2499
3490293 | MILL CREEK RV RESORT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-05-17 | AAA |  | 0.1499
3490293 | MILL CREEK RV RESORT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-05-17 | AAA |  | 0.0249
3490293 | MILL CREEK RV RESORT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-05-17 | AAA |  | 0.0449
3490293 | MILL CREEK RV RESORT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-05-17 | AAA |  | 0.1499
3490293 | MILL CREEK RV RESORT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-05-17 | AAA |  | 0.0249
3490293 | MILL CREEK RV RESORT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-05-17 | AAA |  | 0.0149
3490293 | MILL CREEK RV RESORT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-05-17 | AAA |  | 0.2499
3490293 | MILL CREEK RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.3 | UG/L | 60.4999 | 2021-07-23 | L1 | 1 |  | LOT 505 | 3
3490293 | MILL CREEK RV RESORT | D | DBP | 2950 | TOTAL THMS | 11.7 | UG/L | 80.4999 | 2021-07-23 | L1 | 0.5 |  | LOT 505 | 3
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-09-03 | AAA |  | 0.6499 | POE
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-09-03 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-09-03 | AAA |  | 0.6499 | POE
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-23 | AAA |  | 0.6499
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-01-26 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490293 | MILL CREEK RV RESORT | N | SEC | 1017 | CHLORIDE | 17 | MG/L | 250.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490293 | MILL CREEK RV RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490293 | MILL CREEK RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-26 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-04-19 | AAA |  | 0.6499
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0.52 | UG/L | 6.4999 | 2023-12-14 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490293 | MILL CREEK RV RESORT | N | INOR | 1040 | NITRATE | 0.064 | MG/L | 10.4999 | 2023-12-14 | AAA | 0.024 |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-12-14 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1020 | CHROMIUM | 0.0004 | MG/L | 0.1499 | 2024-05-20 | AAA | 0.0004 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2021-05-17 | AAA |  |  | CHLORIDE: J QUAL., QA = MS BIAS LOW AND LCS W/I LIMIT, SYSTEM NEEDS TO RETEST FOR CHLORIDE - KAOB (2/11/2022)
3490293 | MILL CREEK RV RESORT | N | SEC | 1017 | CHLORIDE | 18.1 | MG/L | 250.4999 | 2022-02-21 | AAA | 0.4
3490293 | MILL CREEK RV RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2024-05-20 | AAA | 0.00033 |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1025 | FLUORIDE | 0.13 | MG/L | 4.0499 | 2024-05-20 | AAA | 0.025 |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1045 | SELENIUM | 0.0006 | MG/L | 0.0549 | 2024-05-20 | AAA | 0.0004 |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1052 | SODIUM | 20 | MG/L | 160.4999 | 2024-05-20 | AAA | 0.12 |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1017 | CHLORIDE | 32 | MG/L | 250.4999 | 2024-05-20 | AAA | 0.4 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1022 | COPPER | 0.002 | MG/L | 1.4999 | 2024-05-20 | AAA | 0.00058 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1025 | FLUORIDE | 0.13 | MG/L | 2.0499 | 2024-05-20 | AAA | 0.025 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1032 | MANGANESE | 0.0012 | MG/L | 0.0549 | 2024-05-20 | AAA | 0.0009 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1055 | SULFATE | 3.1 | MG/L | 250.4999 | 2024-05-20 | AAA | 2 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1095 | ZINC | 0.031 | MG/L | 5.4999 | 2024-05-20 | AAA | 0.0012 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2024-05-20 | AAA | 5 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 160 | MG/L | 500.4999 | 2024-05-20 | AAA | 5 |  | POE
3490293 | MILL CREEK RV RESORT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-05-20 | AAA |  |  | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-05-20 | AAA |  | 0.5499 | POE
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-05-20 | AAA |  | 0.6499 | POE
3490293 | MILL CREEK RV RESORT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.2 | UG/L | 60.4999 | 2024-07-31 | L1 | 0.3 |  | LOT 505 | 3
3490293 | MILL CREEK RV RESORT | D | DBP | 2950 | TOTAL THMS | 20.65 | UG/L | 80.4999 | 2024-07-31 | L1 | 0.5 |  | LOT 505 | 3
3490293 | MILL CREEK RV RESORT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-04-21 | AAA |  | 0.6499 | POE
3490293 | MILL CREEK RV RESORT | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-10-14 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE-MC
3490293 | MILL CREEK RV RESORT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-14 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE-MC
3490314 | CYPRESS COVE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.8 | UG/L | 60.4999 | 2021-07-13 | L1 | 1 |  | WWTP TAP | 3
3490314 | CYPRESS COVE | D | DBP | 2950 | TOTAL THMS | 25.9 | UG/L | 80.4999 | 2021-07-13 | L1 | 0.5 |  | WWTP TAP | 3
3490314 | CYPRESS COVE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1010 | BARIUM | 0.0115 | MG/L | 2.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1052 | SODIUM | 5.82 | MG/L | 160.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1017 | CHLORIDE | 9.38 | MG/L | 250.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1055 | SULFATE | 6.98 | MG/L | 250.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1095 | ZINC | 0.0046 | MG/L | 5.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.2 | LN(10) |  | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 82 | MG/L | 500.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1017 | CHLORIDE | 9.38 | MG/L | 250.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1055 | SULFATE | 6.98 | MG/L | 250.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1095 | ZINC | 0.0046 | MG/L | 5.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.2 | LN(10) |  | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 82 | MG/L | 500.4999 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-11-17 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494427 | HARMONY CDD | N | INOR | 1040 | NITRATE | 0.32 | MG/L | 10.4999 | 2021-01-27 | AAA |  |  | POE
3494427 | HARMONY CDD | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | AAA |  |  | POE
3494427 | HARMONY CDD | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-24 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.0149 | POE
3494427 | HARMONY CDD | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA |  | 1.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 1.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-02-25 | AAA |  | 0.4499 | POE
3494427 | HARMONY CDD | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-02-25 | AAA |  | 9.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-02-25 | AAA |  | 6.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-02-25 | AAA |  | 0.6499 | POE
3494427 | HARMONY CDD | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-02-25 | AAA |  | 2.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-02-25 | AAA |  | 0.0749 | POE
3494427 | HARMONY CDD | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-02-25 | AAA |  | 0.6499 | POE
3494427 | HARMONY CDD | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-02-25 | AAA |  | 0.9499 | POE
3494427 | HARMONY CDD | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-02-25 | AAA |  | 0.0449 | POE
3494427 | HARMONY CDD | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-02-25 | AAA |  | 0.0449 | POE
3494427 | HARMONY CDD | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-02-25 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-02-25 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-02-25 | AAA |  | 0.0149 | POE
3494427 | HARMONY CDD | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-02-25 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2021-02-25 | AAA |  | 0.0055 | POE
3494427 | HARMONY CDD | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.0072 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1017 | CHLORIDE | 107 | MG/L | 250.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.00093 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1025 | FLUORIDE | 0.47 | MG/L | 2.0499 | 2021-05-27 | AAA | 0.029 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1028 | IRON | 0.021 | MG/L | 0.3499 | 2021-05-27 | AAA | 0.016 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.0027 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0033 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1055 | SULFATE | 152 | MG/L | 250.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-05-27 | AAA | 0.0076 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2021-05-27 | AAA | 1 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.9 | LN(10) |  | 2021-05-27 | AAA | 0.1 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 515 | MG/L | 500.4999 | 2021-05-27 | AAA | 5 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-05-27 | AAA | 0.099 |  | TDS 515 MG/L (TDS MCL = 500 MG/L) HLKD
3494427 | HARMONY CDD | N | INOR | 1040 | NITRATE | 0.27 | MG/L | 10.4999 | 2021-05-27 | AAA | 0.025 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1041 | NITRITE | 0.03 | MG/L | 1.4999 | 2021-05-27 | AAA | 0.025 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-27 | AAA | 0.0005 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2021-05-27 | AAA | 0.0062 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-27 | AAA | 0.00067 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.0026 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-27 | AAA | 0.005 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1025 | FLUORIDE | 0.47 | MG/L | 4.0499 | 2021-05-27 | AAA | 0.029 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-05-27 | AAA | 0.00022 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3490314 | CYPRESS COVE | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-17 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-11-17 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-11-17 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-11-17 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-11-17 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-11-17 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-11-17 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-11-17 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-11-17 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-11-17 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-11-17 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-11-17 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-11-17 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-11-17 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-11-17 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-11-17 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-11-17 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-11-17 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-11-17 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-11-17 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-11-17 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-11-17 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-11-17 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-11-17 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-11-17 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-11-17 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-11-17 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-11-17 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-11-17 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3490314 | CYPRESS COVE | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1010 | BARIUM | 0.0095 | MG/L | 2.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1025 | FLUORIDE | 0.1 | MG/L | 4.0499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1052 | SODIUM | 4 | MG/L | 160.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1017 | CHLORIDE | 6 | MG/L | 250.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1025 | FLUORIDE | 0.1 | MG/L | 2.0499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1055 | SULFATE | 8 | MG/L | 250.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 98 | MG/L | 500.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1905 | COLOR | 11 | COLOR UNITS | 15.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.22 | LN(10) |  | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.2 | PCI/L | 15.4999 | 2021-12-28 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2021-12-28 | AAA |  | 0.667 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2021-12-28 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-12-28 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-28 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-12-28 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-12-28 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-12-28 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-12-28 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-12-28 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-12-28 | AAA |  | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-12-28 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-12-28 | AAA |  | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-12-28 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-12-28 | AAA |  | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-12-28 | AAA |  | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-12-28 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-12-28 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-12-28 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-12-28 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-12-28 | AAA |  | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-12-28 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-12-28 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-12-28 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-12-28 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-12-28 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-12-28 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-12-28 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-12-28 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-12-28 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-12-28 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-12-28 | AAA |  | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-12-28 | AAA |  | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-12-28 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008 SUBCONTRACT E84589, E82535, E82001, E82574, E84025
3490314 | CYPRESS COVE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-18 | AAA |  |  | POE
3490314 | CYPRESS COVE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-18 | AAA |  |  | POE
3490314 | CYPRESS COVE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-10-17 | AAA |  |  | POE
3490314 | CYPRESS COVE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-17 | AAA |  |  | POE
3490314 | CYPRESS COVE | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.53 | UG/L | 60.4999 | 2024-07-15 | L1 | 0.98 |  | WWTP HOSE BIB | 3
3490314 | CYPRESS COVE | D | DBP | 2950 | TOTAL THMS | 20.57 | UG/L | 80.4999 | 2024-07-15 | L1 | 0.39 |  | WWTP HOSE BIB | 3
3490314 | CYPRESS COVE | N | SEC | 2905 | FOAMING AGENTS | 0.077 |  | 0.5499 | 2024-10-16 | AAA | 0.04 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2024-10-16 | AAA | 0.003 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-16 | AAA | 0.024 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-16 | AAA | 0.0034 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-10-16 | AAA | 0.00025 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-10-16 | AAA | 0.00025 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-10-16 | AAA | 0.005 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-10-16 | AAA | 0.004 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2024-10-16 | AAA | 0.0099 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-10-16 | AAA | 0.0005 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-10-16 | AAA | 3e-05 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-10-16 | AAA | 0.008 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-10-16 | AAA | 0.0012 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1052 | SODIUM | 6 | MG/L | 160.4999 | 2024-10-16 | AAA | 0.8 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-10-16 | AAA | 0.001 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-10-16 | AAA | 0.002 |  | POE
3490314 | CYPRESS COVE | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-10-16 | AAA | 0.00025 |  | POE
3490314 | CYPRESS COVE | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-10-16 | AAA | 0.024 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1017 | CHLORIDE | 7.7 | MG/L | 250.4999 | 2024-10-16 | AAA | 0.039 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1022 | COPPER | 0.022 | MG/L | 1.4999 | 2024-10-16 | AAA | 0.005 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2024-10-16 | AAA | 0.0099 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-10-16 | AAA | 0.038 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-10-16 | AAA | 0.005 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1050 | SILVER | 0.0026 | MG/L | 0.1499 | 2024-10-16 | AAA | 0.0005 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1055 | SULFATE | 8.7 | MG/L | 250.4999 | 2024-10-16 | AAA | 0.034 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-10-16 | AAA | 0.05 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-10-16 | AAA | 5 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-10-16 | AAA | 1 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 6.48 | LN(10) |  | 2024-10-16 | AAA |  |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 120 | MG/L | 500.4999 | 2024-10-16 | AAA | 10 |  | POE - 2905 J QUALIFIER
3490314 | CYPRESS COVE | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-10-16 | AAA | 0.13333 | 0.667 | POE
3490314 | CYPRESS COVE | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-10-16 | AAA | 0.5 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-10-16 | AAA | 0.24 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-10-16 | AAA | 0.48 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-10-16 | AAA | 0.49 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-10-16 | AAA | 0.44 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-10-16 | AAA | 0.4 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-10-16 | AAA | 0.28 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-10-16 | AAA | 0.4 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-10-16 | AAA | 0.41 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-10-16 | AAA | 0.44 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-10-16 | AAA | 0.32 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-10-16 | AAA | 0.36 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-10-16 | AAA | 0.33 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-16 | AAA | 0.25 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-10-16 | AAA | 0.44 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-10-16 | AAA | 0.49 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-10-16 | AAA | 0.37 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-10-16 | AAA | 0.16 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-10-16 | AAA | 0.2 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-10-16 | AAA | 0.33 | 0.5499 | POE
3490314 | CYPRESS COVE | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-10-16 | AAA | 0.26 | 0.5499 | POE
3490314 | CYPRESS COVE | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2024-10-16 | AAA | 1.1 |  | POE
3490314 | CYPRESS COVE | N | RAD | 4020 | RADIUM-226 | 1 | PCI/L | 3.4999 | 2024-10-16 | AAA | 0.4 | 1.4999 | POE
3490314 | CYPRESS COVE | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-10-16 | AAA | 0.7 | 1.4999 | POE
3494427 | HARMONY CDD | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-27 | AAA | 9e-05 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-27 | AAA | 0.002 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-27 | AAA | 0.00083 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1052 | SODIUM | 83.8 | MG/L | 160.4999 | 2021-05-27 | AAA | 0.59 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-27 | AAA | 0.00021 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-27 | AAA | 0.00058 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-27 | AAA | 0.0005 |  | ASBESTOS POE/D ENT'D SEP WITH SMP TYPE "S"
3494427 | HARMONY CDD | S | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2021-05-28 | AAA | 0.2 |  | POE/D ASBESTOS (ENT'D W/SMP TYPE "S" SINCE POE/D)
3494427 | HARMONY CDD | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-06-28 | AAA |  |  | HARMONY
3494427 | HARMONY CDD | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-06-28 | AAA |  | 1.4999 | HARMONY
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.8 | UG/L | 60.4999 | 2021-07-23 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. (HLKD) TTHMS 144 UG/L, EXCEEDS THE MCL OF 80 UG/L, TRIGGERS QTRLY TESTING | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 144 | UG/L | 80.4999 | 2021-07-23 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. (HLKD) TTHMS 144 UG/L, EXCEEDS THE MCL OF 80 UG/L, TRIGGERS QTRLY TESTING | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.5 | UG/L | 60.4999 | 2021-10-26 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. (HLKD-A 2ND SITE WAS TESTED 10/21 BUT 2ND SITE NOT SET UP AS A VALID DBP LOCATION AS OF 1/24/22-THEREFORE, RESULTS CANNOT BE ENTERED IN PWS-BB) | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 5 | UG/L | 80.4999 | 2021-10-26 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. (HLKD-A 2ND SITE WAS TESTED 10/21 BUT 2ND SITE NOT SET UP AS A VALID DBP LOCATION AS OF 1/24/22-THEREFORE, RESULTS CANNOT BE ENTERED IN PWS-BB) | 2
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-05 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-01-12 | AAA
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.6 | UG/L | 60.4999 | 2022-01-27 | L1 |  |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 9.8 | UG/L | 80.4999 | 2022-01-27 | L1 |  |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 10 | UG/L | 80.4999 | 2022-01-27 | L2 |  |  | ENTERED LATE_AL | 1
3490314 | CYPRESS COVE | N | INOR | 1040 | NITRATE | 0.057 | MG/L | 10.4999 | 2025-12-09 | AAA
3490314 | CYPRESS COVE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-12-09 | AAA
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.7 | UG/L | 60.4999 | 2021-10-26 | L2 |  |  | ENTERED LATE_ MONITORING LOCATIONS JUST UPDATED_AL | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 5.2 | UG/L | 80.4999 | 2021-10-26 | L2 |  |  | ENTERED LATE_ MONITORING LOCATIONS JUST UPDATED_AL | 1
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.1 | UG/L | 60.4999 | 2022-01-27 | L2 |  |  | ENTERED LATE_AL | 1
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-02 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-09 | AAA
3494427 | HARMONY CDD | N | INOR | 1040 | NITRATE | 0.42 | MG/L | 10.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494427 | HARMONY CDD | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-09 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-16 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-06 | AAA
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.4 | UG/L | 60.4999 | 2022-04-25 | L1 |  |  | 3341 SCHOOL HOUSE ( LRAA TTHM= 40.6, HAA5= 15.08) | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 3.6 | UG/L | 80.4999 | 2022-04-25 | L1 |  |  | 3341 SCHOOL HOUSE ( LRAA TTHM= 40.6, HAA5= 15.08) | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.9 | UG/L | 60.4999 | 2022-04-25 | L2 |  |  | ENTERED LATE (LRAA TTH= 9.28, HAA5= 7.83) | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 3.6 | UG/L | 80.4999 | 2022-04-25 | L2 |  |  | ENTERED LATE (LRAA TTH= 9.28, HAA5= 7.83) | 1
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-27 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-04 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-18 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-01 | AAA
3494427 | HARMONY CDD | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-15 | AAA
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.5 | UG/L | 60.4999 | 2022-07-26 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP (HLKD) | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 8.3 | UG/L | 80.4999 | 2022-07-26 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP (HLKD) | 1
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.6 | UG/L | 60.4999 | 2022-07-26 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 6.9 | UG/L | 80.4999 | 2022-07-26 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.8 | UG/L | 60.4999 | 2022-10-25 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 2.9 | UG/L | 80.4999 | 2022-10-25 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.4 | UG/L | 60.4999 | 2022-10-25 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP (HLKD) | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 5 | UG/L | 80.4999 | 2022-10-25 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP (HLKD) | 1
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.9 | UG/L | 60.4999 | 2023-01-27 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 1.7 | UG/L | 80.4999 | 2023-01-27 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.3 | UG/L | 60.4999 | 2023-01-27 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP (HLKD) | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 3.7 | UG/L | 80.4999 | 2023-01-27 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP (HLKD) | 1
3494427 | HARMONY CDD | N | INOR | 1040 | NITRATE | 0.17 | MG/L | 10.4999 | 2023-01-31 | AAA | 0.025 |  | POE
3494427 | HARMONY CDD | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | AAA |  |  | POE
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.9 | UG/L | 60.4999 | 2023-04-25 | L1 | 0.9 |  |  | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 2 | UG/L | 80.4999 | 2023-04-25 | L1 | 0.47 |  |  | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.4 | UG/L | 60.4999 | 2023-04-25 | L2 | 0.9 |  |  | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 2.6 | UG/L | 80.4999 | 2023-04-25 | L2 | 0.47 |  |  | 1
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.9 | UG/L | 60.4999 | 2023-07-27 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 1.7 | UG/L | 80.4999 | 2023-07-27 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.1 | UG/L | 60.4999 | 2023-07-27 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 3.9 | UG/L | 80.4999 | 2023-07-27 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 3.1 | UG/L | 80.4999 | 2023-10-24 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2 | UG/L | 60.4999 | 2023-10-24 | L1 | 0.9 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 1.6 | UG/L | 80.4999 | 2023-10-24 | L1 | 0.47 |  | 3341 SCHOOL HOUSE RD. | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.4 | UG/L | 60.4999 | 2023-10-24 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.5 | UG/L | 60.4999 | 2024-01-26 | L1 | 0.9 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 1.5 | UG/L | 80.4999 | 2024-01-26 | L1 | 0.47 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2 | UG/L | 60.4999 | 2024-01-26 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 1.8 | UG/L | 80.4999 | 2024-01-26 | L2 | 0.47 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | N | INOR | 1040 | NITRATE | 0.24 | MG/L | 10.4999 | 2024-01-30 | AAA | 0.025 |  | POE
3494427 | HARMONY CDD | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | AAA |  |  | POE
3494427 | HARMONY CDD | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-27 | AAA |  | 0.5499 | POE
3494427 | HARMONY CDD | N | INOR | 1010 | BARIUM | 0.0065 | MG/L | 2.4999 | 2024-03-29 | AAA | 0.0024 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1040 | NITRATE | 0.14 | MG/L | 10.4999 | 2024-03-29 | AAA | 0.25 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-29 | AAA | 0.25 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-03-29 | AAA | 0.0005 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-03-29 | AAA | 0.00067 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-03-29 | AAA | 0.0048 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-03-29 | AAA | 0.005 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1025 | FLUORIDE | 0.48 | MG/L | 4.0499 | 2024-03-29 | AAA | 0.0015 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-03-29 | AAA | 0.00025 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-03-29 | AAA | 0.00014 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-03-29 | AAA | 0.002 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-03-29 | AAA | 0.00083 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-03-29 | AAA | 0.00088 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-03-29 | AAA | 0.00019 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-03-29 | AAA | 0.00021 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2024-03-29 | AAA | 0.19 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1017 | CHLORIDE | 60.7 | MG/L | 250.4999 | 2024-03-29 | AAA | 2.5 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-03-29 | AAA | 0.00093 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1025 | FLUORIDE | 0.48 | MG/L | 2.0499 | 2024-03-29 | AAA | 0.015 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1028 | IRON | 0.022 | MG/L | 0.3499 | 2024-03-29 | AAA | 0.021 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-03-29 | AAA | 0.0013 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-03-29 | AAA | 0.0022 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1055 | SULFATE | 66.6 | MG/L | 250.4999 | 2024-03-29 | AAA | 2.5 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-03-29 | AAA | 0.0077 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2024-03-29 | AAA | 5 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-03-29 | AAA | 1 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8 | LN(10) |  | 2024-03-29 | AAA | 0.1 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 314 | MG/L | 500.4999 | 2024-03-29 | AAA | 5 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-03-29 | AAA | 0.099 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.4 | UG/L | 60.4999 | 2024-04-22 | L1 | 0.9 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 6.3 | UG/L | 80.4999 | 2024-04-22 | L1 | 0.75 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.6 | UG/L | 60.4999 | 2024-04-22 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 6.8 | UG/L | 80.4999 | 2024-04-22 | L2 | 0.75 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-04-30 | AAA | 0.0023 | 0.0149 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.0027 | 0.0249 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-04-30 | AAA | 0.023 | 0.1499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-04-30 | AAA | 0.27 | 1.4999 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-04-30 | AAA | 0.49 | 1.4999 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-04-30 | AAA | 0.16 | 0.4499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-04-30 | AAA | 4.2 | 6.4999 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-04-30 | AAA | 0.36 | 0.6499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-04-30 | AAA | 0.46 | 2.4999 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-04-30 | AAA | 0.04 | 0.0749 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-04-30 | AAA | 0.46 | 0.6499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-04-30 | AAA | 0.04 | 0.1499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-04-30 | AAA | 0.16 | 0.2499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-04-30 | AAA | 0.024 | 0.1499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-04-30 | AAA | 0.59 | 0.9499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-04-30 | AAA | 0.015 | 0.1499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-04-30 | AAA | 0.029 | 0.2499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-04-30 | AAA | 0.0029 | 0.0055 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-04-30 | AAA | 0.014 | 0.0449 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.003 | 0.0249 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-04-30 | AAA | 0.096 | 0.1499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-04-30 | AAA | 0.059 | 0.2499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-04-30 | AAA | 0.015 | 0.1499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.019 | 0.0249 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-04-30 | AAA | 0.014 | 0.0449 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-04-30 | AAA | 0.044 | 0.1499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-04-30 | AAA | 0.0063 | 0.0249 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-04-30 | AAA | 0.0073 | 0.0149 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-04-30 | AAA | 0.035 | 0.2499 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494427 | HARMONY CDD | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-05-21 | AAA |  |  | POE
3494427 | HARMONY CDD | N | RAD | 4030 | RADIUM-228 | 0.741 | PCI/L | 2.4999 | 2024-05-21 | AAA | 0.685 | 1.4999 | POE
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.1 | UG/L | 60.4999 | 2024-07-23 | L1 | 0.9 |  | 6820 BAYSHORE DR - TTHM/HAA5 | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 8.1 | UG/L | 80.4999 | 2024-07-23 | L1 | 0.75 |  | 6820 BAYSHORE DR - TTHM/HAA5 | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.5 | UG/L | 60.4999 | 2024-07-23 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP - TTHM/HAA5 | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 8.9 | UG/L | 80.4999 | 2024-07-23 | L2 | 0.75 |  | 7027 BUTTONBUSH LOOP - TTHM/HAA5 | 1
3494427 | HARMONY CDD | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-09-27 | AAA |  | 0.0149 | POE
3494427 | HARMONY CDD | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-09-27 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-09-27 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-09-27 | AAA |  | 1.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-09-27 | AAA |  | 1.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-09-27 | AAA |  | 0.4499 | POE
3494427 | HARMONY CDD | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-09-27 | AAA |  | 9.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-09-27 | AAA |  | 6.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-09-27 | AAA |  | 0.6499 | POE
3494427 | HARMONY CDD | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-09-27 | AAA |  | 2.4999 | POE
3494427 | HARMONY CDD | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-09-27 | AAA |  | 0.0749 | POE
3494427 | HARMONY CDD | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-09-27 | AAA |  | 0.6499 | POE
3494427 | HARMONY CDD | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-09-27 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-09-27 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-09-27 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-09-27 | AAA |  | 0.9499 | POE
3494427 | HARMONY CDD | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-09-27 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-09-27 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-09-27 | AAA |  | 0.0055 | POE
3494427 | HARMONY CDD | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-09-27 | AAA |  | 0.0449 | POE
3494427 | HARMONY CDD | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-09-27 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-09-27 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-09-27 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-09-27 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-09-27 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-09-27 | AAA |  | 0.0449 | POE
3494427 | HARMONY CDD | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-09-27 | AAA |  | 0.1499 | POE
3494427 | HARMONY CDD | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-09-27 | AAA |  | 0.0249 | POE
3494427 | HARMONY CDD | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-09-27 | AAA |  | 0.0149 | POE
3494427 | HARMONY CDD | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-09-27 | AAA |  | 0.2499 | POE
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.9 | UG/L | 60.4999 | 2024-10-25 | L1 | 0.9 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-10-25 | L1 | 0.75 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.1 | UG/L | 60.4999 | 2024-10-25 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 3.4 | UG/L | 80.4999 | 2024-10-25 | L2 | 0.75 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8 | UG/L | 60.4999 | 2025-01-24 | L1 | 0.9 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 14 | UG/L | 80.4999 | 2025-01-24 | L1 | 0.75 |  | 6820 BAYSHORE DR | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.1 | UG/L | 60.4999 | 2025-01-24 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 14.2 | UG/L | 80.4999 | 2025-01-24 | L2 | 0.75 |  | 7027 BUTTONBUSH LOOP | 1
3494427 | HARMONY CDD | N | INOR | 1040 | NITRATE | 0.12 | MG/L | 10.4999 | 2025-03-14 | AAA | 0.025 |  | LOCATION CODE SET BY PWS - 03/10/2008 HARMONY
3494427 | HARMONY CDD | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | AAA | 0 |  | LOCATION CODE SET BY PWS - 03/10/2008 HARMONY
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.9 | UG/L | 60.4999 | 2025-04-24 | L1 | 0.9 |  | 6820 BAYSHORE DR - TTHM/HAA5 | 2
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 5 | UG/L | 80.4999 | 2025-04-24 | L1 | 0.75 |  | 6820 BAYSHORE DR - TTHM/HAA5 | 2
3494427 | HARMONY CDD | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.6 | UG/L | 60.4999 | 2025-04-24 | L2 | 0.9 |  | 7027 BUTTONBUSH LOOP - TTHM/HAA5 | 1
3494427 | HARMONY CDD | D | DBP | 2950 | TOTAL THMS | 8.6 | UG/L | 80.4999 | 2025-04-24 | L2 | 0.75 |  | 7027 BUTTONBUSH LOOP - TTHM/HAA5 | 1
3494434 | CARROLL STREET STATION | N | INOR | 1040 | NITRATE | 0.3 | MG/L | 10.4999 | 2021-12-08 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-08 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.93 | UG/L | 60.4999 | 2022-08-15 | L1 | 0.98 |  | EAST SAMPLE TAP | 3
3494434 | CARROLL STREET STATION | D | DBP | 2950 | TOTAL THMS | 16.63 | UG/L | 80.4999 | 2022-08-15 | L1 | 0.44 |  | EAST SAMPLE TAP | 3
3494434 | CARROLL STREET STATION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-05 | AAA | 0.46 | 0.5499
3494427 | HARMONY CDD | N | INOR | 1052 | SODIUM | 49.4 | MG/L | 160.4999 | 2024-03-29 | AAA | 0.59 |  | HARMONY - SODIUM J QUALIFIER - APPROVED_LMC
3494427 | HARMONY CDD | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-03-29 | AAA | 0.0066 |  | HARMONY - ALUMINUM J QUALIFIER_APPROVED_LMC
3494427 | HARMONY CDD | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-04-30 | AAA | 3.3 | 9.4999 | HARMONY - 2033 J QUALIFIER - ACCEPTED_LMC
3494434 | CARROLL STREET STATION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA | 0.28 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA | 0.32 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-05 | AAA | 0.28 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.44 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-05 | AAA | 0.26 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA | 0.2 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-05 | AAA | 0.18 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.28 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.36 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-05 | AAA | 0.39 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.23 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.24 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.26 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.28 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.12 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.12 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA | 0.17 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-05 | AAA | 0.22 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-05 | AAA | 0.17 | 0.5499
3494434 | CARROLL STREET STATION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.39 | 0.5499
3494434 | CARROLL STREET STATION | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2022-10-05 | AAA | 0.003 |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1040 | NITRATE | 0.14 | MG/L | 10.4999 | 2022-10-05 | AAA | 0.024 |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1025 | FLUORIDE | 0.12 | MG/L | 4.0499 | 2022-10-05 | AAA | 0.0099 |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2022-10-05 | AAA | 0.8 |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-10-05 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.0149 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 1.4999 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-05 | AAA |  | 1.4999 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-10-05 | AAA |  | 0.4499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-10-05 | AAA |  | 9.4999 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-10-05 | AAA |  | 6.4999 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-10-05 | AAA |  | 0.6499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-10-05 | AAA |  | 2.4999 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-10-05 | AAA |  | 0.0749 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-10-05 | AAA |  | 0.6499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-10-05 | AAA |  | 0.9499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA |  | 0.1499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-10-05 | AAA |  | 0.0449 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-10-05 | AAA |  | 0.1499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-10-05 | AAA |  | 0.2499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.1499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-10-05 | AAA |  | 0.0449 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-10-05 | AAA |  | 0.1499 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-10-05 | AAA |  | 0.0249 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-10-05 | AAA |  | 0.0149 | POE
3494434 | CARROLL STREET STATION | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-10-05 | AAA |  | 0.2499 | POE
3494434 | CARROLL STREET STATION | N | INOR | 1040 | NITRATE | 0.066 | MG/L | 10.4999 | 2023-10-16 | AAA | 0.024 |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1040 | NITRATE | 0.08 | MG/L | 10.4999 | 2024-12-02 | AAA | 0.024 |  | POE
3494434 | CARROLL STREET STATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-02 | AAA |  |  | POE
3494434 | CARROLL STREET STATION | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.83 | UG/L | 60.4999 | 2025-08-04 | L1 | 0.98 |  | EAST SAMPLE TAP - TTHM, HAA5 | 3
3494434 | CARROLL STREET STATION | D | DBP | 2950 | TOTAL THMS | 25.39 | UG/L | 80.4999 | 2025-08-04 | L1 | 0.44 |  | EAST SAMPLE TAP - TTHM, HAA5 | 3
3494434 | CARROLL STREET STATION | N | INOR | 1040 | NITRATE | 0.055 | MG/L | 10.4999 | 2025-10-20 | AAA | 0.024 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-10-20 | AAA | 0.00025 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2025-10-20 | AAA | 0.003 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-10-20 | AAA | 0.00025 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-10-20 | AAA | 0.005 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1024 | CYANIDE | 0.0068 | MG/L | 0.2499 | 2025-10-20 | AAA | 0.002 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-10-20 | AAA | 0.0005 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-10-20 | AAA | 3e-05 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-10-20 | AAA | 0.008 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-10-20 | AAA | 0.0012 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1052 | SODIUM | 20 | MG/L | 160.4999 | 2025-10-20 | AAA | 0.8 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-10-20 | AAA | 0.001 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-10-20 | AAA | 0.002 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-10-20 | AAA | 0.00025 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-10-20 | AAA | 0.5 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-10-20 | AAA | 0.45 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-10-20 | AAA | 0.48 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-10-20 | AAA | 0.49 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-10-20 | AAA | 0.44 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-10-20 | AAA | 0.4 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-10-20 | AAA | 0.28 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-10-20 | AAA | 0.4 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-10-20 | AAA | 0.41 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-10-20 | AAA | 0.44 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-10-20 | AAA | 0.32 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-10-20 | AAA | 0.36 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-10-20 | AAA | 0.33 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-20 | AAA | 0.25 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-10-20 | AAA | 0.44 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-10-20 | AAA | 0.49 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-10-20 | AAA | 0.37 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-10-20 | AAA | 0.42 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-10-20 | AAA | 0.46 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-10-20 | AAA | 0.45 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-10-20 | AAA | 0.45 | 0.5499 | POE
3494434 | CARROLL STREET STATION | N | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2025-10-20 | AAA | 0.0099 |  | POE- 1041, 1025 J QUALIFIERS - NITRITE NOT ACCEPTED, FLUORIDE ACCEPTED
3494434 | CARROLL STREET STATION | N | INOR | 1040 | NITRATE | 0.63 | MG/L | 10.4999 | 2025-11-14 | AAA | 0.024 |  | RESAMPLE
3494434 | CARROLL STREET STATION | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-14 | AAA |  |  | RESAMPLE
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-07-12 | L1 | 0.5 |  | CELEBRATION H.S. L.S. LAKE EVELYN WAS SAMPLED BUT NOT ENTERED. NOT REQUIRED. SITE IS INACTIVE_MFC
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 24.8 | UG/L | 80.4999 | 2021-07-12 | L1 | 0.5 |  | CELEBRATION H.S. L.S. LAKE EVELYN WAS SAMPLED BUT NOT ENTERED. NOT REQUIRED. SITE IS INACTIVE_MFC
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.82 | UG/L | 60.4999 | 2022-07-22 | L1 |  |  | CELEBRATION HIGH SCHOOL
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 26.4 | UG/L | 80.4999 | 2022-07-22 | L1 |  |  | CELEBRATION HIGH SCHOOL
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.25 | UG/L | 60.4999 | 2022-07-22 | L2 |  |  | LAKE EVELYN - INACTIVE SYSTEM
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 22.5 | UG/L | 80.4999 | 2022-07-22 | L2 |  |  | LAKE EVELYN - INACTIVE SYSTEM
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.39 | UG/L | 60.4999 | 2023-07-11 | L2 | 0.5 |  | LAKE EVELYN L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 11 | UG/L | 80.4999 | 2023-07-11 | L2 | 0.5 |  | LAKE EVELYN L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.95 | UG/L | 60.4999 | 2023-07-11 | L1 | 0.5 |  | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 14 | UG/L | 80.4999 | 2023-07-11 | L1 | 0.5 |  | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.2 | UG/L | 60.4999 | 2024-08-19 | L2 | 0.28 |  | LAKE EVELYN L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | S | DBP | 2950 | TOTAL THMS | 13 | UG/L | 80.4999 | 2024-08-19 | L2 | 0.5 |  | LAKE EVELYN L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.6 | UG/L | 60.4999 | 2024-08-19 | L1 | 0.28 |  | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | S | DBP | 2950 | TOTAL THMS | 17 | UG/L | 80.4999 | 2024-08-19 | L1 | 0.5 |  | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.9 | UG/L | 60.4999 | 2024-10-23 | L2 | 0.28 |  | LAKE EVELYN LS - TTHM & HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 12 | UG/L | 80.4999 | 2024-10-23 | L2 | 0.5 |  | LAKE EVELYN LS - TTHM & HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.3 | UG/L | 60.4999 | 2024-10-23 | L4 | 0.28 |  | 313 CAMPUS ST
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 15 | UG/L | 80.4999 | 2024-10-23 | L4 | 0.5 |  | 313 CAMPUS ST
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.2 | UG/L | 60.4999 | 2025-01-23 | L2 | 0.28 |  | LAKE EVELYN L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 12 | UG/L | 80.4999 | 2025-01-23 | L2 | 0.5 |  | LAKE EVELYN L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.1 | UG/L | 60.4999 | 2025-01-23 | L4 | 0.28 |  | 313 CAMPUS ST
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 17 | UG/L | 80.4999 | 2025-01-23 | L4 | 0.5 |  | 313 CAMPUS ST
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.8 | UG/L | 60.4999 | 2025-01-23 | L3 | 0.28 |  | 1402 STICKLEY AVE
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 15 | UG/L | 80.4999 | 2025-01-23 | L3 | 0.5 |  | 1402 STICKLEY AVE
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2 | UG/L | 60.4999 | 2025-01-23 | L1 | 0.28 |  | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 16 | UG/L | 80.4999 | 2025-01-23 | L1 | 0.5 |  | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.1 | UG/L | 60.4999 | 2025-04-23 | L3 | 0.765 |  | 1407 STICKLEY AVE - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 19 | UG/L | 80.4999 | 2025-04-23 | L3 | 0.21 |  | 1407 STICKLEY AVE - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.73 | UG/L | 60.4999 | 2025-04-23 | L1 | 0.765 |  | CELEBRATION HS LS - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 22 | UG/L | 80.4999 | 2025-04-23 | L1 | 0.21 |  | CELEBRATION HS LS - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.33 | UG/L | 60.4999 | 2025-04-23 | L4 | 0.765 |  | 313 CAMPUS ST - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 22 | UG/L | 80.4999 | 2025-04-23 | L4 | 0.21 |  | 313 CAMPUS ST - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.04 | UG/L | 60.4999 | 2025-04-23 | L2 | 0.765 |  | LAKE EVELYN LS - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 16 | UG/L | 80.4999 | 2025-04-23 | L2 | 0.21 |  | LAKE EVELYN LS - TTHM SUBCONTRACTED TO E83018
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.6 | UG/L | 60.4999 | 2025-07-23 | L4 | 0.765 |  | 313 CAMPUS ST - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 31 | UG/L | 80.4999 | 2025-07-23 | L4 | 0.21 |  | 313 CAMPUS ST - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.95 | UG/L | 60.4999 | 2025-07-23 | L1 | 0.765 |  | CELEBRATION HS - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 24 | UG/L | 80.4999 | 2025-07-23 | L1 | 0.21 |  | CELEBRATION HS - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.4 | UG/L | 60.4999 | 2025-07-23 | L2 | 0.765 |  | LAKE EVELYN LS - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 0.21 | UG/L | 80.4999 | 2025-07-23 | L2 | 0.21 |  | LAKE EVELYN LS - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.47 | UG/L | 60.4999 | 2025-07-23 | L3 | 0.765 |  | 1402 STICKLEY AVE - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 0.21 | UG/L | 80.4999 | 2025-07-23 | L3 | 0.21 |  | 1402 STICKLEY AVE - TTHM HAA5
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.9 | UG/L | 60.4999 | 2024-10-23 | L3 | 0.28 |  | 1402 STICKLEY AVE
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 14 | UG/L | 80.4999 | 2024-10-23 | L3 | 0.5 |  | 1402 STICKLEY AVE
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.6 | UG/L | 60.4999 | 2024-10-23 | L1 | 0.28 |  | CELEBRATION H.S. L.S.
3494428 | ENTERPRISE CDD (CONSECUTIVE) | D | DBP | 2950 | TOTAL THMS | 16 | UG/L | 80.4999 | 2024-10-23 | L1 | 0.5 |  | CELEBRATION H.S. L.S.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-01-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-01-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-01-06 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-01-21 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-01-22 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-01-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP1 | 0.025 |  | BELLA LAGO WP (NITRATE ENTD. NITRITE HAS J QUALIFIER, NOT ENTD) PLS. ENTER NITRITE RESULT IF ACCEPTABLE. -BB (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-27 | WTP3 | 0.025 |  | PEABODY WP (NO J QUALIFIERS, BOTH NN ENTD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-27 | WTP3 | 0.025 |  | PEABODY WP (NO J QUALIFIERS, BOTH NN ENTD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 2 | MG/L | 10.4999 | 2021-01-27 | WTP6 | 0.025 |  | HURON WP (NITRATE ENTD. NITRITE HAS J QUALIFIER, NOT ENTD) PLS. ENTER NITRITE RESULT IF ACCEPTABLE. -BB (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-02-01 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-02-03 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-02-03 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-02-08 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-02-17 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-02-17 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.1 | LN(10) |  | 2021-02-17 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-02-21 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2021-02-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 35.9 | UG/L | 80.4999 | 2021-02-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.7 | UG/L | 60.4999 | 2021-02-23 | L1 | 0.9 |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 47.7 | UG/L | 80.4999 | 2021-02-23 | L1 | 0.47 |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.2 | UG/L | 60.4999 | 2021-02-23 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 55.1 | UG/L | 80.4999 | 2021-02-23 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.6 | UG/L | 60.4999 | 2021-02-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 46.6 | UG/L | 80.4999 | 2021-02-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-09 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-03-10 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2021-03-10 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-03-23 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2021-03-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-03-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-09 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-04-12 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-26 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-04-26 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-28 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-03-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-03-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-04-13 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-05-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2021-05-06 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-05-06 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-05-10 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-05-19 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2021-05-19 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-20 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26 | UG/L | 60.4999 | 2021-05-26 | L2 |  |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 48.2 | UG/L | 80.4999 | 2021-05-26 | L2 |  |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.6 | UG/L | 60.4999 | 2021-05-26 | L1 |  |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 51.9 | UG/L | 80.4999 | 2021-05-26 | L1 |  |  | 4738 ASHURST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.2 | UG/L | 60.4999 | 2021-05-26 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 36.2 | UG/L | 80.4999 | 2021-05-26 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.9 | UG/L | 60.4999 | 2021-05-26 | L4 |  |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 51.2 | UG/L | 80.4999 | 2021-05-26 | L4 |  |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-05-27 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-06-07 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-14 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-06-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-24 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-06-25 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2021-06-29 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.3 | LN(10) |  | 2021-06-29 | WTP1 |  |  | BELLA
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-07-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-07-07 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-07-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-07-22 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-07-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-08-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-09 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-11 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-17 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-18 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-08-20 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.2 | UG/L | 60.4999 | 2021-08-27 | L2 |  |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 41.3 | UG/L | 80.4999 | 2021-08-27 | L2 |  |  | 3543 BEAU CHENE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.5 | UG/L | 60.4999 | 2021-08-27 | L1 |  |  | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 40.9 | UG/L | 80.4999 | 2021-08-27 | L1 |  |  | 4738 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.9 | UG/L | 60.4999 | 2021-08-27 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 31.6 | UG/L | 80.4999 | 2021-08-27 | L3 |  |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.1 | UG/L | 60.4999 | 2021-08-27 | L4 |  |  | 5508 WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 31.3 | UG/L | 80.4999 | 2021-08-27 | L4 |  |  | 5508 WILLOW BEND
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-04 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-09 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-18 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-09-23 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-09-30 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-12 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-12 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | WTP1 | 0.025 |  | BELLA LAGO WP NITRITE RETEST (NITRITE HAS J QUAL, BIASED HIGH MS/MSD=119/119% RECOV, LCS OK) SINCE BIASED HIGH, PROB. OK. IF OK, PLS. CHANGE SMP TYPE "S" TO SMP TYP "N."
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-10-26 | WTP6 | 0.025 |  | HURON WP NITRITE RETEST (OK)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-26 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-27 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-10-28 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-10 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-10 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-11-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-19 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28 | UG/L | 60.4999 | 2021-11-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 46.5 | UG/L | 80.4999 | 2021-11-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.7 | UG/L | 60.4999 | 2021-11-23 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 52.2 | UG/L | 80.4999 | 2021-11-23 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.3 | UG/L | 60.4999 | 2021-11-23 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 39.2 | UG/L | 80.4999 | 2021-11-23 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.9 | UG/L | 60.4999 | 2021-11-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 43.5 | UG/L | 80.4999 | 2021-11-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-11-27 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-12-14 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2021-12-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-22 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2021-12-28 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-01-04 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-01-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-08 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2022-01-12 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-12 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-20 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-01-30 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-02-02 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-02 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-05 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-11 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-02-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-02-17 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 1.6 | MG/L | 10.4999 | 2022-02-21 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP6 |  |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-02-21 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.1 | UG/L | 60.4999 | 2022-02-22 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2022-02-22 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 41.7 | UG/L | 80.4999 | 2022-02-22 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2022-02-22 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.3 | UG/L | 60.4999 | 2022-02-22 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 30.5 | UG/L | 80.4999 | 2022-02-22 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2022-02-22 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 31.3 | UG/L | 80.4999 | 2022-02-22 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-02-23 | WTP3 |  |  | PEABODY WTP
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-11-07 | AAA |  |  | POE
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-11-07 | AAA |  |  | POE
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1040 | NITRATE | 0.23 | MG/L | 10.4999 | 2023-01-04 | AAA | 0.024 |  | POE
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-04 | AAA | 0 |  | POE
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-08 | AAA |  |  | POE
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-08 | AAA |  |  | POE
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1040 | NITRATE | 0.018 | MG/L | 10.4999 | 2021-03-19 | AAA |  |  | POE
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1040 | NITRATE | 0.4 | MG/L | 10.4999 | 2022-02-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - THIS WILL COUNT AS MAKE-UP FOR 2021 NN'S
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - THIS WILL COUNT AS MAKE-UP FOR 2021 NN'S
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-05 | AAA | 0.024 |  | 2024 N/N
3494430 | POINCIANA CHRISTIAN CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-05 | AAA | 0.0034 |  | 2024 N/N
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-19 | AAA |  |  | POE
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-23 | AAA |  |  | PWS CODE - POE
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-06-23 | AAA | 0.0034 |  | PWS CODE - POE
3494441 | DOLLAR GENERAL HARMONY | D | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-10-16 | AAA |  |  | DIST-- LOCATION - POE
3494441 | DOLLAR GENERAL HARMONY | D | INOR | 1041 | NITRITE | 0.11 | MG/L | 1.4999 | 2023-10-16 | AAA | 0.0034 |  | DIST-- LOCATION - POE
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1040 | NITRATE | 0.099 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-21 | AAA | 0.024 |  | POE
3494441 | DOLLAR GENERAL HARMONY | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA | 0.0034 |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-06 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-06 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-03-16 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-16 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-03-20 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-20 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-03-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-03-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-04-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-08 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-12 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-04-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-04-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-04-24 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-04-25 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-06 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-09 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-05-11 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-11 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-05-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-05-21 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.5 | UG/L | 60.4999 | 2022-05-25 | L2 |  |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 40 | UG/L | 80.4999 | 2022-05-25 | L2 |  |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27 | UG/L | 60.4999 | 2022-05-25 | L1 |  |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 45 | UG/L | 80.4999 | 2022-05-25 | L1 |  |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.1 | UG/L | 60.4999 | 2022-05-25 | L3 |  |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 30.9 | UG/L | 80.4999 | 2022-05-25 | L3 |  |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.8 | UG/L | 60.4999 | 2022-05-25 | L4 |  |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 39.1 | UG/L | 80.4999 | 2022-05-25 | L4 |  |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-05-25 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-06-01 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-01 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-11 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-06-14 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-06-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-24 | WTP6 |  |  | HURON WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-06-26 | WTP3 |  |  | PEABODY WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-07-06 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-06 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-07-06 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-07-19 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-19 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-19 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-08-03 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-08-03 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-08-09 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-08-18 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-08-23 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-08-23 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29 | UG/L | 60.4999 | 2022-08-25 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 51.4 | UG/L | 80.4999 | 2022-08-25 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24 | UG/L | 60.4999 | 2022-08-25 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 48.4 | UG/L | 80.4999 | 2022-08-25 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2022-08-25 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 41.8 | UG/L | 80.4999 | 2022-08-25 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.6 | UG/L | 60.4999 | 2022-08-25 | L4 | 0.9 |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 41.6 | UG/L | 80.4999 | 2022-08-25 | L4 | 0.47 |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-09-07 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-09-07 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-09-07 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-09-20 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-09-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-09-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-10-09 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-10-12 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-10-12 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-10-24 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-10-27 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-10-27 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-11-09 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-09 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-09 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.9 | UG/L | 60.4999 | 2022-11-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 39.6 | UG/L | 80.4999 | 2022-11-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.7 | UG/L | 60.4999 | 2022-11-23 | L1 | 0.9 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 48.2 | UG/L | 80.4999 | 2022-11-23 | L1 | 0.47 |  | 4738 ASHURST ST.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2022-11-23 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 34.8 | UG/L | 80.4999 | 2022-11-23 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.6 | UG/L | 60.4999 | 2022-11-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 34.1 | UG/L | 80.4999 | 2022-11-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR. (HLKD)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-11-23 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-23 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-11-23 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-12-01 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-12-08 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-08 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-12-08 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2022-12-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2022-12-21 | WTP1 |  |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2023-01-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-11 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2023-01-18 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-18 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-19 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-01-20 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP6 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | WTP1 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP1 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 2.1 | MG/L | 10.4999 | 2023-01-31 | WTP6 | 0.025 |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-01-31 | WTP3 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP3 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-03 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-08 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2023-02-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-15 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-16 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP6 | 0.2 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP3 | 0.2 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.2 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.44 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP1 | 0.35 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP1 | 0.33 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP1 | 0.11 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP1 | 0.3 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP1 | 0.12 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP1 | 0.29 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.27 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.3 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP1 | 0.27 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.44 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP1 | 0.4 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP1 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP1 | 0.23 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP3 | 0.35 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP3 | 0.33 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP3 | 0.11 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP3 | 0.44 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP3 | 0.3 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP3 | 0.12 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP3 | 0.29 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP3 | 0.27 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.3 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP3 | 0.27 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP3 | 0.44 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP3 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP3 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP3 | 0.4 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP3 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP3 | 0.23 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP6 | 0.35 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP6 | 0.33 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP6 | 0.11 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP6 | 0.44 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP6 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP6 | 0.3 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP6 | 0.12 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP6 | 0.29 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP6 | 0.27 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP6 | 0.3 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP6 | 0.27 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP6 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP6 | 0.44 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP6 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP6 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP6 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP6 | 0.26 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP6 | 0.4 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP6 | 0.28 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP6 | 0.23 | 0.5499 | STYRENE J QUALIFIER, LCS RECOVERIES BIASED HIGH. RESULT ACCEPTED_SMD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2023-02-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.3 | UG/L | 60.4999 | 2023-02-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 37.4 | UG/L | 80.4999 | 2023-02-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.8 | UG/L | 60.4999 | 2023-02-23 | L1 | 0.9 |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 44.5 | UG/L | 80.4999 | 2023-02-23 | L1 | 0.47 |  | 4738 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.7 | UG/L | 60.4999 | 2023-02-23 | L3 | 0.9 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 37 | UG/L | 80.4999 | 2023-02-23 | L3 | 0.47 |  | 2942 EVANS DR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.4 | UG/L | 60.4999 | 2023-02-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 42.8 | UG/L | 80.4999 | 2023-02-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR.
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-08 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2023-03-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-09 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-20 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-22 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2023-03-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-03-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-03-27 | WTP1 | 0.025
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-27 | WTP1 | 0.025
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-27 | WTP1 | 0.0005
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2023-03-27 | WTP1 | 0.0024
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-27 | WTP1 | 0.00067
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-27 | WTP1 | 0.0026
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-03-27 | WTP1 | 0.005
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1025 | FLUORIDE | 0.37 | MG/L | 4.0499 | 2023-03-27 | WTP1 | 0.015
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-27 | WTP1 | 0.00022
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-27 | WTP1 | 9e-05
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-27 | WTP1 | 0.002
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-27 | WTP1 | 0.00083
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1052 | SODIUM | 12.5 | MG/L | 160.4999 | 2023-03-27 | WTP1 | 0.59
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-27 | WTP1 | 0.00083
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-27 | WTP1 | 0.00019
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-27 | WTP1 | 0.00021
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 1.9 | MG/L | 10.4999 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1005 | ARSENIC | 0.0015 | MG/L | 0.0104 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1010 | BARIUM | 0.016 | MG/L | 2.4999 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1025 | FLUORIDE | 0.65 | MG/L | 4.0499 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1045 | SELENIUM | 0.0012 | MG/L | 0.0549 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1052 | SODIUM | 6.5 | MG/L | 160.4999 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-27 | WTP6
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-03-27 | WTP3
3494431 | MACK FARMS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-02-02 | AAA |  |  | POE
3494431 | MACK FARMS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-02-02 | AAA |  |  | POE
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0.46 | UG/L | 6.4999 | 2021-08-09 | AAA |  | 0.6499 | POE
3494431 | MACK FARMS | N | INOR | 1040 | NITRATE | 0.031 | MG/L | 10.4999 | 2022-03-28 | AAA | 0.02 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-28 | AAA | 0.02 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-03-28 | AAA | 0.00069 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1010 | BARIUM | 0.022 | MG/L | 2.4999 | 2022-03-28 | AAA | 0.002 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-03-28 | AAA | 0.0009 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-03-28 | AAA | 0.002 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-03-28 | AAA | 0.005 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1025 | FLUORIDE | 1.06 | MG/L | 4.0499 | 2022-03-28 | AAA | 0.03 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-03-28 | AAA | 0.00067 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-03-28 | AAA | 0.0002 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-03-28 | AAA | 0.00118 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-03-28 | AAA | 0.00157 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1052 | SODIUM | 57.3 | MG/L | 160.4999 | 2022-03-28 | AAA | 0.034 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2022-03-28 | AAA | 0.5 | 0.667
3494431 | MACK FARMS | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-03-28 | AAA | 0.00226 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1075 | BERYLLIUM | 0.002 | MG/L | 0.0045 | 2022-03-28 | AAA | 8e-05 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-03-28 | AAA | 0.00098 |  | RESULTS RCVD 5-9-22
3494431 | MACK FARMS | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 3.2 | PCI/L | 15.4999 | 2022-03-28 | AAA | 0.9
3494431 | MACK FARMS | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2022-03-28 | AAA | 0.2 | 1.4999
3494431 | MACK FARMS | N | RAD | 4030 | RADIUM-228 | 0.5 | PCI/L | 2.4999 | 2022-03-28 | AAA | 0.5 | 1.4999
3494431 | MACK FARMS | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-03-28 | AAA | 0.5 | 0.5499 | VOC (RESULTS RCVD 5-9-22)
3494431 | MACK FARMS | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-03-28 | AAA | 0.0024 | 0.0149 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-03-28 | AAA | 0.0028 | 0.0249 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-03-28 | AAA | 0.024 | 0.1499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-03-28 | AAA | 0.74 | 1.4999 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-03-28 | AAA | 0.49 | 1.4999 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-03-28 | AAA | 0.16 | 0.4499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-03-28 | AAA | 3.3 | 9.4999 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-03-28 | AAA | 4.2 | 6.4999 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-03-28 | AAA | 0.37 | 0.6499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-03-28 | AAA | 0.46 | 2.4999 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-03-28 | AAA | 0.041 | 0.0749 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-03-28 | AAA | 0.16 | 0.2499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-03-28 | AAA | 0.025 | 0.1499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-03-28 | AAA | 0.59 | 0.9499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-03-28 | AAA | 0.015 | 0.1499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-03-28 | AAA | 0.03 | 0.2499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-03-28 | AAA | 0.014 | 0.0449 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-03-28 | AAA | 0.0031 | 0.0249 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-03-28 | AAA | 0.096 | 0.1499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-03-28 | AAA | 0.053 | 0.2499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-03-28 | AAA | 0.015 | 0.1499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-03-28 | AAA | 0.02 | 0.0249 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-03-28 | AAA | 0.014 | 0.0449 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-03-28 | AAA | 0.048 | 0.1499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-03-28 | AAA | 0.014 | 0.0249 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-03-28 | AAA | 0.01 | 0.0149 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-03-28 | AAA | 0.038 | 0.2499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-03-28 | AAA | 0.04 | 0.1499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2022-09-12 | L1 | 0.5 |  | OFFICE KITCHEN | 3
3494431 | MACK FARMS | D | DBP | 2950 | TOTAL THMS | 3.65 | UG/L | 80.4999 | 2022-09-12 | L1 | 0.5 |  | OFFICE KITCHEN | 3
3494431 | MACK FARMS | N | INOR | 1040 | NITRATE | 0.023 | MG/L | 10.4999 | 2023-02-13 | AAA | 0.02 |  | POE
3494431 | MACK FARMS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-13 | AAA |  |  | POE
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0.63 | UG/L | 6.4999 | 2023-03-01 | AAA | 0.6 | 0.6499 | 2039 DI(2-ETHYLHEXYL)PHTHALATE DETECT
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-05-08 | AAA |  | 0.6499 | POE
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-07-31 | AAA | 0.6 | 0.6499 | Q3 DI(2-ETHYLHEXYL)PHTHALATE
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-30 | AAA |  | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008 POE
3494431 | MACK FARMS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-15 | AAA |  |  | POE
3494431 | MACK FARMS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-15 | AAA |  |  | POE
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-01-31 | AAA |  | 0.6499 | POE
3494431 | MACK FARMS | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-02-25 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-03-28 | AAA | 0.48 | 0.6499 | 27OF29 SOC (RESULTS RCVD 5-9-22) PICLORAM HAS CU QUALIFIER-NOT ENT'D PENDING EVAULATION. ALSO, 2039 DI(2-ETHYLHEXYLPHTHALATE CANNOT BE ENT'D SINCE DOH LAB CERTIF. # IS MISSING ON RESULTS PAGE 8 OF 9)
3494431 | MACK FARMS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-25 | AAA | 0.04 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-25 | AAA | 0.04 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-02-25 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1010 | BARIUM | 0.018 | MG/L | 2.4999 | 2025-02-25 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-02-25 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1025 | FLUORIDE | 1.4 | MG/L | 4.0499 | 2025-02-25 | AAA | 0.04 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-02-25 | AAA | 0.0005 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-02-25 | AAA | 3e-05 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-02-25 | AAA | 0.008 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-02-25 | AAA | 0.0012 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1052 | SODIUM | 57 | MG/L | 160.4999 | 2025-02-25 | AAA | 0.8 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | SEC | 1025 | FLUORIDE | 1.4 | MG/L | 2.0499 | 2025-02-25 | AAA | 0.04 |  | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-02-25 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-02-25 | AAA | 0.002 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-02-25 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008-CYANIDE-1024-J QUALIFIER
3494431 | MACK FARMS | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-02-25 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-02-25 | AAA | 0.27 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-02-25 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-02-25 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-02-25 | AAA | 0.39 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-02-25 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-02-25 | AAA | 0.29 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-02-25 | AAA | 0.22 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-02-25 | AAA | 0.21 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-02-25 | AAA | 0.24 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-02-25 | AAA | 0.29 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-02-25 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-02-25 | AAA | 0.26 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-02-25 | AAA | 0.14 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-02-25 | AAA | 0.27 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-02-25 | AAA | 0.42 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-02-25 | AAA | 0.36 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-02-25 | AAA | 0.26 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-02-25 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-02-25 | AAA | 0.31 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-02-25 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-02-25 | AAA | 0.0076 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-02-25 | AAA | 0.0078 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-02-25 | AAA | 0.0075 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-02-25 | AAA | 0.13 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-02-25 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-02-25 | AAA | 0.37 | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-02-25 | AAA | 6 | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-02-25 | AAA | 5.9 | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-02-25 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-02-25 | AAA | 1.8 | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-02-25 | AAA | 0.06 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-02-25 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-02-25 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-02-25 | AAA | 0.18 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-02-25 | AAA | 0.021 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-02-25 | AAA | 0.67 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-02-25 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-02-25 | AAA | 0.15 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-02-25 | AAA | 0.0066 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-02-25 | AAA | 0.0057 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-02-25 | AAA | 0.095 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-02-25 | AAA | 0.09 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-02-25 | AAA | 0.0069 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-02-25 | AAA | 0.015 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-02-25 | AAA | 0.038 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-02-25 | AAA | 0.1 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-02-25 | AAA | 0.0062 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-02-25 | AAA | 0.0093 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-02-25 | AAA | 0.058 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3494431 | MACK FARMS | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-02-25 | AAA |  |  | J QUALIFIED - ACCEPTED
3494431 | MACK FARMS | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.37 | UG/L | 60.4999 | 2025-09-09 | L1 | 0.98 |  | L-1 OFFICE KITCHEN SINK | 3
3494431 | MACK FARMS | D | DBP | 2950 | TOTAL THMS | 30.6 | UG/L | 80.4999 | 2025-09-09 | L1 | 0.44 |  | L-1 OFFICE KITCHEN SINK | 3
3494431 | MACK FARMS | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2025-09-29 | AAA |  |  | SITE 11-EXCEEDANCE
3494431 | MACK FARMS | N | WQP | 1919 | HARDNESS - CALCIUM | 273.6 | MG/L | 0 | 2025-09-29 | AAA |  |  | SITE 10- EXCEEDANCE
3494431 | MACK FARMS | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-09-29 | AAA |  |  | SITE 10- EXCEEDANCE
3494431 | MACK FARMS | N | WQP | 1919 | HARDNESS - CALCIUM | 273.6 | MG/L | 0 | 2025-09-29 | AAA |  |  | SITE 11-EXCEEDANCE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1025 | FLUORIDE | 0.46 | MG/L | 4.0499 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1052 | SODIUM | 8.7 | MG/L | 160.4999 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-27 | WTP3
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1002 | ALUMINUM | 0.0076 | MG/L | 0.2499 | 2023-03-27 | WTP1 | 0.0072 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1017 | CHLORIDE | 14.2 | MG/L | 250.4999 | 2023-03-27 | WTP1 | 2.5 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1022 | COPPER | 0.001 | MG/L | 1.4999 | 2023-03-27 | WTP1 | 0.00093 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1025 | FLUORIDE | 0.37 | MG/L | 2.0499 | 2023-03-27 | WTP1 | 0.015 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1028 | IRON | 0.019 | MG/L | 0.3499 | 2023-03-27 | WTP1 | 0.016 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1032 | MANGANESE | 0.0031 | MG/L | 0.0549 | 2023-03-27 | WTP1 | 0.00093 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-27 | WTP1 | 0.0013 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1055 | SULFATE | 4.5 | MG/L | 250.4999 | 2023-03-27 | WTP1 | 2.5 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-27 | WTP1 | 0.0076 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-03-27 | WTP1 | 5 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2023-03-27 | WTP1 | 1 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 218 | MG/L | 500.4999 | 2023-03-27 | WTP1 | 5 |  | 2905 J 1920 IS AT THE MCL PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1002 | ALUMINUM | 0.0131 | MG/L | 0.2499 | 2023-03-27 | WTP6 | 0.0072 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1017 | CHLORIDE | 12.6 | MG/L | 250.4999 | 2023-03-27 | WTP6 | 2.5 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1022 | COPPER | 0.0014 | MG/L | 1.4999 | 2023-03-27 | WTP6 | 0.00093 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1025 | FLUORIDE | 0.65 | MG/L | 2.0499 | 2023-03-27 | WTP6 | 0.015 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-27 | WTP6 | 0.016 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-03-27 | WTP6 | 0.00093 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-27 | WTP6 | 0.0013 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1055 | SULFATE | 33.8 | MG/L | 250.4999 | 2023-03-27 | WTP6 | 2.5 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-27 | WTP6 | 0.0076 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-03-27 | WTP6 | 5 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 267 | MG/L | 500.4999 | 2023-03-27 | WTP6 | 5 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1017 | CHLORIDE | 12.6 | MG/L | 250.4999 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1025 | FLUORIDE | 0.46 | MG/L | 2.0499 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1055 | SULFATE | 0 | MG/L | 250.4999 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 214 | MG/L | 500.4999 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-03-27 | WTP3 |  |  | PH Q 1920 IS AT MCL (NOT EXCEEDS)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 1920 | ODOR THRESHOLD | 3 |  | 3.4999 | 2023-03-27 | WTP6 | 1 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-03-27 | WTP6 | 0.099 |  | PH Q
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2023-04-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-04-07 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-04-18 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-19 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2023-04-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-04-19 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-20 | WTP1 | 0.0023 | 0.0149 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.0027 | 0.0249 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-20 | WTP1 | 0.023 | 0.1499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP1 | 0.25 | 1.4999 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-20 | WTP1 | 0.49 | 1.4999 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-20 | WTP1 | 0.16 | 0.4499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-20 | WTP1 | 3.3 | 9.4999 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-20 | WTP1 | 4.2 | 6.4999 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-20 | WTP1 | 0.36 | 0.6499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-20 | WTP1 | 0.46 | 2.4999 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-20 | WTP1 | 0.04 | 0.0749 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-20 | WTP1 | 0.46 | 0.6499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-20 | WTP1 | 0.04 | 0.1499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-20 | WTP1 | 0.16 | 0.2499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-04-20 | WTP1 | 0.024 | 0.1499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-20 | WTP1 | 0.59 | 0.9499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP1 | 0.015 | 0.1499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.003 | 0.0249 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-20 | WTP6 | 3.3 | 9.4999 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-20 | WTP3 | 3.3 | 9.4999 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-20 | WTP1 | 0.029 | 0.2499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-20 | WTP1 | 0.0006 | 0.0055 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-20 | WTP1 | 0.014 | 0.0449 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-20 | WTP1 | 0.096 | 0.1499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-20 | WTP1 | 0.053 | 0.2499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-20 | WTP1 | 0.015 | 0.1499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.019 | 0.0249 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-20 | WTP1 | 0.014 | 0.0449 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-20 | WTP1 | 0.044 | 0.1499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP1 | 0.0064 | 0.0249 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-20 | WTP1 | 0.0076 | 0.0149 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-20 | WTP1 | 0.035 | 0.2499 | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-20 | WTP6 | 0.0023 | 0.0149 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP6 | 0.0027 | 0.0249 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-20 | WTP6 | 0.023 | 0.1499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP6 | 0.25 | 1.4999 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-20 | WTP6 | 0.49 | 1.4999 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-20 | WTP6 | 0.16 | 0.4499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-20 | WTP6 | 4.2 | 6.4999 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-20 | WTP6 | 0.35 | 0.6499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-20 | WTP6 | 0.46 | 2.4999 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-20 | WTP6 | 0.039 | 0.0749 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-20 | WTP6 | 0.46 | 0.6499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-20 | WTP6 | 0.04 | 0.1499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-20 | WTP6 | 0.16 | 0.2499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-04-20 | WTP6 | 0.024 | 0.1499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-20 | WTP6 | 0.59 | 0.9499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP6 | 0.014 | 0.1499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-20 | WTP6 | 0.029 | 0.2499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-20 | WTP6 | 0.00088 | 0.0055 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-20 | WTP6 | 0.013 | 0.0449 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP6 | 0.003 | 0.0249 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-20 | WTP6 | 0.096 | 0.1499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-20 | WTP6 | 0.053 | 0.2499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-20 | WTP6 | 0.014 | 0.1499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP6 | 0.019 | 0.0249 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-20 | WTP6 | 0.014 | 0.0449 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-20 | WTP6 | 0.044 | 0.1499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP6 | 0.0064 | 0.0249 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-20 | WTP6 | 0.0075 | 0.0149 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-20 | WTP6 | 0.035 | 0.2499 | HURON WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-20 | WTP3 | 0.0023 | 0.0149 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.0026 | 0.0249 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-20 | WTP3 | 0.023 | 0.1499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP3 | 0.26 | 1.4999 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-20 | WTP3 | 0.49 | 1.4999 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-20 | WTP3 | 0.16 | 0.4499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-20 | WTP3 | 4.2 | 6.4999 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-20 | WTP3 | 0.35 | 0.6499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-20 | WTP3 | 0.04 | 0.1499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-20 | WTP3 | 0.46 | 2.4999 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-20 | WTP3 | 0.039 | 0.0749 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-20 | WTP3 | 0.45 | 0.6499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-20 | WTP3 | 0.16 | 0.2499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-04-20 | WTP3 | 0.024 | 0.1499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-20 | WTP3 | 0.59 | 0.9499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-20 | WTP3 | 0.014 | 0.1499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-20 | WTP3 | 0.028 | 0.2499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-20 | WTP3 | 0.0018 | 0.0055 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-20 | WTP3 | 0.013 | 0.0449 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.0029 | 0.0249 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-20 | WTP3 | 0.096 | 0.1499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-20 | WTP3 | 0.053 | 0.2499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-20 | WTP3 | 0.014 | 0.1499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.019 | 0.0249 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-20 | WTP3 | 0.014 | 0.0449 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-20 | WTP3 | 0.045 | 0.1499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-20 | WTP3 | 0.0065 | 0.0249 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-20 | WTP3 | 0.0076 | 0.0149 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-20 | WTP3 | 0.036 | 0.2499 | PEABODY WTP-2033 J QUALIFIER ACCEPTABLE BASED ON QA/QC_SG
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2023-05-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-03 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-10 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-10 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2023-05-17 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-17 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-05-19 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.1 | UG/L | 60.4999 | 2023-05-23 | L2 | 0.9
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 45.8 | UG/L | 80.4999 | 2023-05-23 | L2 | 0.47
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29 | UG/L | 60.4999 | 2023-05-23 | L1 | 0.9
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 49.5 | UG/L | 80.4999 | 2023-05-23 | L1 | 0.47
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.1 | UG/L | 60.4999 | 2023-05-23 | L3 | 0.9
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 39.5 | UG/L | 80.4999 | 2023-05-23 | L3 | 0.47
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.7 | UG/L | 60.4999 | 2023-05-23 | L4 | 0.9
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2023-05-23 | L4 | 0.47
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP6 | 0.686 | 1.4999 | HURON LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-24 | WTP1 | 1.49 |  | BELLA LAGO LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP1 | 0.856 | 1.4999 | BELLA LAGO LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-24 | WTP6 | 2.67 |  | HURON LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-24 | WTP3 | 2.54 |  | PEABODY LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-24 | WTP3 | 0.716 | 1.4999 | PEABODY LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-05-24 | WTP6 |  |  | HURON
3494437 | ROGERS FOOD STORE | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-10-28 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1041 | NITRITE | 0.0095 | MG/L | 1.4999 | 2021-10-28 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-27 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | D | INOR | 1040 | NITRATE | 0.077 | MG/L | 10.4999 | 2023-10-16 | AAA | 0.024 |  | DIST- LOCATION POE
3494437 | ROGERS FOOD STORE | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-16 | AAA |  |  | DIST- LOCATION POE
3494437 | ROGERS FOOD STORE | N | INOR | 1040 | NITRATE | 0.092 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1040 | NITRATE | 0.092 | MG/L | 10.4999 | 2024-10-22 | AAA | 0.024 |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-22 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1040 | NITRATE | 0.28 | MG/L | 10.4999 | 2024-11-05 | AAA | 0.1 |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-05 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-21 | AAA |  |  | POE
3494437 | ROGERS FOOD STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-21 | AAA |  |  | POE
3494444 | RACETRAC #1463 | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2023-10-18 | POE |  |  | POE
3494444 | RACETRAC #1463 | N | INOR | 1041 | NITRITE | 0.2 | MG/L | 1.4999 | 2023-10-18 | POE |  |  | POE
3494444 | RACETRAC #1463 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-11-12 | POE |  |  | POE
3494444 | RACETRAC #1463 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-12 | POE |  |  | POE
3494444 | RACETRAC #1463 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-12-08 | POE |  |  | POE
3494444 | RACETRAC #1463 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-12-08 | POE |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1040 | NITRATE | 0.091 | MG/L | 10.4999 | 2022-02-21 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-21 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1017 | CHLORIDE | 49.1 | MG/L | 250.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1055 | SULFATE | 21.3 | MG/L | 250.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1920 | ODOR THRESHOLD | 2 |  | 3.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.6 | LN(10) |  | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 331 | MG/L | 500.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-02-23 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-02-23 | WTP NP. 1 |  | 0.4499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 9.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-02-23 | WTP NP. 1 |  | 6.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-02-23 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-02-23 | WTP NP. 1 |  | 2.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-02-23 | WTP NP. 1 |  | 0.0749 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-02-23 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-02-23 | WTP NP. 1 |  | 0.9499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2022-02-23 | WTP NP. 1 |  | 0.0055 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-02-23 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-02-23 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-02-23 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-02-23 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1010 | BARIUM | 0.0096 | MG/L | 2.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1025 | FLUORIDE | 0.28 | MG/L | 4.0499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1052 | SODIUM | 33.7 | MG/L | 160.4999 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1025 | FLUORIDE | 0.28 | MG/L | 2.0499 | 2022-02-23 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | S | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2022-02-23 | WTP NP. 1 | 0.2 |  | POE/D ASBESTOS (ENT'D SEPARATELY FROM PRIMARY INORGANICS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-03-14 | L3 |  |  | AT POE_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 10.1 | UG/L | 10.4999 | 2022-04-01 | L3 |  |  | HIGH RESULT_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 0.0149 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 1.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-05-24 | WTP NP. 1 |  | 1.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 9.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-05-24 | WTP NP. 1 |  | 0.6499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-05-24 | WTP NP. 1 |  | 2.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-05-24 | WTP NP. 1 |  | 0.0749 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-05-24 | WTP NP. 1 |  | 0.6499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-05-24 | WTP NP. 1 |  | 0.9499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2022-05-24 | WTP NP. 1 |  | 0.0055 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-05-24 | WTP NP. 1 |  | 0.0449 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.0449 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-05-24 | WTP NP. 1 |  | 0.1499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-05-24 | WTP NP. 1 |  | 0.0249 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-05-24 | WTP NP. 1 |  | 0.0149 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 0.2499 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2991 | TOLUENE | 0.41 | UG/L | 1499.9999 | 2022-05-24 | WTP NP. 1 | 0.28 | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-05-24 | WTP NP. 1 |  | 0.5499 | POE. TOLUNE 0.41, LESS THAN 0.5 UG/L.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-05-27 | L3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-05-27 | WTP NP. 1 | 1 |  | MARKED "WELL 1 FINISHED WATER" (POE/D)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-06-03 | L3 |  |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 4 | UG/L | 10.4999 | 2022-07-01 | L3 | 0.22 |  | BROMATE - JULY
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-07-08 | WTP NP. 1 | 0.16 | 0.4499 | DIQUAT RETESTED DUE TO J QUALIFIER 5/22
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-08-02 | WTP NP. 1 | 2.44 |  | RADS
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.615 | 1.4999 | RADS
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-02 | WTP NP. 1 | 0.35 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-02 | WTP NP. 1 | 0.33 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-02 | WTP NP. 1 | 0.11 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-02 | WTP NP. 1 | 0.44 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-02 | WTP NP. 1 | 0.3 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.12 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-02 | WTP NP. 1 | 0.29 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 0.27 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.3 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-02 | WTP NP. 1 | 0.27 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.28 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-02 | WTP NP. 1 | 0.44 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-02 | WTP NP. 1 | 0.28 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 0.26 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.4 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2991 | TOLUENE | 0.28 | UG/L | 1499.9999 | 2022-08-02 | WTP NP. 1 | 0.28 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-02 | WTP NP. 1 | 0.23 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 0.2 | 0.5499 | VOC (TOLUENE 0.28 UG/L, < RDL OF 0.5 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.019 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-05-24 | WTP NP. 1 |  |  | ENTERED LATE_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-05-24 | WTP NP. 1 |  | 1.4999 | ENTERED LATE_AL
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2022-05-31 | WTP NP. 1 | 1 |  | MARKED "WELL 2 FINISHED WATER" (POE/D) "SULFIDE" IS REPORTED AS 0.16 MG/L
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.003 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-08-02 | WTP NP. 1 | 0.096 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-08-02 | WTP NP. 1 | 0.053 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.0449 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-08-02 | WTP NP. 1 | 0.045 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.0065 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-08-02 | WTP NP. 1 | 0.0076 | 0.0149 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.036 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | S | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-08-02 | WTP NP. 1 | 3.4 | 6.4999 | GLYPHOSATE W/ J QUALIFIER-ONLY 11% MS RECOVERY-UNACCEPTABLE-WILL RETEST 9/22 (NO PAGE 1 FOR THIS REPORT 810-33545-1 E87775, SUBCONTRACTED FROM PACE E83079 SAMPLE 35736874001, WHICH IS THE 8/2/22 SOCS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.7 | 1.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.0023 | 0.0149 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-08-02 | WTP NP. 1 | 0.0027 | 0.0249 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-08-02 | WTP NP. 1 | 0.023 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-08-02 | WTP NP. 1 | 0.49 | 1.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-08-02 | WTP NP. 1 | 0.16 | 0.4499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-08-02 | WTP NP. 1 | 3.3 | 9.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-08-02 | WTP NP. 1 | 0.36 | 0.6499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-08-02 | WTP NP. 1 | 0.46 | 2.4999 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-08-02 | WTP NP. 1 | 0.04 | 0.0749 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-08-02 | WTP NP. 1 | 0.46 | 0.6499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-08-02 | WTP NP. 1 | 0.04 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-08-02 | WTP NP. 1 | 0.16 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-08-02 | WTP NP. 1 | 0.024 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-08-02 | WTP NP. 1 | 0.59 | 0.9499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.1499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-08-02 | WTP NP. 1 | 0.029 | 0.2499 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2022-08-02 | WTP NP. 1 | 0.0021 | 0.0055 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-08-02 | WTP NP. 1 | 0.014 | 0.0449 | 28 OF 29 SOC PLUS DIOXIN (GLY TESTED SEP 9/22)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-08-05 | L3 | 1.1 |  | 8/22 BROMATE (HLKD)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 6.7 | UG/L | 10.4999 | 2022-09-02 | L3 | 1.1 |  | 9/22 BROMATE (HLKD)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-09-16 | WTP NP. 1 |  | 6.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.6 | UG/L | 60.4999 | 2022-09-23 | L1 | 0.9 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2950 | TOTAL THMS | 41.7 | UG/L | 80.4999 | 2022-09-23 | L1 | 0.47 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.3 | UG/L | 60.4999 | 2022-09-23 | L2 | 0.9 |  | 5690 BARLETTA DR_AL | 1
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2950 | TOTAL THMS | 41.1 | UG/L | 80.4999 | 2022-09-23 | L2 | 0.47 |  | 5690 BARLETTA DR_AL | 1
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 15.9 | UG/L | 10.4999 | 2022-10-07 | L3 | 2.2 |  | 10/22 BROMATE (BROMATE 15.9 UG/L, SINGLE SAMPLE OVER MCL OF 10 UG/L)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 6.5 | UG/L | 10.4999 | 2022-10-25 | L3 | 1.1 |  | 10/22 BROMATE (RE-SAMPLE) BROMATE 6.5 UG/L
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0.0024 | UG/L | 2.4999 | 2022-10-28 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0.053 | UG/L | 54.9999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0.0027 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0.024 | UG/L | 44.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0.69 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0.49 | UG/L | 249.9999 | 2022-10-28 | WTP NP. 1 |  | 1.4999 | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-07 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.5 | MG/L |  | 2023-06-07 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-07 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-13 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-06-21 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-21 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.5 | MG/L |  | 2023-06-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-21 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-06-26 | DIST |  |  | 406 NAPLE CT
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-06-26 | DIST |  |  | 601 COUNTRY CLUB RD
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-06-26 | DIST |  |  | 401 SCORE LN
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-06-26 | DIST |  |  | 801 TOLEDO CT
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-06-26 | DIST |  |  | 806 HALIFAX DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1044 | ORTHOPHOSPHATE | 2.1 | MG/L |  | 2023-06-26 | DIST |  |  | 4670 HURON BAY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-06-26 | DIST |  |  | 4670 HURON BAY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-06-26 | DIST |  |  | 2940 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.5 | MG/L |  | 2023-07-10 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-10 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-10 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-13 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.4 | MG/L |  | 2023-07-24 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-07-24 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-26 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-28 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-02 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-07 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2023-08-09 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-09 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2023-08-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-23 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-24 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.9 | UG/L | 60.4999 | 2023-08-25 | L2 | 0.9 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 48.8 | UG/L | 80.4999 | 2023-08-25 | L2 | 0.47 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.1 | UG/L | 60.4999 | 2023-08-25 | L1 | 0.9 |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 54.6 | UG/L | 80.4999 | 2023-08-25 | L1 | 0.47 |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.1 | UG/L | 60.4999 | 2023-08-25 | L3 | 0.9 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 36.6 | UG/L | 80.4999 | 2023-08-25 | L3 | 0.47 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.8 | UG/L | 60.4999 | 2023-08-25 | L4 | 0.9 |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 33.6 | UG/L | 80.4999 | 2023-08-25 | L4 | 0.47 |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-27 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-05 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.4 | MG/L |  | 2023-09-13 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-13 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-19 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-24 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-26 | WTP3 | 0.014 | 0.1499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-26 | WTP3 | 0.028 | 0.2499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-26 | WTP3 | 0.0035 | 0.0055 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-26 | WTP3 | 0.013 | 0.0449 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP3 | 0.0029 | 0.0249 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-26 | WTP3 | 0.096 | 0.1499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-26 | WTP3 | 0.053 | 0.2499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-26 | WTP3 | 0.014 | 0.1499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP3 | 0.019 | 0.0249 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-26 | WTP3 | 0.014 | 0.0449 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-26 | WTP3 | 0.044 | 0.1499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP3 | 0.0065 | 0.0249 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-26 | WTP3 | 0.0076 | 0.0149 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-26 | WTP3 | 0.035 | 0.2499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-26 | WTP6 |  | 0.0149 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP6 |  | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-26 | WTP6 |  | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-26 | WTP6 |  | 1.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-26 | WTP6 |  | 1.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-26 | WTP6 |  | 0.4499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-26 | WTP6 |  | 9.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-26 | WTP6 |  | 6.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-26 | WTP6 |  | 0.6499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-26 | WTP6 |  | 2.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-26 | WTP6 |  | 0.0749 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-26 | WTP6 |  | 0.6499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-26 | WTP6 |  | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-26 | WTP6 |  | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-26 | WTP6 |  | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-26 | WTP6 |  | 0.9499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-26 | WTP6 |  | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-26 | WTP6 |  | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-26 | WTP6 |  | 0.0055 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-26 | WTP6 |  | 0.0449 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP6 |  | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-26 | WTP6 |  | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-26 | WTP6 |  | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-26 | WTP6 |  | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP6 |  | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-26 | WTP6 |  | 0.0449 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-26 | WTP6 |  | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP6 |  | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-26 | WTP6 |  | 0.0149 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-26 | WTP6 |  | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-26 | WTP1 | 0.0023 | 0.0149 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP1 | 0.0026 | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-26 | WTP1 | 0.023 | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-26 | WTP1 | 0.25 | 1.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-26 | WTP1 | 0.49 | 1.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-26 | WTP1 | 0.16 | 0.4499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-26 | WTP1 | 3.3 | 9.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-26 | WTP1 | 4.2 | 6.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-26 | WTP1 | 0.35 | 0.6499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-26 | WTP1 | 0.46 | 2.4999 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-26 | WTP1 | 0.039 | 0.0749 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-26 | WTP1 | 0.45 | 0.6499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-26 | WTP1 | 0.04 | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-26 | WTP1 | 0.16 | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-26 | WTP1 | 0.024 | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-26 | WTP1 | 0.59 | 0.9499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-09-26 | WTP1 | 0.014 | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-09-26 | WTP1 | 0.028 | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-09-26 | WTP1 | 0.0043 | 0.0055 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-09-26 | WTP1 | 0.013 | 0.0449 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP1 | 0.0029 | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-09-26 | WTP1 | 0.096 | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-09-26 | WTP1 | 0.053 | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-09-26 | WTP1 | 0.014 | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP1 | 0.019 | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-09-26 | WTP1 | 0.014 | 0.0449 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-09-26 | WTP1 | 0.044 | 0.1499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP1 | 0.0065 | 0.0249 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-09-26 | WTP1 | 0.0077 | 0.0149 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-09-26 | WTP1 | 0.035 | 0.2499 | POE LMC
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-09-26 | WTP3 | 0.0022 | 0.0149 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-09-26 | WTP3 | 0.0026 | 0.0249 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-09-26 | WTP3 | 0.022 | 0.1499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-09-26 | WTP3 | 0.25 | 1.4999 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-26 | WTP3 | 0.49 | 1.4999 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-09-26 | WTP3 | 0.16 | 0.4499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-09-26 | WTP3 | 3.3 | 9.4999 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-09-26 | WTP3 | 4.2 | 6.4999 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-09-26 | WTP3 | 0.35 | 0.6499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-09-26 | WTP3 | 0.46 | 2.4999 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-09-26 | WTP3 | 0.038 | 0.0749 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-09-26 | WTP3 | 0.45 | 0.6499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-09-26 | WTP3 | 0.04 | 0.1499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-09-26 | WTP3 | 0.16 | 0.2499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-09-26 | WTP3 | 0.023 | 0.1499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-09-26 | WTP3 | 0.59 | 0.9499 | POE LME
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.6 | MG/L |  | 2023-09-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-08 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.9 | MG/L |  | 2023-10-11 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-11 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-12 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-20 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-10-24 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.8 | MG/L |  | 2023-10-25 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-25 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.8 | MG/L |  | 2023-11-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-08 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-12 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.9 | MG/L |  | 2023-11-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.2 | UG/L | 60.4999 | 2023-11-22 | L2 | 0.9 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 55.9 | UG/L | 80.4999 | 2023-11-22 | L2 | 0.47 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.6 | UG/L | 60.4999 | 2023-11-22 | L1 | 0.9 |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 60 | UG/L | 80.4999 | 2023-11-22 | L1 | 0.47 |  | 4738 ASHURST STREET, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.8 | UG/L | 60.4999 | 2023-11-22 | L3 | 0.9 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 36 | UG/L | 80.4999 | 2023-11-22 | L3 | 0.47 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.3 | UG/L | 60.4999 | 2023-11-22 | L4 | 0.9 |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 46.7 | UG/L | 80.4999 | 2023-11-22 | L4 | 0.47 |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-22 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-23 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-11-25 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-01 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-05 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.5 | MG/L |  | 2023-12-13 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-12-13 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-19 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-12-25 | WTP3 |  |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.5 | MG/L |  | 2023-12-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-12-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.4 | MG/L |  | 2024-01-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-01-04 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.21 | MG/L |  | 2024-01-29 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-01-29 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-30 | WTP1 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP1 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-30 | WTP3 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP3 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 2 | MG/L | 10.4999 | 2024-01-30 | WTP6 | 0.025 |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP6 |  |  | POE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2024-02-07 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-02-07 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.31 | MG/L |  | 2024-02-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-02-20 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.7 | UG/L | 60.4999 | 2024-02-23 | L5 | 0.9 |  | 4719 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 40.7 | UG/L | 80.4999 | 2024-02-23 | L5 | 0.47 |  | 4719 ASHURST STREET
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19 | UG/L | 60.4999 | 2024-02-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 37.3 | UG/L | 80.4999 | 2024-02-23 | L2 | 0.47 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.6 | UG/L | 60.4999 | 2024-02-23 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 34.8 | UG/L | 80.4999 | 2024-02-23 | L3 | 0.47 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.7 | UG/L | 60.4999 | 2024-02-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 40.5 | UG/L | 80.4999 | 2024-02-23 | L4 | 0.47 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.7 | MG/L |  | 2024-03-18 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-03-18 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.7 | MG/L |  | 2024-03-25 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-03-25 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.87 | MG/L |  | 2024-04-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-04-08 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.62 | MG/L |  | 2024-04-24 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-04-24 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.3 | MG/L |  | 2024-05-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-05-14 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2024-05-24 | L2 | 0.9 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 34.9 | UG/L | 80.4999 | 2024-05-24 | L2 | 0.75 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.4 | UG/L | 60.4999 | 2024-05-24 | L5 | 0.9 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2024-05-24 | L5 | 0.75 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.3 | UG/L | 60.4999 | 2024-05-24 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 35 | UG/L | 80.4999 | 2024-05-24 | L3 | 0.75 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.1 | UG/L | 60.4999 | 2024-05-24 | L4 | 0.9 |  | 5508 WILLOW BEND DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 42.2 | UG/L | 80.4999 | 2024-05-24 | L4 | 0.75 |  | 5508 WILLOW BEND DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.41 | MG/L |  | 2024-05-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-05-27 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.6 | MG/L |  | 2024-06-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-06-05 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1044 | ORTHOPHOSPHATE | 1.4 | MG/L |  | 2024-06-26 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-06-26 | WTP1 |  |  | BELLA LAGO WTP
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-07-02 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-07-06 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-07-06 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-07-17 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-07-23 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-07-31 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-08-03 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-08-07 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-08-08 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-08-21 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 41.5 | UG/L | 80.4999 | 2024-08-22 | L5 | 0.75 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.9 | UG/L | 60.4999 | 2024-08-22 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 33.9 | UG/L | 80.4999 | 2024-08-22 | L3 | 0.75 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.3 | UG/L | 60.4999 | 2024-08-22 | L4 | 0.9 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 56.4 | UG/L | 80.4999 | 2024-08-22 | L4 | 0.75 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.5 | UG/L | 60.4999 | 2024-08-22 | L2 | 0.9 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 51.9 | UG/L | 80.4999 | 2024-08-22 | L2 | 0.75 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.1 | UG/L | 60.4999 | 2024-08-22 | L5 | 0.9 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-08-24 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-08-27 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-09-04 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-09-05 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-09-08 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-09-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-09-23 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-09-25 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-10-08 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-10-13 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-10-16 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-10-25 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-10-26 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-10-30 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-11-02 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-11-02 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-11-13 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-11-16 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 40.7 | UG/L | 80.4999 | 2024-11-22 | L5 | 0.75 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.7 | UG/L | 60.4999 | 2024-11-22 | L2 | 0.9 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 39 | UG/L | 80.4999 | 2024-11-22 | L2 | 0.75 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.2 | UG/L | 60.4999 | 2024-11-22 | L5 | 0.9 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.3 | UG/L | 60.4999 | 2024-11-22 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 30.7 | UG/L | 80.4999 | 2024-11-22 | L3 | 0.75 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.1 | UG/L | 60.4999 | 2024-11-22 | L4 | 0.9 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 53.5 | UG/L | 80.4999 | 2024-11-22 | L4 | 0.75 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-11-27 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-11-28 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-12-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-12-07 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-12-12 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-12-25 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-12-25 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2024-12-30 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-01-15 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-01-01 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-01-04 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-01-13 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-01-17 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-01-25 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-02-05 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-02-05 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-02-07 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-02-20 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-02-20 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-02-25 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.8 | UG/L | 60.4999 | 2025-02-26 | L2 | 0.9 |  | 3543 BEAU CHENE DR - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 39.4 | UG/L | 80.4999 | 2025-02-26 | L2 | 0.75 |  | 3543 BEAU CHENE DR - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.3 | UG/L | 60.4999 | 2025-02-26 | L5 | 0.9 |  | 4719 ASHURST ST - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 47.2 | UG/L | 80.4999 | 2025-02-26 | L5 | 0.75 |  | 4719 ASHURST ST - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.2 | UG/L | 60.4999 | 2025-02-26 | L3 | 0.9 |  | 2942 EVANS DR - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 28.9 | UG/L | 80.4999 | 2025-02-26 | L3 | 0.75 |  | 2942 EVANS DR - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.3 | UG/L | 60.4999 | 2025-02-26 | L4 | 0.9 |  | WILLOW BEND TR - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 39.3 | UG/L | 80.4999 | 2025-02-26 | L4 | 0.75 |  | WILLOW BEND TR - TTHM & HAA5
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-03-03 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-03-03 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-03-10 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-14 | WTP1 | 0.025 |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO)-NITRITE J QUALIFIER
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-14 | WTP3 | 0.025 |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP3 | 0.025 |  | PEABODY WTP (ORIG. WP2 3494315 PEABODY RD.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1040 | NITRATE | 1.8 | MG/L | 10.4999 | 2025-03-14 | WTP6 | 0.025 |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP6 | 0.025 |  | HURON WTP (ORIG. WP5 3535076 HEMLOCK AVE.)
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-03-19 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-03-19 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-03-21 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-25 | WTP1 | 0 |  | BELLA LAGO WTP (WP6 ORIG. 3494429 BELLALAGO) BELLA LARGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-04-02 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-04-04 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-04-16 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-04-16 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-04-22 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-04-28 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2025-05-06 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-05-12 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-05-17 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.8 | UG/L | 60.4999 | 2025-05-23 | L2 | 0.9 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 36.8 | UG/L | 80.4999 | 2025-05-23 | L2 | 0.75 |  | 3543 BEAU CHENE DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.5 | UG/L | 60.4999 | 2025-05-23 | L6 | 0.9 |  | 548 DAVINCI PASS, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 50.5 | UG/L | 80.4999 | 2025-05-23 | L6 | 0.75 |  | 548 DAVINCI PASS, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.6 | UG/L | 60.4999 | 2025-05-23 | L7 | 0.9 |  | 1231 APOPKA LANE, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 17.3 | UG/L | 80.4999 | 2025-05-23 | L7 | 0.75 |  | 1231 APOPKA LANE, KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23 | UG/L | 60.4999 | 2025-05-23 | L5 | 0.9 |  | 4719 ASHURST STREET,KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 40 | UG/L | 80.4999 | 2025-05-23 | L5 | 0.75 |  | 4719 ASHURST STREET,KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.9 | UG/L | 60.4999 | 2025-05-23 | L3 | 0.9 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 30.1 | UG/L | 80.4999 | 2025-05-23 | L3 | 0.75 |  | 2942 EVANS DR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26 | UG/L | 60.4999 | 2025-05-23 | L4 | 0.9 |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 47.9 | UG/L | 80.4999 | 2025-05-23 | L4 | 0.75 |  | 5508 WILLOW BEND TR., KISSIMMEE
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2025-05-27 | WTP1 |  |  | 4476 SPRING BLOSSOM DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-05-27 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2025-05-30 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-05-30 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2025-06-04 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-06-05 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-06-11 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-06-21 | WTP3 |  |  | PEABODY
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-06-23 | WTP6 |  |  | HURON
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2025-06-27 | WTP1 |  |  | BELLA LAGO
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.1 | UG/L | 60.4999 | 2025-08-22 | L2 | 0.9 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 30.2 | UG/L | 80.4999 | 2025-08-22 | L2 | 0.75 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.4 | UG/L | 60.4999 | 2025-08-22 | L6 | 0.9 |  | 548 DAVINCI PASS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 46.4 | UG/L | 80.4999 | 2025-08-22 | L6 | 0.75 |  | 548 DAVINCI PASS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.6 | UG/L | 60.4999 | 2025-08-22 | L7 | 0.9 |  | 1231 APOPKA LN
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 15 | UG/L | 80.4999 | 2025-08-22 | L7 | 0.75 |  | 1231 APOPKA LN
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.1 | UG/L | 60.4999 | 2025-08-22 | L5 | 0.9 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 43.1 | UG/L | 80.4999 | 2025-08-22 | L5 | 0.75 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24 | UG/L | 60.4999 | 2025-08-22 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 28.4 | UG/L | 80.4999 | 2025-08-22 | L3 | 0.75 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.3 | UG/L | 60.4999 | 2025-08-22 | L4 | 0.9 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 43.2 | UG/L | 80.4999 | 2025-08-22 | L4 | 0.75 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 50 | UG/L | 80.4999 | 2025-11-25 | L6 | 0.75 |  | 548 DAVINCI PASS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.1 | UG/L | 60.4999 | 2025-11-25 | L2 | 0.9 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 45 | UG/L | 80.4999 | 2025-11-25 | L2 | 0.75 |  | 3543 BEAU CHENE DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.2 | UG/L | 60.4999 | 2025-11-25 | L6 | 0.9 |  | 548 DAVINCI PASS
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.5 | UG/L | 60.4999 | 2025-11-25 | L7 | 0.9 |  | 1231 APOPKA LN
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 17.9 | UG/L | 80.4999 | 2025-11-25 | L7 | 0.75 |  | 1231 APOPKA LN
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.9 | UG/L | 60.4999 | 2025-11-25 | L5 | 0.9 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 43.7 | UG/L | 80.4999 | 2025-11-25 | L5 | 0.75 |  | 4719 ASHURST ST
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24 | UG/L | 60.4999 | 2025-11-25 | L3 | 0.9 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 35.8 | UG/L | 80.4999 | 2025-11-25 | L3 | 0.75 |  | 2942 EVANS DR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.7 | UG/L | 60.4999 | 2025-11-25 | L4 | 0.9 |  | 5508 WILLOW BEND TR
3494429 | TOHO WATER AUTHORITY-POINCIANA SYSTEM | D | DBP | 2950 | TOTAL THMS | 58.5 | UG/L | 80.4999 | 2025-11-25 | L4 | 0.75 |  | 5508 WILLOW BEND TR
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0.16 | UG/L | 24.9999 | 2022-10-28 | WTP NP. 1 |  | 0.4499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 3.3 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 9.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 4.2 | UG/L | 749.9999 | 2022-10-28 | WTP NP. 1 |  | 6.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0.36 | UG/L | 449.9999 | 2022-10-28 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0.04 | UG/L | 549.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0.16 | UG/L | 7.4999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.024 | UG/L | 54.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0.59 | UG/L | 44.9999 | 2022-10-28 | WTP NP. 1 |  | 0.9499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2050 | ATRAZINE | 0.015 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0.029 | UG/L | 2.4999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0.0037 | NG/L | 0.0349 | 2022-10-28 | WTP NP. 1 |  | 0.0055 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0.014 | UG/L | 0.4499 | 2022-10-28 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0.003 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0.096 | UG/L | 74.9999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0.015 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0.02 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0.014 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.0449 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0.044 | UG/L | 0.5499 | 2022-10-28 | WTP NP. 1 |  | 0.1499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0.0062 | UG/L | 0.2499 | 2022-10-28 | WTP NP. 1 |  | 0.0249 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0.0073 | UG/L | 0.0249 | 2022-10-28 | WTP NP. 1 |  | 0.0149 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0.035 | UG/L | 2.4999 | 2022-10-28 | WTP NP. 1 |  | 0.2499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0.46 | UG/L | 249.9999 | 2022-10-28 | WTP NP. 1 |  | 2.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2037 | SIMAZINE | 0.04 | UG/L | 4.4999 | 2022-10-28 | WTP NP. 1 |  | 0.0749 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0.47 | UG/L | 6.4999 | 2022-10-28 | WTP NP. 1 |  | 0.6499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-10-28 | WTP NP. 1 | 2.56 |  | 4Q RADS (HLKD SINCE 4TH QTR RADS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-10-28 | WTP NP. 1 | 0.604 | 1.4999 | 4Q RADS (HLKD SINCE 4TH QTR RADS)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-28 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 37.9 | UG/L | 10.4999 | 2022-11-09 | L3 | 1.1 |  | 11/22 BROMATE (BROMATE 37.9 UG/L, MCL = 10 UG/L, OVER 3 TIMES MCL) HLKD
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.9 | UG/L | 10.4999 | 2022-11-23 | L3 | 1.1 |  | 11/22 BROMATE (MARKED RESAMPLE)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-01-03 | WTP NP. 1 | 0.16 | 0.4499 | PARTIAL SOC (2032, 2034) GLYPHOSATE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.1 | UG/L | 10.4999 | 2023-01-06 | L3 |  |  | POE BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-31 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2023-01-31 | WTP NP. 1 | 0.025 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-01-31 | WTP NP. 1 | 0.029 | 0.2499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-01-31 | WTP NP. 1 | 0.0017 | 0.0055 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-01-31 | WTP NP. 1 | 0.014 | 0.0449 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-01-31 | WTP NP. 1 | 0.003 | 0.0249 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-01-31 | WTP NP. 1 | 0.096 | 0.1499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-01-31 | WTP NP. 1 | 0.053 | 0.2499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-01-31 | WTP NP. 1 | 0.015 | 0.1499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0.024 | UG/L | 0.2499 | 2023-01-31 | WTP NP. 1 | 0.019 | 0.0249 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-01-31 | WTP NP. 1 | 0.014 | 0.0449 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-01-31 | WTP NP. 1 | 0.044 | 0.1499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-01-31 | WTP NP. 1 | 0.0065 | 0.0249 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-01-31 | WTP NP. 1 | 0.0076 | 0.0149 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-01-31 | WTP NP. 1 | 0.035 | 0.2499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-01-31 | WTP NP. 1 | 0.0023 | 0.0149 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-01-31 | WTP NP. 1 | 0.0027 | 0.0249 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-01-31 | WTP NP. 1 | 0.023 | 0.1499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-01-31 | WTP NP. 1 | 0.69 | 1.4999 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-01-31 | WTP NP. 1 | 0.49 | 1.4999 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-01-31 | WTP NP. 1 | 0.16 | 0.4499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-01-31 | WTP NP. 1 | 3.3 | 9.4999 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-01-31 | WTP NP. 1 | 4.2 | 6.4999 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-01-31 | WTP NP. 1 | 0.36 | 0.6499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-01-31 | WTP NP. 1 | 0.46 | 2.4999 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-01-31 | WTP NP. 1 | 0.47 | 0.6499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-01-31 | WTP NP. 1 | 0.04 | 0.1499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-01-31 | WTP NP. 1 | 0.16 | 0.2499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-01-31 | WTP NP. 1 | 0.024 | 0.1499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-01-31 | WTP NP. 1 | 0.59 | 0.9499 | 2037, 2050 J QUALIFIER. 2306 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 6.4 | UG/L | 10.4999 | 2023-02-10 | L3 | 1.1 |  | 2/23 BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP NP. 1 | 2 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP NP. 1 | 0.35 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-22 | WTP NP. 1 | 0.33 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-22 | WTP NP. 1 | 0.11 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP NP. 1 | 0.44 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-22 | WTP NP. 1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-22 | WTP NP. 1 | 0.3 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP NP. 1 | 0.12 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-22 | WTP NP. 1 | 0.29 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP NP. 1 | 0.27 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP NP. 1 | 0.3 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-22 | WTP NP. 1 | 0.27 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP NP. 1 | 0.28 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP NP. 1 | 0.44 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP NP. 1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-22 | WTP NP. 1 | 0.28 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-22 | WTP NP. 1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-22 | WTP NP. 1 | 0.26 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-22 | WTP NP. 1 | 0.4 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-22 | WTP NP. 1 | 0.28 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-22 | WTP NP. 1 | 0.23 | 0.5499 | STYRENE J QUALIFIER, BIASED HIGH, ACCEPTED_JMF
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.3 | UG/L | 10.4999 | 2023-03-15 | L3 | 1.1 |  | 3/23 BROMATE (HLKD)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 11 | UG/L | 10.4999 | 2023-04-14 | L3 | 2.2 |  | BROMATE EXCEEDANCE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-21 | WTP NP. 1 |  | 0.4499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-21 | WTP NP. 1 |  | 6.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP NP. 1 | 0.019 | 0.0249 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-04-21 | WTP NP. 1 | 0.014 | 0.0449 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-04-21 | WTP NP. 1 | 0.44 | 0.1499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP NP. 1 | 0.0064 | 0.0249 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-04-21 | WTP NP. 1 | 0.0076 | 0.0149 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-04-21 | WTP NP. 1 | 0.035 | 0.2499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-04-21 | WTP NP. 1 | 0.0023 | 0.0149 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP NP. 1 | 0.0027 | 0.0249 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-04-21 | WTP NP. 1 | 0.023 | 0.1499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP NP. 1 | 0.25 | 1.4999 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-21 | WTP NP. 1 | 0.49 | 1.4999 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-04-21 | WTP NP. 1 | 0.16 | 0.4499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-04-21 | WTP NP. 1 | 3.3 | 9.4999 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-04-21 | WTP NP. 1 | 4.2 | 6.4999 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-04-21 | WTP NP. 1 | 0.45 | 0.6499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-04-21 | WTP NP. 1 | 0.46 | 2.4999 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-04-21 | WTP NP. 1 | 0.039 | 0.0749 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-04-21 | WTP NP. 1 | 0.46 | 0.6499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-04-21 | WTP NP. 1 | 0.04 | 0.1499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-04-21 | WTP NP. 1 | 0.16 | 0.2499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.055 | UG/L | 54.9999 | 2023-04-21 | WTP NP. 1 | 0.024 | 0.1499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-04-21 | WTP NP. 1 | 0.59 | 0.9499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-04-21 | WTP NP. 1 | 0.014 | 0.1499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-04-21 | WTP NP. 1 | 0.029 | 0.2499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-04-21 | WTP NP. 1 | 0.00087 | 0.0055 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-04-21 | WTP NP. 1 | 0.013 | 0.0449 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-04-21 | WTP NP. 1 | 0.003 | 0.0249 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-21 | WTP NP. 1 | 0.096 | 0.1499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-04-21 | WTP NP. 1 | 0.053 | 0.2499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-04-21 | WTP NP. 1 | 0.014 | 0.1499 | 2042 DETECT
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 11.1 | UG/L | 10.4999 | 2023-05-12 | L3 | 1.1 |  | BROMATE EXCEEDANCE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.5 | UG/L | 10.4999 | 2023-06-09 | L3 | 1.1 |  | BROMATE POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 9.1 | UG/L | 10.4999 | 2023-08-04 | L3 | 1.1 |  | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 10.3 | UG/L | 10.4999 | 2023-09-08 | L3 | 1.1 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.6 | UG/L | 10.4999 | 2023-10-06 | L3 | 1.1 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-24 | WTP NP. 1 | 0.0022 | 0.0149 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-24 | WTP NP. 1 | 0.0026 | 0.0249 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-24 | WTP NP. 1 | 0.022 | 0.1499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-24 | WTP NP. 1 | 0.25 | 1.4999 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-24 | WTP NP. 1 | 0.49 | 1.4999 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-24 | WTP NP. 1 | 0.16 | 0.4499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-24 | WTP NP. 1 | 4.2 | 6.4999 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-24 | WTP NP. 1 | 0.038 | 0.0749 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.9 | UG/L | 10.4999 | 2023-07-07 | L3 | 1.1 |  | BROMATE POE (SUNBRIDGE)
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28 | UG/L | 60.4999 | 2023-09-25 | L1 | 0.9 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2950 | TOTAL THMS | 50.1 | UG/L | 80.4999 | 2023-09-25 | L1 | 0.47 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.6 | UG/L | 60.4999 | 2023-09-25 | L2 | 0.9 |  | 5690 BARLETTA DR | 1
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2950 | TOTAL THMS | 48.2 | UG/L | 80.4999 | 2023-09-25 | L2 | 0.47 |  | 5690 BARLETTA DR | 1
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-24 | WTP NP. 1 | 0.35 | 0.6499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-24 | WTP NP. 1 | 0.46 | 2.4999 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-24 | WTP NP. 1 | 0.45 | 0.6499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-24 | WTP NP. 1 | 0.04 | 0.1499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-24 | WTP NP. 1 | 0.16 | 0.2499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0.034 | UG/L | 54.9999 | 2023-10-24 | WTP NP. 1 | 0.023 | 0.1499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-24 | WTP NP. 1 | 0.59 | 0.9499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-24 | WTP NP. 1 | 0.014 | 0.1499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-24 | WTP NP. 1 | 0.028 | 0.2499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-10-24 | WTP NP. 1 | 0.0029 | 0.0055 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-24 | WTP NP. 1 | 0.013 | 0.0449 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-24 | WTP NP. 1 | 0.0029 | 0.0249 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-24 | WTP NP. 1 | 0.096 | 0.1499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-24 | WTP NP. 1 | 0.059 | 0.2499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-24 | WTP NP. 1 | 0.014 | 0.1499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-24 | WTP NP. 1 | 0.019 | 0.0249 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-24 | WTP NP. 1 | 0.014 | 0.0449 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-24 | WTP NP. 1 | 0.044 | 0.1499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-24 | WTP NP. 1 | 0.0065 | 0.0249 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-24 | WTP NP. 1 | 0.0076 | 0.0149 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-24 | WTP NP. 1 | 0.035 | 0.2499 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.1 | UG/L | 10.4999 | 2023-11-03 | L3 | 1.1 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.1 | UG/L | 10.4999 | 2023-12-01 | L3 | 1.1 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1040 | NITRATE | 0.047 | MG/L | 10.4999 | 2024-01-30 | WTP NP. 1 | 0.025 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-30 | WTP NP. 1 |  |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.3 | UG/L | 10.4999 | 2024-02-02 | L3 | 1.1 |  | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP NP. 1 |  | 0.5499 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.3 | UG/L | 10.4999 | 2024-03-01 | L3 | 1.1 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-03-29 | WTP NP. 1 | 0.005 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-03-29 | WTP NP. 1 | 0.0086 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2024-03-29 | WTP NP. 1 | 0.025 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-29 | WTP NP. 1 | 0.025 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1005 | ARSENIC | 0.0006 | MG/L | 0.0104 | 2024-03-29 | WTP NP. 1 | 0.0005 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2024-03-29 | WTP NP. 1 | 0.0024 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-03-29 | WTP NP. 1 | 0.00067 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-03-29 | WTP NP. 1 | 0.0048 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2024-03-29 | WTP NP. 1 | 0.015 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-03-29 | WTP NP. 1 | 0.00025 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-03-29 | WTP NP. 1 | 0.00014 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-03-29 | WTP NP. 1 | 0.002 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-03-29 | WTP NP. 1 | 0.00083 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1052 | SODIUM | 38.7 | MG/L | 160.4999 | 2024-03-29 | WTP NP. 1 | 0.59 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-03-29 | WTP NP. 1 | 0.00088 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-03-29 | WTP NP. 1 | 0.00019 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-03-29 | WTP NP. 1 | 0.00021 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2024-03-29 | WTP NP. 1 | 0.19 |  | SUNBRIDGE - CYANIDE J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1017 | CHLORIDE | 53.2 | MG/L | 250.4999 | 2024-03-29 | WTP NP. 1 | 2.5 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1022 | COPPER | 0.0018 | MG/L | 1.4999 | 2024-03-29 | WTP NP. 1 | 0.00093 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1025 | FLUORIDE | 0.17 | MG/L | 2.0499 | 2024-03-29 | WTP NP. 1 | 0.015 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-03-29 | WTP NP. 1 | 0.021 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1032 | MANGANESE | 0.0014 | MG/L | 0.0549 | 2024-03-29 | WTP NP. 1 | 0.0013 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-03-29 | WTP NP. 1 | 0.0022 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1055 | SULFATE | 21.4 | MG/L | 250.4999 | 2024-03-29 | WTP NP. 1 | 2.5 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-03-29 | WTP NP. 1 | 0.0077 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2024-03-29 | WTP NP. 1 | 5 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-03-29 | WTP NP. 1 | 1 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.6 | LN(10) |  | 2024-03-29 | WTP NP. 1 | 0.1 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 324 | MG/L | 500.4999 | 2024-03-29 | WTP NP. 1 | 5 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-03-29 | WTP NP. 1 | 0.099 |  | SUNBRIDGE - ALUMINUM J QUALIFIER
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 5.9 | UG/L | 10.4999 | 2024-04-05 | L3 | 1.1 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-04-30 | WTP NP. 1 |  | 0.0149 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-04-30 | WTP NP. 1 |  | 0.0249 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-04-30 | WTP NP. 1 |  | 9.4999 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-24 | WTP NP. 1 | 3.3 | 9.4999 | E87605/DIOXIN (2042 HEX.... 0.034, RDL = 0.1) ENDOTHALL 3.3 U, MS/MSD=53/40% RECOVERY - AT LOWEST RECOVERY 40%, ENDO IS 8.25 U AT 100%, WHICH IS < RDL OF 9 UG/L ACCEPTABLE. J QUAL ON PG 25 OF 37.
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-04-30 | WTP NP. 1 |  | 0.1499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-04-30 | WTP NP. 1 |  | 1.4999 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-04-30 | WTP NP. 1 |  | 1.4999 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-04-30 | WTP NP. 1 |  | 0.4499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-04-30 | WTP NP. 1 |  | 6.4999 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-04-30 | WTP NP. 1 |  | 0.6499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-04-30 | WTP NP. 1 |  | 2.4999 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-04-30 | WTP NP. 1 |  | 0.0749 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-04-30 | WTP NP. 1 |  | 0.6499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-04-30 | WTP NP. 1 |  | 0.1499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-04-30 | WTP NP. 1 |  | 0.2499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-04-30 | WTP NP. 1 |  | 0.1499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-04-30 | WTP NP. 1 |  | 0.9499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-04-30 | WTP NP. 1 |  | 0.1499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-04-30 | WTP NP. 1 |  | 0.2499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2024-04-30 | WTP NP. 1 |  | 0.0055 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-04-30 | WTP NP. 1 |  | 0.0449 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-04-30 | WTP NP. 1 |  | 0.0249 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-04-30 | WTP NP. 1 |  | 0.1499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-04-30 | WTP NP. 1 |  | 0.2499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-04-30 | WTP NP. 1 |  | 0.1499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-04-30 | WTP NP. 1 |  | 0.0249 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-04-30 | WTP NP. 1 |  | 0.0449 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-04-30 | WTP NP. 1 |  | 0.1499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-04-30 | WTP NP. 1 |  | 0.0249 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-04-30 | WTP NP. 1 |  | 0.0149 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-04-30 | WTP NP. 1 |  | 0.2499 | POE-SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.6 | UG/L | 10.4999 | 2024-05-03 | L3 | 1.1 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.14 | PCI/L | 15.4999 | 2024-05-21 | WTP NP. 1 | 0.977 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4030 | RADIUM-228 | 0.775 | PCI/L | 2.4999 | 2024-05-21 | WTP NP. 1 | 0.775 | 1.4999 | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.14 | PCI/L | 15.4999 | 2024-05-21 | WTP NP. 1 | 0.977 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-05-21 | WTP NP. 1 | 0.775 | 1.4999 | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 9.5 | UG/L | 10.4999 | 2024-06-07 | L3 | 1.1 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.2 | UG/L | 10.4999 | 2024-08-02 | L3 | 1.1 |  | SUNBRIDGE POE - BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7 | UG/L | 10.4999 | 2024-09-06 | L3 | 1.1 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30 | UG/L | 60.4999 | 2024-09-24 | L1 | 0.9 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2950 | TOTAL THMS | 53.4 | UG/L | 80.4999 | 2024-09-24 | L1 | 0.75 |  | 2722 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.9 | UG/L | 60.4999 | 2024-09-24 | L2 | 0.9 |  | 5690 BARLETTA DR | 1
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2950 | TOTAL THMS | 56.9 | UG/L | 80.4999 | 2024-09-24 | L2 | 0.75 |  | 5690 BARLETTA DR | 1
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.4 | UG/L | 10.4999 | 2024-10-04 | L3 | 1.1 |  | SUNBRIDGE - BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.1 | UG/L | 10.4999 | 2024-11-01 | L3 | 1.1 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.2 | UG/L | 10.4999 | 2024-12-06 | L3 | 1.1 |  | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-01-28 | WTP NP. 1 |  | 0.5499 | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.6 | UG/L | 10.4999 | 2025-03-07 | L3 | 1.1 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2025-03-14 | WTP NP. 1 | 0.025 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-14 | WTP NP. 1 | 0 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7 | UG/L | 10.4999 | 2025-04-04 | L3 | 1.1 |  | SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.8 | UG/L | 10.4999 | 2025-05-02 | L3 | 1.1 |  | POE SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 5.1 | UG/L | 10.4999 | 2025-06-06 | L3 | 1.1 |  | POE - BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 5.9 | UG/L | 10.4999 | 2025-09-05 | L3 | 1.1 |  | BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.2 | UG/L | 60.4999 | 2025-09-23 | L1 | 0.9 |  | 2720 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 2950 | TOTAL THMS | 52.4 | UG/L | 80.4999 | 2025-09-23 | L1 | 0.75 |  | 2720 MATERA DR | 3
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 1011 | BROMATE | 6.2 | UG/L | 10.4999 | 2025-10-03 | L3 | 1.1 |  | BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | D | DBP | 1011 | BROMATE | 6.2 | UG/L | 10.4999 | 2025-11-07 | L3 | 2.4 |  | POE BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 6.1 | UG/L | 10.4999 | 2025-12-05 | L3 | 2.4 |  | BROMATE - SUNBRIDGE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.6 | UG/L | 10.4999 | 2025-08-01 | L3 | 1.1 |  | POE - BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 8.4 | UG/L | 10.4999 | 2025-01-03 | L3 | 1.1 |  | POE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 5.9 | UG/L | 10.4999 | 2025-01-09 | L3 | 2.4 |  | BROMATE
3494439 | TWA SUNBRIDGE WATER TREATMENT PLANT | N | DBP | 1011 | BROMATE | 7.9 | UG/L | 10.4999 | 2025-02-14 | L3 | 1.1 |  | POE SUNBRIDGE

## Seminole
PWS ID | Mailing Name | Sample Type | Contam Group | Contam Code | Contam Desc | Results | UOM | MCL | Sample Date | Loc Code | MDL | RDL | Remark | Max Qtr
3594125 | TRUE LIFE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-06-20 | AAA
3594125 | TRUE LIFE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-20 | AAA
3594125 | TRUE LIFE CHURCH | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-19 | AAA | 0.2 |  | SAMPLED AT MENS RESTROOM-SAMPLE TYPE IS ALSO MARKED AS PT. OF ENTRY TO DISTRIBUTION SYSTEM (?) - ENT'D WITH SAMPLE TYPE "S" PENDING EVALUATION. (THE SYS. NEEDS BOTH NN FROM POE/D.)
3594125 | TRUE LIFE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-03-21 | AAA | 0.2 |  | 2022 MAKEUP RCVD 3/27/23 FW
3594125 | TRUE LIFE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-21 | AAA | 0.2 |  | 2022 MAKEUP RCVD 3/27/23 FW
3594125 | TRUE LIFE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-09-24 | AAA |  |  | 2023 N/N SAMPLING
3594125 | TRUE LIFE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-09-24 | AAA |  |  | 2023 N/N SAMPLING
3594125 | TRUE LIFE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-01 | AAA |  |  | POE
3594125 | TRUE LIFE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-01 | AAA |  |  | POE
3594125 | TRUE LIFE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-01-31 | AAA |  |  | POE 2024 MAKEUP SAMPLES
3594125 | TRUE LIFE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-31 | AAA |  |  | POE 2024 MAKEUP SAMPLES
3594125 | TRUE LIFE CHURCH | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-08-07 | AAA | 0.1 |  | 2025 N/N
3594125 | TRUE LIFE CHURCH | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-07 | AAA | 0.1 |  | 2025 N/N
3594138 | RIGHTWAY FUELS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-09 | AAA | 0.2
3594138 | RIGHTWAY FUELS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-09 | AAA | 0.2
3594138 | RIGHTWAY FUELS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-02-20 | AAA | 0.2 |  | 2022 MAKEUP SAMPLES
3594138 | RIGHTWAY FUELS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-02-20 | AAA | 0.2 |  | 2022 MAKEUP SAMPLES
3594138 | RIGHTWAY FUELS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-11-03 | AAA |  |  | POE
3594138 | RIGHTWAY FUELS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-03 | AAA |  |  | POE
3594138 | RIGHTWAY FUELS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-11-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594138 | RIGHTWAY FUELS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-03 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594138 | RIGHTWAY FUELS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-07-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594138 | RIGHTWAY FUELS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-15 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594138 | RIGHTWAY FUELS | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-09-07 | AAA | 0.024 |  | 2025 N/N
3594138 | RIGHTWAY FUELS | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-09-07 | AAA | 0.0034 |  | 2025 N/N
3594141 | CIRCLE K #9746 | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2021-12-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594141 | CIRCLE K #9746 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-22 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594141 | CIRCLE K #9746 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-27 | AAA | 0.024
3594141 | CIRCLE K #9746 | N | INOR | 1041 | NITRITE | 0.1 | MG/L | 1.4999 | 2022-10-27 | AAA | 0.0034
3594141 | CIRCLE K #9746 | R | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-03-08 | AAA |  |  | RAW
3594141 | CIRCLE K #9746 | R | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-03-08 | AAA |  |  | RAW
3594141 | CIRCLE K #9746 | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2025-01-30 | AAA | 0.024 |  | POE
3594141 | CIRCLE K #9746 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-30 | AAA |  |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-11-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594148 | SPEEDY FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-11-29 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594148 | SPEEDY FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594148 | SPEEDY FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-31 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594148 | SPEEDY FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-11-05 | AAA |  |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-05 | AAA |  |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-11-05 | AAA |  |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-05 | AAA |  |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1040 | NITRATE | 0.081 | MG/L | 10.4999 | 2024-11-17 | AAA | 0.024 |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-17 | AAA |  |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1040 | NITRATE | 0.063 | MG/L | 10.4999 | 2025-11-17 | AAA | 0.024 |  | POE
3594148 | SPEEDY FOOD MART | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-11-17 | AAA |  |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-07-29 | AAA | 0.048 |  | NN BOTH HAVE J4 QUALIFIERS (NITRATE MS/MSD 197/197 % RECOVERIES, NITRITE MS/MSD 0/0 % RECOVERIES) ENTERED NITRATE (SINCE BIASED HIGH) BUT DID NOT ENTER NITRITE SINCE HAD 0% RECOVERY. BB
3594156 | CIRCLE K #2655 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-07-29 | AAA | 0.0075 |  | NN BOTH HAVE J4 QUALIFIERS (NITRATE MS/MSD 197/197 % RECOVERIES, NITRITE MS/MSD 0/0 % RECOVERIES) ENTERED NITRATE (SINCE BIASED HIGH) BUT DID NOT ENTER NITRITE SINCE HAD 0% RECOVERY. BB
3594156 | CIRCLE K #2655 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-12-22 | AAA |  |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-22 | AAA |  |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1040 | NITRATE | 0.086 | MG/L | 10.4999 | 2023-10-24 | AAA | 0.024 |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-24 | AAA |  |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-11 | AAA |  |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-11 | AAA |  |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-12 | AAA |  |  | POE
3594156 | CIRCLE K #2655 | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-12 | AAA |  |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1040 | NITRATE | 0.976 | MG/L | 10.4999 | 2021-09-13 | AAA |  |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-09-13 | AAA |  |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-08-30 | AAA |  |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-30 | AAA |  |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-08-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-08-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1040 | NITRATE | 0.17 | MG/L | 10.4999 | 2023-08-01 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-01 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1040 | NITRATE | 0.17 | MG/L | 10.4999 | 2023-08-01 | AAA | 0.024 |  | POE - NO2/NO3
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-01 | AAA | 0.0034 |  | POE - NO2/NO3
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1040 | NITRATE | 0.082 | MG/L | 10.4999 | 2024-07-30 | AAA | 0.024 |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-30 | AAA |  |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1040 | NITRATE | 0.068 | MG/L | 10.4999 | 2025-05-15 | AAA | 0.024 |  | POE
3594168 | QUICK SERV CONVENIENCE STORE | N | INOR | 1041 | NITRITE | 0.073 | MG/L | 1.4999 | 2025-05-15 | AAA | 0.0034 |  | POE
3594166 | FOREST CITY CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-10-27 | AAA |  |  | POE
3594166 | FOREST CITY CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-10-27 | AAA |  |  | POE
3594166 | FOREST CITY CENTER | N | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2024-08-21 | AAA
3594166 | FOREST CITY CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-21 | AAA
3594166 | FOREST CITY CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-20 | AAA |  |  | POE
3594166 | FOREST CITY CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-20 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-26 | AAA | 0.44 | 0.5499 | XYLENES (HLKD). 11/10/21 EMAIL FROM ALLEN RAINEY: "OPERATOR TIMELY TOOK SAMPLE IN SEPT. 2021. LAB INDICATES THAT SAMPLE WAS INCORRECTLY LOGGED AND ANALYZED FOR DBPS"
3594166 | FOREST CITY CENTER | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-12-27 | AAA | 0.025
3594166 | FOREST CITY CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-27 | AAA | 0.025
3594166 | FOREST CITY CENTER | N | INOR | 1040 | NITRATE | 7.8 | MG/L | 10.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594166 | FOREST CITY CENTER | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594180 | DOUBLE R SCHOOL | N | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2021-11-14 | AAA | 0.0075 |  | NITRATE OK. NITRITE OVER THE 48-HR HOLDING TIME. SMP DATE/TM TO ANALY DATE/TM 11/14/21 10:05 AM TO 11/16/21 18.14.
3594180 | DOUBLE R SCHOOL | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-12-20 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594180 | DOUBLE R SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-12-20 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594180 | DOUBLE R SCHOOL | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.87 | UG/L | 60.4999 | 2022-09-01 | L1 | 0.98 |  | 721 INSIDE FOUNTAIN | 3
3594180 | DOUBLE R SCHOOL | D | DBP | 2950 | TOTAL THMS | 18.01 | UG/L | 80.4999 | 2022-09-01 | L1 | 0.39 |  | 721 INSIDE FOUNTAIN | 3
3594180 | DOUBLE R SCHOOL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-10-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594180 | DOUBLE R SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-10-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3594180 | DOUBLE R SCHOOL | N | WQP | 1064 | CONDUCTIVITY | 453 | MG/L | 0 | 2022-11-15 | AAA |  |  | POE_WQP SET #1_FRWA USED THEIR OWN TESTING KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-11-15 | AAA |  |  | POE_WQP SET #1_FRWA USED THEIR OWN TESTING KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23 |  |  | 2022-11-15 | AAA |  |  | POE_WQP SET #1_FRWA USED THEIR OWN TESTING KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1016 | CALCIUM | 120 | MG/L |  | 2022-11-15 | AAA |  |  | POE_WQP SET #1_FRWA USED THEIR OWN TESTING KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1929 | ALKALINITY - CARBONATE | 100 | MG/L | 0 | 2022-11-15 | AAA |  |  | POE_WQP SET #1_FRWA USED THEIR OWN TESTING KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-11-15 | AAA |  |  | DISTRIBUTION_WQP SET #1_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1929 | ALKALINITY - CARBONATE | 100 | MG/L | 0 | 2022-11-15 | AAA |  |  | DISTRIBUTION_WQP SET #1_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 19.1 |  |  | 2022-11-15 | AAA |  |  | DISTRIBUTION_WQP SET #1_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1016 | CALCIUM | 110 | MG/L |  | 2022-11-15 | AAA |  |  | DISTRIBUTION_WQP SET #1_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1064 | CONDUCTIVITY | 390 | MG/L | 0 | 2022-11-15 | AAA |  |  | DISTRIBUTION_WQP SET #1_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1924 | pH (FIELD) | 7.28 | LN(10) |  | 2022-12-14 | AAA |  |  | POE_WQP SET #2__ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1929 | ALKALINITY - CARBONATE | 110 | MG/L | 0 | 2022-12-14 | AAA |  |  | POE_WQP SET #2__ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1064 | CONDUCTIVITY | 396 | MG/L | 0 | 2022-12-14 | AAA |  |  | POE_WQP SET #2__ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23 |  |  | 2022-12-14 | AAA |  |  | POE_WQP SET #2__ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1016 | CALCIUM | 120 | MG/L |  | 2022-12-14 | AAA |  |  | POE_WQP SET #2__ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2022-12-14 | AAA |  |  | DISTRIBUTION_WQP SET #2_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1929 | ALKALINITY - CARBONATE | 100 | MG/L | 0 | 2022-12-14 | AAA |  |  | DISTRIBUTION_WQP SET #2_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.3 |  |  | 2022-12-14 | AAA |  |  | DISTRIBUTION_WQP SET #2_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1016 | CALCIUM | 110 | MG/L |  | 2022-12-14 | AAA |  |  | DISTRIBUTION_WQP SET #2_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | WQP | 1064 | CONDUCTIVITY | 420 | MG/L | 0 | 2022-12-14 | AAA |  |  | DISTRIBUTION_WQP SET #2_LOCATION : PRESCHOOL OUTSIDE FOUNTAIN_ FRWA USED THEIR OWN TEST KITS_CC
3594180 | DOUBLE R SCHOOL | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-12-19 | AAA | 0.9 | 0.9499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-12-19 | AAA | 0.0096 | 0.1499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-12-19 | AAA | 0.0096 | 0.2499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-12-19 | AAA | 0.012 | 0.0249 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-12-19 | AAA | 0.02 | 0.0249 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-12-19 | AAA | 0.01 | 0.0149 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-12-19 | AAA | 0.02 | 0.2499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-12-19 | AAA | 0.019 | 0.6499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-12-19 | AAA | 0.0096 | 0.1499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-12-19 | AAA | 0.0096 | 0.1499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-12-19 | AAA | 0.0096 | 0.1499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-12-19 | AAA | 0.0038 | 0.0249 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-12-19 | AAA | 0.0042 | 0.0449 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-12-19 | AAA | 0.002
3594180 | DOUBLE R SCHOOL | N | INOR | 1010 | BARIUM | 0.012 | MG/L | 2.4999 | 2022-12-19 | AAA | 0.002
3594180 | DOUBLE R SCHOOL | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-12-19 | AAA | 0.001
3594180 | DOUBLE R SCHOOL | N | INOR | 1020 | CHROMIUM | 0.0022 | MG/L | 0.1499 | 2022-12-19 | AAA | 0.001
3594180 | DOUBLE R SCHOOL | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-12-19 | AAA | 0.005
3594180 | DOUBLE R SCHOOL | N | INOR | 1025 | FLUORIDE | 0.06 | MG/L | 4.0499 | 2022-12-19 | AAA | 0.05
3594180 | DOUBLE R SCHOOL | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-12-19 | AAA | 0.001
3594180 | DOUBLE R SCHOOL | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-12-19 | AAA | 0.0002
3594180 | DOUBLE R SCHOOL | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-12-19 | AAA | 0.002
3594180 | DOUBLE R SCHOOL | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-12-19 | AAA | 0.002
3594180 | DOUBLE R SCHOOL | N | INOR | 1052 | SODIUM | 25 | MG/L | 160.4999 | 2022-12-19 | AAA | 0.1
3594180 | DOUBLE R SCHOOL | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-12-19 | AAA | 0.001
3594180 | DOUBLE R SCHOOL | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-12-19 | AAA | 0.0005
3594180 | DOUBLE R SCHOOL | N | INOR | 1085 | THALLIUM | 0.0011 | MG/L | 0.0025 | 2022-12-19 | AAA | 0.0005
3594180 | DOUBLE R SCHOOL | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-12-19 | AAA | 0.11 | 1.4999 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-12-19 | AAA | 0.4 | 0.4499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-12-19 | AAA | 6 | 6.4999 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-12-19 | AAA | 2 | 2.4999 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-12-19 | AAA | 0.029 | 0.0749 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-12-19 | AAA | 0.096 | 0.6499 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | INOR | 1025 | FLUORIDE | 0.06 | MG/L | 4.0499 | 2022-12-19 | AAA | 0.05
3594180 | DOUBLE R SCHOOL | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-12-19 | AAA | 0.5 | 0.5499 | J3 QUALIFIER ON 2964 DIC. ACCEPTED % RECOVERY._CC
3594180 | DOUBLE R SCHOOL | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-12-19 | AAA | 0.0095 | 0.0149 | MISSING LINDANE AND PCB, ENDOTHALL J3, 6 Q QUALIFIERS
3594180 | DOUBLE R SCHOOL | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-12-19 | AAA | 1.61
3594180 | DOUBLE R SCHOOL | N | RAD | 4020 | RADIUM-226 | 1.43 | PCI/L | 3.4999 | 2022-12-19 | AAA | 0.0947 | 1.4999
3594180 | DOUBLE R SCHOOL | N | RAD | 4030 | RADIUM-228 | 0.72 | PCI/L | 2.4999 | 2022-12-19 | AAA | 0.398 | 1.4999
3594180 | DOUBLE R SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-01-30 | AAA |  | 1.4999 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-01-30 | AAA |  | 9.4999 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-01-30 | AAA |  | 0.6499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-01-30 | AAA |  | 0.0749 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-01-30 | AAA |  | 0.6499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-01-30 | AAA |  | 0.1499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-01-30 | AAA |  | 0.2499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-01-30 | AAA |  | 0.1499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-01-30 | AAA |  | 0.2499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-01-30 | AAA |  | 0.1499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-01-30 | AAA |  | 0.2499 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-01-30 | AAA |  | 0.0249 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-01-30 | AAA |  | 0.0449 | MAKEUP SAMPLES FROM LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-02-10 | AAA |  | 0.0149 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-02-10 | AAA |  | 0.0249 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-02-10 | AAA |  | 0.1499 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-02-10 | AAA |  | 1.4999 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-02-10 | AAA |  | 0.1499 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-02-10 | AAA |  | 0.0449 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-02-10 | AAA |  | 0.0249 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-02-10 | AAA |  | 0.1499 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-02-10 | AAA |  | 0.1499 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-02-10 | AAA |  | 0.2499 | MAKEUP SAMPLES FROM THE LATE REPORTING
3594180 | DOUBLE R SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-09-11 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3594180 | DOUBLE R SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-09-11 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-11-05 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-11-05 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1040 | NITRATE | 0.087 | MG/L | 10.4999 | 2024-12-04 | AAA | 0.024 |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-04 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-12-05 | AAA | 0.48 | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1040 | NITRATE | 0.06 | MG/L | 10.4999 | 2025-08-28 | AAA | 0.024 |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1005 | ARSENIC | 0.0006 | MG/L | 0.0104 | 2025-08-28 | AAA | 0.00025 |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1010 | BARIUM | 0.014 | MG/L | 2.4999 | 2025-08-28 | AAA | 0.003 |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1052 | SODIUM | 28 | MG/L | 160.4999 | 2025-08-28 | AAA | 0.8 |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-08-28 | AAA |  |  | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-08-28 | AAA |  | 0.5499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-08-28 | AAA |  | 0.0149 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-08-28 | AAA |  | 0.0249 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-08-28 | AAA |  | 0.1499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-08-28 | AAA |  | 1.4999 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-08-28 | AAA |  | 1.4999 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-08-28 | AAA |  | 0.4499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-08-28 | AAA |  | 9.4999 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-08-28 | AAA |  | 6.4999 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-08-28 | AAA |  | 0.6499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-08-28 | AAA |  | 2.4999 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-08-28 | AAA |  | 0.0749 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-08-28 | AAA |  | 0.6499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-08-28 | AAA |  | 0.9499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-08-28 | AAA |  | 0.1499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-08-28 | AAA |  | 0.2499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-08-28 | AAA |  | 0.1499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-08-28 | AAA |  | 0.1499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-08-28 | AAA |  | 0.2499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-08-28 | AAA |  | 0.0449 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-08-28 | AAA |  | 0.0249 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-08-28 | AAA |  | 0.1499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-08-28 | AAA |  | 0.2499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-08-28 | AAA |  | 0.1499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-08-28 | AAA |  | 0.0249 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-08-28 | AAA |  | 0.0449 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-08-28 | AAA |  | 0.1499 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-08-28 | AAA |  | 0.0249 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-08-28 | AAA |  | 0.0149 | POE
3594180 | DOUBLE R SCHOOL | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-08-28 | AAA |  | 0.2499 | POE
3594180 | DOUBLE R SCHOOL | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.96 | UG/L | 60.4999 | 2025-09-01 | L1 | 0.98 |  | 721 INSIDE FOUNTAIN - TTHM SUBCONTRACTED TO E2535; HAA5 SUBCONTRACTED TO E84589 | 3
3594180 | DOUBLE R SCHOOL | M | DBP | 2950 | TOTAL THMS | 16.58 | UG/L | 80.4999 | 2025-09-01 | L1 | 0.44 |  | 721 INSIDE FOUNTAIN - TTHM SUBCONTRACTED TO E2535; HAA5 SUBCONTRACTED TO E84589 | 3
3590069 | BEAR LAKE MANOR | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-04-15 | AAA | 0.2
3590069 | BEAR LAKE MANOR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-15 | AAA | 0.2
3590069 | BEAR LAKE MANOR | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | INOR | 1010 | BARIUM | 0.0085 | MG/L | 2.4999 | 2021-04-15 | AAA | 0.002
3590069 | BEAR LAKE MANOR | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | INOR | 1020 | CHROMIUM | 0.0013 | MG/L | 0.1499 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-04-15 | AAA | 0.005
3590069 | BEAR LAKE MANOR | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-04-15 | AAA | 0.2
3590069 | BEAR LAKE MANOR | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-04-15 | AAA | 2e-05
3590069 | BEAR LAKE MANOR | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-04-15 | AAA | 0.002
3590069 | BEAR LAKE MANOR | N | INOR | 1052 | SODIUM | 17.7 | MG/L | 160.4999 | 2021-04-15 | AAA | 0.5
3590069 | BEAR LAKE MANOR | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-04-15 | AAA | 0.0005
3590069 | BEAR LAKE MANOR | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2021-04-15 | AAA | 0.3 | 1.4999 | TEST AGAIN IN 2027
3590069 | BEAR LAKE MANOR | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-04-15 | AAA | 0.01 | 0.0149 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-04-15 | AAA | 0.01 | 0.2499 | SOC
3590069 | BEAR LAKE MANOR | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-04-15 | AAA | 1.4 |  | TEST AGAIN IN 2027
3590069 | BEAR LAKE MANOR | N | RAD | 4030 | RADIUM-228 | 0.7 | PCI/L | 2.4999 | 2021-04-15 | AAA | 0.7 | 1.4999 | TEST AGAIN IN 2027
3590069 | BEAR LAKE MANOR | N | SEC | 1028 | IRON | 0.0344 | MG/L | 0.3499 | 2021-04-15 | AAA | 0.01
3590069 | BEAR LAKE MANOR | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-04-15 | AAA | 0.01
3590069 | BEAR LAKE MANOR | N | SEC | 1017 | CHLORIDE | 28.3 | MG/L | 250.4999 | 2021-04-15 | AAA | 0.4
3590069 | BEAR LAKE MANOR | N | SEC | 1022 | COPPER | 0.0022 | MG/L | 1.4999 | 2021-04-15 | AAA | 0.001
3590069 | BEAR LAKE MANOR | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-04-15 | AAA | 0.2
3590069 | BEAR LAKE MANOR | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-04-15 | AAA | 0.01
3590069 | BEAR LAKE MANOR | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-04-15 | AAA | 0.0005
3590069 | BEAR LAKE MANOR | N | SEC | 1055 | SULFATE | 9.54 | MG/L | 250.4999 | 2021-04-15 | AAA | 1
3590069 | BEAR LAKE MANOR | N | SEC | 1095 | ZINC | 0.0047 | MG/L | 5.4999 | 2021-04-15 | AAA | 0.002
3590069 | BEAR LAKE MANOR | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-04-15 | AAA | 5
3590069 | BEAR LAKE MANOR | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-04-15 | AAA | 0.2
3590069 | BEAR LAKE MANOR | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-04-15 | AAA | 1
3590069 | BEAR LAKE MANOR | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.2 | LN(10) |  | 2021-04-15 | AAA | 0.01
3590069 | BEAR LAKE MANOR | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 234 | MG/L | 500.4999 | 2021-04-15 | AAA | 2.5
3590069 | BEAR LAKE MANOR | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-15 | AAA | 0.5 | 0.5499 | VOC
3590069 | BEAR LAKE MANOR | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-15 | AAA | 0.01 | 0.0149 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-15 | AAA | 0.01 | 0.0249 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-15 | AAA | 0.05 | 0.1499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-04-15 | AAA | 0.5 | 1.4999 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-04-15 | AAA | 0.1 | 1.4999 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-04-15 | AAA | 0.4 | 0.4499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-04-15 | AAA | 9 | 9.4999 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-04-15 | AAA | 6 | 6.4999 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-04-15 | AAA | 0.6 | 0.6499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-04-15 | AAA | 2 | 2.4999 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-15 | AAA | 0.07 | 0.0749 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-15 | AAA | 0.6 | 0.6499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-04-15 | AAA | 0.1 | 0.1499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-04-15 | AAA | 0.2 | 0.2499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-15 | AAA | 0.1 | 0.1499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-04-15 | AAA | 0.9 | 0.9499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-15 | AAA | 0.1 | 0.1499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-15 | AAA | 0.2 | 0.2499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-15 | AAA | 0.01 | 0.0449 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-15 | AAA | 0.01 | 0.0249 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-04-15 | AAA | 0.1 | 0.1499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-04-15 | AAA | 0.2 | 0.2499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-15 | AAA | 0.1 | 0.1499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-04-15 | AAA | 0.02 | 0.0249 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-04-15 | AAA | 0.04 | 0.0449 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-04-15 | AAA | 0.1 | 0.1499 | SOC
3590069 | BEAR LAKE MANOR | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-04-15 | AAA | 0.02 | 0.0249 | SOC
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.52 | UG/L | 60.4999 | 2021-08-10 | L1 |  |  | 3701 ANNA DR | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 53.08 | UG/L | 80.4999 | 2021-08-10 | L1 |  |  | 3701 ANNA DR | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.44 | UG/L | 60.4999 | 2021-08-10 | L2 |  |  | 1207 ALTON DR | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 35.61 | UG/L | 80.4999 | 2021-08-10 | L2 |  |  | 1207 ALTON DR | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.95 | UG/L | 60.4999 | 2022-08-11 | L1 | 0.98 |  | 3701 ANNA DRIVE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 60.86 | UG/L | 80.4999 | 2022-08-11 | L1 | 0.39 |  | 3701 ANNA DRIVE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.3 | UG/L | 60.4999 | 2022-08-11 | L2 | 0.98 |  | 1207 ALTON DR. | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 45.6 | UG/L | 80.4999 | 2022-08-11 | L2 | 0.39 |  | 1207 ALTON DR. | 3
3590069 | BEAR LAKE MANOR | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-11-08 | AAA |  |  | POE
3590069 | BEAR LAKE MANOR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-11-08 | AAA |  |  | POE
3590069 | BEAR LAKE MANOR | N | INOR | 1040 | NITRATE | 0.074 | MG/L | 10.4999 | 2023-01-27 | AAA | 0.024 |  | POE
3590069 | BEAR LAKE MANOR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-27 | AAA |  |  | POE
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.37 | UG/L | 60.4999 | 2023-08-08 | L1 |  |  | 3701 ANNA DRIVE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 48.17 | UG/L | 80.4999 | 2023-08-08 | L1 |  |  | 3701 ANNA DRIVE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.81 | UG/L | 60.4999 | 2023-08-08 | L2 |  |  | 1207 ALTON DRIVE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 43.7 | UG/L | 80.4999 | 2023-08-08 | L2 |  |  | 1207 ALTON DRIVE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.56 | UG/L | 60.4999 | 2024-08-12 | L1 | 0.98 |  | 3701 ANNA DRIVE (LATE ENTRY FD) | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 27.11 | UG/L | 80.4999 | 2024-08-12 | L1 | 0.39 |  | 3701 ANNA DRIVE (LATE ENTRY FD) | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.64 | UG/L | 60.4999 | 2024-08-12 | L2 | 0.98 |  | 1207 ALTON DRIVE (LATE ENTRY FD) | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 25.91 | UG/L | 80.4999 | 2024-08-12 | L2 | 0.39 |  | 1207 ALTON DRIVE (LATE ENTRY FD) | 3
3590069 | BEAR LAKE MANOR | N | SEC | 2905 | FOAMING AGENTS | 0.085 |  | 0.5499 | 2024-09-17 | AAA | 0.04 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2024-09-17 | AAA | 0.3 | 1.4999 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-17 | AAA | 0.9 | 1.4999 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SEC | 1017 | CHLORIDE | 25 | MG/L | 250.4999 | 2024-09-17 | AAA | 0.039 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-09-17 | AAA | 0.002 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-09-17 | AAA | 0.00025 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-09-17 | AAA | 0.024 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2024-09-17 | AAA | 0.005 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1025 | FLUORIDE | 0.19 | MG/L | 2.0499 | 2024-09-17 | AAA | 0.0099 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-09-17 | AAA | 0.038 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1032 | MANGANESE | 0.0051 | MG/L | 0.0549 | 2024-09-17 | AAA | 0.005 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-09-17 | AAA | 0.0005 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1055 | SULFATE | 8.9 | MG/L | 250.4999 | 2024-09-17 | AAA | 0.034 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-09-17 | AAA | 0.05 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1905 | COLOR | 8.9 | COLOR UNITS | 15.4999 | 2024-09-17 | AAA | 5 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-09-17 | AAA | 1 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.02 | LN(10) |  | 2024-09-17 | AAA |  |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 230 | MG/L | 500.4999 | 2024-09-17 | AAA | 10 |  | POE TO DIST, 2905 J QUALIFIER (REVISED, 2905 JQUAL ERROR. RESULTS OK. FD)
3590069 | BEAR LAKE MANOR | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-09-17 | AAA | 0.13333 | 0.667 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-09-17 | AAA | 0.5 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-09-17 | AAA | 0.24 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-09-17 | AAA | 0.48 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-09-17 | AAA | 0.49 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-09-17 | AAA | 0.44 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-09-17 | AAA | 0.4 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-09-17 | AAA | 0.28 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-09-17 | AAA | 0.4 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-09-17 | AAA | 0.41 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-09-17 | AAA | 0.44 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-09-17 | AAA | 0.32 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-09-17 | AAA | 0.36 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-09-17 | AAA | 0.33 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-17 | AAA | 0.25 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-09-17 | AAA | 0.44 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-09-17 | AAA | 0.49 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-09-17 | AAA | 0.37 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-09-17 | AAA | 0.16 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-09-17 | AAA | 0.2 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-09-17 | AAA | 0.33 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-09-17 | AAA | 0.26 | 0.5499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-09-17 | AAA | 0.0069 | 0.0149 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-09-17 | AAA | 0.0071 | 0.0249 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-09-17 | AAA | 0.0068 | 0.1499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-09-17 | AAA | 0.12 | 1.4999 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-09-17 | AAA | 0.9 | 1.4999 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-09-17 | AAA | 0.37 | 0.4499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-09-17 | AAA | 6 | 9.4999 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-09-17 | AAA | 5.9 | 6.4999 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-09-17 | AAA | 0.5 | 0.6499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-09-17 | AAA | 1.8 | 2.4999 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-09-17 | AAA | 0.06 | 0.0749 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-09-17 | AAA | 0.5 | 0.6499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-09-17 | AAA | 0.09 | 0.1499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-09-17 | AAA | 0.18 | 0.2499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-09-17 | AAA | 0.019 | 0.1499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-09-17 | AAA | 0.67 | 0.9499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-09-17 | AAA | 0.09 | 0.1499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-09-17 | AAA | 0.15 | 0.2499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-09-17 | AAA | 0.006 | 0.0449 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-09-17 | AAA | 0.0052 | 0.0249 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-09-17 | AAA | 0.095 | 0.1499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-09-17 | AAA | 0.09 | 0.2499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-09-17 | AAA | 0.0063 | 0.1499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-09-17 | AAA | 0.015 | 0.0249 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-09-17 | AAA | 0.038 | 0.0449 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-09-17 | AAA | 0.093 | 0.1499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-09-17 | AAA | 0.0057 | 0.0249 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-09-17 | AAA | 0.0085 | 0.0149 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-09-17 | AAA | 0.053 | 0.2499 | POE TO DIST
3590069 | BEAR LAKE MANOR | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.4 | PCI/L | 15.4999 | 2024-09-17 | AAA | 0.7 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-09-17 | AAA | 0.001 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1040 | NITRATE | 0.053 | MG/L | 10.4999 | 2024-09-17 | AAA | 0.024 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-17 | AAA | 0.0034 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-17 | AAA | 0.00025 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1010 | BARIUM | 0.0086 | MG/L | 2.4999 | 2024-09-17 | AAA | 0.003 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-09-17 | AAA | 0.00025 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-09-17 | AAA | 0.005 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-09-17 | AAA | 0.004 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2024-09-17 | AAA | 0.0099 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-09-17 | AAA | 0.0005 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-09-17 | AAA | 3e-05 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-09-17 | AAA | 0.008 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-09-17 | AAA | 0.0012 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | N | INOR | 1052 | SODIUM | 18 | MG/L | 160.4999 | 2024-09-17 | AAA | 0.8 |  | POE TO DIST
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.11 | UG/L | 60.4999 | 2025-08-08 | L1 | 0.98 |  | 3701 ANNA DRIVE- EXCEEDANCE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 89.12 | UG/L | 80.4999 | 2025-08-08 | L1 | 0.44 |  | 3701 ANNA DRIVE- EXCEEDANCE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.76 | UG/L | 60.4999 | 2025-08-08 | L2 | 0.98 |  | 1207 ALTON DRIVE | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 47.04 | UG/L | 80.4999 | 2025-08-08 | L2 | 0.44 |  | 1207 ALTON DRIVE | 3
3590069 | BEAR LAKE MANOR | D | INOR | 1040 | NITRATE | 0.076 | MG/L | 10.4999 | 2025-08-13 | AAA | 0.024 |  | POE
3590069 | BEAR LAKE MANOR | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-08-13 | AAA |  |  | POE
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.21 | UG/L | 60.4999 | 2025-11-11 | L1 | 0.98 |  | 3701 ANNA DR - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 64.16 | UG/L | 80.4999 | 2025-11-11 | L1 | 0.44 |  | 3701 ANNA DR - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.21 | UG/L | 60.4999 | 2025-11-11 | L2 | 0.98 |  | 1207 ALTON DR - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3590069 | BEAR LAKE MANOR | D | DBP | 2950 | TOTAL THMS | 48.96 | UG/L | 80.4999 | 2025-11-11 | L2 | 0.44 |  | 1207 ALTON DR - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589 | 3
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.41 | MG/L |  | 2021-01-04 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2021-01-04 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2021-01-11 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-01-11 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-01-11 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2021-01-04 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2021-01-04 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2021-01-11 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-01-13 | POE | 3.7 |  | 1/21 BROMATE - AUX. WP (HLKD)
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2021-01-19 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-01-19 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2021-01-19 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-01-19 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2021-01-25 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2021-01-25 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2021-01-25 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-01-25 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-01-06 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-01-06 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-01-06 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-01-06 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-01-20 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-01-20 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-01-20 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-01-20 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.3 | UG/L | 60.4999 | 2021-01-27 | L1 | 0.9 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 39.5 | UG/L | 80.4999 | 2021-01-27 | L1 | 0.47 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.8 | UG/L | 60.4999 | 2021-01-27 | L2 | 0.9 |  | 342 BRANTLEY CLUB PLC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.6 | UG/L | 80.4999 | 2021-01-27 | L2 | 0.47 |  | 342 BRANTLEY CLUB PLC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.3 | UG/L | 60.4999 | 2021-01-27 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.5 | UG/L | 80.4999 | 2021-01-27 | L4 | 0.47 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.3 | UG/L | 60.4999 | 2021-01-27 | L3 | 0.9 |  | 1021 ARDEN ST. (3/21 DISINF BYP. RPRT RCVD)**SAMPLE DATE ON LAB REPORT IS 10/28/20 INSTEAD OF 1/27/21 PER CHAIN OF CUSTODY-PG 1 -BB. 4/22/21 REVISED_MFC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 30.5 | UG/L | 80.4999 | 2021-01-27 | L3 | 0.47 |  | 1021 ARDEN ST. (3/21 DISINF BYP. RPRT RCVD)**SAMPLE DATE ON LAB REPORT IS 10/28/20 INSTEAD OF 1/27/21 PER CHAIN OF CUSTODY-PG 1 -BB. 4/22/21 REVISED_MFC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-02-03 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-02-03 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-02-03 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-02-03 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-02-17 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-02-17 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-02-17 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-02-17 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-03-03 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-03 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-03-03 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-03 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-03-17 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-17 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2021-03-17 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-17 | WTP5 |  |  | 1207 MCNEIL RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-02-01 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2021-02-01 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2021-02-01 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-02-01 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-02-08 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2021-02-08 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-02-08 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2021-02-08 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-02-08 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2021-02-15 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2021-02-15 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2021-02-15 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2021-02-15 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.48 | MG/L |  | 2021-02-22 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2021-02-22 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2021-02-22 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-02-22 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.48 | UG/L | 60.4999 | 2021-02-24 | S02_L05 | 0.98 |  | 3751 E. S.R. 46
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-02-08 | WTP2 |  |  | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-02-08 | WTP2 |  |  | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2021-02-08 | WTP2 |  | 1.4999 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-02-08 | WTP2 |  | 1.4999 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.84 | UG/L | 60.4999 | 2021-02-24 | S01_L01 | 0.98 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.91 | UG/L | 80.4999 | 2021-02-24 | S01_L01 | 0.39 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 75.2 | UG/L | 80.4999 | 2021-02-24 | S02_L05 | 0.39 |  | 3751 E. S.R. 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.64 | UG/L | 60.4999 | 2021-02-24 | S02_L06 | 0.98 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 61.68 | UG/L | 80.4999 | 2021-02-24 | S02_L06 | 0.39 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.75 | UG/L | 60.4999 | 2021-02-24 | S01_L02 | 0.98 |  | 100 WELDON BLVD. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 68.91 | UG/L | 80.4999 | 2021-02-24 | S01_L02 | 0.39 |  | 100 WELDON BLVD. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2021-02-28 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2021-02-28 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2021-02-28 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-02-28 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.49 | MG/L |  | 2021-03-07 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.48 | LN(10) |  | 2021-03-07 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.49 | MG/L |  | 2021-03-07 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-03-07 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-03-08 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.57 | MG/L |  | 2021-03-14 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2021-03-14 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.48 | MG/L |  | 2021-03-14 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-03-14 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.57 | MG/L |  | 2021-03-21 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2021-03-21 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.51 | MG/L |  | 2021-03-21 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-03-21 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2021-03-28 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-03-28 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2021-03-28 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-28 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.54 | MG/L |  | 2021-04-04 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2021-04-04 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2021-04-04 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-04-04 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.53 | MG/L |  | 2021-04-11 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2021-04-11 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2021-04-11 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-04-11 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-04-14 | POE | 3.8 |  | 4/21 BROMATE - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2021-04-19 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-04-19 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.42 | MG/L |  | 2021-04-19 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-04-19 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.46 | MG/L |  | 2021-04-25 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2021-04-25 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2021-04-25 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2021-04-25 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.85 | UG/L | 60.4999 | 2021-04-26 | S01_L01 |  |  | 531 N PALMETTO
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 52.66 | UG/L | 80.4999 | 2021-04-26 | S01_L01 |  |  | 531 N PALMETTO
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.49 | UG/L | 60.4999 | 2021-04-26 | S02_L05 |  |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 67.58 | UG/L | 80.4999 | 2021-04-26 | S02_L05 |  |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.12 | UG/L | 60.4999 | 2021-04-26 | S02_L06 |  |  | 2501 LAKE MARY
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.54 | UG/L | 80.4999 | 2021-04-26 | S02_L06 |  |  | 2501 LAKE MARY
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.67 | UG/L | 60.4999 | 2021-04-26 | S01_L02 |  |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 49.83 | UG/L | 80.4999 | 2021-04-26 | S01_L02 |  |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2021-05-03 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2021-05-03 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2021-05-03 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.48 | MG/L |  | 2021-05-09 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-09 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-05-12 | POE | 3.8 |  | 5/21 BROMATE - AUX. WP (HLKD)
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2021-05-16 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-16 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.46 | MG/L |  | 2021-05-16 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2021-05-03 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2021-05-09 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2021-05-09 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.54 | LN(10) |  | 2021-05-16 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-05-17 | WTP2 |  |  | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 1.33 | PCI/L | 3.4999 | 2021-05-17 | WTP2 |  | 1.4999 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-05-17 | WTP2 |  | 1.4999 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-17 | WTP2 |  |  | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2021-05-23 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-05-23 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-05-23 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-05-23 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.41 | MG/L |  | 2021-05-30 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-05-30 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2021-05-30 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2021-06-06 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2021-06-06 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2021-06-13 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-06-13 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2021-06-13 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2021-05-30 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.49 | MG/L |  | 2021-06-06 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2021-06-06 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2021-06-13 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2021-06-21 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2021-06-21 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2021-06-21 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-06-21 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.046 | MG/L | 10.4999 | 2021-06-23 | WTP1 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP1 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.29 | MG/L | 10.4999 | 2021-06-23 | WTP2 |  |  | POE- AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-06-23 | WTP2 |  |  | POE- AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2021-06-27 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-06-27 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2021-06-27 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2021-06-27 | WTP2 |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2021-07-04 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-07-04 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-07-04 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2021-07-04 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2021-07-11 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-07-11 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.48 | MG/L |  | 2021-07-11 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2021-07-11 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-07-14 | POE | 3.8 |  | 7/21 BROMATE - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2021-07-19 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-07-19 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.56 | MG/L |  | 2021-07-19 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2021-07-19 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2021-07-25 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-07-25 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.54 | MG/L |  | 2021-07-25 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2021-07-25 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.87 | UG/L | 60.4999 | 2021-07-26 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.32 | UG/L | 80.4999 | 2021-07-26 | S01_L01 | 0.39 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.46 | UG/L | 60.4999 | 2021-07-26 | S02_L05 | 0.98 |  | 3751 E SR 46 [ 3Q TTHM LRAA=73.76;OEL= 77.47]_MFC
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 83.54 | UG/L | 80.4999 | 2021-07-26 | S02_L05 | 0.39 |  | 3751 E SR 46 [ 3Q TTHM LRAA=73.76;OEL= 77.47]_MFC
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.57 | UG/L | 60.4999 | 2021-07-26 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.55 | UG/L | 80.4999 | 2021-07-26 | S02_L06 | 0.39 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.07 | UG/L | 60.4999 | 2021-07-26 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 48.36 | UG/L | 80.4999 | 2021-07-26 | S01_L02 | 0.39 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2021-08-01 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2021-08-01 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.52 | MG/L |  | 2021-08-01 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2021-08-01 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.36 | LN(10) |  | 2021-08-10 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2021-08-09 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2021-08-09 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.52 | MG/L |  | 2021-08-10 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-08-11 | POE | 3.8 |  | 8/21 BROMATE - AUX. WP (HLKD) **DID NOT SEE 6/21 BROMATE**
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.38 | MG/L |  | 2021-08-17 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-08-17 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2021-08-17 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.34 | LN(10) |  | 2021-08-17 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.38 | MG/L |  | 2021-08-22 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-08-22 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.48 | MG/L |  | 2021-08-22 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2021-08-22 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.53 | MG/L |  | 2021-08-29 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2021-08-29 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.53 | MG/L |  | 2021-08-29 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-08-29 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-08-30 | WTP2 | 0.0005 |  | ARSENIC - AUX. WP2 (DUE TO ASR WELL)
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-08-30 | WTP2 | 2.7 |  | RADS - AUX. WP (DUE TO ASR WELL)
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.707 | PCI/L | 3.4999 | 2021-08-30 | WTP2 | 0.547 | 1.4999 | RADS - AUX. WP (DUE TO ASR WELL)
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-08-30 | WTP2 | 0.621 | 1.4999 | RADS - AUX. WP (DUE TO ASR WELL)
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2021-09-05 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-09-05 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.53 | MG/L |  | 2021-09-05 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-09-05 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2021-09-12 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2021-09-12 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.51 | MG/L |  | 2021-09-13 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-13 | WTP2 |  |  | ORLANDO
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-03-31 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-31 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-03-31 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-03-31 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2021-04-14 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-04-14 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-04-14 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-04-14 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.6 | UG/L | 60.4999 | 2021-04-28 | L1 | 0.9 |  | 230 W. STATE RD. 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 27.1 | UG/L | 80.4999 | 2021-04-28 | L1 | 0.47 |  | 230 W. STATE RD. 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.3 | UG/L | 60.4999 | 2021-04-28 | L2 | 0.9 |  | 342 BRANTLEY CLUB PL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 27.9 | UG/L | 80.4999 | 2021-04-28 | L2 | 0.47 |  | 342 BRANTLEY CLUB PL.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.8 | UG/L | 60.4999 | 2021-04-28 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 42.7 | UG/L | 80.4999 | 2021-04-28 | L4 | 0.47 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.5 | UG/L | 60.4999 | 2021-04-28 | L3 | 0.9 |  | 1021 ARDEN ST. (RSLTS RCVD WITH 6/21 QTR DISINF BYP RPRT) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 25.3 | UG/L | 80.4999 | 2021-04-28 | L3 | 0.47 |  | 1021 ARDEN ST. (RSLTS RCVD WITH 6/21 QTR DISINF BYP RPRT) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-04-28 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-04-28 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-04-28 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-04-28 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-12 | WTP5 | 0.004 |  | WP5 (NITRITE REPORTED INCORRECTLY-HLKD, LAB REVISION REMOVING THE MINUS SYMBOL IS NEEDED)REVISED RCVD 9/22/2021_MFC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-12 | WTP2 | 0.004 |  | WP2 (NITRITE REPORTED INCORRECTLY-HLKD, LAB REVISION REMOVING THE MINUS SYMBOL IS NEEDED)REVISED RCVD 9/22/21_MFC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-05-12 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-12 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-05-12 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-12 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0.017 | MG/L | 10.4999 | 2021-05-12 | WTP2 | 0.004 |  | WP2 (NITRITE REPORTED INCORRECTLY-HLKD, LAB REVISION REMOVING THE MINUS SYMBOL IS NEEDED)REVISED RCVD 9/22/21_MFC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0.007 | MG/L | 10.4999 | 2021-05-12 | WTP5 | 0.004 |  | WP5 (NITRITE REPORTED INCORRECTLY-HLKD, LAB REVISION REMOVING THE MINUS SYMBOL IS NEEDED)REVISED RCVD 9/22/2021_MFC
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-05-26 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-05-26 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-05-26 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-05-26 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-06-09 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-06-09 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-06-09 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-06-09 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-06-23 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-06-23 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2021-06-23 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-06-23 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-07-07 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-07-07 | WTP2 |  |  | NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-07-07 | WTP2 |  |  | NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-07-07 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-07-21 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-07-21 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-07-21 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-07-21 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.3 | UG/L | 60.4999 | 2021-07-28 | L2 |  |  | BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 64 | UG/L | 80.4999 | 2021-07-28 | L2 |  |  | BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.3 | UG/L | 60.4999 | 2021-07-28 | L4 |  |  | CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.3 | UG/L | 80.4999 | 2021-07-28 | L4 |  |  | CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.3 | UG/L | 60.4999 | 2021-07-28 | L1 |  |  | SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45 | UG/L | 80.4999 | 2021-07-28 | L1 |  |  | SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.7 | UG/L | 60.4999 | 2021-07-28 | L3 |  |  | ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 29.5 | UG/L | 80.4999 | 2021-07-28 | L3 |  |  | ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-08-04 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-04 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-08-04 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-08-04 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-08-18 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-08-18 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-08-18 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-08-18 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-09-01 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-01 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-09-01 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-01 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-09-15 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2021-09-15 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-09-15 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-15 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-09-29 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-29 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-09-29 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-09-29 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-10-13 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-13 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-10-13 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-13 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.72 | UG/L | 60.4999 | 2021-10-27 | L2 |  |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.67 | UG/L | 80.4999 | 2021-10-27 | L2 |  |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 42.16 | UG/L | 60.4999 | 2021-10-27 | L4 |  |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 52.25 | UG/L | 80.4999 | 2021-10-27 | L4 |  |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.96 | UG/L | 60.4999 | 2021-10-27 | L3 |  |  | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 27.31 | UG/L | 80.4999 | 2021-10-27 | L3 |  |  | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2021-10-27 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-10-27 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2021-10-27 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-11-10 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-10-27 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-11-10 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-11-10 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.15 | UG/L | 60.4999 | 2021-10-27 | L1 | 0.98 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 42.75 | UG/L | 80.4999 | 2021-10-27 | L1 | 0.39 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2021-11-10 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-11-24 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-11-24 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-11-24 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-11-24 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2021-12-08 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-08 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-12-08 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-12-08 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-12-22 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2021-12-22 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-12-22 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-12-22 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.27 | UG/L | 60.4999 | 2022-01-26 | L1 | 0.98 |  | 230 W STATE RD 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 38.11 | UG/L | 80.4999 | 2022-01-26 | L1 | 0.39 |  | 230 W STATE RD 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.54 | UG/L | 60.4999 | 2022-01-26 | L2 | 0.98 |  | 342 BRANTLEY CLUB PLC.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 46.52 | UG/L | 80.4999 | 2022-01-26 | L2 | 0.39 |  | 342 BRANTLEY CLUB PLC.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.66 | UG/L | 60.4999 | 2022-01-26 | L3 | 0.98 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 28.96 | UG/L | 80.4999 | 2022-01-26 | L3 | 0.39 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.76 | UG/L | 60.4999 | 2022-01-26 | L4 | 0.98 |  | 496 CENTRAL PARKWAY (RSLTS RCVD W/ 3/22 QTR DISINF BYP RPRT) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47.51 | UG/L | 80.4999 | 2022-01-26 | L4 | 0.39 |  | 496 CENTRAL PARKWAY (RSLTS RCVD W/ 3/22 QTR DISINF BYP RPRT) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.88 | UG/L | 60.4999 | 2022-04-27 | L1 | 0.98 |  | 230 W. STATE RD 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.63 | UG/L | 80.4999 | 2022-04-27 | L1 | 0.39 |  | 230 W. STATE RD 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.6 | UG/L | 60.4999 | 2022-04-27 | L2 | 0.98 |  | 342 BRANTLEY CLUB PLC.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.09 | UG/L | 80.4999 | 2022-04-27 | L2 | 0.39 |  | 342 BRANTLEY CLUB PLC.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.66 | UG/L | 60.4999 | 2022-04-27 | L3 | 0.98 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 35.77 | UG/L | 80.4999 | 2022-04-27 | L3 | 0.39 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.08 | UG/L | 60.4999 | 2022-04-27 | L4 | 0.98 |  | 496 CENTRAL PARKWAY (6/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 52.68 | UG/L | 80.4999 | 2022-04-27 | L4 | 0.39 |  | 496 CENTRAL PARKWAY (6/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0.006 | MG/L | 10.4999 | 2022-06-29 | WTP2 |  |  | WTP2 POE NITRATE NITRITE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-29 | WTP2 |  |  | WTP2 POE NITRATE NITRITE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0.011 | MG/L | 10.4999 | 2022-06-29 | WTP5 |  |  | WTP5 POE NITRATE NITRITE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-29 | WTP5 |  |  | WTP5 POE NITRATE NITRITE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2022-07-06 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-07-06 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-07-06 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-07-06 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-07-20 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-07-20 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-07-20 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-07-20 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.92 | UG/L | 60.4999 | 2022-07-27 | L3 | 0.98 |  | 1021 ARDEN ST TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 34.11 | UG/L | 80.4999 | 2022-07-27 | L3 | 0.39 |  | 1021 ARDEN ST TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.46 | UG/L | 60.4999 | 2022-07-27 | L1 | 0.98 |  | 230 W SR 436 TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 65.41 | UG/L | 80.4999 | 2022-07-27 | L1 | 0.39 |  | 230 W SR 436 TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.82 | UG/L | 60.4999 | 2022-07-27 | L4 | 0.98 |  | 496 CENTRAL PARKWAY TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.48 | UG/L | 80.4999 | 2022-07-27 | L4 | 0.39 |  | 496 CENTRAL PARKWAY TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.99 | UG/L | 60.4999 | 2022-07-27 | L2 | 0.98 |  | 342 BRANTLEY CLUB PLACE TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.45 | UG/L | 80.4999 | 2022-07-27 | L2 | 0.39 |  | 342 BRANTLEY CLUB PLACE TTHM HAA5 (NOTE HAA5 CONDUCTED BY LAB E82535)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-08-03 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-08-03 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-08-03 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-08-03 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2022-08-17 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-08-17 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2022-08-17 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-08-17 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-08-31 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-08-31 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-08-31 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-08-31 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2022-09-14 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-09-14 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2022-09-14 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2022-09-14 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-09-28 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2022-10-12 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-09-28 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-09-28 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-09-28 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-10-12 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2022-10-12 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-10-12 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-10-26 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2022-10-26 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-10-26 | WTP2 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-10-26 | WTP2 |  |  | MCNEIL
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2021-09-19 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-09-19 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2021-09-19 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.32 | LN(10) |  | 2021-09-19 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-09-22 | POE | 3.8 |  | 9/21 BROMATE - AUX. WP (9/21 QTR BROMATE RAA SUBMITTED WITH THESE RESULTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2021-09-26 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-09-26 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.46 | MG/L |  | 2021-09-26 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.25 | LN(10) |  | 2021-09-26 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2021-10-10 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-10-10 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.46 | MG/L |  | 2021-10-10 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2021-10-10 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2021-10-17 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-10-17 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-10-18 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2021-10-18 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2021-10-24 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-10-24 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.41 | MG/L |  | 2021-10-24 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2021-10-24 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2021-10-31 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2021-10-31 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-10-31 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2021-10-31 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-11-02 | WTP2 |  |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-11-02 | WTP2 |  |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2021-11-02 | WTP2 |  | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0.825 | PCI/L | 2.4999 | 2021-11-02 | WTP2 |  | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2021-11-07 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-11-07 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-11-07 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2021-11-07 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2021-11-14 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-11-14 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.42 | MG/L |  | 2021-11-14 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2021-11-14 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-11-18 | POE | 3.8 |  | N811J-AUX PLANT WTP # 2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 5.9 | MG/L |  | 2021-11-21 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-11-21 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2021-11-21 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2021-11-21 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.37 | UG/L | 60.4999 | 2021-11-23 | S01_L01 |  |  | 531 N PALMETTO AV
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 65.07 | UG/L | 80.4999 | 2021-11-23 | S01_L01 |  |  | 531 N PALMETTO AV
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.64 | UG/L | 60.4999 | 2021-11-23 | S02_L05 |  |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.27 | UG/L | 80.4999 | 2021-11-23 | S02_L05 |  |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.27 | UG/L | 60.4999 | 2021-11-23 | S02_L06 |  |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 38.5 | UG/L | 80.4999 | 2021-11-23 | S02_L06 |  |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.76 | UG/L | 60.4999 | 2021-11-23 | S01_L02 |  |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 39.51 | UG/L | 80.4999 | 2021-11-23 | S01_L02 |  |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.41 | MG/L |  | 2021-12-01 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2021-12-01 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-12-01 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.46 | LN(10) |  | 2021-12-01 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2021-12-08 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2021-12-08 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2021-12-08 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.26 | LN(10) |  | 2021-12-08 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2021-12-13 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-12-13 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2021-12-13 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2021-12-13 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2021-12-27 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-12-27 | WTP1 |  |  | COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.51 | MG/L |  | 2021-12-27 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2021-12-27 | WTP2 |  |  | ORLANDO
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2022-01-03 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2022-01-03 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-01-13 | POE | 3.8 |  | 1/22 BROMATE - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-01-13 | POE |  |  | N136L - AUX PLANT WTP # 2
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2022-01-17 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2022-01-17 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2022-01-31 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-10-11 | POE | 3.8 |  | AUX PLANT WTP #2 POE - BROMATE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2021-12-02 | POE | 3.8 |  | AUX PLANT WTP #2 POE - BROMATE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2022-01-03 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2022-01-03 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2022-01-17 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2022-01-17 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-01-31 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.36 | MG/L |  | 2022-01-31 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2022-01-31 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2022-02-14 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2022-02-14 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2022-02-14 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.52 | LN(10) |  | 2022-02-14 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-02-17 | WTP2 |  |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-02-17 | WTP2 |  |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.765 | PCI/L | 3.4999 | 2022-02-17 | WTP2 |  | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-02-17 | WTP2 |  | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-02-21 | POE |  |  | N 235L - AUX PLANT WTP #2
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 90.82 | UG/L | 80.4999 | 2022-02-23 | S01_L01 | 0.44 |  | 531 N PALMETTO AVE. TTHM ONLY. ALL FEB 2022 HAA5 SAMPLES HAD QC PROBLEM SO SYSTEM INCURRED MISSED MONITORING VIOS FOR HAA5 ONLY_AMF
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 78.65 | UG/L | 80.4999 | 2022-02-23 | S02_L05 | 0.44 |  | 3751 E SR 46 TTHM ONLY
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 70.06 | UG/L | 80.4999 | 2022-02-23 | S02_L06 | 0.44 |  | 2501 LAKE MARY BLVD; TTHM ONLY
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 79.6 | UG/L | 80.4999 | 2022-02-23 | S01_L02 | 0.44 |  | 100 WELDON BLVD; TTHM ONLY
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2022-02-28 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-02-28 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2022-02-28 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2022-02-28 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2022-03-14 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-03-14 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2022-03-14 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2022-03-14 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.83 | UG/L | 60.4999 | 2022-03-17 | S01_L01 |  |  | 531 N PALMETTO AVE. QC PROBLEM WITH ORIGINAL FEB SAMPLE. RESAMPLED 3/17/22_AMF
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2950 | TOTAL THMS | 67.84 | UG/L | 80.4999 | 2022-03-17 | S01_L01 |  |  | 531 N PALMETTO AVE. QC PROBLEM WITH ORIGINAL FEB SAMPLE. RESAMPLED 3/17/22_AMF
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.28 | UG/L | 60.4999 | 2022-03-17 | S02_L05 |  |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2950 | TOTAL THMS | 68.96 | UG/L | 80.4999 | 2022-03-17 | S02_L05 |  |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.93 | UG/L | 60.4999 | 2022-03-17 | S02_L06 |  |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2950 | TOTAL THMS | 47.71 | UG/L | 80.4999 | 2022-03-17 | S02_L06 |  |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.19 | UG/L | 60.4999 | 2022-03-17 | S01_L02 |  |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | S | DBP | 2950 | TOTAL THMS | 60.39 | UG/L | 80.4999 | 2022-03-17 | S01_L02 |  |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-03-21 | POE |  |  | N 294 L - AUX PLANT WTP # 2
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2022-03-28 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-03-28 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2022-03-28 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2022-03-28 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2022-04-11 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-04-11 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2022-04-11 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.36 | LN(10) |  | 2022-04-11 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-04-20 | WTP2 | 0.0005 |  | ARSENIC - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-04-20 | WTP2 | 2.98 |  | RADS - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.369 | PCI/L | 3.4999 | 2022-04-20 | WTP2 | 0.167 | 1.4999 | RADS - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-04-20 | WTP2 | 0.713 | 1.4999 | RADS - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.51 | MG/L |  | 2022-04-25 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-04-25 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.46 | MG/L |  | 2022-04-25 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.25 | LN(10) |  | 2022-04-25 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.36 | UG/L | 60.4999 | 2022-04-27 | S01_L01 | 0.98 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 87.44 | UG/L | 80.4999 | 2022-04-27 | S01_L01 | 0.39 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.25 | UG/L | 60.4999 | 2022-04-27 | S02_L05 | 0.98 |  | 3751 E. SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 77.3 | UG/L | 80.4999 | 2022-04-27 | S02_L05 | 0.39 |  | 3751 E. SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.02 | UG/L | 60.4999 | 2022-04-27 | S02_L06 | 0.98 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.48 | UG/L | 80.4999 | 2022-04-27 | S02_L06 | 0.39 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.48 | UG/L | 60.4999 | 2022-04-27 | S01_L02 | 0.98 |  | 100 WELDON BLVD. (6/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 85.01 | UG/L | 80.4999 | 2022-04-27 | S01_L02 | 0.39 |  | 100 WELDON BLVD. (6/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.47 | MG/L |  | 2022-05-09 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-05-09 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2022-05-09 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2022-05-09 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-05-09 | POE | 3.8 |  | 5/22 BROMATE - AUX. WP (HLKD)
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.42 | MG/L |  | 2022-05-23 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2022-05-23 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2022-05-23 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2022-05-23 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.38 | MG/L |  | 2022-06-06 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2022-06-06 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2022-06-06 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2022-06-06 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.3 | MG/L | 10.4999 | 2022-06-08 | WTP2 | 0.025 |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-08 | WTP2 |  |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.061 | MG/L | 10.4999 | 2022-06-08 | WTP1 |  |  | MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-08 | WTP1 |  |  | MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-06-09 | POE | 3.8 |  | 6/22 BROMATE - AUX. WP (HLKD) 6/22 BROMATE RAA RCVD W/RSLTS
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.41 | MG/L |  | 2022-06-13 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-06-13 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.46 | MG/L |  | 2022-06-13 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.27 | LN(10) |  | 2022-06-13 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.38 | MG/L |  | 2022-06-27 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2022-06-27 | WTP1 |  |  | COUNTRY CLUB RD WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2022-06-27 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.34 | LN(10) |  | 2022-06-27 | WTP2 |  |  | ORLANDO DR WQP
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-07-13 | POE |  |  | N 596-L AUX PLANT WTP #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2022-07-18 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-04-11 | POE | 3.8 |  | 4/22 BROMATE - AUX. WP (HLKD)
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2022-07-05 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-07-05 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2022-07-05 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.26 | LN(10) |  | 2022-07-05 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2022-07-18 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2022-07-18 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2022-07-18 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.27 | UG/L | 60.4999 | 2022-07-28 | S01_L01 | 0.98 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.71 | UG/L | 80.4999 | 2022-07-28 | S01_L01 | 0.39 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.21 | UG/L | 60.4999 | 2022-07-28 | S02_L05 | 0.98 |  | 3751 E. S.R. 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 78.83 | UG/L | 80.4999 | 2022-07-28 | S02_L05 | 0.39 |  | 3751 E. S.R. 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.73 | UG/L | 60.4999 | 2022-07-28 | S02_L06 | 0.98 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 50.07 | UG/L | 80.4999 | 2022-07-28 | S02_L06 | 0.39 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.58 | UG/L | 60.4999 | 2022-07-28 | S01_L02 | 0.98 |  | 100 WELDON BLVD. (9/22 DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 46.39 | UG/L | 80.4999 | 2022-07-28 | S01_L02 | 0.39 |  | 100 WELDON BLVD. (9/22 DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2022-08-01 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2022-08-01 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2022-08-01 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.25 | LN(10) |  | 2022-08-01 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-08-08 | WTP2 | 2.37 |  | RADS - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.739 | PCI/L | 3.4999 | 2022-08-08 | WTP2 | 0.604 | 1.4999 | RADS - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-08-08 | WTP2 | 0.763 | 1.4999 | RADS - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-08-08 | WTP2 | 0.0005 |  | ARSENIC - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2022-08-15 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2022-08-15 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2022-08-15 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2022-08-15 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-08-15 | POE | 3.8 |  | 8/22 BROMATE - AUX. WP (HLKD)
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2022-08-29 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2022-08-29 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2022-08-29 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2022-08-29 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-09-07 | POE | 0.4 |  | 9/22 BROMATE - AUX. WP (HLKD) 9/22 QTR BROMATE RAA SUBMITTED W/RESULTS
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2022-09-12 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2022-09-12 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2022-09-12 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.55 | LN(10) |  | 2022-09-12 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2022-09-26 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2022-09-26 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2022-09-26 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2022-09-26 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2022-10-10 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.613 | LN(10) |  | 2022-10-10 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2022-10-10 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.378 | LN(10) |  | 2022-10-10 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2022-10-24 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2022-10-24 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2022-10-24 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.32 | LN(10) |  | 2022-10-24 | WTP2 |  |  | ORLANDO DR
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.73 | UG/L | 60.4999 | 2022-10-26 | L1 |  |  | 230 W SR 436 TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 26.69 | UG/L | 80.4999 | 2022-10-26 | L1 |  |  | 230 W SR 436 TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.98 | UG/L | 60.4999 | 2022-10-26 | L2 |  |  | 342 BRANTLEY CLUB PL TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 56.94 | UG/L | 80.4999 | 2022-10-26 | L2 |  |  | 342 BRANTLEY CLUB PL TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 36.49 | UG/L | 60.4999 | 2022-10-26 | L4 |  |  | 496 CENTRAL PARKWAY TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 60.04 | UG/L | 80.4999 | 2022-10-26 | L4 |  |  | 496 CENTRAL PARKWAY TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.65 | UG/L | 60.4999 | 2022-10-26 | L3 |  |  | 1021 ARDEN STREET TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 29.83 | UG/L | 80.4999 | 2022-10-26 | L3 |  |  | 1021 ARDEN STREET TTHM HAA5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-11-09 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-11-09 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-11-09 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-11-09 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-11-23 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-11-23 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-11-23 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-11-23 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-12-07 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-12-07 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-12-07 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-07 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2022-12-21 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-12-21 | WTP2 |  |  | NEWPORT
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2022-12-21 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-12-21 | WTP5 |  |  | MCNEIL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-01-18 | WTP2 |  |  | 700 NEWPORT AVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-10-26 | POE | 0.4 |  | 10/22 BROMATE - AUX. WP (HLKD)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-01-04 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-01-04 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-01-04 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-04 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-01-18 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-01-18 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-18 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.06 | UG/L | 60.4999 | 2023-01-25 | L2 | 0.98 |  | 342 BRANTLEY CLUB PL. (SINGLE SAMPLE TTHM EXCEEDANCE)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 81.02 | UG/L | 80.4999 | 2023-01-25 | L2 | 0.39 |  | 342 BRANTLEY CLUB PL. (SINGLE SAMPLE TTHM EXCEEDANCE)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.6 | UG/L | 60.4999 | 2023-01-25 | L1 | 0.98 |  | 230 W SR 436 (REPLACED 235 S. WYMORE)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 49.81 | UG/L | 80.4999 | 2023-01-25 | L1 | 0.39 |  | 230 W SR 436 (REPLACED 235 S. WYMORE)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.01 | UG/L | 60.4999 | 2023-01-25 | L3 | 0.98 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 34.63 | UG/L | 80.4999 | 2023-01-25 | L3 | 0.39 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.28 | UG/L | 60.4999 | 2023-01-25 | L4 | 0.98 |  | 496 CENTRAL PARKWAY (3/23 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 68.85 | UG/L | 80.4999 | 2023-01-25 | L4 | 0.39 |  | 496 CENTRAL PARKWAY (3/23 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-02-01 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-01 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-02-01 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-02-01 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-02-15 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-15 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-02-15 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-02-15 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-03-01 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-03-01 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-03-01 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-01 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-03-15 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-03-15 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-03-15 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2023-03-15 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-03-29 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-03-29 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-03-29 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2023-03-29 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-04-12 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-04-12 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-04-12 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-04-12 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2023-04-26 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-04-26 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2023-04-26 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-04-26 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 42.48 | UG/L | 80.4999 | 2023-04-26 | L2 | 0.39 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.99 | UG/L | 60.4999 | 2023-04-26 | L4 | 0.98 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.57 | UG/L | 80.4999 | 2023-04-26 | L4 | 0.39 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.93 | UG/L | 60.4999 | 2023-04-26 | L2 | 0.98 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.76 | UG/L | 60.4999 | 2023-04-26 | L1 | 0.98 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 39.17 | UG/L | 80.4999 | 2023-04-26 | L1 | 0.39 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.55 | UG/L | 60.4999 | 2023-04-26 | L3 | 0.98 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 32.56 | UG/L | 80.4999 | 2023-04-26 | L3 | 0.39 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-05-10 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-05-10 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-05-10 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-05-10 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1010 | BARIUM | 0.0086 | MG/L | 2.4999 | 2023-05-17 | WTP2 | 0.0024 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-05-17 | WTP2 | 0.025 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-05-17 | WTP2 | 0.025 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-05-17 | WTP2 | 0.0005 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-05-17 | WTP2 | 0.00067 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-05-17 | WTP2 | 0.0026 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-05-17 | WTP2 | 0.005 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1025 | FLUORIDE | 0.62 | MG/L | 4.0499 | 2023-05-17 | WTP2 | 0.015 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1030 | LEAD | 0.001 | MG/L | 0.0154 | 2023-05-17 | WTP2 | 0.00022 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-05-17 | WTP2 | 9e-05 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1036 | NICKEL | 0.003 | MG/L | 0.1499 | 2023-05-17 | WTP2 | 0.002 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-05-17 | WTP2 | 0.00083 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1052 | SODIUM | 9.1 | MG/L | 160.4999 | 2023-05-17 | WTP2 | 0.59 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-05-17 | WTP2 | 0.00083 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-05-17 | WTP2 | 0.00019 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-05-17 | WTP2 | 0.00021 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1002 | ALUMINUM | 0.014 | MG/L | 0.2499 | 2023-05-17 | WTP2 | 0.0072 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1017 | CHLORIDE | 14 | MG/L | 250.4999 | 2023-05-17 | WTP2 | 2.5 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1022 | COPPER | 0.15 | MG/L | 1.4999 | 2023-05-17 | WTP2 | 0.00093 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1025 | FLUORIDE | 0.62 | MG/L | 2.0499 | 2023-05-17 | WTP2 | 0.015 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-05-17 | WTP2 | 0.016 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1032 | MANGANESE | 0.0013 | MG/L | 0.0549 | 2023-05-17 | WTP2 | 0.00093 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-05-17 | WTP2 | 0.0013 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1055 | SULFATE | 5.4 | MG/L | 250.4999 | 2023-05-17 | WTP2 | 2.5 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1095 | ZINC | 0.16 | MG/L | 5.4999 | 2023-05-17 | WTP2 | 0.0076 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-05-17 | WTP2 | 5 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-05-17 | WTP2 | 1 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2023-05-17 | WTP2 | 0.1 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 132 | MG/L | 500.4999 | 2023-05-17 | WTP2 | 5 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-05-17 | WTP2 | 0.099 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-17 | WTP2 | 2.84 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2023-05-17 | WTP2 | 0.19 | 0.667 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2023-05-17 | WTP2 | 0.774 | 1.4999 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-17 | WTP2 | 0.538 | 1.4999 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP2 | 0.35 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP2 | 0.33 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-05-17 | WTP2 | 0.11 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP2 | 0.44 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-05-17 | WTP2 | 0.3 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP2 | 0.12 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-05-17 | WTP2 | 0.29 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP2 | 0.27 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.3 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-05-17 | WTP2 | 0.27 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.28 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP2 | 0.44 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP2 | 0.28 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP2 | 0.4 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-05-17 | WTP2 | 0.28 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-05-17 | WTP2 | 0.23 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP2 | 0.2 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-05-17 | WTP2 | 0.0024 | 0.0149 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP2 | 0.0027 | 0.0249 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-05-17 | WTP2 | 0.024 | 0.1499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.25 | 1.4999 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-05-17 | WTP2 | 0.49 | 1.4999 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-05-17 | WTP2 | 3.3 | 9.4999 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-05-17 | WTP2 | 4.2 | 6.4999 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-05-17 | WTP2 | 0.36 | 0.6499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-05-17 | WTP2 | 0.46 | 2.4999 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-05-17 | WTP2 | 0.04 | 0.0749 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-05-17 | WTP2 | 0.47 | 0.6499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-05-17 | WTP2 | 0.04 | 0.1499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-05-17 | WTP2 | 0.16 | 0.2499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-05-17 | WTP2 | 0.024 | 0.1499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-05-17 | WTP2 | 0.59 | 0.9499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.015 | 0.1499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-05-17 | WTP2 | 0.029 | 0.2499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-05-17 | WTP2 | 0.014 | 0.0449 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP2 | 0.003 | 0.0249 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-05-17 | WTP2 | 0.096 | 0.1499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-05-17 | WTP2 | 0.053 | 0.2499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP2 | 0.015 | 0.1499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP2 | 0.02 | 0.0249 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-05-17 | WTP2 | 0.014 | 0.0449 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-05-17 | WTP2 | 0.044 | 0.1499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP2 | 0.0065 | 0.0249 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-05-17 | WTP2 | 0.00077 | 0.0149 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-05-17 | WTP2 | 0.035 | 0.2499 | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP5 | 0.35 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP5 | 0.33 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-05-17 | WTP5 | 0.11 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP5 | 0.44 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-05-17 | WTP5 | 0.3 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP5 | 0.12 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-05-17 | WTP5 | 0.29 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.28 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP5 | 0.27 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.3 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-05-17 | WTP5 | 0.27 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP5 | 0.44 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP5 | 0.28 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP5 | 0.4 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-05-17 | WTP5 | 0.28 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-05-17 | WTP5 | 0.23 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP5 | 0.2 | 0.5499 | WTP#5 (PEARL LK.CSWY)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP5 | 0.0067 | 0.0249 | WTP#5 (PEARL LK.CSWY) TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-05-17 | WTP5 | 0.0079 | 0.0149 | WTP#5 (PEARL LK.CSWY) TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP2 | 0.0065 | 0.0249 | WTP#2 (SPRING LAKE/SOUTHWEST)- TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-05-17 | WTP2 | 0.0076 | 0.0149 | WTP#2 (SPRING LAKE/SOUTHWEST)- TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP2 | 0.35 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP2 | 0.33 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-05-17 | WTP2 | 0.11 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP2 | 0.44 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-05-17 | WTP2 | 0.3 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP2 | 0.12 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-05-17 | WTP2 | 0.29 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP2 | 0.27 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.3 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-05-17 | WTP2 | 0.27 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.28 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP2 | 0.44 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP2 | 0.28 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP2 | 0.26 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP2 | 0.4 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-05-17 | WTP2 | 0.28 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-05-17 | WTP2 | 0.23 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP2 | 0.2 | 0.5499 | WTP#2 (SPRING LAKE/SOUTHWEST)-TRIP BLANK?
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1010 | BARIUM | 0.0058 | MG/L | 2.4999 | 2023-05-17 | WTP5 | 0.0024 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-05-17 | WTP5 | 0.025 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-05-17 | WTP5 | 0.025 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-05-17 | WTP5 | 0.0005 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-05-17 | WTP5 | 0.0067 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-05-17 | WTP5 | 0.0026 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-05-17 | WTP5 | 0.005 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-05-17 | WTP5 | 0.00022 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-05-17 | WTP5 | 0.00083 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-05-17 | WTP5 | 9e-05 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1036 | NICKEL | 0.0024 | MG/L | 0.1499 | 2023-05-17 | WTP5 | 0.002 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-05-17 | WTP5 | 0.00083 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-05-17 | WTP5 | 0.00019 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-05-17 | WTP5 | 0.00021 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-05-17 | WTP5 | 0.0072 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1025 | FLUORIDE | 0.61 | MG/L | 2.0499 | 2023-05-17 | WTP5 | 0.15 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-05-17 | WTP5 | 0.016 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1032 | MANGANESE | 0.0023 | MG/L | 0.0549 | 2023-05-17 | WTP5 | 0.00093 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-05-17 | WTP5 | 0.0013 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-05-17 | WTP5 | 0.0076 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-05-17 | WTP5 | 5 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-05-17 | WTP5 | 1 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.6 | LN(10) |  | 2023-05-17 | WTP5 | 0.1 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 192 | MG/L | 500.4999 | 2023-05-17 | WTP5 | 5 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-17 | WTP5 | 0.921 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2023-05-17 | WTP5 | 0.19 | 0.667 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2023-05-17 | WTP5 | 0.552 | 1.4999 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-05-17 | WTP5 | 0.639 | 1.4999 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP5 | 0.35 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-05-17 | WTP5 | 0.33 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-05-17 | WTP5 | 0.11 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP5 | 0.44 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-05-17 | WTP5 | 0.3 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP5 | 0.12 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-05-17 | WTP5 | 0.29 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP5 | 0.27 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.3 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-05-17 | WTP5 | 0.27 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.28 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP5 | 0.44 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-05-17 | WTP5 | 0.28 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP5 | 0.26 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP5 | 0.4 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-05-17 | WTP5 | 0.28 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-05-17 | WTP5 | 0.23 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-05-17 | WTP5 | 0.2 | 0.5499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-05-17 | WTP5 | 0.0023 | 0.0149 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP5 | 0.0027 | 0.0249 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-05-17 | WTP5 | 0.023 | 0.1499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.25 | 1.4999 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-05-17 | WTP5 | 0.49 | 1.4999 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-05-17 | WTP5 | 3.3 | 9.4999 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-05-17 | WTP5 | 4.2 | 6.4999 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-05-17 | WTP5 | 0.36 | 0.6499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-05-17 | WTP5 | 0.46 | 2.4999 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-05-17 | WTP5 | 0.039 | 0.0749 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-05-17 | WTP5 | 0.16 | 0.2499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1017 | CHLORIDE | 23.9 | MG/L | 250.4999 | 2023-05-17 | WTP5 | 2.5 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1022 | COPPER | 0.0052 | MG/L | 1.4999 | 2023-05-17 | WTP5 | 0.00093 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 1055 | SULFATE | 3.7 | MG/L | 250.4999 | 2023-05-17 | WTP5 | 2.5 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-05-17 | WTP5 | 0.46 | 0.6499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-05-17 | WTP5 | 0.04 | 0.1499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-05-17 | WTP5 | 0.024 | 0.1499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-05-17 | WTP5 | 0.59 | 0.9499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-05-17 | WTP5 | 0.014 | 0.1499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-05-17 | WTP5 | 0.029 | 0.2499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-05-17 | WTP5 | 0.013 | 0.0449 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP5 | 0.003 | 0.0249 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-05-17 | WTP5 | 0.096 | 0.1499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-05-17 | WTP5 | 0.053 | 0.2499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-05-17 | WTP5 | 0.014 | 0.1499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP5 | 0.019 | 0.0249 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-05-17 | WTP5 | 0.014 | 0.0449 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-05-17 | WTP5 | 0.044 | 0.1499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-05-17 | WTP5 | 0.0066 | 0.0249 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-05-17 | WTP5 | 0.0078 | 0.0149 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-05-17 | WTP5 | 0.035 | 0.2499 | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-05-17 | WTP2 | 0.025 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-05-17 | WTP2 | 0.025 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-05-17 | WTP2 | 0.0005 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1010 | BARIUM | 0.0086 | MG/L | 2.4999 | 2023-05-17 | WTP2 | 0.0024 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-05-17 | WTP2 | 0.0067 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-05-17 | WTP2 | 0.0026 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-05-17 | WTP2 | 0.005 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1025 | FLUORIDE | 0.62 | MG/L | 4.0499 | 2023-05-17 | WTP2 | 0.015 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1030 | LEAD | 0.001 | MG/L | 0.0154 | 2023-05-17 | WTP2 | 0.00022 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-05-17 | WTP2 | 9e-05 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1036 | NICKEL | 0.003 | MG/L | 0.1499 | 2023-05-17 | WTP2 | 0.002 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-05-17 | WTP2 | 0.00083 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1052 | SODIUM | 9.1 | MG/L | 160.4999 | 2023-05-17 | WTP2 | 0.59 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-05-17 | WTP2 | 0.00083 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-05-17 | WTP2 | 0.00019 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-05-17 | WTP2 | 0.00021 |  | WTP#2 (SPRING LAKE/SOUTHWEST)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-05-17 | WTP5 | 0.099 |  | WTP#5 (PEARL LK.CSWY),
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1025 | FLUORIDE | 0.61 | MG/L | 4.0499 | 2023-05-17 | WTP5 | 0.015 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1052 | SODIUM | 14.6 | MG/L | 160.4999 | 2023-05-17 | WTP5 | 0.59 |  | WTP#5 (PEARL LK.CSWY)
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-05-24 | WTP5 |  | 0.4499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-05-24 | WTP2 |  | 0.4499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-05-24 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-05-24 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-05-24 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-05-24 | WTP5 |  |  | 1207 MCNEIL RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-11-07 | POE | 0.4 |  | 11/22 BROMATE - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2022-11-07 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2022-11-07 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.45 | MG/L |  | 2022-11-07 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.391 | LN(10) |  | 2022-11-07 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-11-16 | WTP2 |  |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-11-16 | WTP2 |  |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.504 | PCI/L | 3.4999 | 2022-11-16 | WTP2 |  | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-11-16 | WTP2 |  | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2022-11-21 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.58 | LN(10) |  | 2022-11-21 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2022-11-21 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.399 | LN(10) |  | 2022-11-21 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.53 | UG/L | 60.4999 | 2022-11-28 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.46 | UG/L | 80.4999 | 2022-11-28 | S01_L01 | 0.39 |  | 531 N PALMETTO AVE TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.69 | UG/L | 60.4999 | 2022-11-28 | S02_L05 | 0.98 |  | 3751 E SR 46 TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.59 | UG/L | 80.4999 | 2022-11-28 | S02_L05 | 0.39 |  | 3751 E SR 46 TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.73 | UG/L | 60.4999 | 2022-11-28 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.72 | UG/L | 80.4999 | 2022-11-28 | S02_L06 | 0.39 |  | 2501 LAKE MARY BLVD TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.98 | UG/L | 60.4999 | 2022-11-28 | S01_L02 | 0.98 |  | 100 WELDON BLVD TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.08 | UG/L | 80.4999 | 2022-11-28 | S01_L02 | 0.39 |  | 100 WELDON BLVD TTHM HAA5
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2022-12-05 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-12-05 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2022-12-05 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.436 | LN(10) |  | 2022-12-05 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2022-12-07 | POE |  |  | 12/2022 BROMATE WTP2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2022-12-19 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-12-19 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2022-12-19 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.377 | LN(10) |  | 2022-12-19 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2022-12-26 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2022-12-26 | WTP1 |  |  | COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2022-12-26 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.36 | LN(10) |  | 2022-12-26 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-01-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2023-01-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-01-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2023-01-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-01-11 | POE | 0.4 |  | BROMATE POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-01-16 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2023-01-16 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-01-16 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2023-01-16 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-01-17 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-01-17 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.8 | PCI/L | 3.4999 | 2023-01-17 | WTP2 | 0.743 | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-01-17 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-01-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-01-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-01-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.32 | LN(10) |  | 2023-01-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-01-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2023-01-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-01-30 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.36 | LN(10) |  | 2023-01-30 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2023-02-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-02-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-02-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2023-02-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-02-06 | POE | 0.4 |  | 2/23 BROMATE - AUX. WP
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-02-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2023-02-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-02-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-02-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-02-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-02-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-02-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2023-02-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.9 | UG/L | 60.4999 | 2023-02-27 | S01_L01 | 0.98 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 46.37 | UG/L | 80.4999 | 2023-02-27 | S01_L01 | 0.39 |  | 531 N. PALMETTO AVE.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.83 | UG/L | 60.4999 | 2023-02-27 | S02_L05 | 0.98 |  | 3751 E. S.R. 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.58 | UG/L | 80.4999 | 2023-02-27 | S02_L05 | 0.39 |  | 3751 E. S.R. 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.56 | UG/L | 60.4999 | 2023-02-27 | S02_L06 | 0.98 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.4 | UG/L | 80.4999 | 2023-02-27 | S02_L06 | 0.39 |  | 2501 E. LAKE MARY BLVD.
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.72 | UG/L | 60.4999 | 2023-02-27 | S01_L02 | 0.98 |  | 100 WELDON BLVD. (3/23 DISINF BYP RPRT RCVD W/RSULTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47.95 | UG/L | 80.4999 | 2023-02-27 | S01_L02 | 0.39 |  | 100 WELDON BLVD. (3/23 DISINF BYP RPRT RCVD W/RSULTS) HLKD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-02-27 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2023-02-27 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-02-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-02-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2023-03-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-03-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-03-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2023-03-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2023-03-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2023-03-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-03-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2023-03-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-03-15 | POE | 0.4 |  | BROMATE POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2023-03-19 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-03-19 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2023-03-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2023-03-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2023-03-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-03-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-03-27 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.47 | LN(10) |  | 2023-03-27 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-04-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2023-04-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-04-03 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.34 | LN(10) |  | 2023-04-03 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-04-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-04-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-04-10 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.32 | LN(10) |  | 2023-04-10 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-04-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-04-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2023-04-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-04-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.8 | UG/L | 60.4999 | 2023-04-24 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 64.12 | UG/L | 80.4999 | 2023-04-24 | S01_L01 | 0.39 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.45 | UG/L | 60.4999 | 2023-04-24 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.77 | UG/L | 80.4999 | 2023-04-24 | S02_L05 | 0.39 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.63 | UG/L | 60.4999 | 2023-04-24 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 50.81 | UG/L | 80.4999 | 2023-04-24 | S02_L06 | 0.39 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.78 | UG/L | 60.4999 | 2023-04-24 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45.9 | UG/L | 80.4999 | 2023-04-24 | S01_L02 | 0.39 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-04-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-04-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-04-24 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-04-24 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-05-01 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-05-01 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-05-01 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2023-05-01 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-05-08 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2023-05-08 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-05-08 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2023-05-08 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-05-15 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-05-15 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-05-15 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2023-05-15 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-05-22 | POE | 0.4 |  | AUX PLANT WTP #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-05-22 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2023-05-22 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-05-22 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2023-05-22 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 25 | MG/L |  | 2023-05-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.62 | LN(10) |  | 2023-05-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-05-30 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2023-05-30 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-06-05 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.65 | LN(10) |  | 2023-06-05 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-06-05 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2023-06-05 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-06-12 | POE | 0.4 |  | AUX PLANT WTP #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-06-12 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-06-12 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2023-06-12 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2023-06-12 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-06-13 | 3701 COUNTRY CLUB RD |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-04-06 | POE | 0.4 |  | 4/23 BROMATE - AUX. WP (HLKD)
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-05-22 | POE | 0.4 |  | POE-AUX PLANT WTP #2
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-05-22 | WTP2 | 0.0005 |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-05-22 | WTP2 | 1.87 |  | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.743 | PCI/L | 3.4999 | 2023-05-22 | WTP2 | 0.497 | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0.673 | PCI/L | 2.4999 | 2023-05-22 | WTP2 | 0.558 | 1.4999 | AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-06-13 | 3100 ORLANDO DR. |  |  | 3100 ORLANDO DR.
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.24 | LN(10) |  | 2023-06-13 | 3100 ORLANDO DR. |  |  | 3100 ORLANDO DR.
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.88 | LN(10) |  | 2023-06-13 | 3701 COUNTRY CLUB RD |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2023-06-13 | 1201 W SEMINOLE BLVD |  |  | 1201 W SEMINOLE BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.93 | LN(10) |  | 2023-06-13 | 1201 W SEMINOLE BLVD |  |  | 1201 W SEMINOLE BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-06-13 | 145 ANTHONY DR |  |  | 145 ANTHONY DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2023-06-13 | 145 ANTHONY DR |  |  | 145 ANTHONY DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-06-13 | 380 HIDDEN LAKE DR |  |  | 380 HIDDEN LAKE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.15 | LN(10) |  | 2023-06-13 | 380 HIDDEN LAKE DR |  |  | 380 HIDDEN LAKE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2023-06-13 | 118 BRISTOL CIR |  |  | 118 BRISTOL CIR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.81 | LN(10) |  | 2023-06-13 | 118 BRISTOL CIR |  |  | 118 BRISTOL CIR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2023-06-13 | 2801 GROVE DR |  |  | 2801 GROVE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2023-06-13 | 2801 GROVE DR |  |  | 2801 GROVE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.42 | MG/L |  | 2023-06-13 | 1303 S FRENCH AVE |  |  | 1303 S FRENCH AVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.83 | LN(10) |  | 2023-06-13 | 1303 S FRENCH AVE |  |  | 1303 S FRENCH AVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2023-06-13 | 2515 JEWETT LN |  |  | 2515 JEWETT LN
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-06-13 | 2515 JEWETT LN |  |  | 2515 JEWETT LN
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-06-13 | 203 MEADOW BLVD |  |  | 203 MEADOW BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.68 | LN(10) |  | 2023-06-13 | 203 MEADOW BLVD |  |  | 203 MEADOW BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-06-13 | 1301 W 20TH ST. |  |  | 1301 W 20TH ST.
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.52 | LN(10) |  | 2023-06-13 | 1301 W 20TH ST. |  |  | 1301 W 20TH ST.
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-06-13 | 830 CENTRAL PARK DR |  |  | 830 CENTRAL PARK DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.73 | LN(10) |  | 2023-06-13 | 830 CENTRAL PARK DR |  |  | 830 CENTRAL PARK DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-06-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.61 | LN(10) |  | 2023-06-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-06-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2023-06-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2023-06-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-06-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-06-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.28 | LN(10) |  | 2023-06-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2023-07-03 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-07-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2023-07-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-07-03 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-07-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-07-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2023-07-10 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.95 | LN(10) |  | 2023-07-10 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-07-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-07-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2023-07-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2023-07-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.72 | UG/L | 60.4999 | 2023-07-24 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.09 | UG/L | 80.4999 | 2023-07-24 | S01_L01 | 0.39 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.99 | UG/L | 60.4999 | 2023-07-24 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47 | UG/L | 80.4999 | 2023-07-24 | S02_L05 | 0.39 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.32 | UG/L | 60.4999 | 2023-07-24 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.66 | UG/L | 80.4999 | 2023-07-24 | S02_L06 | 0.39 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.83 | UG/L | 60.4999 | 2023-07-24 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 42.37 | UG/L | 80.4999 | 2023-07-24 | S01_L02 | 0.39 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-07-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2023-07-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2023-07-24 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2023-07-24 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-07-19 | POE | 0.4 |  | AUX PLANT #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.24 | MG/L | 10.4999 | 2023-07-26 | WTP2 | 0.025 |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1010 | BARIUM | 0.022 | MG/L | 2.4999 | 2023-07-26 | WTP2 | 0.0024 |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1025 | FLUORIDE | 0.74 | MG/L | 4.0499 | 2023-07-26 | WTP2 | 0.015 |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1052 | SODIUM | 20.6 | MG/L | 160.4999 | 2023-07-26 | WTP2 | 0.59 |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2023-07-26 | WTP2 |  |  | POE- AUXIL PLANT PC 2087A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-07-26 | WTP2 |  |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1017 | CHLORIDE | 73.9 | MG/L | 250.4999 | 2023-07-26 | WTP2 | 2.5 |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-07-26 | WTP2 |  |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1025 | FLUORIDE | 0.74 | MG/L | 2.0499 | 2023-07-26 | WTP2 | 0.015 |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1028 | IRON | 0.063 | MG/L | 0.3499 | 2023-07-26 | WTP2 | 0.016 |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-07-26 | WTP2 |  |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-07-26 | WTP2 |  |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1055 | SULFATE | 11.7 | MG/L | 250.4999 | 2023-07-26 | WTP2 | 2.5 |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-07-26 | WTP2 |  |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-07-26 | WTP2 | 5 |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-07-26 | WTP2 |  |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2023-07-26 | WTP2 | 0.1 |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 315 | MG/L | 500.4999 | 2023-07-26 | WTP2 | 5 |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-07-26 | WTP2 |  |  | POE AUXILIARY WP2 PC 2087 A
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.26 | MG/L | 10.4999 | 2023-07-26 | WTP1 | 0.025 |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1010 | BARIUM | 0.011 | MG/L | 2.4999 | 2023-07-26 | WTP1 | 0.0024 |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1025 | FLUORIDE | 0.69 | MG/L | 4.0499 | 2023-07-26 | WTP1 | 0.015 |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1052 | SODIUM | 38.3 | MG/L | 160.4999 | 2023-07-26 | WTP1 | 0.59 |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1094 | ASBESTOS | 0 | MF/L | 7.4999 | 2023-07-26 | WTP1 |  |  | POE - MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-07-26 | WTP1 |  |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1017 | CHLORIDE | 33.5 | MG/L | 250.4999 | 2023-07-26 | WTP1 | 2.5 |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-07-26 | WTP1 |  |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1025 | FLUORIDE | 0.69 | MG/L | 2.0499 | 2023-07-26 | WTP1 | 0.015 |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-07-26 | WTP1 |  |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-07-26 | WTP1 |  |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1050 | SILVER | 0.0014 | MG/L | 0.1499 | 2023-07-26 | WTP1 | 0.0013 |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1055 | SULFATE | 15.9 | MG/L | 250.4999 | 2023-07-26 | WTP1 | 2.5 |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-07-26 | WTP1 |  |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1905 | COLOR | 5 | COLOR UNITS | 15.4999 | 2023-07-26 | WTP1 | 5 |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-07-26 | WTP1 |  |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.8 | LN(10) |  | 2023-07-26 | WTP1 | 0.1 |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 266 | MG/L | 500.4999 | 2023-07-26 | WTP1 | 5 |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-07-26 | WTP1 |  |  | POE- MAIN WP 1 (MAYFAIR G.C.)
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-07-31 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-07-31 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2023-07-31 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2023-07-31 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-08-07 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-08-07 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2023-08-07 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.15 | LN(10) |  | 2023-08-07 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-08-10 | WTP2 | 0.35 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-08-10 | WTP2 | 0.33 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-08-10 | WTP2 | 0.11 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-08-10 | WTP2 | 0.44 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-08-10 | WTP2 | 0.26 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-08-10 | WTP2 | 0.3 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP2 | 0.3 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-08-10 | WTP2 | 0.12 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-08-10 | WTP2 | 0.29 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-08-10 | WTP2 | 0.27 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-08-10 | WTP2 | 0.27 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP2 | 0.28 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-08-10 | WTP2 | 0.44 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP2 | 0.26 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-08-10 | WTP2 | 0.28 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP2 | 0.26 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-08-10 | WTP2 | 0.26 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-08-10 | WTP2 | 0.4 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-08-10 | WTP2 | 0.28 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-08-10 | WTP2 | 0.23 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-08-10 | WTP2 | 0.2 | 0.5499 | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP2 | 0.26 | 1.4999 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-08-10 | WTP2 | 0.49 | 1.4999 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-08-10 | WTP2 | 0.16 | 0.4499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-08-10 | WTP2 | 3.3 | 9.4999 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-08-10 | WTP2 | 4.2 | 6.4999 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-08-10 | WTP2 | 0.46 | 2.4999 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-08-10 | WTP2 | 0.04 | 0.1499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-08-10 | WTP2 | 0.16 | 0.2499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-08-10 | WTP2 | 0.59 | 0.9499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-08-10 | WTP2 | 0.0042 | 0.0055 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-08-10 | WTP2 | 0.096 | 0.1499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-08-10 | WTP2 | 0.053 | 0.2499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-08-10 | WTP2 | 0.014 | 0.0449 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-08-10 | WTP2 | 0.045 | 0.1499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-08-10 | WTP2 | 0.0065 | 0.0249 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-08-10 | WTP2 | 0.0077 | 0.0149 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-08-10 | WTP2 | 0.036 | 0.2499 | AUX PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-08-10 | WTP1 | 0.35 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-08-10 | WTP1 | 0.33 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-08-10 | WTP1 | 0.11 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-08-10 | WTP1 | 0.44 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-08-10 | WTP1 | 0.26 | 0.5499 | MAIN PLANT POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-06-07 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-07 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-06-07 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-06-07 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.59 | MG/L |  | 2023-06-19 | DIST |  |  | 653 E. ALTAMONTE DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-06-19 | DIST |  |  | 653 E. ALTAMONTE DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2023-06-19 | DIST |  |  | 605 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-06-19 | DIST |  |  | 605 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-06-19 | DIST |  |  | 861 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2023-06-19 | DIST |  |  | 861 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2023-06-19 | DIST |  |  | 1061 ORIENTA AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2023-06-19 | DIST |  |  | 1061 ORIENTA AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2023-06-19 | DIST |  |  | 741 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2023-06-19 | DIST |  |  | 741 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2023-06-19 | DIST |  |  | 1065 RAINER DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2023-06-19 | DIST |  |  | 1065 RAINER DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-06-21 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-06-21 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-06-21 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-06-21 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-07-05 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-05 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-07-05 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2023-07-05 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-07-19 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-07-19 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-07-19 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-07-19 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14 | UG/L | 60.4999 | 2023-07-26 | L1 | 0.9 |  | L1- W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47.6 | UG/L | 80.4999 | 2023-07-26 | L1 | 0.47 |  | L1- W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.5 | UG/L | 60.4999 | 2023-07-26 | L2 | 0.9 |  | L2-342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 37 | UG/L | 80.4999 | 2023-07-26 | L2 | 0.47 |  | L2-342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.5 | UG/L | 60.4999 | 2023-07-26 | L3 | 0.9 |  | L3- 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 29.5 | UG/L | 80.4999 | 2023-07-26 | L3 | 0.47 |  | L3- 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2023-07-26 | L4 | 0.9 |  | L4- 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 44.5 | UG/L | 80.4999 | 2023-07-26 | L4 | 0.47 |  | L4- 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP5 |  | 0.5499 | POE WTP5 TRIP BLANK
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-07-27 | WTP2 |  | 0.5499 | POE TRIP BLANK WTP#2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP2 |  | 0.0249 | POE TRIP BLANK WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-27 | WTP2 |  | 0.0149 | POE TRIP BLANK WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP5 |  | 0.0249 | POE TRIP BALNK WTP 5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-27 | WTP5 |  | 0.0149 | POE TRIP BALNK WTP 5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-07-27 | WTP2 |  | 0.0149 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP2 |  | 0.0249 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-07-27 | WTP2 |  | 0.1499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-07-27 | WTP2 |  | 9.4999 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 1.4999 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-07-27 | WTP2 |  | 1.4999 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-07-27 | WTP2 |  | 0.4499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-07-27 | WTP2 |  | 6.4999 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-07-27 | WTP2 |  | 0.6499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-07-27 | WTP2 |  | 2.4999 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-07-27 | WTP2 |  | 0.0749 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-07-27 | WTP2 |  | 0.6499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-07-27 | WTP2 |  | 0.1499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-07-27 | WTP2 |  | 0.2499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-07-27 | WTP2 |  | 0.1499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-07-27 | WTP2 |  | 0.9499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP2 |  | 0.1499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-07-27 | WTP2 |  | 0.2499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-07-27 | WTP2 |  | 0.0449 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP2 |  | 0.0249 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-07-27 | WTP2 |  | 0.1499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-07-27 | WTP2 |  | 0.2499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP2 |  | 0.1499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP2 |  | 0.0249 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-07-27 | WTP2 |  | 0.0449 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-07-27 | WTP2 |  | 0.1499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP2 |  | 0.0249 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-27 | WTP2 |  | 0.0149 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-07-27 | WTP2 |  | 0.2499 | POE WTP 2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-07-27 | WTP5 |  | 0.0149 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP5 |  | 0.0249 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-07-27 | WTP5 |  | 0.1499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 1.4999 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-07-27 | WTP5 |  | 1.4999 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-07-27 | WTP5 |  | 0.4499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-07-27 | WTP5 |  | 9.4999 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-07-27 | WTP5 |  | 6.4999 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-07-27 | WTP5 |  | 0.6499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-07-27 | WTP5 |  | 2.4999 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-07-27 | WTP5 |  | 0.0749 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-07-27 | WTP5 |  | 0.6499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-07-27 | WTP5 |  | 0.1499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-07-27 | WTP5 |  | 0.2499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-07-27 | WTP5 |  | 0.1499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-07-27 | WTP5 |  | 0.9499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-07-27 | WTP5 |  | 0.1499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-07-27 | WTP5 |  | 0.2499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-07-27 | WTP5 |  | 0.0449 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP5 |  | 0.0249 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-07-27 | WTP5 |  | 0.1499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-07-27 | WTP5 |  | 0.2499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-07-27 | WTP5 |  | 0.1499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP5 |  | 0.0249 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-07-27 | WTP5 |  | 0.0449 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-07-27 | WTP5 |  | 0.1499 | POE WTP5
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-08-10 | WTP1 | 0.3 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-08-10 | WTP1 | 0.12 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-08-10 | WTP1 | 0.29 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-08-10 | WTP1 | 0.27 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP1 | 0.3 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-08-10 | WTP1 | 0.27 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP1 | 0.28 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-08-10 | WTP1 | 0.44 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP1 | 0.26 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-08-10 | WTP1 | 0.28 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP1 | 0.26 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-08-10 | WTP1 | 0.26 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-08-10 | WTP1 | 0.4 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-08-10 | WTP1 | 0.28 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-08-10 | WTP1 | 0.23 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-08-10 | WTP1 | 3.3 | 9.4999 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-08-10 | WTP1 | 0.2 | 0.5499 | MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-08-10 | WTP1 | 0.26 | 1.4999 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-08-10 | WTP1 | 0.49 | 1.4999 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-08-10 | WTP1 | 0.16 | 0.4499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-08-10 | WTP1 | 4.2 | 6.4999 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-08-10 | WTP1 | 0.46 | 2.4999 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-08-10 | WTP1 | 0.04 | 0.1499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-08-10 | WTP1 | 0.16 | 0.2499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-08-10 | WTP1 | 0.59 | 0.9499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2063 | DIOXIN (NG/L) | 0 | NG/L | 0.0349 | 2023-08-10 | WTP1 | 0.0022 | 0.0055 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-08-10 | WTP1 | 0.096 | 0.1499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-08-10 | WTP1 | 0.053 | 0.2499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-08-10 | WTP1 | 0.014 | 0.0449 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-08-10 | WTP1 | 0.045 | 0.1499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-08-10 | WTP1 | 0.0065 | 0.0249 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-08-10 | WTP1 | 0.0076 | 0.0149 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-08-10 | WTP1 | 0.036 | 0.2499 | MAIN PLANT POE- ALL SOCS WERE SAMPLED; HOWEVER (13) HAVE TO RESAMPLE DUE TO QC FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-08-14 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-08-14 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2023-08-14 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.28 | LN(10) |  | 2023-08-14 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-08-17 | POE | 0.4 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2023-08-21 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2023-08-21 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2023-08-21 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2023-08-21 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-08-24 | WTP1 | 1.98 |  | MWP1 POE - SUBCONTRACTED TO E87683
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 1.1 | PCI/L | 3.4999 | 2023-08-24 | WTP1 | 0.352 | 1.4999 | MWP1 POE - SUBCONTRACTED TO E87683
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0.738 | PCI/L | 2.4999 | 2023-08-24 | WTP1 | 0.338 | 1.4999 | MWP1 POE - SUBCONTRACTED TO E87683
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-08-24 | WTP2 | 4.58 |  | WP2 AUX POE - SUBCONTRACTED TO E87683
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.666 | PCI/L | 3.4999 | 2023-08-24 | WTP2 | 0.164 | 1.4999 | WP2 AUX POE - SUBCONTRACTED TO E87683
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-08-24 | WTP2 | 0.591 | 1.4999 | WP2 AUX POE - SUBCONTRACTED TO E87683
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-08-24 | WTP2 | 0.0005 |  | WP2 AUX POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-08-28 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2023-08-28 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2023-08-28 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2023-08-28 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-09-11 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2023-09-11 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.38 | MG/L |  | 2023-09-11 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2023-09-11 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-09-18 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-09-18 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.41 | MG/L |  | 2023-09-18 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.26 | LN(10) |  | 2023-09-18 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-09-25 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.64 | LN(10) |  | 2023-09-25 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2023-09-25 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.23 | LN(10) |  | 2023-09-25 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-09-25 | POE | 0.4 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-09-26 | 3701 COUNTRY CLUB RD |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2023-09-26 | 3701 COUNTRY CLUB RD |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.31 | MG/L |  | 2023-09-26 | 145 ANTHONY DR |  |  | 145 ANTHONY DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2023-09-26 | 145 ANTHONY DR |  |  | 145 ANTHONY DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-09-26 | 380 HIDDEN LAKE DR |  |  | 380 HIDDEN LAKE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2023-09-26 | 380 HIDDEN LAKE DR |  |  | 380 HIDDEN LAKE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.43 | MG/L |  | 2023-09-26 | 118 BRISTOL CIR |  |  | 118 BRISTOL CIR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.26 | LN(10) |  | 2023-09-26 | 118 BRISTOL CIR |  |  | 118 BRISTOL CIR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.42 | MG/L |  | 2023-09-26 | 2801 GROVE DR |  |  | 2801 GROVE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.34 | LN(10) |  | 2023-09-26 | 2801 GROVE DR |  |  | 2801 GROVE DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.44 | MG/L |  | 2023-09-26 | 1303 S FRENCH AVE |  |  | 1303 S FRENCH AVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2023-09-26 | 1303 S FRENCH AVE |  |  | 1303 S FRENCH AVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.33 | MG/L |  | 2023-09-26 | 2515 JEWETT LN |  |  | 2515 JEWETT LN
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2023-09-26 | 2515 JEWETT LN |  |  | 2515 JEWETT LN
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-09-26 | 203 MEADOW BLVD |  |  | 203 MEADOW BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2023-09-26 | 203 MEADOW BLVD |  |  | 203 MEADOW BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2023-09-26 | 1301 W 20TH ST |  |  | 1301 W 20TH ST
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-09-26 | 1301 W 20TH ST |  |  | 1301 W 20TH ST
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2023-09-26 | 830 CENTRAL PARK DR |  |  | 830 CENTRAL PARK DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2023-09-26 | 830 CENTRAL PARK DR |  |  | 830 CENTRAL PARK DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2023-09-27 | 3100 ORLANDO DR |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2023-09-27 | 3100 ORLANDO DR |  |  | 3100 ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2023-09-27 | 1201 W SEMINOLE BLVD |  |  | 1201 W SEMINOLE BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2023-09-27 | 1201 W SEMINOLE BLVD |  |  | 1201 W SEMINOLE BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-10-02 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-10-02 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.35 | MG/L |  | 2023-10-02 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.23 | LN(10) |  | 2023-10-02 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-10-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-10-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.38 | MG/L |  | 2023-10-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.45 | LN(10) |  | 2023-10-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-11 | WTP2 | 0.0023 | 0.0149 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-11 | WTP2 | 0.0027 | 0.0249 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-11 | WTP2 | 0.023 | 0.1499 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-11 | WTP2 | 0.35 | 0.6499 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-11 | WTP2 | 0.039 | 0.0749 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-11 | WTP2 | 0.46 | 0.6499 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-11 | WTP2 | 0.024 | 0.1499 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-11 | WTP2 | 0.014 | 0.1499 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-11 | WTP2 | 0.029 | 0.2499 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-11 | WTP2 | 0.013 | 0.0449 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-11 | WTP2 | 0.003 | 0.0249 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-11 | WTP2 | 0.014 | 0.1499 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-11 | WTP2 | 0.019 | 0.0249 | AUX PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-11 | WTP1 | 0.0023 | 0.0149 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-11 | WTP1 | 0.0027 | 0.0249 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-11 | WTP1 | 0.023 | 0.1499 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-11 | WTP1 | 0.36 | 0.6499 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-11 | WTP1 | 0.039 | 0.0749 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-11 | WTP1 | 0.46 | 0.6499 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-11 | WTP1 | 0.024 | 0.1499 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-11 | WTP1 | 0.014 | 0.1499 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-11 | WTP1 | 0.029 | 0.2499 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-11 | WTP1 | 0.013 | 0.0449 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-11 | WTP1 | 0.003 | 0.0249 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-11 | WTP1 | 0.014 | 0.1499 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-11 | WTP1 | 0.019 | 0.0249 | MAIN PLANT POE- RESAMPLED SET OF SOCS DUE TO QC LAB FAILURE_SG
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-10-16 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-10-16 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.37 | MG/L |  | 2023-10-16 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.11 | LN(10) |  | 2023-10-16 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-10-19 | POE | 0.4 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-10-19 | POE | 0.4 |  | POE AUX PLANT WTP #2
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-10-23 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2023-10-23 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2023-10-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.26 | LN(10) |  | 2023-10-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2023-10-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-10-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2023-10-30 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 6.89 | LN(10) |  | 2023-10-30 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-11-06 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 27.8 | UG/L | 80.4999 | 2023-08-10 | POE | 0.47 |  | TTHM TESTED AT POE AUX PLANT
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 2.9 | UG/L | 80.4999 | 2023-08-10 | POE | 0.47 |  | TTHM TESTED AT POE MAIN PLANT
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-11-06 | WTP2 |  | 0.0149 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP2 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-11-06 | WTP2 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-11-06 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-11-06 | WTP2 |  | 0.4499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-11-06 | WTP2 |  | 9.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-11-06 | WTP2 |  | 6.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-11-06 | WTP2 |  | 0.6499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-11-06 | WTP2 |  | 2.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-11-06 | WTP2 |  | 0.0749 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-11-06 | WTP2 |  | 0.6499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-11-06 | WTP2 |  | 0.9499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-11-06 | WTP2 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-11-06 | WTP2 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-11-06 | WTP2 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-11-06 | WTP2 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-11-06 | WTP2 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-11-06 | WTP2 |  | 0.0449 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP2 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-11-06 | WTP2 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-11-06 | WTP2 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-11-06 | WTP2 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP2 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-11-06 | WTP2 |  | 0.0449 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-11-06 | WTP2 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP2 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-11-06 | WTP2 |  | 0.0149 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-11-06 | WTP2 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-11-06 | WTP1 |  | 0.0149 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP1 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-11-06 | WTP1 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-11-06 | WTP1 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-11-06 | WTP1 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-11-06 | WTP1 |  | 0.4499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-11-06 | WTP1 |  | 9.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-11-06 | WTP1 |  | 6.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-11-06 | WTP1 |  | 0.6499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-11-06 | WTP1 |  | 2.4999 | POE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-27 | WTP5 |  | 0.0249 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-27 | WTP5 |  | 0.0149 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-07-27 | WTP5 |  | 0.2499 | POE WTP5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-08-02 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-02 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-08-02 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-08-02 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-08-16 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-08-16 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-08-16 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-08-16 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2023-08-23 | DIST |  |  | 653 E. ALTAMONTE DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-08-23 | DIST |  |  | 653 E. ALTAMONTE DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.54 | MG/L |  | 2023-08-23 | DIST |  |  | 605 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-08-23 | DIST |  |  | 605 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.56 | MG/L |  | 2023-08-23 | DIST |  |  | 861 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-08-23 | DIST |  |  | 861 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2023-08-23 | DIST |  |  | 1061 ORIENTA AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-08-23 | DIST |  |  | 1061 ORIENTA AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.73 | MG/L |  | 2023-08-23 | DIST |  |  | 741 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-08-23 | DIST |  |  | 741 MAITLAND AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.51 | MG/L |  | 2023-08-23 | DIST |  |  | 1065 RAINER DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2023-08-23 | DIST |  |  | 1065 RAINER DR.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.49 | MG/L |  | 2023-08-23 | DIST |  |  | 301 JAMESTOWN BLVD.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2023-08-23 | DIST |  |  | 301 JAMESTOWN BLVD.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-08-30 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-08-30 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-08-30 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-08-30 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-09-13 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-09-13 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-09-13 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-09-13 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-09-27 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-09-27 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-09-27 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-09-27 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-10-11 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-10-11 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-10-11 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-10-11 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-10-25 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-10-25 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-10-25 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-10-25 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.9 | UG/L | 60.4999 | 2023-10-25 | L1 | 0.9 |  | 230 W SR 436 REPLACED 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 39 | UG/L | 80.4999 | 2023-10-25 | L1 | 0.47 |  | 230 W SR 436 REPLACED 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.8 | UG/L | 60.4999 | 2023-10-25 | L2 | 0.9 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 40.1 | UG/L | 80.4999 | 2023-10-25 | L2 | 0.47 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.9 | UG/L | 60.4999 | 2023-10-25 | L3 | 0.9 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 18.8 | UG/L | 80.4999 | 2023-10-25 | L3 | 0.47 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20 | UG/L | 60.4999 | 2023-10-25 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45.3 | UG/L | 80.4999 | 2023-10-25 | L4 | 0.47 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-11-08 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2023-11-08 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-11-08 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-11-08 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-11-22 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.2 | LN(10) |  | 2023-11-22 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-11-22 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-11-22 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-12-06 | WTP2 |  |  | 700 NEWPORTAVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-12-06 | WTP2 |  |  | 700 NEWPORTAVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-12-06 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-12-06 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-12-20 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2023-12-20 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-12-20 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2023-12-20 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.1 | UG/L | 60.4999 | 2024-01-24 | L1 | 0.9 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 35.8 | UG/L | 80.4999 | 2024-01-24 | L1 | 0.47 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.3 | UG/L | 60.4999 | 2024-01-24 | L2 | 0.9 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.6 | UG/L | 80.4999 | 2024-01-24 | L2 | 0.47 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.4 | UG/L | 60.4999 | 2024-01-24 | L3 | 0.9 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 25.2 | UG/L | 80.4999 | 2024-01-24 | L3 | 0.47 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.7 | UG/L | 60.4999 | 2024-01-24 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.9 | UG/L | 80.4999 | 2024-01-24 | L4 | 0.47 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.5 | UG/L | 60.4999 | 2024-04-24 | L1 | 0.9 |  | TTHM/HAA5 - 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 50.8 | UG/L | 80.4999 | 2024-04-24 | L1 | 0.75 |  | TTHM/HAA5 - 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.5 | UG/L | 60.4999 | 2024-04-24 | L2 | 0.9 |  | TTHM/HAA5 - 342 BRANTLEY CLUB PL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 58.4 | UG/L | 80.4999 | 2024-04-24 | L2 | 0.75 |  | TTHM/HAA5 - 342 BRANTLEY CLUB PL
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.6 | UG/L | 60.4999 | 2024-04-24 | L3 | 0.9 |  | TTHM/HAA5 - 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 32.5 | UG/L | 80.4999 | 2024-04-24 | L3 | 0.75 |  | TTHM/HAA5 - 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.6 | UG/L | 60.4999 | 2024-04-24 | L4 | 0.9 |  | TTHM/HAA5 - 496 CENTRAL PKWY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 60.4 | UG/L | 80.4999 | 2024-04-24 | L4 | 0.75 |  | TTHM/HAA5 - 496 CENTRAL PKWY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-07-03 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-07-03 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-07-03 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-07-03 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-07-17 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-07-17 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-07-17 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-07-17 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.5 | UG/L | 60.4999 | 2024-07-24 | L3 | 0.9 |  | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 26.5 | UG/L | 80.4999 | 2024-07-24 | L3 | 0.75 |  | 1021 ARDEN ST
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.4 | UG/L | 60.4999 | 2024-07-24 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 58.4 | UG/L | 80.4999 | 2024-07-24 | L4 | 0.75 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 44.8 | UG/L | 60.4999 | 2024-07-24 | L2 | 0.9 |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.2 | UG/L | 80.4999 | 2024-07-24 | L2 | 0.75 |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.3 | UG/L | 60.4999 | 2024-07-24 | L1 | 0.9 |  | 230 W SR 43
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 63.5 | UG/L | 80.4999 | 2024-07-24 | L1 | 0.75 |  | 230 W SR 43
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-31 | WTP2 | 0.004 |  | WTP 2, 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-07-31 | WTP5 | 0.004 |  | WTP 5, 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-07-31 | WTP5 | 0.004 |  | WTP 5, 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-07-31 | WTP2 | 0.004 |  | WTP 2, 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-07-31 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-08-14 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-07-31 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-07-31 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-07-31 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-08-14 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-08-14 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-08-14 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-08-28 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-08-28 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-08-28 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-08-28 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-09-11 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-09-11 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-09-11 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-09-11 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-09-25 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-09-25 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-09-25 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-09-25 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-10-09 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-10-09 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-10-09 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2024-10-09 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2024-10-23 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-10-23 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-10-23 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-10-23 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27 | UG/L | 60.4999 | 2024-10-23 | L1 | 0.9 |  | 230 W SR 436 REPLACED 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.8 | UG/L | 80.4999 | 2024-10-23 | L1 | 0.75 |  | 230 W SR 436 REPLACED 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.6 | UG/L | 60.4999 | 2024-10-23 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 46.2 | UG/L | 80.4999 | 2024-10-23 | L4 | 0.75 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 37.9 | UG/L | 60.4999 | 2024-10-23 | L3 | 0.9 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.1 | UG/L | 80.4999 | 2024-10-23 | L3 | 0.75 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.3 | UG/L | 60.4999 | 2024-10-23 | L2 | 0.9 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 58.6 | UG/L | 80.4999 | 2024-10-23 | L2 | 0.75 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2024-11-06 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-11-06 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2024-11-06 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2024-11-06 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-11-20 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-11-20 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2024-11-20 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-11-20 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-12-11 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-12-11 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2024-12-11 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2024-12-11 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-12-25 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-12-25 | WTP2 |  |  | 700 NEWPORT AVENUE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-12-25 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-12-25 | WTP5 |  |  | 1207 MCNEIL ROAD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-01-08 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-01-08 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-01-08 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-01-08 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.4 | UG/L | 60.4999 | 2025-01-22 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 39.2 | UG/L | 80.4999 | 2025-01-22 | L4 | 0.75 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.4 | UG/L | 60.4999 | 2025-01-22 | L3 | 0.9 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 24.9 | UG/L | 80.4999 | 2025-01-22 | L3 | 0.75 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-01-22 | WTP2 |  |  | 700 NEWPORT RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-01-22 | WTP2 |  |  | 700 NEWPORT RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-01-22 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-01-22 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23 | UG/L | 60.4999 | 2025-01-22 | L2 | 0.9 |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 37.6 | UG/L | 80.4999 | 2025-01-22 | L2 | 0.75 |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.8 | UG/L | 60.4999 | 2025-01-22 | L1 | 0.9 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 37.4 | UG/L | 80.4999 | 2025-01-22 | L1 | 0.75 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-02-05 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-02-05 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-02-05 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-02-05 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-02-19 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-02-19 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-02-19 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-02-19 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-24 | WTP2 | 0.004 |  | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-24 | WTP5 | 0.004 |  | WTP 5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-02-24 | WTP5 | 0.004 |  | WTP 5
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-02-24 | WTP2 | 0.004 |  | WTP2
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-03-05 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-03-05 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-03-05 | WTP2 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-03-05 | WTP2 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-03-19 | WTP2 |  |  | 700 NEWPORT RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-03-19 | WTP2 |  |  | 700 NEWPORT RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-03-19 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-03-19 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-04-02 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-04-02 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-04-02 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-04-02 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-04-16 | WTP5 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.5 | LN(10) |  | 2025-04-16 | WTP5 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-04-16 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-04-16 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.2 | UG/L | 60.4999 | 2025-04-23 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2025-04-23 | L4 | 0.75 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.5 | UG/L | 60.4999 | 2025-04-23 | L3 | 0.9 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.4 | UG/L | 80.4999 | 2025-04-23 | L3 | 0.75 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.4 | UG/L | 60.4999 | 2025-04-23 | L2 | 0.9 |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47.1 | UG/L | 80.4999 | 2025-04-23 | L2 | 0.75 |  | 342 BRANTLEY CLUB
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2025-04-23 | L1 | 0.9 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 48.6 | UG/L | 80.4999 | 2025-04-23 | L1 | 0.75 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-04-30 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-04-30 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-04-30 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-04-30 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-05-14 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-05-14 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-05-14 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-05-14 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-05-28 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-05-28 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-05-28 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-05-28 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-06-11 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-06-11 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-06-11 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-06-11 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-06-25 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-06-25 | WTP5 |  |  | 1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-06-25 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-06-25 | WTP2 |  |  | 700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-07-09 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-07-09 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-07-09 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-07-09 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.8 | UG/L | 60.4999 | 2025-07-23 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 38.1 | UG/L | 80.4999 | 2025-07-23 | L4 | 0.75 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.4 | UG/L | 60.4999 | 2025-07-23 | L3 | 0.9 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 26 | UG/L | 80.4999 | 2025-07-23 | L3 | 0.75 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23 | UG/L | 60.4999 | 2025-07-23 | L2 | 0.9 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45.1 | UG/L | 80.4999 | 2025-07-23 | L2 | 0.75 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.9 | UG/L | 60.4999 | 2025-07-23 | L1 | 0.9 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 36 | UG/L | 80.4999 | 2025-07-23 | L1 | 0.75 |  | 230 W SR 436
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-07-23 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-07-23 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-07-23 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-07-23 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-08-06 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-08-06 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2025-08-06 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-08-06 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-08-20 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2025-08-20 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.4 | MG/L |  | 2025-08-20 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-08-20 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-09-03 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-09-03 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-09-03 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-09-03 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2025-09-17 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-09-17 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2025-09-17 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-09-17 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-10-01 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-10-01 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-10-01 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-10-01 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2025-10-15 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-10-15 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-10-15 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-10-15 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.6 | UG/L | 60.4999 | 2025-10-22 | L4 | 0.9 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.4 | UG/L | 80.4999 | 2025-10-22 | L4 | 0.75 |  | 496 CENTRAL PARKWAY
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.1 | UG/L | 60.4999 | 2025-10-22 | L3 | 0.9 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 39.9 | UG/L | 80.4999 | 2025-10-22 | L3 | 0.75 |  | 1021 ARDEN ST.
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.1 | UG/L | 60.4999 | 2025-10-22 | L2 | 0.9 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 46.6 | UG/L | 80.4999 | 2025-10-22 | L2 | 0.75 |  | 342 BRANTLEY CLUB PLACE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.6 | UG/L | 60.4999 | 2025-10-22 | L1 | 0.9 |  | 230 W SR 436 REPLACED 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47.4 | UG/L | 80.4999 | 2025-10-22 | L1 | 0.75 |  | 230 W SR 436 REPLACED 235 S. WYMORE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-10-29 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-10-29 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-10-29 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-10-29 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-11-12 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-11-12 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-11-26 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-11-26 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-11-26 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.5 | MG/L |  | 2025-11-12 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-11-12 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-11-26 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-12-10 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-12-10 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2025-12-10 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-12-10 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-12-24 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-12-24 | WTP2 |  |  | WTP#2 (SPRING LAKE/SOUTHWEST)-700 NEWPORT AVE
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-12-24 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590026 | ALTAMONTE SPRINGS WATER DEPT (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-12-24 | WTP5 |  |  | WTP#5 (PEARL LK.CSWY)-1207 MCNEIL RD
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-11-06 | WTP1 |  | 0.0749 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-11-06 | WTP1 |  | 0.6499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-11-06 | WTP1 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-11-06 | WTP1 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-11-06 | WTP1 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-11-06 | WTP1 |  | 0.9499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-11-06 | WTP1 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-11-06 | WTP1 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-11-06 | WTP1 |  | 0.0449 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP1 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-11-06 | WTP1 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-11-06 | WTP1 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-11-06 | WTP1 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP1 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-11-06 | WTP1 |  | 0.0449 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-11-06 | WTP1 |  | 0.1499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-11-06 | WTP1 |  | 0.0249 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-11-06 | WTP1 |  | 0.0149 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-11-06 | WTP1 |  | 0.2499 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2023-11-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-11-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2023-11-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.39 | MG/L |  | 2023-11-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.3 | MG/L |  | 2023-11-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2023-11-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.34 | MG/L |  | 2023-11-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.21 | LN(10) |  | 2023-11-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-11-14 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-11-14 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2023-11-14 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-11-14 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-11-16 | POE | 0.4 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2023-11-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.19 | LN(10) |  | 2023-11-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2023-11-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2023-11-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-11-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-11-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-11-27 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.27 | LN(10) |  | 2023-11-27 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.56 | UG/L | 60.4999 | 2023-11-27 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 56.09 | UG/L | 80.4999 | 2023-11-27 | S01_L01 | 0.39 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.91 | UG/L | 60.4999 | 2023-11-27 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 63.41 | UG/L | 80.4999 | 2023-11-27 | S02_L05 | 0.39 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30 | UG/L | 60.4999 | 2023-11-27 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 46.15 | UG/L | 80.4999 | 2023-11-27 | S02_L06 | 0.39 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.59 | UG/L | 60.4999 | 2023-11-27 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.12 | UG/L | 80.4999 | 2023-11-27 | S01_L02 | 0.39 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.59 | UG/L | 60.4999 | 2023-11-27 | S01_L02 | 0.98
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.12 | UG/L | 80.4999 | 2023-11-27 | S01_L02 | 0.39
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-12-04 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.56 | LN(10) |  | 2023-12-04 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-12-04 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2023-12-04 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2023-12-06 | POE | 0.4 |  | POE AUX PLANT #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-12-11 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-12-11 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2023-12-11 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2023-12-11 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2023-12-19 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.03 | LN(10) |  | 2023-12-19 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2023-12-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.04 | LN(10) |  | 2023-12-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2023-12-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.04 | LN(10) |  | 2023-12-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2023-12-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2023-12-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2023-12-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.21 | LN(10) |  | 2023-12-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-01-08 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2024-01-08 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2024-01-08 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2024-01-08 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-01-08 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-01-08 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-01-17 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-01-17 | WTP2 |  |  | POE - AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.293 | PCI/L | 3.4999 | 2024-01-17 | WTP2 | 1.99 | 1.4999 | POE - AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-01-17 | WTP2 |  | 1.4999 | POE - AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2024-01-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-01-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2024-01-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.18 | LN(10) |  | 2024-01-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2024-01-22 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.11 | LN(10) |  | 2024-01-22 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2024-01-22 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2024-01-22 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2024-01-22 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.11 | LN(10) |  | 2024-01-22 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2024-01-29 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2024-01-29 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2024-01-29 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2024-01-29 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2024-02-05 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2024-02-05 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-02-05 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2024-02-05 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2024-02-05 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2024-02-05 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 6.7 | UG/L | 10.4999 | 2024-02-07 | POE | 1.1 |  | POE AUX PLANT WTP 2 - Q QUALIFIER
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2024-02-12 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2024-02-12 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2024-02-12 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.25 | LN(10) |  | 2024-02-12 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-02-19 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2024-02-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2024-02-19 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-02-19 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2024-02-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.41 | LN(10) |  | 2024-02-19 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.04 | UG/L | 60.4999 | 2024-02-26 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 49.89 | UG/L | 80.4999 | 2024-02-26 | S01_L01 | 0.39 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.24 | UG/L | 60.4999 | 2024-02-26 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47.17 | UG/L | 80.4999 | 2024-02-26 | S02_L05 | 0.39 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.12 | UG/L | 60.4999 | 2024-02-26 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 44.24 | UG/L | 80.4999 | 2024-02-26 | S02_L06 | 0.39 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.72 | UG/L | 60.4999 | 2024-02-26 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 44.72 | UG/L | 80.4999 | 2024-02-26 | S01_L02 | 0.39 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2024-02-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2024-02-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-02-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.17 | LN(10) |  | 2024-02-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-03-04 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2024-03-04 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-03-04 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-03-04 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-03-04 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.2 | LN(10) |  | 2024-03-04 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-03-11 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2024-03-11 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2024-03-11 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.34 | LN(10) |  | 2024-03-11 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2024-03-18 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2024-03-18 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2024-03-18 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2024-03-18 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-03-18 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2024-03-18 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-03-20 | POE | 0.4 |  | POE AUX PLANT WTP 2 - Q QUALIFIER
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2024-03-25 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-03-25 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-03-25 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.3 | LN(10) |  | 2024-03-25 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-04-01 | WTP1 |  |  | 3701 COUNTRY CLUB
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.24 | LN(10) |  | 2024-04-01 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-04-01 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-04-01 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2024-04-01 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.24 | LN(10) |  | 2024-04-01 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.19 | LN(10) |  | 2024-04-08 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-04-08 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2024-04-08 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2024-04-08 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-04-15 | POE | 0.4 |  | WQE 046 - AUX PLANT WTP 2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-04-15 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2024-04-15 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-04-15 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-04-15 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-04-15 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.35 | LN(10) |  | 2024-04-15 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0.0005 | MG/L | 0.0104 | 2024-04-16 | WTP2 | 0.0005 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-04-16 | WTP2 |  |  | POE AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-04-16 | WTP2 |  | 1.4999 | POE AUXILIARY WP2
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2024-04-22 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2024-04-22 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.18 | MG/L |  | 2024-04-22 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2024-04-22 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2024-04-29 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2024-04-29 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-04-29 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.57 | LN(10) |  | 2024-04-29 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2024-04-29 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2024-04-29 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.16 | UG/L | 60.4999 | 2021-07-08 | L2 |  |  |  | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 34.38 | UG/L | 80.4999 | 2021-07-08 | L2 |  |  |  | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.94 | UG/L | 60.4999 | 2021-07-08 | L1 |  |  |  | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 43.08 | UG/L | 80.4999 | 2021-07-08 | L1 |  |  |  | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.66 | UG/L | 60.4999 | 2022-07-13 | L2 |  |  | 561 E. OAKHURST ST. | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 48.73 | UG/L | 80.4999 | 2022-07-13 | L2 |  |  | 561 E. OAKHURST ST. | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.22 | UG/L | 60.4999 | 2022-07-13 | L1 |  |  | 350 VIRGINIA AVE. | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 49.55 | UG/L | 80.4999 | 2022-07-13 | L1 |  |  | 350 VIRGINIA AVE. | 3
3590039 | APPLE VALLEY (CONSEC) | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.2 | UG/L | 60.4999 | 2023-07-13 | L2 | 0.98 |  |  | 3
3590039 | APPLE VALLEY (CONSEC) | M | DBP | 2950 | TOTAL THMS | 33.34 | UG/L | 80.4999 | 2023-07-13 | L2 | 1 |  |  | 3
3590039 | APPLE VALLEY (CONSEC) | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.92 | UG/L | 60.4999 | 2023-07-13 | L1 | 0.98 |  | LATE DATA ENTRY. FW | 3
3590039 | APPLE VALLEY (CONSEC) | M | DBP | 2950 | TOTAL THMS | 36.36 | UG/L | 80.4999 | 2023-07-13 | L1 | 1 |  | LATE DATA ENTRY. FW | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.68 | UG/L | 60.4999 | 2024-07-11 | L1 | 0.98 |  | 350 VIRGINIA AVE. | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 42.98 | UG/L | 80.4999 | 2024-07-11 | L1 | 0.39 |  | 350 VIRGINIA AVE. | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.14 | UG/L | 60.4999 | 2024-07-11 | L2 | 0.98 |  | 561 E. OAKHURST ST. | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 44.48 | UG/L | 80.4999 | 2024-07-11 | L2 | 0.39 |  | 561 E. OAKHURST ST. | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.51 | UG/L | 60.4999 | 2025-07-10 | L1 | 0.98 |  | 350 VIRGINIA AVE; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 48.49 | UG/L | 80.4999 | 2025-07-10 | L1 | 0.44 |  | 350 VIRGINIA AVE; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.69 | UG/L | 60.4999 | 2025-07-10 | L2 | 0.98 |  | 651 E OAKHURST ST; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590039 | APPLE VALLEY (CONSEC) | D | DBP | 2950 | TOTAL THMS | 44.39 | UG/L | 80.4999 | 2025-07-10 | L2 | 0.44 |  | 651 E OAKHURST ST; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.01 | UG/L | 60.4999 | 2021-07-08 | L3 |  |  |  | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 32.94 | UG/L | 80.4999 | 2021-07-08 | L3 |  |  |  | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.91 | UG/L | 60.4999 | 2021-07-08 | L4 |  |  |  | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 53.55 | UG/L | 80.4999 | 2021-07-08 | L4 |  |  |  | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.31 | UG/L | 60.4999 | 2022-07-13 | L4 |  |  | 813 ORANOLE RD. | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 45.1 | UG/L | 80.4999 | 2022-07-13 | L4 |  |  | 813 ORANOLE RD. | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.45 | UG/L | 60.4999 | 2022-07-13 | L3 |  |  | 1201 ORANOLE RD | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 40.44 | UG/L | 80.4999 | 2022-07-13 | L3 |  |  | 1201 ORANOLE RD | 3
3590111 | DRUID HILLS (CONSEC.) | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.82 | UG/L | 60.4999 | 2023-07-13 | L3 | 0.98 |  |  | 3
3590111 | DRUID HILLS (CONSEC.) | M | DBP | 2950 | TOTAL THMS | 44.46 | UG/L | 80.4999 | 2023-07-13 | L3 | 1 |  |  | 3
3590111 | DRUID HILLS (CONSEC.) | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.42 | UG/L | 60.4999 | 2023-07-13 | L4 | 0.98 |  | LATE DATA ENTRY. FW. | 3
3590111 | DRUID HILLS (CONSEC.) | M | DBP | 2950 | TOTAL THMS | 49.84 | UG/L | 80.4999 | 2023-07-13 | L4 | 1 |  | LATE DATA ENTRY. FW. | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.06 | UG/L | 60.4999 | 2024-07-11 | L3 | 0.98 |  | 1201 ORANOLE RD | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 37.31 | UG/L | 80.4999 | 2024-07-11 | L3 | 0.39 |  | 1201 ORANOLE RD | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.82 | UG/L | 60.4999 | 2024-07-11 | L4 | 0.98 |  | 813 ORANOLE RD | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 35.99 | UG/L | 80.4999 | 2024-07-11 | L4 | 0.39 |  | 813 ORANOLE RD | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.03 | UG/L | 60.4999 | 2025-07-10 | L3 | 0.98 |  | 1201 ORANOLE RD; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 42.87 | UG/L | 80.4999 | 2025-07-10 | L3 | 0.44 |  | 1201 ORANOLE RD; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.38 | UG/L | 60.4999 | 2025-07-10 | L4 | 0.98 |  | 813 ORANOLE RD; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590111 | DRUID HILLS (CONSEC.) | D | DBP | 2950 | TOTAL THMS | 42 | UG/L | 80.4999 | 2025-07-10 | L4 | 0.44 |  | 813 ORANOLE RD; HAA5 SUBCONTRACTED TO E84589; TTHM SUBCONTRACTED TO E82535 | 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2021-01-13 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2021-01-13 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-01-13 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.3 |  |  | 2021-01-13 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.3 |  |  | 2021-01-13 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.73 | MG/L |  | 2021-01-13 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2021-01-13 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-01-13 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP2 |  | 0.5499 | NORTH PLANT WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP3 |  | 0.5499 | NORTH PLANT WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-01-14 | WTP2 |  | 1.4999 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-01-14 | WTP1 |  | 0.5499 | NORTH PLANT WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1919 | HARDNESS - CALCIUM | 32 | MG/L | 0 | 2021-01-26 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1043 | PHOSPHATE - TOTAL | 0.63 | MG/L | 0 | 2021-01-26 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.16 | MG/L |  | 2021-01-26 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1064 | CONDUCTIVITY | 280 | MG/L | 0 | 2021-01-26 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2021-01-26 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1043 | PHOSPHATE - TOTAL | 0.68 | MG/L | 0 | 2021-01-26 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-01-26 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.18 | MG/L |  | 2021-01-26 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1064 | CONDUCTIVITY | 270 | MG/L | 0 | 2021-01-26 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1919 | HARDNESS - CALCIUM | 33 | MG/L | 0 | 2021-01-26 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.57 | MG/L |  | 2021-01-27 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2021-01-27 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2021-01-27 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.9 |  |  | 2021-01-27 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2021-01-27 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.66 | LN(10) |  | 2021-01-27 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2021-01-27 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.9 |  |  | 2021-01-27 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.84 | UG/L | 60.4999 | 2021-02-02 | L3 | 0.98 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 52.85 | UG/L | 80.4999 | 2021-02-02 | L3 | 0.39 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.37 | UG/L | 60.4999 | 2021-02-02 | L4 | 0.98 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 35.61 | UG/L | 80.4999 | 2021-02-02 | L4 | 0.39 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.13 | UG/L | 60.4999 | 2021-02-02 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 40.14 | UG/L | 80.4999 | 2021-02-02 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.16 | UG/L | 60.4999 | 2021-02-02 | L2 | 0.98 |  | 261 LYMAN RD. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.06 | UG/L | 80.4999 | 2021-02-02 | L2 | 0.39 |  | 261 LYMAN RD. (3/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2021-02-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2021-02-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-02-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2021-02-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.84 | MG/L |  | 2021-02-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2021-02-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-02-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.1 |  |  | 2021-02-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2021-02-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2021-02-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-02-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2021-02-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.88 | MG/L |  | 2021-02-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-02-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-02-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.6 |  |  | 2021-02-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.1 |  |  | 2021-03-08 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2021-03-08 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2021-03-08 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-03-08 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.03 | MG/L |  | 2021-03-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2021-03-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-03-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.2 |  |  | 2021-03-10 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.9 | MG/L |  | 2021-03-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-03-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2021-03-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.7 |  |  | 2021-03-10 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2021-03-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.06 | LN(10) |  | 2021-03-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-03-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.7 |  |  | 2021-03-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2021-03-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2021-03-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-03-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.4 |  |  | 2021-03-24 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-03-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2021-03-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-03-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.7 |  |  | 2021-03-24 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2021-04-07 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2021-04-07 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-04-07 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.1 |  |  | 2021-04-07 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.08 | MG/L |  | 2021-04-08 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-04-08 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-04-08 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2021-04-08 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.95 | MG/L |  | 2021-04-08 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-04-08 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-04-08 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.9 |  |  | 2021-04-08 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1025 | FLUORIDE | 0.15 | MG/L | 4.0499 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1052 | SODIUM | 11 | MG/L | 160.4999 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1017 | CHLORIDE | 15 | MG/L | 250.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1025 | FLUORIDE | 0.15 | MG/L | 2.0499 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1055 | SULFATE | 4.4 | MG/L | 250.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.21 | LN(10) |  | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 140 | MG/L | 500.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2024-05-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2024-05-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2024-05-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.25 | LN(10) |  | 2024-05-06 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-05-13 | POE | 0.4 |  | WQE 056 - AUX PLANT WTP 2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-05-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-05-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-05-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-05-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2024-05-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-05-13 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2024-05-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2024-05-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-05-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2024-05-20 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.35 | UG/L | 60.4999 | 2024-05-22 | S02_L06 | 0.98 |  | 2501 E. LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.51 | UG/L | 60.4999 | 2024-05-22 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 61.18 | UG/L | 80.4999 | 2024-05-22 | S02_L06 | 0.39 |  | 2501 E. LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45.71 | UG/L | 80.4999 | 2024-05-22 | S01_L02 | 0.39 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.27 | UG/L | 60.4999 | 2024-05-22 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 61.69 | UG/L | 80.4999 | 2024-05-22 | S01_L01 | 0.39 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.94 | UG/L | 60.4999 | 2024-05-22 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 76.02 | UG/L | 80.4999 | 2024-05-22 | S02_L05 | 0.39 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-06-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2024-06-03 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2024-06-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-06-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2024-06-03 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2024-06-03 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-06-10 | POE | 0.4 |  | WQE 069 - AUX PLANT WTP 2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2024-06-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2024-06-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-06-10 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2024-06-10 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2024-06-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-06-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-06-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2024-06-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2024-06-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2024-06-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2024-06-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2024-06-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-06-24 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.21 | LN(10) |  | 2024-06-24 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2024-07-01 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-07-01 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-07-01 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.32 | LN(10) |  | 2024-07-01 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2024-07-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2024-07-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.18 | MG/L |  | 2024-07-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2024-07-17 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-07-23 | POE | 0.4 |  | WQE 108 AUX PLANT WTP #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2024-07-29 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2024-07-29 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.18 | MG/L |  | 2024-07-29 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.32 | LN(10) |  | 2024-07-29 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-08-08 | POE | 0.4 |  | WQE 116 AUX PLANT WTP #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2024-08-12 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2024-08-12 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2024-08-12 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.43 | LN(10) |  | 2024-08-12 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.61 | UG/L | 60.4999 | 2024-08-26 | S02_L06 | 0.98 |  | WQE 125" S02 L06 - 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.79 | UG/L | 60.4999 | 2024-08-26 | S01_L01 | 0.98 |  | WQE 123" S01 L01 - 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 63.92 | UG/L | 80.4999 | 2024-08-26 | S01_L01 | 0.39 |  | WQE 123" S01 L01 - 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.57 | UG/L | 60.4999 | 2024-08-26 | S02_L05 | 0.98 |  | WQE 124: S02 L05 - 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 58.82 | UG/L | 80.4999 | 2024-08-26 | S02_L05 | 0.39 |  | WQE 124: S02 L05 - 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45.24 | UG/L | 80.4999 | 2024-08-26 | S02_L06 | 0.39 |  | WQE 125" S02 L06 - 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.56 | UG/L | 60.4999 | 2024-08-26 | S01_L02 | 0.98 |  | WQE 126" S01 L02 - 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.12 | UG/L | 80.4999 | 2024-08-26 | S01_L02 | 0.39 |  | WQE 126" S01 L02 - 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2024-08-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.81 | LN(10) |  | 2024-08-26 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.19 | MG/L |  | 2024-08-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.22 | LN(10) |  | 2024-08-26 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-09-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2024-09-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-09-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.24 | LN(10) |  | 2024-09-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-09-10 | POE | 0.4 |  | WQE 132 AUX PLANT WTP #2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-09-12 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-09-12 | WTP2 |  | 0.667 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.829 | PCI/L | 3.4999 | 2024-09-12 | WTP2 | 0.731 | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-09-12 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-09-12 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.29 | MG/L | 10.4999 | 2024-09-12 | WTP1 | 0.025 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-12 | WTP1 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-09-12 | WTP1 |  |  | WQE 122 - MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-12 | WTP1 |  |  | WQE 122 - MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.29 | MG/L | 10.4999 | 2024-09-12 | WTP2 | 0.025 |  | AUXILIARY WP2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-09-12 | WTP2 |  |  | AUXILIARY WP2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-09-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2024-09-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2024-09-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.27 | LN(10) |  | 2024-09-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2024-10-07 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.59 | LN(10) |  | 2024-10-07 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0.0007 | MG/L | 0.0104 | 2024-10-21 | WTP2 | 0.0005 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-10-21 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0 | PCI/L | 3.4999 | 2024-10-21 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-10-21 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2024-10-21 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.17 | MG/L |  | 2024-10-07 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.36 | LN(10) |  | 2024-10-07 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2024-10-21 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-10-21 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2024-10-21 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.32 | MG/L |  | 2024-11-04 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2024-11-04 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-11-05 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2024-11-05 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-11-25 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2024-11-25 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2024-11-25 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2024-11-25 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.77 | UG/L | 60.4999 | 2024-11-25 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.24 | UG/L | 80.4999 | 2024-11-25 | S01_L01 | 0.44 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.7 | UG/L | 60.4999 | 2024-11-25 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45.09 | UG/L | 80.4999 | 2024-11-25 | S02_L05 | 0.44 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.32 | UG/L | 60.4999 | 2024-11-25 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.39 | UG/L | 80.4999 | 2024-11-25 | S02_L06 | 0.44 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.94 | UG/L | 60.4999 | 2024-11-25 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 47.41 | UG/L | 80.4999 | 2024-11-25 | S01_L02 | 0.44 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2024-12-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-12-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2024-12-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2024-12-09 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2024-12-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2024-12-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.28 | MG/L |  | 2024-12-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.4 | LN(10) |  | 2024-12-23 | WTP2 |  |  | 3100 ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2024-12-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2024-12-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.29 | MG/L |  | 2024-12-30 | WTP2 |  |  | 3100 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2024-12-30 | WTP2 |  |  | 3100 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-01-06 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2025-01-06 | WTP1 |  |  | 3701 COUNTRY CLUB RD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2025-01-06 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.21 | LN(10) |  | 2025-01-06 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-01-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.69 | LN(10) |  | 2025-01-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-01-13 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.27 | LN(10) |  | 2025-01-13 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-01-13 | POE | 0.4 |  | POE #2 WQE 193
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2025-01-20 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.25 | LN(10) |  | 2025-01-20 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2025-01-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2025-01-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2025-01-27 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.27 | LN(10) |  | 2025-01-27 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2025-01-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2025-01-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-01-30 | WTP1 | 0.0005 |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2025-01-30 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 1.31 | PCI/L | 3.4999 | 2025-01-30 | WTP2 | 0.137 | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0.787 | PCI/L | 2.4999 | 2025-01-30 | WTP2 | 0.631 | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.27 | MG/L |  | 2025-02-03 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.36 | LN(10) |  | 2025-02-03 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2025-02-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2025-02-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-02-10 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2025-02-10 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-02-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2025-02-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-02-13 | POE | 0.4 |  | WQE 203 - AUX PLANT WTP # 2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-02-17 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2025-02-17 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2025-02-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-02-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-02-24 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.44 | LN(10) |  | 2025-02-24 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-02-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2025-02-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-12 | WTP1 |  | 0.5499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-04-12 | WTP1 |  | 0.0149
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-04-12 | WTP1 |  | 0.0249
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-04-12 | WTP1 |  | 0.1499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-04-12 | WTP1 |  | 1.4999
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-04-12 | WTP1 |  | 1.4999
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-04-12 | WTP1 |  | 0.4499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-04-12 | WTP1 |  | 9.4999
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-04-12 | WTP1 |  | 6.4999
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-04-12 | WTP1 |  | 0.6499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-04-12 | WTP1 |  | 2.4999
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-04-12 | WTP1 |  | 0.0749
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-04-12 | WTP1 |  | 0.6499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-04-12 | WTP1 |  | 0.1499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-04-12 | WTP1 |  | 0.2499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-04-12 | WTP1 |  | 0.1499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-04-12 | WTP1 |  | 0.9499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-04-12 | WTP1 |  | 0.1499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-04-12 | WTP1 |  | 0.2499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-04-12 | WTP1 |  | 0.0449
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-04-12 | WTP1 |  | 0.0249
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-04-12 | WTP1 |  | 0.1499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-04-12 | WTP1 |  | 0.2499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-04-12 | WTP1 |  | 0.1499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-04-12 | WTP1 |  | 0.0249
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-04-12 | WTP1 |  | 0.0449
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-04-12 | WTP1 |  | 0.1499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-04-12 | WTP1 |  | 0.0249
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-04-12 | WTP1 |  | 0.0149
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-04-12 | WTP1 |  | 0.2499
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2021-04-12 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4020 | RADIUM-226 | 0.9 | PCI/L | 3.4999 | 2021-04-12 | WTP1 |  | 1.4999
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2021-04-12 | WTP1 |  | 1.4999
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.07 | MG/L | 10.4999 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-12 | WTP1 |  |  | N/N JQ RESULTS ACCEPTED BASED ON MS/MSD QC DATA. SEE REPORT_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.12 | MG/L |  | 2021-04-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2021-04-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-04-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2021-04-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.1 | MG/L |  | 2021-04-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.06 | LN(10) |  | 2021-04-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-04-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.7 |  |  | 2021-04-21 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2021-04-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2021-04-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-04-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.7 |  |  | 2021-04-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.054 | MG/L | 10.4999 | 2021-04-29 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-29 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.22 | MG/L | 10.4999 | 2021-04-29 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-29 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.054 | MG/L | 10.4999 | 2021-04-29 | WTP1 |  |  | HOWELL PARK WP - NITRITE J4 ( ACCEPTED BASED ON MS/MSD-83,82%,90-110%_MFC)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-04-29 | WTP2 |  | 1.4999 | NORTH WTP POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-04-29 | WTP1 |  |  | HOWELL PARK WP - NITRITE J4 ( ACCEPTED BASED ON MS/MSD-83,82%,90-110%_MFC)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.41 | UG/L | 60.4999 | 2021-05-03 | L3 | 0.98 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 25.59 | UG/L | 80.4999 | 2021-05-03 | L3 | 0.39 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.69 | UG/L | 60.4999 | 2021-05-03 | L4 | 0.98 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 18.48 | UG/L | 80.4999 | 2021-05-03 | L4 | 0.39 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.12 | UG/L | 60.4999 | 2021-05-03 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 18.31 | UG/L | 80.4999 | 2021-05-03 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.93 | UG/L | 60.4999 | 2021-05-03 | L2 | 0.98 |  | 261 LYMAN RD. (6/21 QTR DISINF BYP RPRT RCVD W/RESULTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 52.78 | UG/L | 80.4999 | 2021-05-03 | L2 | 0.39 |  | 261 LYMAN RD. (6/21 QTR DISINF BYP RPRT RCVD W/RESULTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.08 | MG/L |  | 2021-05-05 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.26 | LN(10) |  | 2021-05-05 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-05-05 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25 |  |  | 2021-05-05 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.05 | MG/L |  | 2021-05-05 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.07 | LN(10) |  | 2021-05-05 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2021-05-05 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.4 |  |  | 2021-05-05 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.86 | MG/L |  | 2021-05-05 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-05-05 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-05-05 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2021-05-05 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.04 | MG/L |  | 2021-05-19 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2021-05-19 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-05-19 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25 |  |  | 2021-05-19 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.05 | MG/L |  | 2021-05-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.05 | LN(10) |  | 2021-05-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2021-05-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2021-05-21 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.93 | MG/L |  | 2021-05-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2021-05-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-05-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.2 |  |  | 2021-05-21 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.95 | MG/L |  | 2021-06-02 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2021-06-02 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2021-06-02 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2021-06-02 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.82 | MG/L |  | 2021-06-02 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2021-06-02 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-06-02 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.5 |  |  | 2021-06-02 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2021-06-02 | WTP3 |  |  | SOUTH
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-10-21 | POE | 0.4 |  | POE- WQE 148 - AUX PLANT WTP # 2
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 6.4 | UG/L | 10.4999 | 2024-11-13 | POE | 0.4 |  | POE-WQE 160 - AUX PLANT WTP #2
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2024-12-12 | POE | 0.4 |  | POE-WQE 180 - AUX PLANT WTP #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.85 | MG/L |  | 2021-06-02 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-06-02 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2021-06-02 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.95 | MG/L |  | 2021-06-16 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2021-06-16 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-06-16 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2021-06-16 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.95 | MG/L |  | 2021-06-16 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.07 | LN(10) |  | 2021-06-16 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-06-16 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2021-06-16 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.89 | MG/L |  | 2021-06-16 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2021-06-16 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-06-16 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.4 |  |  | 2021-06-16 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.85 | MG/L |  | 2021-06-30 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.4 | LN(10) |  | 2021-06-30 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2021-06-30 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2021-06-30 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.82 | MG/L |  | 2021-06-30 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2021-06-30 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-06-30 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.5 |  |  | 2021-06-30 | WTP1 |  |  | HOWEL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2021-06-30 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2021-06-30 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-06-30 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2021-06-30 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.78 | MG/L |  | 2021-07-14 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2021-07-14 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-07-14 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2021-07-14 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2021-07-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2021-07-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-07-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2021-07-14 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2021-07-14 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2021-07-14 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2021-07-14 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 96 | MG/L |  | 2021-07-14 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-07-20 | WTP2 |  | 1.4999 | NORTH WTP POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2021-07-28 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.06 | LN(10) |  | 2021-07-28 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-07-28 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2021-07-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2021-07-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-07-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2021-08-11 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2021-08-11 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 93 | MG/L |  | 2021-08-11 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2021-08-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.09 | LN(10) |  | 2021-08-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2021-08-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2021-08-11 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2021-08-11 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-08-11 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.22 | UG/L | 60.4999 | 2021-08-23 | L3 | 0.89 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK. ENTERED AS "S" DUE TO SAMPLED DURING THE WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2950 | TOTAL THMS | 47.49 | UG/L | 80.4999 | 2021-08-23 | L3 | 0.39 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK. ENTERED AS "S" DUE TO SAMPLED DURING THE WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.48 | UG/L | 60.4999 | 2021-08-23 | L4 | 0.89 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P. ENTERED AS "S" DUE TO SAMPLUNG ON WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2950 | TOTAL THMS | 22.35 | UG/L | 80.4999 | 2021-08-23 | L4 | 0.39 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P. ENTERED AS "S" DUE TO SAMPLUNG ON WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.88 | UG/L | 60.4999 | 2021-08-23 | L1 | 0.89 |  | CWP4 1817 DOVER RD. ENTERED AS "S" DUE TO SAMPLED DURING THE WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2950 | TOTAL THMS | 39.07 | UG/L | 80.4999 | 2021-08-23 | L1 | 0.39 |  | CWP4 1817 DOVER RD. ENTERED AS "S" DUE TO SAMPLED DURING THE WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.12 | UG/L | 60.4999 | 2021-08-23 | L2 | 0.89 |  | CWP5 261 LYMAN RD. (NOT DR.) ENTERED AS "S" DUE TO SAMPLED DURING THE WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | S | DBP | 2950 | TOTAL THMS | 62.19 | UG/L | 80.4999 | 2021-08-23 | L2 | 0.39 |  | CWP5 261 LYMAN RD. (NOT DR.) ENTERED AS "S" DUE TO SAMPLED DURING THE WRONG WEEK_MFC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2021-08-25 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2021-08-25 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 93 | MG/L |  | 2021-08-25 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2021-08-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2021-08-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-08-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2021-08-25 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-08-25 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-08-25 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.82 | MG/L |  | 2021-09-08 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2021-09-08 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2021-09-08 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.84 | MG/L |  | 2021-09-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.17 | LN(10) |  | 2021-09-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2021-09-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2021-09-08 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2021-09-08 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-09-08 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2021-09-22 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2021-09-22 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2021-09-22 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-09-22 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.16 | LN(10) |  | 2021-09-22 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-09-22 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.73 | MG/L |  | 2021-09-22 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2021-09-22 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2021-09-22 | WTP3 |  |  | SOUTH
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.92 | UG/L | 60.4999 | 2025-02-25 | S01_L01 | 0.98 |  | WQE 207:SO1 LO1 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.85 | UG/L | 80.4999 | 2025-02-25 | S01_L01 | 0.44 |  | WQE 207:SO1 LO1 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.79 | UG/L | 60.4999 | 2025-02-25 | S02_L05 | 0.98 |  | WQE 208: SO2 LO5 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 50.62 | UG/L | 80.4999 | 2025-02-25 | S02_L05 | 0.44 |  | WQE 208: SO2 LO5 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.02 | UG/L | 60.4999 | 2025-02-25 | S02_L06 | 0.98 |  | WQE 209: SO2 LO6 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 48.13 | UG/L | 80.4999 | 2025-02-25 | S02_L06 | 0.44 |  | WQE 209: SO2 LO6 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.63 | UG/L | 60.4999 | 2025-02-25 | S01_L02 | 0.98 |  | WQE 210: SO1 LO2 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.55 | UG/L | 80.4999 | 2025-02-25 | S01_L02 | 0.44 |  | WQE 210: SO1 LO2 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-03-03 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.16 | LN(10) |  | 2025-03-03 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-03-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2025-03-03 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-03-10 | WTP1 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.17 | LN(10) |  | 2025-03-10 | WTP1 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-03-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2025-03-10 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-03-17 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.16 | LN(10) |  | 2025-03-17 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-03-17 | POE | 0.4 |  | WQE 216 - AUX PLANT WTP # 2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-03-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2025-03-17 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-03-24 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.34 | LN(10) |  | 2025-03-24 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-03-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 7.79 | MG/L |  | 2025-03-24 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-03-31 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.31 | LN(10) |  | 2025-03-31 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-03-31 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2025-03-31 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.2 | MG/L |  | 2025-04-07 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.38 | LN(10) |  | 2025-04-07 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-04-07 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2025-04-07 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2025-04-14 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.27 | LN(10) |  | 2025-04-14 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-04-14 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2025-04-14 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2025-04-21 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.19 | LN(10) |  | 2025-04-21 | WTP2 |  |  | ORLANDO DR
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-04-21 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2025-04-21 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2025-04-28 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2025-04-28 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-04-28 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2025-04-28 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-04-29 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2025-04-29 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 2.03 | PCI/L | 3.4999 | 2025-04-29 | WTP2 | 0.166 | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 1.09 | PCI/L | 2.4999 | 2025-04-29 | WTP2 | 0.702 | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.078 | MG/L | 10.4999 | 2025-04-29 | WTP1 | 0.025 |  | POE-WQE 241 - MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-29 | WTP1 |  |  | POE-WQE 241 - MAIN PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.26 | MG/L | 10.4999 | 2025-04-29 | WTP2 | 0.025 |  | WQE 242 - AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-04-29 | WTP2 |  |  | WQE 242 - AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2025-05-05 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.42 | LN(10) |  | 2025-05-05 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-05-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2025-05-06 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-05-13 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2025-05-13 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-05-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2025-05-13 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.21 | MG/L |  | 2025-05-19 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.33 | LN(10) |  | 2025-05-19 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-05-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2025-05-20 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.55 | UG/L | 60.4999 | 2025-05-22 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 70.6 | UG/L | 80.4999 | 2025-05-22 | S01_L01 | 0.44 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.17 | UG/L | 60.4999 | 2025-05-22 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.94 | UG/L | 80.4999 | 2025-05-22 | S02_L05 | 0.44 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.31 | UG/L | 60.4999 | 2025-05-22 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 60.18 | UG/L | 80.4999 | 2025-05-22 | S02_L06 | 0.44 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.68 | UG/L | 60.4999 | 2025-05-22 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.86 | UG/L | 80.4999 | 2025-05-22 | S01_L02 | 0.44 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-05-27 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2025-05-27 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.26 | MG/L |  | 2025-05-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2025-05-27 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-06-02 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.23 | LN(10) |  | 2025-06-02 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.25 | MG/L |  | 2025-06-02 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2025-06-02 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.18 | MG/L |  | 2025-06-09 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.39 | LN(10) |  | 2025-06-09 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-06-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2025-06-09 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-06-16 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2025-06-16 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-06-16 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2025-06-16 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.22 | MG/L |  | 2025-06-23 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.29 | LN(10) |  | 2025-06-23 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.24 | MG/L |  | 2025-06-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-06-23 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-06-30 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.04 | LN(10) |  | 2025-06-30 | WTP2 |  |  | ORLANDO DRIVE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.23 | MG/L |  | 2025-06-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0.0006 | MG/L | 0.0104 | 2025-07-21 | WTP2 | 0.0005
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2025-07-21 | WTP2 | 2.7
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 1.24 | PCI/L | 3.4999 | 2025-07-21 | WTP2 | 0.819 | 1.4999
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-07-21 | WTP2 | 0.662 | 1.4999
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.38 | UG/L | 60.4999 | 2025-08-26 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.95 | UG/L | 80.4999 | 2025-08-26 | S01_L01 | 0.44 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 65.74 | UG/L | 80.4999 | 2025-08-26 | S02_L05 | 0.44 |  | 3751 E SR 46 - HAA5 J QUAL - SAMPLE BIASED HIGH, ACCEPTED_LMC
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.6 | UG/L | 80.4999 | 2025-08-26 | S02_L06 | 0.44 |  | 2501 LAKE MARY BLVD - HAA5 J QUAL - SAMPLE BIASED HIGH, ACCEPTED_LMC
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.75 | UG/L | 60.4999 | 2025-08-26 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 58.61 | UG/L | 80.4999 | 2025-08-26 | S01_L02 | 0.44 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 6.7 | UG/L | 10.4999 | 2025-09-15 | POE | 0.4 |  | AUX PLANT BROMATE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-04-17 | POE | 0.4 |  | AUX PLANT POE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 6.6 | UG/L | 10.4999 | 2025-05-08 | POE | 0.4 |  | AUX PLANT POE BROMATE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-06-10 | POE | 0.4 |  | BROMATE AUX PLANT
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-07-14 | POE | 0.4 |  | BROMATE AUX PLANT
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-08-11 | POE | 0.4 |  | AUX PLANT BROMATE
3590205 | SANFORD, CITY OF (2 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2025-06-30 | WTP1 |  |  | 3701 COUNTRY CLUB ROAD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.03 | UG/L | 60.4999 | 2025-08-26 | S02_L05 | 0.98 |  | 3751 E SR 46 - HAA5 J QUAL - SAMPLE BIASED HIGH, ACCEPTED_LMC
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.36 | UG/L | 60.4999 | 2025-08-26 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD - HAA5 J QUAL - SAMPLE BIASED HIGH, ACCEPTED_LMC
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-10-16 | POE | 0.4 |  | BROMATE- WQE 331 AUX PLANT WTP2 POE
3590205 | SANFORD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2025-10-23 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2025-10-23 | WTP2 |  |  | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4020 | RADIUM-226 | 0.939 | PCI/L | 3.4999 | 2025-10-23 | WTP2 | 0.141 | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2025-10-23 | WTP2 |  | 1.4999 | POE
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 0 | UG/L | 10.4999 | 2025-11-13 | POE | 0.4 |  | BROMATE- WQE 341 AUX PLANT WTP2 POE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.79 | UG/L | 60.4999 | 2025-11-24 | S01_L01 | 0.98 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 64.52 | UG/L | 80.4999 | 2025-11-24 | S01_L01 | 0.44 |  | 531 N PALMETTO AVE
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.84 | UG/L | 60.4999 | 2025-11-24 | S02_L05 | 0.98 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 61.94 | UG/L | 80.4999 | 2025-11-24 | S02_L05 | 0.44 |  | 3751 E SR 46
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.35 | UG/L | 60.4999 | 2025-11-24 | S02_L06 | 0.98 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 57.27 | UG/L | 80.4999 | 2025-11-24 | S02_L06 | 0.44 |  | 2501 LAKE MARY BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.05 | UG/L | 60.4999 | 2025-11-24 | S01_L02 | 0.98 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 58.89 | UG/L | 80.4999 | 2025-11-24 | S01_L02 | 0.44 |  | 100 WELDON BLVD
3590205 | SANFORD, CITY OF (2 WPS) | N | DBP | 1011 | BROMATE | 3.2 | UG/L | 10.4999 | 2025-12-01 | POE | 0.4 |  | BROMATE- WQE 349 AUX PLANT WTP2 POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.93 | MG/L |  | 2021-10-06 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.49 | LN(10) |  | 2021-10-06 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 129 | MG/L |  | 2021-10-06 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2021-10-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.16 | LN(10) |  | 2021-10-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2021-10-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2021-10-06 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-10-06 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-10-06 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.96 | MG/L |  | 2021-10-20 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.37 | LN(10) |  | 2021-10-20 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-10-20 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2021-10-20 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.13 | LN(10) |  | 2021-10-20 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2021-10-20 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2021-10-20 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2021-10-20 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2021-10-20 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 1.5 | UG/L | 249.9999 | 2021-10-21 | WTP2 | 0.9 | 1.4999 | HSP #7 ( NORTH WTP) POE (DALAPON 1.5 UG/L). THIS 1.5 ENTRY WILL TRIGGER QUARTERLY TESTING IN PWS.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.77 | UG/L | 60.4999 | 2021-11-02 | L3 |  |  | 7603 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 37.44 | UG/L | 80.4999 | 2021-11-02 | L3 |  |  | 7603 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.06 | UG/L | 60.4999 | 2021-11-02 | L4 |  |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 29.19 | UG/L | 80.4999 | 2021-11-02 | L4 |  |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.87 | UG/L | 60.4999 | 2021-11-02 | L1 |  |  | 1817 DOVER RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 28.77 | UG/L | 80.4999 | 2021-11-02 | L1 |  |  | 1817 DOVER RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.4 | UG/L | 60.4999 | 2021-11-02 | L2 |  |  | 261 LYMAN RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.36 | UG/L | 80.4999 | 2021-11-02 | L2 |  |  | 261 LYMAN RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.95 | MG/L |  | 2021-11-03 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.23 | LN(10) |  | 2021-11-03 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2021-11-03 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2021-11-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.09 | LN(10) |  | 2021-11-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2021-11-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.82 | MG/L |  | 2021-11-03 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-11-03 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2021-11-03 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.96 | MG/L |  | 2021-11-17 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2021-11-17 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 124 | MG/L |  | 2021-11-17 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2021-11-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.07 | LN(10) |  | 2021-11-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2021-11-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2021-11-17 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2021-11-17 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2021-11-17 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.84 | MG/L |  | 2021-12-01 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2021-12-01 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2021-12-01 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2021-12-01 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.05 | LN(10) |  | 2021-12-01 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2021-12-01 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2021-12-01 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2021-12-01 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2021-12-01 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2021-12-15 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2021-12-15 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2021-12-15 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2021-12-15 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2021-12-15 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-12-15 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2021-12-15 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2021-12-15 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2021-12-15 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2021-12-29 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2021-12-29 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2021-12-29 | WTP2 |  |  | NORTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2021-12-29 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2021-12-29 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2021-12-29 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.73 | MG/L |  | 2021-12-29 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2021-12-29 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2021-12-29 | WTP3 |  |  | SOUTH
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP1 |  | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0.43 | UG/L | 74.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP2 |  | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-01-11 | WTP3 |  | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-01-11 | WTP2 |  | 1.4999 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.093 | MG/L | 10.4999 | 2022-01-11 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-11 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.19 | MG/L | 10.4999 | 2022-01-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.097 | MG/L | 10.4999 | 2022-01-11 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0.09 | MG/L | 1.4999 | 2022-01-11 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-01-12 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.78 | MG/L |  | 2022-01-12 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2022-01-12 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2022-01-12 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2022-01-12 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 125 | MG/L |  | 2022-01-12 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-01-26 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2022-01-26 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-01-26 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-01-26 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2022-01-26 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-01-26 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.88 | MG/L |  | 2022-01-26 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-01-12 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-01-12 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2022-01-12 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-01-26 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-01-26 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.25 | UG/L | 60.4999 | 2022-02-01 | L4 | 0.98 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 30.23 | UG/L | 80.4999 | 2022-02-01 | L4 | 0.39 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.29 | UG/L | 60.4999 | 2022-02-01 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 34.26 | UG/L | 80.4999 | 2022-02-01 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.78 | UG/L | 60.4999 | 2022-02-01 | L2 | 0.98 |  | 261 LYMAN RD. (HLKD)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 51.99 | UG/L | 80.4999 | 2022-02-01 | L2 | 0.39 |  | 261 LYMAN RD. (HLKD)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2022-02-09 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-02-09 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2022-02-09 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2022-02-09 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.6 | LN(10) |  | 2022-02-09 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2022-02-09 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.78 | MG/L |  | 2022-02-09 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2022-02-09 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-02-09 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.73 | MG/L |  | 2022-02-23 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-02-23 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2022-02-23 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2022-02-23 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-02-23 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-02-23 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-02-23 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2022-02-23 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-02-23 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-03-09 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2022-03-09 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-03-09 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2022-03-09 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-03-09 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-03-09 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2022-03-09 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2022-03-09 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2022-03-09 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-03-23 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2022-03-23 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2022-03-23 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-03-23 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.05 | LN(10) |  | 2022-03-23 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 94 | MG/L |  | 2022-03-23 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.85 | MG/L |  | 2022-03-23 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2022-03-23 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-03-23 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2022-04-06 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-04-06 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-04-06 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-04-06 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-04-06 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2022-04-06 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2022-04-06 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2022-04-06 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-04-06 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-04-06 | WTP2 |  | 1.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.78 | MG/L |  | 2022-04-20 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2022-04-20 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2022-04-20 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2022-04-20 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-04-20 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-04-20 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.82 | MG/L |  | 2022-04-20 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2022-04-20 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2022-04-20 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.39 | UG/L | 60.4999 | 2021-01-28 | L1 | 0.98 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 44.45 | UG/L | 80.4999 | 2021-01-28 | L1 | 0.39 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.98 | UG/L | 60.4999 | 2021-01-28 | L2 | 0.98 |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 3.55 | UG/L | 80.4999 | 2021-01-28 | L2 | 0.39 |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.91 | UG/L | 60.4999 | 2021-02-25 | L1 | 0.98 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 25.54 | UG/L | 80.4999 | 2021-02-25 | L1 | 0.39 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.81 | UG/L | 60.4999 | 2021-02-25 | L2 | 0.98 |  | 390 LAKE LENELLE (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 20.4 | UG/L | 80.4999 | 2021-02-25 | L2 | 0.39 |  | 390 LAKE LENELLE (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.41 | UG/L | 60.4999 | 2021-03-26 | L1 |  |  | 803 MAZURKA. 1Q AVERAGE TTHM =32.06 ; HAA5 = 7.24 | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 26.18 | UG/L | 80.4999 | 2021-03-26 | L1 |  |  | 803 MAZURKA. 1Q AVERAGE TTHM =32.06 ; HAA5 = 7.24 | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.25 | UG/L | 60.4999 | 2021-03-26 | L2 |  |  | LAKE LENELLE. 1Q21 AVERAGE TTHM= 15.96 ; HAA5= 8.01 | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 23.92 | UG/L | 80.4999 | 2021-03-26 | L2 |  |  | LAKE LENELLE. 1Q21 AVERAGE TTHM= 15.96 ; HAA5= 8.01 | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.64 | UG/L | 60.4999 | 2021-04-23 | L1 |  |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 27.21 | UG/L | 80.4999 | 2021-04-23 | L1 |  |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.82 | UG/L | 60.4999 | 2021-04-23 | L2 |  |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 25.12 | UG/L | 80.4999 | 2021-04-23 | L2 |  |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.94 | UG/L | 60.4999 | 2021-06-25 | L1 | 0.98 |  | 803 MAZURKA DR. | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 51.24 | UG/L | 80.4999 | 2021-06-25 | L1 | 0.39 |  | 803 MAZURKA DR. | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 8.86 | UG/L | 60.4999 | 2021-06-25 | L2 | 0.98 |  | 390 LAKE LENELLE (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 47.98 | UG/L | 80.4999 | 2021-06-25 | L2 | 0.39 |  | 390 LAKE LENELLE (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.8 | UG/L | 60.4999 | 2021-07-23 | L1 |  |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 8.37 | UG/L | 80.4999 | 2021-07-23 | L1 |  |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.42 | UG/L | 60.4999 | 2021-07-23 | L2 |  |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 10.25 | UG/L | 80.4999 | 2021-07-23 | L2 |  |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2021-09-15 | WTP2 |  |  | WP2
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-09-15 | WTP2 |  |  | WP2
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.74 | UG/L | 60.4999 | 2021-10-26 | L1 | 0.98 |  | 803 MAZURKA DR. | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 49.85 | UG/L | 80.4999 | 2021-10-26 | L1 | 0.39 |  | 803 MAZURKA DR. | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.41 | UG/L | 60.4999 | 2021-10-26 | L2 | 0.98 |  | 390 LAKE LENELLE DR. (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 45.24 | UG/L | 80.4999 | 2021-10-26 | L2 | 0.39 |  | 390 LAKE LENELLE DR. (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.35 | UG/L | 60.4999 | 2022-01-27 | L1 | 0.98 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 24.87 | UG/L | 80.4999 | 2022-01-27 | L1 | 0.39 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.78 | UG/L | 60.4999 | 2022-01-27 | L2 | 0.98 |  | 390 LAKE LENELLE (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 22.58 | UG/L | 80.4999 | 2022-01-27 | L2 | 0.39 |  | 390 LAKE LENELLE (HLKD) | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.93 | UG/L | 60.4999 | 2022-10-25 | L1 | 0.98 |  | 803 MAZURKA (HAA5). TTHM ALL HAVE Q QUALIFIERS-NOT ENT'D. | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.86 | UG/L | 60.4999 | 2022-10-25 | L2 | 0.98 |  | 390 LAKE LENELLE (HAA5). TTHMS ALL HAVE Q QUALIFIERS-NOT ENTD. | 4
3590186 | CHULUOTA WATER SYSTEM | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.33 | UG/L | 60.4999 | 2022-12-12 | L2 |  |  | MAKEUP SAMPLES FOR 10/2022. OCT SAMPLES WERE ANALYZED OUTSIDE OF HOLD TIME_SMD | 4
3590186 | CHULUOTA WATER SYSTEM | S | DBP | 2950 | TOTAL THMS | 49.97 | UG/L | 80.4999 | 2022-12-12 | L2 |  |  | MAKEUP SAMPLES FOR 10/2022. OCT SAMPLES WERE ANALYZED OUTSIDE OF HOLD TIME_SMD | 4
3590186 | CHULUOTA WATER SYSTEM | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 11.01 | UG/L | 60.4999 | 2022-12-12 | L1 |  |  | MAKEUP SAMPLES FOR 10/2022. OCT SAMPLES WERE ANALYZED OUTSIDE OF HOLD TIME_SMD | 4
3590186 | CHULUOTA WATER SYSTEM | S | DBP | 2950 | TOTAL THMS | 46.91 | UG/L | 80.4999 | 2022-12-12 | L1 |  |  | MAKEUP SAMPLES FOR 10/2022. OCT SAMPLES WERE ANALYZED OUTSIDE OF HOLD TIME_SMD | 4
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.17 | MG/L | 10.4999 | 2022-12-14 | WTP2 | 0.024 |  | 2022 NITRATE NITRITE_SMD
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-14 | WTP2 | 0.0034 |  | 2022 NITRATE NITRITE_SMD
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.098 | MG/L | 10.4999 | 2023-03-14 | WTP2 | 0.024 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-03-14 | WTP2 | 0.5 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1010 | BARIUM | 0.019 | MG/L | 2.4999 | 2023-03-14 | WTP2 | 0.003 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1025 | FLUORIDE | 0.16 | MG/L | 4.0499 | 2023-03-14 | WTP2 | 0.0099 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-14 | WTP2 | 0.0005 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-14 | WTP2 | 1e-05 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-14 | WTP2 | 0.0012 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1052 | SODIUM | 78 | MG/L | 160.4999 | 2023-03-14 | WTP2 | 0.8 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1025 | FLUORIDE | 0.16 | MG/L | 2.0499 | 2023-03-14 | WTP2 | 0.0099 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-14 | WTP2 | 0.0067 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-14 | WTP2 | 0.0005 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1055 | SULFATE | 16 | MG/L | 250.4999 | 2023-03-14 | WTP2 | 0.034 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-14 | WTP2 | 0.05 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 6.01 | LN(10) |  | 2023-03-14 | WTP2 |  |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 420 | MG/L | 500.4999 | 2023-03-14 | WTP2 | 5 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 2905 | FOAMING AGENTS | 0.051 |  | 0.5499 | 2023-03-14 | WTP2 | 0.04 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-03-14 | WTP2 | 0.24 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-03-14 | WTP2 | 0.48 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-03-14 | WTP2 | 0.49 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-03-14 | WTP2 | 0.44 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-03-14 | WTP2 | 0.4 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-03-14 | WTP2 | 0.28 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-03-14 | WTP2 | 0.4 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-03-14 | WTP2 | 0.41 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-03-14 | WTP2 | 0.44 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-03-14 | WTP2 | 0.32 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-03-14 | WTP2 | 0.36 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-03-14 | WTP2 | 0.33 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-14 | WTP2 | 0.25 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-03-14 | WTP2 | 0.44 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-14 | WTP2 | 0.49 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-03-14 | WTP2 | 0.37 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-03-14 | WTP2 | 0.16 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-03-14 | WTP2 | 0.2 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-03-14 | WTP2 | 0.33 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-03-14 | WTP2 | 6 | 9.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-03-14 | WTP2 | 0.37 | 0.4499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.39 | UG/L | 60.4999 | 2022-02-01 | L3 | 0.98 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 40.04 | UG/L | 80.4999 | 2022-02-01 | L3 | 0.39 |  | 7603 CITRUS AVE.
3590186 | CHULUOTA WATER SYSTEM | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-03-14 | WTP2 | 0.26 | 0.5499 | VOC (ALL OK)
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-03-14 | WTP2 | 0.0069 | 0.0149 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-03-14 | WTP2 | 0.0071 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-03-14 | WTP2 | 0.0068 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-03-14 | WTP2 | 0.12 | 1.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-03-14 | WTP2 | 0.9 | 1.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-03-14 | WTP2 | 5.9 | 6.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-03-14 | WTP2 | 0.5 | 0.6499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-03-14 | WTP2 | 1.8 | 2.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-03-14 | WTP2 | 0.06 | 0.0749 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-03-14 | WTP2 | 0.5 | 0.6499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-03-14 | WTP2 | 0.09 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-03-14 | WTP2 | 0.18 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-03-14 | WTP2 | 0.51 | 0.9499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-03-14 | WTP2 | 0.09 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-03-14 | WTP2 | 0.15 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-03-14 | WTP2 | 0.0052 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-03-14 | WTP2 | 0.09 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-03-14 | WTP2 | 0.0063 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-03-14 | WTP2 | 0.0061 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-03-14 | WTP2 | 0.0091 | 0.0149 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.8 | PCI/L | 15.4999 | 2023-03-14 | WTP2 | 1.4 |  | URANIUM WAS NOT REPORTED IN PCI/L-RESULT NOT ENTERED. GROSS ALPHA SUBS FOR URANIUM.
3590186 | CHULUOTA WATER SYSTEM | N | RAD | 4020 | RADIUM-226 | 1.3 | PCI/L | 3.4999 | 2023-03-14 | WTP2 | 0.4 | 1.4999 | URANIUM WAS NOT REPORTED IN PCI/L-RESULT NOT ENTERED. GROSS ALPHA SUBS FOR URANIUM.
3590186 | CHULUOTA WATER SYSTEM | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-03-14 | WTP2 | 0.6 | 1.4999 | URANIUM WAS NOT REPORTED IN PCI/L-RESULT NOT ENTERED. GROSS ALPHA SUBS FOR URANIUM.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-03-14 | WTP2 | 6 | 9.4999 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-03-14 | WTP2 | 0.019 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-03-14 | WTP2 | 0.006 | 0.0449 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-03-14 | WTP2 | 0.0052 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-03-14 | WTP2 | 0.095 | 0.1499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-03-14 | WTP2 | 0.015 | 0.0249 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-03-14 | WTP2 | 0.38 | 0.0449 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-03-14 | WTP2 | 0.053 | 0.2499 | SOC (MDLS IN ANALYSIS RESULT COLUMN DO NOT MATCH THOSE IN THE LAB MDL COLUMN FOR ENDO,2042 HEX...,HEP,2,4-D,BENZO,PENTA,PCB,CHLOR-NOT ENT'D) THERE ARE NO J QUALIFIERS ON THE SOCS.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.35 | UG/L | 60.4999 | 2022-05-02 | L3 | 0.98 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 49.17 | UG/L | 80.4999 | 2022-05-02 | L3 | 0.39 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.29 | UG/L | 60.4999 | 2022-05-02 | L4 | 0.98 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 39.87 | UG/L | 80.4999 | 2022-05-02 | L4 | 0.39 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.08 | UG/L | 60.4999 | 2022-05-02 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 37.65 | UG/L | 80.4999 | 2022-05-02 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.63 | UG/L | 60.4999 | 2022-05-02 | L2 | 0.98 |  | 261 LYMAN RD. (HLKD)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 62.09 | UG/L | 80.4999 | 2022-05-02 | L2 | 0.39 |  | 261 LYMAN RD. (HLKD)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-05-04 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-05-04 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2022-05-04 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2022-05-04 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-05-04 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2022-05-04 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-05-05 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-05-05 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-05-05 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.82 | MG/L |  | 2022-05-18 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-05-18 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-05-18 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-05-18 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2022-05-18 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 99 | MG/L |  | 2022-05-18 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2022-05-18 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-05-18 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2022-05-18 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2022-06-01 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-06-01 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-06-01 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-06-01 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-06-01 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-06-01 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2022-06-01 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.03 | LN(10) |  | 2022-06-01 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-06-01 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-06-15 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2022-06-15 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-06-15 | WTP3 |  |  | SOUTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-06-15 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-06-15 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-06-15 | WTP1 |  |  | HOWELL PARK WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2022-06-15 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2022-06-15 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-06-15 | WTP2 |  |  | NORTH WP PH PO4 ALKALINITY
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-07-11 | WTP2 | 0.9 | 1.4999 | DALAPON - NORTH WP (PLUS EXTRA CHEMS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-07-11 | WTP2 | 0.09 | 0.1499 | DALAPON - NORTH WP (PLUS EXTRA CHEMS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-07-11 | WTP2 | 0.18 | 0.2499 | DALAPON - NORTH WP (PLUS EXTRA CHEMS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-07-11 | WTP2 | 0.095 | 0.1499 | DALAPON - NORTH WP (PLUS EXTRA CHEMS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-07-11 | WTP2 | 0.09 | 0.2499 | DALAPON - NORTH WP (PLUS EXTRA CHEMS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-07-11 | WTP2 | 0.038 | 0.0449 | DALAPON - NORTH WP (PLUS EXTRA CHEMS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-07-13 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-13 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-07-13 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2022-07-13 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-07-13 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-07-13 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-07-13 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.91 | MG/L |  | 2022-07-13 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2022-07-13 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2022-07-27 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2022-07-27 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2022-07-27 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2022-07-27 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2022-07-27 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 97 | MG/L |  | 2022-07-27 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.82 | MG/L |  | 2022-07-27 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2022-07-27 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-07-27 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.65 | UG/L | 60.4999 | 2022-08-01 | L3 | 0.98 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 66.19 | UG/L | 80.4999 | 2022-08-01 | L3 | 0.39 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.91 | UG/L | 60.4999 | 2022-08-01 | L4 | 0.98 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 52.08 | UG/L | 80.4999 | 2022-08-01 | L4 | 0.39 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.75 | UG/L | 60.4999 | 2022-08-01 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.66 | UG/L | 80.4999 | 2022-08-01 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.15 | UG/L | 60.4999 | 2022-08-01 | L2 | 0.98 |  | 261 LYMAN RD. (HLKD) ON 9/22/22 RCVD "REVISED" REPORT WHICH INCLUDED 9/22 QTR DISINF BYP REPORT (HLKD THIS ALSO)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 76.04 | UG/L | 80.4999 | 2022-08-01 | L2 | 0.39 |  | 261 LYMAN RD. (HLKD) ON 9/22/22 RCVD "REVISED" REPORT WHICH INCLUDED 9/22 QTR DISINF BYP REPORT (HLKD THIS ALSO)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-08-10 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-08-10 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-08-10 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2022-08-10 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-08-10 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2022-08-10 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.91 | MG/L |  | 2022-08-10 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2022-08-10 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2022-08-10 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2022-08-24 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2022-08-24 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-08-24 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2022-08-24 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2022-08-24 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2022-08-24 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1 | MG/L |  | 2022-08-24 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2022-08-24 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2022-08-24 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2022-09-07 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-09-07 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-09-07 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2022-09-07 | WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-09-07 | WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-09-07 | WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.78 | MG/L |  | 2022-09-07 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2022-09-07 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-09-07 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2022-09-21 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2022-09-21 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 0.84 | MG/L |  | 2022-09-21 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2022-09-21 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2022-09-21 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 84 | MG/L |  | 2022-09-21 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2022-09-21 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-09-21 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 84 | MG/L |  | 2022-09-21 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2022-10-04 | WTP2 |  | 1.4999 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-10-05 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2022-10-05 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2022-10-05 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-10-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2022-10-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2022-10-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2022-10-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-10-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2022-10-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2022-10-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2022-10-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-10-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2022-10-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2022-10-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2022-10-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.87 | MG/L |  | 2022-10-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-10-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2022-10-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.35 | UG/L | 60.4999 | 2022-11-01 | L3 | 0.98 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 57.32 | UG/L | 80.4999 | 2022-11-01 | L3 | 0.39 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.81 | UG/L | 60.4999 | 2022-11-01 | L4 | 0.98 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 61.53 | UG/L | 80.4999 | 2022-11-01 | L4 | 0.39 |  | 5401 LAKE HOWELL RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.92 | UG/L | 60.4999 | 2022-11-01 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 50.32 | UG/L | 80.4999 | 2022-11-01 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.49 | UG/L | 60.4999 | 2022-11-01 | L2 | 0.98 |  | 261 LYMAN RD. (12/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 68.98 | UG/L | 80.4999 | 2022-11-01 | L2 | 0.39 |  | 261 LYMAN RD. (12/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-11-02 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2022-11-02 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2022-11-02 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-11-02 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2022-11-02 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2022-11-02 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2022-11-02 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2022-11-02 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2022-11-02 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-11-16 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-11-16 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-11-16 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-11-16 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2022-11-16 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2022-11-16 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2022-11-16 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2022-11-16 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-11-16 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-11-30 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2022-11-30 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-11-30 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2022-11-30 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2022-11-30 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-11-30 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2022-11-30 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2022-11-30 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2022-11-30 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2022-12-13 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-12-13 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-12-13 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2022-12-13 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2022-12-13 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2022-12-13 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.84 | MG/L |  | 2022-12-13 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2022-12-13 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2022-12-13 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2022-12-28 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-12-28 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-12-28 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2022-12-28 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2022-12-28 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2022-12-28 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.88 | MG/L |  | 2022-12-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2022-12-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 3 | UG/L | 10499.9999 | 2023-01-03 | WTP2 | 0.44 | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0.36 | UG/L | 1499.9999 | 2023-01-03 | WTP2 | 0.33 | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0.49 | UG/L | 749.9999 | 2023-01-03 | WTP2 | 0.31 | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NWP - WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLAND WELL # 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-01-03 | WTP2 |  | 0.5499 | NORTH PLANT - WELL #3
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-14 | WTP2 | 0.00025 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-14 | WTP2 | 0.00025 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-14 | WTP2 | 0.005 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-03-14 | WTP2 | 0.004 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-14 | WTP2 | 0.008 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-14 | WTP2 | 0.001 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-14 | WTP2 | 0.002 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-14 | WTP2 | 0.00025 |  | RE-SAMPLE NITRITE (J QUALIFIED)
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-03-14 | WTP2 | 0.021 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1017 | CHLORIDE | 140 | MG/L | 250.4999 | 2023-03-14 | WTP2 | 0.039 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-03-14 | WTP2 | 0.005 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-03-14 | WTP2 | 0.005 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-03-14 | WTP2 | 5 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-03-14 | WTP2 | 1 |  | J QUALIFIED CHLORIDE
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-20 | WTP2 | 0.0069 | 0.0149 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-20 | WTP2 | 0.0071 | 0.0249 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-20 | WTP2 | 0.0068 | 0.1499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-20 | WTP2 | 0.12 | 1.4999 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-20 | WTP2 | 0.9 | 1.4999 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-20 | WTP2 | 0.37 | 0.4499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-20 | WTP2 | 6 | 9.4999 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2034 | GLYPHOSATE | 5.9 | UG/L | 749.9999 | 2023-06-20 | WTP2 | 5.9 | 6.4999 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-20 | WTP2 | 0.5 | 0.6499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-20 | WTP2 | 1.8 | 2.4999 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-20 | WTP2 | 0.06 | 0.0749 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-20 | WTP2 | 0.5 | 0.6499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-20 | WTP2 | 0.09 | 0.1499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-20 | WTP2 | 0.18 | 0.2499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-20 | WTP2 | 0.019 | 0.1499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-20 | WTP2 | 0.51 | 0.9499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-20 | WTP2 | 0.09 | 0.1499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-20 | WTP2 | 0.15 | 0.2499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-20 | WTP2 | 0.006 | 0.0449 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-20 | WTP2 | 0.0052 | 0.0249 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-20 | WTP2 | 0.095 | 0.1499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-20 | WTP2 | 0.09 | 0.2499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-20 | WTP2 | 0.0063 | 0.1499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-20 | WTP2 | 0.015 | 0.0249 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-20 | WTP2 | 0.038 | 0.0449 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-20 | WTP2 | 0.093 | 0.1499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-20 | WTP2 | 0.0063 | 0.0249 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-20 | WTP2 | 0.0093 | 0.0149 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-20 | WTP2 | 0.053 | 0.2499 | WP2
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2023-09-05 | WTP2 | 0.024 |  | POE - CHULUOTA
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-09-05 | WTP2 |  |  | POE - CHULUOTA
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2023-09-05 | WTP2 | 0.024 |  | WP2 POE
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-09-05 | WTP2 |  |  | WP2 POE
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.29 | UG/L | 60.4999 | 2023-10-05 | L1 | 0.98 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 32.26 | UG/L | 80.4999 | 2023-10-05 | L1 | 0.39 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.67 | UG/L | 60.4999 | 2024-10-01 | L2 | 0.98 |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 65.04 | UG/L | 80.4999 | 2024-10-01 | L2 | 0.39 |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 9.5 | UG/L | 60.4999 | 2024-10-01 | L1 | 0.98 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 54.85 | UG/L | 80.4999 | 2024-10-01 | L1 | 0.39 |  | 803 MAZURKA | 4
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.12 | MG/L | 10.4999 | 2024-11-26 | WTP2 | 0.0024 |  | PLANT POE
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-26 | WTP2 | 0.0034 |  | PLANT POE
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.96 | UG/L | 60.4999 | 2025-10-06 | L2 | 0.98 |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 56.17 | UG/L | 80.4999 | 2025-10-06 | L2 | 0.44 |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.97 | UG/L | 60.4999 | 2025-10-06 | L1 | 0.98 |  | 803 MAZUKA DR | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 44.4 | UG/L | 80.4999 | 2025-10-06 | L1 | 0.44 |  | 803 MAZUKA DR | 4
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2025-10-06 | WTP2 | 0.024 |  | POE
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-06 | WTP2 |  |  | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2023-01-03 | WTP2 | 0.024 |  | POE- NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2022-12-28 | WTP3 |  |  | SOUTH WP
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1040 | NITRATE | 0.1 | MG/L | 10.4999 | 2023-09-05 | WTP2 | 0.024 |  | POE- RESAMPLE
3590186 | CHULUOTA WATER SYSTEM | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-09-05 | WTP2 | 0.0034 |  | POE- RESAMPLE
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 10.4 | UG/L | 60.4999 | 2023-10-05 | L2 | 0.98 |  | 390 LAKE LENELLE | 4
3590186 | CHULUOTA WATER SYSTEM | D | DBP | 2950 | TOTAL THMS | 36.2 | UG/L | 80.4999 | 2023-10-05 | L2 | 0.39 |  | 390 LAKE LENELLE | 4
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2023-01-03 | WTP2 | 0.24 |  | POE - NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-03 | WTP2 |  |  | POE - NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.21 | MG/L | 10.4999 | 2023-01-03 | WTP3 | 0.024 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-03 | WTP3 | 0.0034 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2023-01-03 | WTP1 | 0.024 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-03 | WTP1 | 0.0034 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2023-01-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-01-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-01-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.36 | MG/L |  | 2023-01-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2023-01-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-01-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.78 | MG/L |  | 2023-01-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2023-01-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 101 | MG/L |  | 2023-01-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 105 | MG/L |  | 2023-01-25 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.96 | LN(10) |  | 2023-01-25 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-01-25 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2023-01-25 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2023-01-11 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-01-11 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-01-11 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2023-01-25 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 95 | MG/L |  | 2023-01-25 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56 | UG/L | 80.4999 | 2023-02-01 | L4 | 0.39 |  | 5401 LAKE HOWELL RD.I
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.88 | UG/L | 60.4999 | 2023-02-01 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 62.73 | UG/L | 80.4999 | 2023-02-01 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.63 | UG/L | 60.4999 | 2023-02-01 | L2 | 0.98 |  | 261 LYMAN RD. (2/23 DISINF BYP RPRT MARKED "REVISED" RCVD SEP FROM RESULTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 49.22 | UG/L | 80.4999 | 2023-02-01 | L2 | 0.39 |  | 261 LYMAN RD. (2/23 DISINF BYP RPRT MARKED "REVISED" RCVD SEP FROM RESULTS) HLKD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2023-02-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2023-02-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-02-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.93 | MG/L |  | 2023-02-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-02-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-02-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.88 | MG/L |  | 2023-02-08 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2023-02-08 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-02-08 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2023-02-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2023-02-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-02-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-02-23 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2023-02-23 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-02-23 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.84 | MG/L |  | 2023-02-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2023-02-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-02-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2023-03-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-03-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 100 | MG/L |  | 2023-03-08 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.83 | MG/L |  | 2023-03-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-03-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-03-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.78 | MG/L |  | 2023-03-08 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2023-03-08 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-03-08 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.98 | MG/L |  | 2023-03-22 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2023-03-22 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-03-22 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2023-03-22 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2023-03-22 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-03-22 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2023-03-22 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2023-03-22 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-03-22 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.95 | MG/L |  | 2023-04-05 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2023-04-05 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-04-05 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.11 | MG/L |  | 2023-04-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-04-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-04-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2023-04-05 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-04-05 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-04-05 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.86 | MG/L |  | 2023-04-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-04-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-04-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 1.2 | MG/L |  | 2023-04-17 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2023-04-17 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2023-04-17 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.87 | MG/L |  | 2023-04-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.35 | UG/L | 60.4999 | 2023-05-01 | L3 | 0.98 |  | 7603 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 57 | UG/L | 80.4999 | 2023-05-01 | L3 | 0.39 |  | 7603 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.3 | UG/L | 60.4999 | 2023-05-01 | L4 | 0.98 |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 76.83 | UG/L | 80.4999 | 2023-05-01 | L4 | 0.39 |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.14 | UG/L | 60.4999 | 2023-05-01 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 39.72 | UG/L | 80.4999 | 2023-05-01 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.66 | UG/L | 60.4999 | 2023-05-01 | L2 | 0.98 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.32 | UG/L | 80.4999 | 2023-05-01 | L2 | 0.39 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2023-05-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2023-05-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2023-05-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.97 | MG/L |  | 2023-05-03 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-05-03 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-05-03 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.89 | MG/L |  | 2023-05-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.51 | UG/L | 60.4999 | 2023-02-01 | L3 | 0.98 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 51.6 | UG/L | 80.4999 | 2023-02-01 | L3 | 0.39 |  | 7603 CITRUS AVE.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.95 | UG/L | 60.4999 | 2023-02-01 | L4 | 0.98 |  | 5401 LAKE HOWELL RD.I
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-04-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2023-04-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2023-05-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2023-05-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2023-05-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-05-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-05-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.97 | MG/L |  | 2023-05-17 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-05-17 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-05-17 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.88 | MG/L |  | 2023-05-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2023-05-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-05-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2023-05-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2023-05-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-05-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.99 | MG/L |  | 2023-05-31 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2023-05-31 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-05-31 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-05-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2023-05-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-05-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.8 | MG/L |  | 2023-06-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.85 | LN(10) |  | 2023-06-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-06-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-06-14 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2023-06-14 | WTP3 |  | 1.4999 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-06-14 | WTP3 |  | 1.4999 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2023-06-14 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2023-06-14 | WTP2 |  | 1.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-06-14 | WTP2 |  | 1.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 1.7 | PCI/L | 15.4999 | 2023-06-14 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4020 | RADIUM-226 | 0.4 | PCI/L | 3.4999 | 2023-06-14 | WTP1 |  | 1.4999 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2023-06-14 | WTP1 |  | 1.4999 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.99 | MG/L |  | 2023-06-14 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2023-06-14 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-06-14 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.18 | MG/L | 10.4999 | 2023-06-14 | WTP3 | 0.024 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-14 | WTP3 | 0.0034 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-06-14 | WTP3 | 0.005 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-06-14 | WTP3 | 0.00025 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1010 | BARIUM | 0.016 | MG/L | 2.4999 | 2023-06-14 | WTP3 | 0.003 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-06-14 | WTP3 | 0.00025 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-06-14 | WTP3 | 0.004 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1025 | FLUORIDE | 0.19 | MG/L | 4.0499 | 2023-06-14 | WTP3 | 0.0099 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-06-14 | WTP3 | 0.0005 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-06-14 | WTP3 | 1e-05 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-06-14 | WTP3 | 0.008 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-06-14 | WTP3 | 0.0012 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1052 | SODIUM | 9.8 | MG/L | 160.4999 | 2023-06-14 | WTP3 | 0.8 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-06-14 | WTP3 | 0.001 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-06-14 | WTP3 | 0.002 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-06-14 | WTP3 | 0.00025 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-06-14 | WTP3 | 0.021 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1017 | CHLORIDE | 13 | MG/L | 250.4999 | 2023-06-14 | WTP3 | 0.039 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-06-14 | WTP3 | 0.005 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1025 | FLUORIDE | 0.19 | MG/L | 2.0499 | 2023-06-14 | WTP3 | 0.0099 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-06-14 | WTP3 | 0.0067 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-06-14 | WTP3 | 0.005 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-06-14 | WTP3 | 0.0005 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1055 | SULFATE | 7.3 | MG/L | 250.4999 | 2023-06-14 | WTP3 | 0.034 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-06-14 | WTP3 | 0.05 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-06-14 | WTP3 | 5 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-06-14 | WTP3 | 1 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 140 | MG/L | 500.4999 | 2023-06-14 | WTP3 | 5 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-06-14 | WTP3 | 0.04 |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-06-14 | WTP3 | 0.5 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-06-14 | WTP3 | 0.24 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-06-14 | WTP3 | 0.48 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP3 | 0.49 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-06-14 | WTP3 | 0.44 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-06-14 | WTP3 | 0.4 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP3 | 0.28 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-06-14 | WTP3 | 0.4 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP3 | 0.41 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP3 | 0.44 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-06-14 | WTP3 | 0.32 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP3 | 0.36 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP3 | 0.33 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP3 | 0.25 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP3 | 0.44 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP3 | 0.49 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP3 | 0.37 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP3 | 0.16 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-06-14 | WTP3 | 0.2 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-06-14 | WTP3 | 0.33 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP3 | 0.26 | 0.5499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-14 | WTP3 | 0.0077 | 0.0149 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP3 | 0.0079 | 0.0249 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-14 | WTP3 | 0.0076 | 0.1499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-14 | WTP3 | 6 | 9.4999 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP3 | 0.13 | 1.4999 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-14 | WTP3 | 0.9 | 1.4999 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-14 | WTP3 | 0.37 | 0.4499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-14 | WTP3 | 5.9 | 6.4999 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-14 | WTP3 | 0.5 | 0.6499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-14 | WTP3 | 1.8 | 2.4999 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-14 | WTP3 | 0.06 | 0.0749 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-14 | WTP3 | 0.5 | 0.6499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-14 | WTP3 | 0.09 | 0.1499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-14 | WTP3 | 0.18 | 0.2499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-14 | WTP3 | 0.021 | 0.1499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-14 | WTP3 | 0.51 | 0.9499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP3 | 0.09 | 0.1499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-14 | WTP3 | 0.15 | 0.2499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-14 | WTP3 | 0.0067 | 0.0449 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP3 | 0.0058 | 0.0249 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-14 | WTP3 | 0.095 | 0.1499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-14 | WTP3 | 0.09 | 0.2499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP3 | 0.007 | 0.1499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP3 | 0.015 | 0.0249 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-14 | WTP3 | 0.038 | 0.0449 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-14 | WTP3 | 0.1 | 0.1499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP3 | 0.0062 | 0.0249 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-14 | WTP3 | 0.0093 | 0.0149 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-14 | WTP3 | 0.059 | 0.2499 | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.073 | MG/L | 10.4999 | 2023-06-14 | WTP2 | 0.024 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-14 | WTP2 | 0.0034 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-06-14 | WTP2 | 0.00025 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1010 | BARIUM | 0.0087 | MG/L | 2.4999 | 2023-06-14 | WTP2 | 0.003 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-06-14 | WTP2 | 0.00025 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-06-14 | WTP2 | 0.005 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-06-14 | WTP2 | 0.004 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2023-06-14 | WTP2 | 0.0099 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-06-14 | WTP2 | 0.0005 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-06-14 | WTP2 | 1e-05 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-06-14 | WTP2 | 0.008 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-06-14 | WTP2 | 0.0012 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2023-06-14 | WTP2 | 0.8 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-06-14 | WTP2 | 0.001 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-06-14 | WTP2 | 0.002 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-06-14 | WTP2 | 0.00025 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-06-14 | WTP2 | 0.021 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1017 | CHLORIDE | 20 | MG/L | 250.4999 | 2023-06-14 | WTP2 | 0.039 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-06-14 | WTP2 | 0.005 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1025 | FLUORIDE | 0.18 | MG/L | 2.0499 | 2023-06-14 | WTP2 | 0.0099 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-06-14 | WTP2 | 0.0067 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-06-14 | WTP2 | 0.005 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-06-14 | WTP2 | 0.0005 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1055 | SULFATE | 4.7 | MG/L | 250.4999 | 2023-06-14 | WTP2 | 0.034 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-06-14 | WTP2 | 0.05 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-06-14 | WTP2 | 0.04 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-06-14 | WTP2 | 5 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-06-14 | WTP2 | 1 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 160 | MG/L | 500.4999 | 2023-06-14 | WTP2 | 5 |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-06-14 | WTP2 | 0.5 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-06-14 | WTP2 | 0.24 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-06-14 | WTP2 | 0.48 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP2 | 0.49 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-06-14 | WTP2 | 0.44 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-06-14 | WTP2 | 0.4 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP2 | 0.28 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-06-14 | WTP2 | 0.4 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP2 | 0.41 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP2 | 0.44 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-06-14 | WTP2 | 0.32 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP2 | 0.36 | 0.5499 | NORTH WP
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1040 | NITRATE | 6.9 | MG/L | 10.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - THESE ARE MAKE-UP SAMPLES FOR 2021 AS OF 9/20/22 - CJL
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-30 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008 - THESE ARE MAKE-UP SAMPLES FOR 2021 AS OF 9/20/22 - CJL
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1040 | NITRATE | 0.046 | MG/L | 10.4999 | 2022-12-27 | AAA | 0.025 |  | POE
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-12-27 | AAA |  |  | POE
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-06-15 | AAA |  |  | POE
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-15 | AAA |  |  | POE
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2025-03-20 | AAA |  |  | POE
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-03-20 | AAA |  |  | POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-01-06 | AAA | 0.35 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-01-06 | AAA | 0.33 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-01-06 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-01-06 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-01-06 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-01-06 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-01-06 | AAA | 0.12 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-01-06 | AAA | 0.29 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-01-06 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-01-06 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-01-06 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-01-06 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-01-06 | AAA | 0.13 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-06 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-01-06 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-01-06 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-01-06 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-01-06 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-01-06 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-01-06 | AAA | 0.23 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-01-06 | AAA | 0.2 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-02-03 | AAA | 0.35 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-02-03 | AAA | 0.33 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-02-03 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-02-03 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-02-03 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-02-03 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-02-03 | AAA | 0.12 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-02-03 | AAA | 0.29 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-02-03 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-02-03 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-02-03 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-02-03 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-02-03 | AAA | 0.13 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-03 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-02-03 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-02-03 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-02-03 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-02-03 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-02-03 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-02-03 | AAA | 0.23 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-02-03 | AAA | 0.2 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.7 | UG/L | 60.4999 | 2021-02-10 | L4 | 0.9 |  | 419 PALM CREST LN. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 54.9 | UG/L | 80.4999 | 2021-02-10 | L4 | 0.47 |  | 419 PALM CREST LN. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.5 | UG/L | 60.4999 | 2021-02-10 | L1 | 0.9 |  | 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 48.3 | UG/L | 80.4999 | 2021-02-10 | L1 | 0.47 |  | 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.4 | UG/L | 60.4999 | 2021-02-10 | L3 | 0.9 |  | 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 61.8 | UG/L | 80.4999 | 2021-02-10 | L3 | 0.47 |  | 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 12.9 | UG/L | 60.4999 | 2021-02-10 | L2 | 0.9 |  | 930 WILLISTON PARK PT (3/21 DISINF BYP RPRT RCVD W/RSLTS) HLKD | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 50.3 | UG/L | 80.4999 | 2021-02-10 | L2 | 0.47 |  | 930 WILLISTON PARK PT (3/21 DISINF BYP RPRT RCVD W/RSLTS) HLKD | 3
3590201 | LAKE MARY, CITY OF | N | INOR | 1040 | NITRATE | 0.23 | MG/L | 10.4999 | 2021-03-02 | AAA |  |  | POE
3590201 | LAKE MARY, CITY OF | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-03-02 | AAA |  |  | POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-03-02 | AAA | 0.35 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-03-02 | AAA | 0.33 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-03-02 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-03-02 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-03-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-03-02 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-03-02 | AAA | 0.12 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-03-02 | AAA | 0.29 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-03-02 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-03-02 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-03-02 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-03-02 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-03-02 | AAA | 0.13 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-03-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-03-02 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-03-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-03-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-03-02 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-03-02 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-03-02 | AAA | 0.23 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-03-02 | AAA | 0.2 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.07 | UG/L | 60.4999 | 2021-02-17 | L3 | 0.98 |  | RAVEN LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 40.69 | UG/L | 80.4999 | 2021-02-17 | L3 | 0.39 |  | RAVEN LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.37 | UG/L | 60.4999 | 2021-02-17 | L4 | 0.98 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 40.55 | UG/L | 80.4999 | 2021-02-17 | L4 | 0.39 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.29 | UG/L | 60.4999 | 2021-02-17 | L1 | 0.98 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 40.11 | UG/L | 80.4999 | 2021-02-17 | L1 | 0.39 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.96 | UG/L | 60.4999 | 2021-02-17 | L2 | 0.98 |  | 1057 N. HWY 17-92 (HLKD) 3/21 DISINF BYP RPRT RCVD W/RSLTS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 48.82 | UG/L | 80.4999 | 2021-02-17 | L2 | 0.39 |  | 1057 N. HWY 17-92 (HLKD) 3/21 DISINF BYP RPRT RCVD W/RSLTS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.5 | UG/L | 60.4999 | 2021-05-18 | L3 | 0.98 |  | RAVEN AVE. L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 49.9 | UG/L | 80.4999 | 2021-05-18 | L3 | 0.39 |  | RAVEN AVE. L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.14 | UG/L | 60.4999 | 2021-05-18 | L4 | 0.98 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 60.08 | UG/L | 80.4999 | 2021-05-18 | L4 | 0.39 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.77 | UG/L | 60.4999 | 2021-05-18 | L1 | 0.98 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 44.08 | UG/L | 80.4999 | 2021-05-18 | L1 | 0.39 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.83 | UG/L | 60.4999 | 2021-05-18 | L2 | 0.98 |  | 1057 N. HWY 17-92 (6/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 49.06 | UG/L | 80.4999 | 2021-05-18 | L2 | 0.39 |  | 1057 N. HWY 17-92 (6/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.15 | UG/L | 60.4999 | 2021-08-18 | L3 | 0.89 |  | RAVEN AVE. L/S (TTHMS SINGLE SMP EXCEEDANCE) **OE EXCEEDANCE OF 81.06 AT THIS SITE PER 9/21 QTR DISINF BYP RPRT** (HLKD)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 116.82 | UG/L | 80.4999 | 2021-08-18 | L3 | 0.39 |  | RAVEN AVE. L/S (TTHMS SINGLE SMP EXCEEDANCE) **OE EXCEEDANCE OF 81.06 AT THIS SITE PER 9/21 QTR DISINF BYP RPRT** (HLKD)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.93 | UG/L | 60.4999 | 2021-08-18 | L4 | 0.89 |  | 900 NORTH ST. (TTHM SINGLE SMP EXCEEDANCE)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 92.56 | UG/L | 80.4999 | 2021-08-18 | L4 | 0.39 |  | 900 NORTH ST. (TTHM SINGLE SMP EXCEEDANCE)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.12 | UG/L | 60.4999 | 2021-08-18 | L1 | 0.89 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.95 | UG/L | 80.4999 | 2021-08-18 | L1 | 0.39 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.04 | UG/L | 60.4999 | 2021-08-18 | L2 | 0.89 |  | 1057 N. HWY 17-92 (TTHM SINGLE SMP EXCEEDANCE)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 80.8 | UG/L | 80.4999 | 2021-08-18 | L2 | 0.39 |  | 1057 N. HWY 17-92 (TTHM SINGLE SMP EXCEEDANCE)
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.056 | MG/L | 10.4999 | 2021-09-16 | WTP1 | 0.0075 |  | WTP1. BOTH RESULTS JQ. NO3 112/113%, NO2 85/85%; 90-110%. ACCEPTED_MFC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0.048 | MG/L | 1.4999 | 2021-09-16 | WTP1 | 0.048 |  | WTP1. BOTH RESULTS JQ. NO3 112/113%, NO2 85/85%; 90-110%. ACCEPTED_MFC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.062 | MG/L | 10.4999 | 2021-09-16 | WTP2 | 0.0075 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0.048 | MG/L | 1.4999 | 2021-09-16 | WTP2 | 0.048 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.97 | UG/L | 60.4999 | 2021-11-19 | L3 | 0.98 |  | T1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.66 | UG/L | 80.4999 | 2021-11-19 | L3 | 0.39 |  | T1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.79 | UG/L | 60.4999 | 2021-11-19 | L4 | 0.98 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.45 | UG/L | 80.4999 | 2021-11-19 | L4 | 0.39 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.51 | UG/L | 60.4999 | 2021-11-19 | L2 | 0.98 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 50.98 | UG/L | 80.4999 | 2021-11-19 | L2 | 0.39 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.18 | UG/L | 60.4999 | 2021-11-20 | L1 | 0.98 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 40.18 | UG/L | 80.4999 | 2021-11-20 | L1 | 0.39 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.65 | UG/L | 60.4999 | 2022-02-20 | L3 | 0.89 |  | RAVEN AVE. L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 73.17 | UG/L | 80.4999 | 2022-02-20 | L3 | 0.44 |  | RAVEN AVE. L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.94 | UG/L | 60.4999 | 2022-02-20 | L4 | 0.89 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 68.43 | UG/L | 80.4999 | 2022-02-20 | L4 | 0.44 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.53 | UG/L | 60.4999 | 2022-02-20 | L1 | 0.89 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 57.78 | UG/L | 80.4999 | 2022-02-20 | L1 | 0.44 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 35.03 | UG/L | 60.4999 | 2022-02-20 | L2 | 0.89 |  | 1057 N. HWY 17-92 (3/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 82.34 | UG/L | 80.4999 | 2022-02-20 | L2 | 0.44 |  | 1057 N. HWY 17-92 (3/22 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.11 | UG/L | 60.4999 | 2022-05-18 | L3 | 0.98 |  | RAVEN AVE. LIFT STATION (MARK REVISED)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.72 | UG/L | 80.4999 | 2022-05-18 | L3 | 0.39 |  | RAVEN AVE. LIFT STATION (MARK REVISED)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.96 | UG/L | 60.4999 | 2022-05-18 | L4 | 0.98 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 53.79 | UG/L | 80.4999 | 2022-05-18 | L4 | 0.39 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.78 | UG/L | 60.4999 | 2022-05-18 | L1 | 0.98 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 37.59 | UG/L | 80.4999 | 2022-05-18 | L1 | 0.39 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.25 | UG/L | 60.4999 | 2022-05-18 | L2 | 0.98 |  | 1057 N. HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 52.89 | UG/L | 80.4999 | 2022-05-18 | L2 | 0.39 |  | 1057 N. HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.062 | MG/L | 10.4999 | 2022-06-07 | WTP1 | 0.024 |  | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0.083 | MG/L | 1.4999 | 2022-06-07 | WTP1 | 0.0034 |  | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.071 | MG/L | 10.4999 | 2022-06-07 | WTP2 | 0.024 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0.089 | MG/L | 1.4999 | 2022-06-07 | WTP2 | 0.0034 |  | WTP2
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2021-05-26 | AAA |  |  | POE
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1040 | NITRATE | 0.25 | MG/L | 10.4999 | 2024-12-10 | AAA
3594196 | ALL IN THE FAMILY BAR | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-10 | AAA
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-01-04 | AAA | 0.2 |  | 2020 NN MAKEUP SAMPLE
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-04 | AAA | 0.2 |  | 2020 NN MAKEUP SAMPLE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.0085 | MG/L | 2.4999 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 29.2 | MG/L | 160.4999 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-05-26 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2021-05-26 | AAA |  | 0.0149 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2021-05-26 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2021-05-26 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2021-05-26 | AAA |  | 1.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-05-26 | AAA |  | 1.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2021-05-26 | AAA |  | 0.4499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2021-05-26 | AAA |  | 9.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2021-05-26 | AAA |  | 6.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2021-05-26 | AAA |  | 0.6499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2021-05-26 | AAA |  | 2.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2021-05-26 | AAA |  | 0.0749 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2021-05-26 | AAA |  | 0.6499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2021-05-26 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2021-05-26 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2021-05-26 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2021-05-26 | AAA |  | 0.9499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2021-05-26 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2021-05-26 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2021-05-26 | AAA |  | 0.0449 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2021-05-26 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2021-05-26 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2021-05-26 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2021-05-26 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2021-05-26 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2021-05-26 | AAA |  | 0.0449 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2021-05-26 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2021-05-26 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2021-05-26 | AAA |  | 0.0149 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2021-05-26 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0.2 | MG/L | 1.4999 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2021-05-26 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-07-12 | L2 |  |  | 3849 ELDER SPRINGS CIR. NOT ON PLAN, CANNOT ACCEPT FOR COMPLIANCE_MER
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | DBP | 2950 | TOTAL THMS | 2.18 | UG/L | 80.4999 | 2021-07-12 | L2 |  |  | 3849 ELDER SPRINGS CIR. NOT ON PLAN, CANNOT ACCEPT FOR COMPLIANCE_MER
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 1.44 | MG/L | 250.4999 | 2021-07-12 | AAA |  |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2021-07-12 | AAA | 1 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 8.01 | LN(10) |  | 2021-07-12 | AAA | 0.01 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 252 | MG/L | 500.4999 | 2021-07-12 | AAA | 2.5 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2021-07-12 | AAA | 0.2 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1028 | IRON | 0.0715 | MG/L | 0.3499 | 2021-07-12 | AAA | 0.01 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2021-07-12 | AAA | 0.01 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2021-07-12 | AAA | 0.001 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0 | MG/L | 2.0499 | 2021-07-12 | AAA | 0.2 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2021-07-12 | AAA | 0.01 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2021-07-12 | AAA | 0.0005 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0.0147 | MG/L | 5.4999 | 2021-07-12 | AAA | 0.002 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2021-07-12 | AAA | 5 |  | CHLORIDE & SULFATE HAVE J QUALIFIERS-NOT ENTD (CHLORIDE IS 44.6 MG/L, SULFATE IS 1.44 MG/L) SULFATE ALSO HAS AN I QUALIFIER (I QUALIFIER IS OK) HLKD
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | RAD | 4000 | GROSS ALPHA EXCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-02-04 | AAA |  | 3.4999 | 2021 MAKE UP SAMPLES
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2022-02-04 | AAA |  |  | 2021 MAKE UP SAMPLES
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2022-02-04 | AAA |  | 0.667 | 2021 MAKE UP SAMPLES
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | RAD | 4020 | RADIUM-226 | 0.6 | PCI/L | 3.4999 | 2022-02-04 | AAA |  | 1.4999 | 2021 MAKE UP SAMPLES
3590338 | ELDER SPRINGS MOBILE HOME PARK | S | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2022-02-04 | AAA |  | 1.4999 | 2021 MAKE UP SAMPLES
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2022-06-23 | AAA | 0.2 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0.2 | MG/L | 1.4999 | 2022-06-23 | AAA | 0.2 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.055 | MG/L | 10.4999 | 2024-08-15 | AAA | 0.024 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-08-15 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1010 | BARIUM | 0.0091 | MG/L | 2.4999 | 2024-11-05 | AAA | 0.003 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1025 | FLUORIDE | 0.17 | MG/L | 4.0499 | 2024-11-05 | AAA | 0.0099 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2024-11-05 | AAA | 3e-05 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1052 | SODIUM | 34 | MG/L | 160.4999 | 2024-11-05 | AAA | 0.8 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 55 | MG/L | 250.4999 | 2024-11-05 | AAA | 0.039 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1022 | COPPER | 0.008 | MG/L | 1.4999 | 2024-11-05 | AAA | 0.005 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1025 | FLUORIDE | 0.17 | MG/L | 2.0499 | 2024-11-05 | AAA | 0.0099 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1055 | SULFATE | 3.7 | MG/L | 250.4999 | 2024-11-05 | AAA | 0.034 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 250 | MG/L | 500.4999 | 2024-11-05 | AAA | 10 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2024-11-05 | AAA |  |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | RAD | 4006 | COMBINED URANIUM | 0 | PCI/L | 20.4999 | 2024-11-05 | AAA |  | 0.667 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2024-11-05 | AAA |  | 0.0149 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2024-11-05 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2024-11-05 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2024-11-05 | AAA |  | 1.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-11-05 | AAA |  | 1.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2024-11-05 | AAA |  | 0.4499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2024-11-05 | AAA |  | 9.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2024-11-05 | AAA |  | 0.6499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2024-11-05 | AAA |  | 0.0749 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2024-11-05 | AAA |  | 0.6499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2024-11-05 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2024-11-05 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2024-11-05 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2024-11-05 | AAA |  | 0.0449 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2024-11-05 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2024-11-05 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2024-11-05 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2024-11-05 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2024-11-05 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-11-06 | AAA |  | 0.5499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-11-06 | AAA |  | 1.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2024-11-06 | AAA |  | 6.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2024-11-06 | AAA |  | 2.4999 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2024-11-06 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2024-11-06 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2024-11-06 | AAA |  | 0.9499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-11-06 | AAA |  | 0.1499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2024-11-06 | AAA |  | 0.2499 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2024-11-06 | AAA |  | 0.0449 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2024-11-06 | AAA |  | 0.0249 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2024-11-06 | AAA |  | 0.0149 | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | RAD | 4002 | GROSS ALPHA INCL RADON AND URANIUM | 0 | PCI/L | 15.4999 | 2024-11-11 | AAA | 1.6
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | RAD | 4020 | RADIUM-226 | 0.3 | PCI/L | 3.4999 | 2024-11-11 | AAA | 0.2 | 1.4999
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | RAD | 4030 | RADIUM-228 | 0 | PCI/L | 2.4999 | 2024-11-11 | AAA | 0.7 | 1.4999
3590338 | ELDER SPRINGS MOBILE HOME PARK | M | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.48 | UG/L | 60.4999 | 2024-11-15 | L1 | 0.89 |  | 3841 ELDER SPRINGS CRICLEE TTHM HAA5 (MAKE-UP SAMPLING) | 3
3590338 | ELDER SPRINGS MOBILE HOME PARK | M | DBP | 2950 | TOTAL THMS | 8.76 | UG/L | 80.4999 | 2024-11-15 | L1 | 0.44 |  | 3841 ELDER SPRINGS CRICLEE TTHM HAA5 (MAKE-UP SAMPLING) | 3
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0.13 | MG/L | 10.4999 | 2025-02-20 | AAA | 0.024 |  | POE
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0.15 | MG/L | 1.4999 | 2025-02-20 | AAA | 0.0034 |  | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP2 | 0.33 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP2 | 0.25 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP2 | 0.44 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP2 | 0.49 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP2 | 0.37 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP2 | 0.16 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-06-14 | WTP2 | 0.2 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-06-14 | WTP2 | 0.33 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP2 | 0.26 | 0.5499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-14 | WTP2 | 0.007 | 0.0149 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP2 | 0.0072 | 0.0249 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-14 | WTP2 | 0.0069 | 0.1499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP2 | 0.12 | 1.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-14 | WTP2 | 0.9 | 1.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-14 | WTP2 | 0.37 | 0.4499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-14 | WTP2 | 6 | 9.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-14 | WTP2 | 5.9 | 6.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-14 | WTP2 | 0.5 | 0.6499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-14 | WTP2 | 1.8 | 2.4999 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-14 | WTP2 | 0.06 | 0.0749 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-14 | WTP2 | 0.5 | 0.6499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-14 | WTP2 | 0.09 | 0.1499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-14 | WTP2 | 0.18 | 0.2499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-14 | WTP2 | 0.019 | 0.1499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-14 | WTP2 | 0.51 | 0.9499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP2 | 0.09 | 0.1499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-14 | WTP2 | 0.15 | 0.2499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-14 | WTP2 | 0.0061 | 0.0449 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP2 | 0.0053 | 0.0249 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-14 | WTP2 | 0.095 | 0.1499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-14 | WTP2 | 0.09 | 0.2499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP2 | 0.0064 | 0.1499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP2 | 0.015 | 0.0249 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-14 | WTP2 | 0.038 | 0.0449 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-14 | WTP2 | 0.094 | 0.1499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-06-14 | WTP1 | 0.0034 |  | HOWELL PARK WP
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | SEC | 1017 | CHLORIDE | 44.8 | MG/L | 250.4999 | 2021-10-28 | AAA |  |  | CHLORIDE ONLY
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2023-08-10 | AAA | 0.2 |  | RCVD PROPER FORMAT 1-17-24 FW
3590338 | ELDER SPRINGS MOBILE HOME PARK | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-08-10 | AAA | 0.2 |  | RCVD PROPER FORMAT 1-17-24 FW
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP2 | 0.0062 | 0.0249 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-14 | WTP2 | 0.0092 | 0.0149 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-14 | WTP2 | 0.053 | 0.2499 | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.076 | MG/L | 10.4999 | 2023-06-14 | WTP1 | 0.024 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-06-14 | WTP1 | 0.00025 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1010 | BARIUM | 0.0093 | MG/L | 2.4999 | 2023-06-14 | WTP1 | 0.003 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-06-14 | WTP1 | 0.00025 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-06-14 | WTP1 | 0.005 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-06-14 | WTP1 | 0.004 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1025 | FLUORIDE | 0.18 | MG/L | 4.0499 | 2023-06-14 | WTP1 | 0.0099 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-06-14 | WTP1 | 0.0005 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-06-14 | WTP1 | 1e-05 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-06-14 | WTP1 | 0.008 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-06-14 | WTP1 | 0.0012 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1052 | SODIUM | 14 | MG/L | 160.4999 | 2023-06-14 | WTP1 | 0.8 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-06-14 | WTP1 | 0.001 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-06-14 | WTP1 | 0.002 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-06-14 | WTP1 | 0.00025 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-06-14 | WTP1 | 0.021 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1017 | CHLORIDE | 19 | MG/L | 250.4999 | 2023-06-14 | WTP1 | 0.039 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-06-14 | WTP1 | 0.005 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1025 | FLUORIDE | 0.18 | MG/L | 2.0499 | 2023-06-14 | WTP1 | 0.0099 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1028 | IRON | 0.019 | MG/L | 0.3499 | 2023-06-14 | WTP1 | 0.0067 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-06-14 | WTP1 | 0.005 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-06-14 | WTP1 | 0.005 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1055 | SULFATE | 4.8 | MG/L | 250.4999 | 2023-06-14 | WTP1 | 0.034 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-06-14 | WTP1 | 0.05 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1905 | COLOR | 0 | COLOR UNITS | 15.4999 | 2023-06-14 | WTP1 | 5 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 0 |  | 3.4999 | 2023-06-14 | WTP1 | 1 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 150 | MG/L | 500.4999 | 2023-06-14 | WTP1 | 5 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0 |  | 0.5499 | 2023-06-14 | WTP1 | 0.04 |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-06-14 | WTP1 | 0.5 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-06-14 | WTP1 | 0.24 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-06-14 | WTP1 | 0.48 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP1 | 0.49 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-06-14 | WTP1 | 0.44 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-06-14 | WTP1 | 0.4 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP1 | 0.28 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-06-14 | WTP1 | 0.4 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP1 | 0.41 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP1 | 0.44 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-06-14 | WTP1 | 0.32 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP1 | 0.36 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP1 | 0.33 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP1 | 0.25 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-06-14 | WTP1 | 0.44 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP1 | 0.49 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP1 | 0.37 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP1 | 0.16 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-06-14 | WTP1 | 0.2 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-06-14 | WTP1 | 0.33 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-06-14 | WTP1 | 0.26 | 0.5499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-06-14 | WTP1 | 0.007 | 0.0149 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP1 | 0.0072 | 0.0249 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-06-14 | WTP1 | 0.0069 | 0.1499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP1 | 0.12 | 1.4999 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-06-14 | WTP1 | 0.9 | 1.4999 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-06-14 | WTP1 | 0.37 | 0.4499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-06-14 | WTP1 | 6 | 9.4999 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-06-14 | WTP1 | 5.9 | 6.4999 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-06-14 | WTP1 | 0.5 | 0.6499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-06-14 | WTP1 | 1.8 | 2.4999 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-06-14 | WTP1 | 0.06 | 0.0749 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-06-14 | WTP1 | 0.5 | 0.6499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-06-14 | WTP1 | 0.09 | 0.1499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-06-14 | WTP1 | 0.18 | 0.2499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-06-14 | WTP1 | 0.019 | 0.1499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-06-14 | WTP1 | 0.51 | 0.9499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-06-14 | WTP1 | 0.09 | 0.1499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-06-14 | WTP1 | 0.15 | 0.2499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-06-14 | WTP1 | 0.0061 | 0.0449 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP1 | 0.0053 | 0.0249 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-06-14 | WTP1 | 0.095 | 0.1499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-06-14 | WTP1 | 0.09 | 0.2499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-06-14 | WTP1 | 0.0064 | 0.1499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP1 | 0.015 | 0.0249 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-06-14 | WTP1 | 0.038 | 0.0449 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-06-14 | WTP1 | 0.095 | 0.1499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-06-14 | WTP1 | 0.0063 | 0.0249 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-06-14 | WTP1 | 0.0093 | 0.0149 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-06-14 | WTP1 | 0.0054 | 0.2499 | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2023-06-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2023-06-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-06-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2023-06-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2023-06-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-06-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.99 | MG/L |  | 2023-06-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2023-06-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-06-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2023-06-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2023-06-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2023-06-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2023-07-12 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2023-07-12 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-07-12 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2023-07-12 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2023-07-12 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2023-07-12 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2023-07-26 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2023-07-12 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-07-12 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-07-12 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2023-07-26 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 98 | MG/L |  | 2023-07-26 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2023-07-26 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2023-07-26 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-07-26 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2023-07-26 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2023-07-26 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-07-26 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.6 | UG/L | 60.4999 | 2023-08-02 | L3 | 0.98 |  | L3- CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 48.52 | UG/L | 80.4999 | 2023-08-02 | L3 | 0.39 |  | L3- CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.76 | UG/L | 60.4999 | 2023-08-02 | L4 | 0.98 |  | L4- 5401 LAKE HOWELL
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 61.61 | UG/L | 80.4999 | 2023-08-02 | L4 | 0.39 |  | L4- 5401 LAKE HOWELL
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.52 | UG/L | 60.4999 | 2023-08-02 | L1 | 0.98 |  | L1- 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 29.89 | UG/L | 80.4999 | 2023-08-02 | L1 | 0.39 |  | L1- 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.4 | UG/L | 60.4999 | 2023-08-02 | L2 | 0.98 |  | L2-261 LYMAN RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.43 | UG/L | 80.4999 | 2023-08-02 | L2 | 0.39 |  | L2-261 LYMAN RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2023-08-09 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-08-09 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 103 | MG/L |  | 2023-08-09 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.77 | MG/L |  | 2023-08-09 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-08-09 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-08-09 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2023-08-09 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2023-08-09 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-08-09 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2023-08-23 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-08-23 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2023-08-23 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2023-08-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2023-08-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-08-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2023-08-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2023-08-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-08-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2023-09-06 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-09-06 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-09-06 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2023-09-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2023-09-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2023-09-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2023-09-06 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2023-09-06 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2023-09-06 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-09-07 | WTP2 |  | 1.4999 | NORTH WP POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2023-09-20 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2023-09-20 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-09-20 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2023-09-20 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-09-20 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-09-20 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.79 | MG/L |  | 2023-09-20 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2023-09-20 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-09-20 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2023-10-04 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-10-04 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-10-04 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2023-10-04 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2023-10-04 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2023-10-04 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.85 | MG/L |  | 2023-10-04 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2023-10-04 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-10-04 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-16 | WTP2 |  | 0.0149 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP2 |  | 1.4999 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-16 | WTP2 |  | 1.4999 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-16 | WTP2 |  | 0.4499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-16 | WTP2 |  | 9.4999 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-16 | WTP2 |  | 6.4999 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-16 | WTP2 |  | 0.6499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-16 | WTP2 |  | 2.4999 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-16 | WTP2 |  | 0.0749 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-16 | WTP2 |  | 0.6499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-16 | WTP2 |  | 0.2499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-16 | WTP2 |  | 0.9499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP2 |  | 0.1499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-16 | WTP2 |  | 0.2499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-16 | WTP2 |  | 0.0449 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-16 | WTP2 |  | 0.2499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-16 | WTP2 |  | 0.1499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-16 | WTP2 |  | 0.0449 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-16 | WTP2 |  | 0.1499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-16 | WTP2 |  | 0.0149 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-16 | WTP2 |  | 0.2499 | POE NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-16 | WTP1 |  | 0.0149 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP1 |  | 1.4999 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-16 | WTP1 |  | 1.4999 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-16 | WTP1 |  | 0.4499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-16 | WTP1 |  | 9.4999 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-16 | WTP1 |  | 6.4999 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-16 | WTP1 |  | 0.6499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-16 | WTP1 |  | 2.4999 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-16 | WTP1 |  | 0.0749 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-16 | WTP1 |  | 0.6499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-16 | WTP1 |  | 0.2499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-16 | WTP1 |  | 0.9499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP1 |  | 0.1499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-16 | WTP1 |  | 0.2499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-16 | WTP1 |  | 0.0449 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-16 | WTP1 |  | 0.2499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-16 | WTP1 |  | 0.1499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-16 | WTP1 |  | 0.0449 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-16 | WTP1 |  | 0.1499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-16 | WTP1 |  | 0.0149 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-16 | WTP1 |  | 0.2499 | POE WTP1 H P
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-16 | WTP2 |  | 0.0149 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP2 |  | 1.4999 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-16 | WTP2 |  | 1.4999 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-16 | WTP2 |  | 0.4499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-16 | WTP2 |  | 9.4999 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-16 | WTP2 |  | 6.4999 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-16 | WTP2 |  | 0.6499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-16 | WTP2 |  | 2.4999 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-16 | WTP2 |  | 0.0749 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-16 | WTP2 |  | 0.6499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-16 | WTP2 |  | 0.9499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-16 | WTP2 |  | 0.2499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP2 |  | 0.1499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-16 | WTP2 |  | 0.2499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-16 | WTP2 |  | 0.0449 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-16 | WTP2 |  | 0.1499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-16 | WTP2 |  | 0.2499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-16 | WTP2 |  | 0.1499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-16 | WTP2 |  | 0.0449 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-16 | WTP2 |  | 0.1499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP2 |  | 0.0249 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-16 | WTP2 |  | 0.0149 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-16 | WTP2 |  | 0.2499 | POE N P WTP2
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-16 | WTP1 |  | 0.0149 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP1 |  | 1.4999 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-16 | WTP1 |  | 1.4999 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-16 | WTP1 |  | 0.4499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-16 | WTP1 |  | 9.4999 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-16 | WTP1 |  | 6.4999 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-16 | WTP1 |  | 0.6499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-16 | WTP1 |  | 2.4999 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-16 | WTP1 |  | 0.0749 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-16 | WTP1 |  | 0.6499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-16 | WTP1 |  | 0.2499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-16 | WTP1 |  | 0.9499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP1 |  | 0.1499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-16 | WTP1 |  | 0.2499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-16 | WTP1 |  | 0.0449 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-16 | WTP1 |  | 0.1499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-16 | WTP1 |  | 0.2499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-16 | WTP1 |  | 0.1499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-16 | WTP1 |  | 0.0449 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-16 | WTP1 |  | 0.1499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP1 |  | 0.0249 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-16 | WTP1 |  | 0.0149 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-16 | WTP1 |  | 0.2499 | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-10-16 | WTP3 |  | 0.0149 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP3 |  | 0.0249 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-10-16 | WTP3 |  | 0.1499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP3 |  | 1.4999 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-16 | WTP3 |  | 1.4999 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-10-16 | WTP3 |  | 0.4499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-10-16 | WTP3 |  | 9.4999 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-10-16 | WTP3 |  | 6.4999 | POE WTP3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-04-07 | AAA | 0.35 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-04-07 | AAA | 0.33 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-04-07 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-04-07 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-04-07 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-04-07 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-04-07 | AAA | 0.12 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-04-07 | AAA | 0.29 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-04-07 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-04-07 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-04-07 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-04-07 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-04-07 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-07 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-04-07 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-04-07 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-04-07 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-04-07 | AAA | 0.4 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-04-07 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-05-05 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (Q QUALIFIERS ON ALL VOCS EXC. XYLENES, ONLY XYLENES ENTD) - ALL RESULTS BDL (SYSTEM TESTS MONTHLY FOR ALL VOCS ANYWAY - WILL TEST AGAIN 6/21)
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.4 | UG/L | 60.4999 | 2021-05-11 | L4 | 0.9 |  | LKM-28, 419 PALM CREST LANE | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 52.6 | UG/L | 80.4999 | 2021-05-11 | L4 | 0.47 |  | LKM-28, 419 PALM CREST LANE | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.4 | UG/L | 60.4999 | 2021-05-11 | L1 | 0.9 |  | LKM-33, 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 42.1 | UG/L | 80.4999 | 2021-05-11 | L1 | 0.47 |  | LKM-33, 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.4 | UG/L | 60.4999 | 2021-05-11 | L3 | 0.9 |  | LKM-32, 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 58.8 | UG/L | 80.4999 | 2021-05-11 | L3 | 0.47 |  | LKM-32, 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 14.2 | UG/L | 60.4999 | 2021-05-11 | L2 | 0.9 |  | LKM-51, 930 WILLISTON PARK POINT (6/21 DISINF BYP RPRT RCVD W/RESULTS) HLKD | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 50.5 | UG/L | 80.4999 | 2021-05-11 | L2 | 0.47 |  | LKM-51, 930 WILLISTON PARK POINT (6/21 DISINF BYP RPRT RCVD W/RESULTS) HLKD | 3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-06-02 | AAA | 0.35 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-06-02 | AAA | 0.33 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-06-02 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-06-02 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-06-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-06-02 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-06-02 | AAA | 0.12 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-06-02 | AAA | 0.29 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-06-02 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-06-02 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-06-02 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-06-02 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-06-02 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-06-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-06-02 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-06-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-06-02 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-06-02 | AAA | 0.4 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-06-02 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-06-02 | AAA | 0.23 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-06-02 | AAA | 0.2 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-07-08 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-04-07 | AAA | 0.23 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-04-07 | AAA | 0.2 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-07-08 | AAA | 0.35 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-07-08 | AAA | 0.33 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-07-08 | AAA | 0.11 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-07-08 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-07-08 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-07-08 | AAA | 0.12 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-07-08 | AAA | 0.29 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-07-08 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-07-08 | AAA | 0.3 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-07-08 | AAA | 0.27 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-07-08 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-07-08 | AAA | 0.44 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-08 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-07-08 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-07-08 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-07-08 | AAA | 0.26 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-07-08 | AAA | 0.4 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-07-08 | AAA | 0.28 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-07-08 | AAA | 0.23 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-07-08 | AAA | 0.2 | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-08-04 | AAA |  | 0.5499 | LKM7-POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 3.3 | UG/L | 80.4999 | 2021-08-10 | L4 |  |  |  | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 3.8 | UG/L | 80.4999 | 2021-08-10 | L1 |  |  | 3580 N HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 4.4 | UG/L | 80.4999 | 2021-08-10 | L3 |  |  | 455 N COUNTRY CLUB RD | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 6.4 | UG/L | 80.4999 | 2021-08-10 | L2 |  |  | 930 WILLISTON PARK | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-08-10 | L4 |  |  | 419 PALM CREST - HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-08-10 | L1 |  |  | 3580 N HWY 17-92 HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-08-10 | L3 |  |  | 455 N COUNTRY CLUB HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2021-08-10 | L2 |  |  | 930 WILLISTON PARK HAA5 | 3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-09-01 | AAA |  | 0.5499 | LKM 7- POE
3590201 | LAKE MARY, CITY OF | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 7 POE, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0.31 | UG/L | 7.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-10-06 | AAA |  | 0.5499 | LKM 1-WELL 1, 235 RINEHART RD
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-11-03 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-11-03 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-11-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-11-03 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-11-03 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-11-03 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-11-03 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-10-16 | WTP3 |  | 0.6499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-10-16 | WTP3 |  | 2.4999 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-10-16 | WTP3 |  | 0.0749 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-10-16 | WTP3 |  | 0.6499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-10-16 | WTP3 |  | 0.1499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-10-16 | WTP3 |  | 0.2499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-10-16 | WTP3 |  | 0.1499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-10-16 | WTP3 |  | 0.9499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-10-16 | WTP3 |  | 0.1499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-10-16 | WTP3 |  | 0.2499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-10-16 | WTP3 |  | 0.0449 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP3 |  | 0.0249 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-16 | WTP3 |  | 0.1499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-10-16 | WTP3 |  | 0.2499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-10-16 | WTP3 |  | 0.1499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP3 |  | 0.0249 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-10-16 | WTP3 |  | 0.0449 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-10-16 | WTP3 |  | 0.1499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-10-16 | WTP3 |  | 0.0249 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-10-16 | WTP3 |  | 0.0149 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-10-16 | WTP3 |  | 0.2499 | POE WTP3
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2023-10-18 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2023-10-18 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2023-10-18 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2023-10-18 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.82 | LN(10) |  | 2023-10-18 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-10-18 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2023-10-18 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2023-10-18 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 93 | MG/L |  | 2023-10-18 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2023-11-01 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2023-11-01 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 104 | MG/L |  | 2023-11-01 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2023-11-01 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2023-11-01 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-11-01 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2023-11-01 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2023-11-01 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-11-01 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 32.98 | UG/L | 60.4999 | 2023-11-06 | L3 | 0.98 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.29 | UG/L | 80.4999 | 2023-11-06 | L3 | 0.39 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.99 | UG/L | 60.4999 | 2023-11-06 | L4 | 0.98 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 33.44 | UG/L | 80.4999 | 2023-11-06 | L4 | 0.39 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.69 | UG/L | 60.4999 | 2023-11-06 | L1 | 0.98 |  | CWP4 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 32.77 | UG/L | 80.4999 | 2023-11-06 | L1 | 0.39 |  | CWP4 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.25 | UG/L | 60.4999 | 2023-11-06 | L2 | 0.98 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.24 | UG/L | 80.4999 | 2023-11-06 | L2 | 0.39 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2023-11-15 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2023-11-15 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2023-11-15 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2023-11-15 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2023-11-15 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-11-15 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2023-11-15 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2023-11-15 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-11-15 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2023-11-29 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2023-11-29 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2023-11-29 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2023-11-29 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2023-11-29 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2023-11-29 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2023-11-29 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8 | LN(10) |  | 2023-11-29 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2023-11-29 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2023-12-13 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2023-12-13 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2023-12-13 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2023-12-13 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2023-12-13 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-12-13 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2023-12-13 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2023-12-13 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2023-12-13 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2023-12-27 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2023-12-27 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2023-12-27 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2023-12-27 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2023-12-27 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2023-12-27 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2023-12-27 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2023-12-27 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2023-12-27 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-01-03 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2024-01-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2024-01-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-09 | WTP2 | 0.024 |  | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-09 | WTP2 | 0.0034 |  | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-09 | WTP3 | 0.024 |  | SOUTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-01-09 | WTP3 | 0.0034 |  | SOUTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-01-09 | WTP2 |  | 1.4999 | NORTH WP -
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-01-09 | WTP1 | 0.024 |  | J QUALIFIED NITRATE AND NITRITE. NITRATE ACCEPTABLE. NITRITE IS NOT._LMC
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-01-09 | WTP2 | 0.5 | 0.5499 | NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-01-17 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2024-01-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.93 | LN(10) |  | 2024-01-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2024-01-31 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2024-01-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2024-01-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.23 | UG/L | 60.4999 | 2024-02-01 | L3 | 0.98 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 40.23 | UG/L | 80.4999 | 2024-02-01 | L3 | 0.39 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.49 | UG/L | 60.4999 | 2024-02-01 | L4 | 0.98 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 39.63 | UG/L | 80.4999 | 2024-02-01 | L4 | 0.39 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.62 | UG/L | 60.4999 | 2024-02-01 | L1 | 0.98 |  | CWP4 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 40.83 | UG/L | 80.4999 | 2024-02-01 | L1 | 0.39 |  | CWP4 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.83 | UG/L | 60.4999 | 2024-02-01 | L2 | 0.98 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.65 | UG/L | 80.4999 | 2024-02-01 | L2 | 0.39 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-02-14 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-02-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.97 | LN(10) |  | 2024-02-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-27 | WTP2 | 0.4 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP2 | 0.28 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-27 | WTP2 | 0.4 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.41 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-27 | WTP2 | 0.32 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.36 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.33 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.25 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.49 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.37 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP2 | 0.16 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-27 | WTP2 | 0.2 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-27 | WTP2 | 0.33 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.26 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP2 | 0.5 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP2 | 0.24 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-27 | WTP2 | 0.48 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.49 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-27 | WTP2 | 0.4 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP2 | 0.28 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-27 | WTP2 | 0.4 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.41 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-27 | WTP2 | 0.32 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.36 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.33 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.25 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.49 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.37 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP2 | 0.16 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-27 | WTP2 | 0.2 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-27 | WTP2 | 0.33 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.26 | 0.5499 | NORTH WTP WELL #3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP2 | 0.5 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP2 | 0.24 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-27 | WTP2 | 0.48 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.49 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2024-02-27 | WTP2 | 0.4 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP2 | 0.28 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2024-02-27 | WTP2 | 0.4 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.41 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2024-02-27 | WTP2 | 0.32 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.36 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.33 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.25 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.44 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2024-02-27 | WTP2 | 0.49 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.37 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2024-02-27 | WTP2 | 0.16 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2024-02-27 | WTP2 | 0.2 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-02-27 | WTP2 | 0.33 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2024-02-27 | WTP2 | 0.26 | 0.5499 | NORTH WTP WELL #2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP2 | 0.5 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2024-02-27 | WTP2 | 0.24 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-02-27 | WTP2 | 0.48 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2024-02-27 | WTP2 | 0.49 | 0.5499 | NORTH WTP WELL #1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-02-28 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-02-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-02-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-03-13 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-03-13 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2024-03-13 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.76 | LN(10) |  | 2024-03-27 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-03-27 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2024-03-27 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2024-04-10 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-04-10 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2024-04-10 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-04-24 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-04-24 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-04-24 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.94 | UG/L | 60.4999 | 2024-05-01 | L3 | 0.98 |  | 7603 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 47.47 | UG/L | 80.4999 | 2024-05-01 | L3 | 0.39 |  | 7603 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 30.51 | UG/L | 60.4999 | 2024-05-01 | L4 | 0.98 |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 37.13 | UG/L | 80.4999 | 2024-05-01 | L4 | 0.39 |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 34.21 | UG/L | 60.4999 | 2024-05-01 | L1 | 0.98 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 36.77 | UG/L | 80.4999 | 2024-05-01 | L1 | 0.39 |  | 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.25 | UG/L | 60.4999 | 2024-05-01 | L2 | 0.98 |  | 261 LYMAN RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 48.19 | UG/L | 80.4999 | 2024-05-01 | L2 | 0.39 |  | 261 LYMAN RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-05-07 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-05-07 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2024-05-07 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-05-22 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-05-22 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2024-05-22 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-06-05 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-06-05 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2024-06-05 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2024-06-19 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-06-19 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2024-06-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.79 | LN(10) |  | 2024-07-03 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-07-03 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2024-07-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2024-07-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-07-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2024-07-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2024-07-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.8 |  |  | 2024-07-03 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2024-07-03 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2024-07-03 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.78 | LN(10) |  | 2024-07-17 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2024-07-17 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2024-07-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2024-07-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2024-07-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2024-07-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2024-07-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.7 |  |  | 2024-07-17 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2024-07-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2024-07-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.6 |  |  | 2024-07-03 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2024-07-17 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2024-07-17 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.5 |  |  | 2024-07-17 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-07-31 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2024-07-31 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.03 | LN(10) |  | 2024-07-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2024-07-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2024-07-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2024-07-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2024-07-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.8 |  |  | 2024-07-31 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2024-07-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-07-31 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-07-31 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-07-31 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.3 | UG/L | 60.4999 | 2024-08-06 | L3 | 0.98 |  | 7603 CITRUS AVE - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.13 | UG/L | 80.4999 | 2024-08-06 | L3 | 0.39 |  | 7603 CITRUS AVE - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.24 | UG/L | 60.4999 | 2024-08-06 | L4 | 0.98 |  | 5401 LAKE HOWELL RD - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 38.74 | UG/L | 80.4999 | 2024-08-06 | L4 | 0.39 |  | 5401 LAKE HOWELL RD - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.21 | UG/L | 60.4999 | 2024-08-06 | L1 | 0.98 |  | 1817 DOVER RD - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 34.96 | UG/L | 80.4999 | 2024-08-06 | L1 | 0.39 |  | 1817 DOVER RD - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.01 | UG/L | 60.4999 | 2024-08-06 | L2 | 0.98 |  | 261 LYMAN RD - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 46.64 | UG/L | 80.4999 | 2024-08-06 | L2 | 0.39 |  | 261 LYMAN RD - SUBCONTRACTED TO E84589,E82535
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-08-14 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2024-08-14 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.05 | LN(10) |  | 2024-08-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2024-08-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2024-08-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-08-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.73 | MG/L |  | 2024-08-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.7 |  |  | 2024-08-14 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2024-08-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2024-08-14 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2024-08-14 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.9 |  |  | 2024-08-14 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.68 | LN(10) |  | 2024-08-28 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2024-08-28 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.03 | LN(10) |  | 2024-08-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2024-08-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2024-08-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-08-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2024-08-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.7 |  |  | 2024-08-28 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2024-08-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.1 |  |  | 2024-08-28 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2024-08-28 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-08-28 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.63 | LN(10) |  | 2024-09-11 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-09-11 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.09 | LN(10) |  | 2024-09-11 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2024-09-11 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2024-09-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2024-09-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2024-09-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 26.4 |  |  | 2024-09-11 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2024-09-11 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-09-11 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2024-09-11 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-09-11 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-09-17 | WTP2 |  | 1.4999 | POE - N PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-09-17 | WTP2 |  | 1.4999 | POE NORTH PL
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.71 | LN(10) |  | 2024-09-25 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2024-09-25 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.08 | LN(10) |  | 2024-09-25 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-09-25 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.95 | LN(10) |  | 2024-09-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-09-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2024-09-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.9 |  |  | 2024-09-25 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2024-09-25 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-09-25 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2024-09-25 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-09-25 | WTP3 |  |  | SOUTH PLANT
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-11-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-11-03 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-11-03 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-11-03 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-11-03 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.3 | UG/L | 60.4999 | 2021-11-08 | L4 | 0.9 |  | LKM-28, 419 PALM CREST LANE | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 9.1 | UG/L | 80.4999 | 2021-11-08 | L4 | 0.47 |  | LKM-28, 419 PALM CREST LANE | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.2 | UG/L | 60.4999 | 2021-11-08 | L1 | 0.9 |  | LKM-33, 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 12.6 | UG/L | 80.4999 | 2021-11-08 | L1 | 0.47 |  | LKM-33, 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 1.9 | UG/L | 60.4999 | 2021-11-08 | L3 | 0.9 |  | LKM-32, 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 6.6 | UG/L | 80.4999 | 2021-11-08 | L3 | 0.47 |  | LKM-32, 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.1 | UG/L | 60.4999 | 2021-11-08 | L2 | 0.9 |  | LKM-51, 930 WILLISTON PARK PT. (12/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 12.9 | UG/L | 80.4999 | 2021-11-08 | L2 | 0.47 |  | LKM-51, 930 WILLISTON PARK PT. (12/21 QTR DISINF BYP RPRT RCVD W/RSLTS) HLKD | 3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2021-12-07 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-01-06 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-01-06 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-01-06 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-01-06 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-01-06 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-01-06 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-01-06 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-01-06 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-01-06 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-01-06 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-01-06 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-01-06 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-01-06 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-06 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-01-06 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-01-06 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-01-06 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-01-06 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-01-06 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-01-06 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-01-06 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-02-03 | AAA |  | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.1 | UG/L | 60.4999 | 2022-02-09 | L4 |  |  | 419 PALM CREST LANE | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 14.7 | UG/L | 80.4999 | 2022-02-09 | L4 |  |  | 419 PALM CREST LANE | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 2.2 | UG/L | 60.4999 | 2022-02-09 | L1 |  |  | 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 8.5 | UG/L | 80.4999 | 2022-02-09 | L1 |  |  | 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.8 | UG/L | 60.4999 | 2022-02-09 | L3 |  |  | 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 13.3 | UG/L | 80.4999 | 2022-02-09 | L3 |  |  | 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 3.1 | UG/L | 60.4999 | 2022-02-09 | L2 |  |  | 930 WILLISTON PARK PT | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 10.1 | UG/L | 80.4999 | 2022-02-09 | L2 |  |  | 930 WILLISTON PARK PT | 3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-03-09 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-03-09 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-03-09 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-03-09 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-03-09 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-03-09 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-03-09 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-03-09 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-03-09 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-03-09 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-03-09 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-03-09 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-03-09 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-03-09 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-03-09 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-03-09 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-03-09 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-03-09 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | INOR | 1040 | NITRATE | 0.17 | MG/L | 10.4999 | 2022-03-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-03-09 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-04-08 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-04-08 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-04-08 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-04-08 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-04-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-04-08 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-04-08 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-04-08 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-04-08 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-04-08 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-04-08 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-04-08 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-04-08 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-04-08 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-04-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-04-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-04-08 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-04-08 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-04-08 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-04-08 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-05-05 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-05-05 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-05-05 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-05-05 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-05-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-05-05 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-05-05 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-05-05 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-05-05 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-05-05 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-05-05 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-05-05 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-05-05 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-05-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-05-05 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-05-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-05-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-05-05 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-05-05 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-05-05 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-05-05 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.7 | UG/L | 60.4999 | 2022-05-11 | L4 | 0.9 |  | 419 PALM CREST LN. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 22.3 | UG/L | 80.4999 | 2022-05-11 | L4 | 0.47 |  | 419 PALM CREST LN. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.6 | UG/L | 60.4999 | 2022-05-11 | L1 | 0.9 |  | 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 13.4 | UG/L | 80.4999 | 2022-05-11 | L1 | 0.47 |  | 3580 N. HWY 17-92 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 4.9 | UG/L | 60.4999 | 2022-05-11 | L3 | 0.9 |  | 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 20.1 | UG/L | 80.4999 | 2022-05-11 | L3 | 0.47 |  | 455 N. COUNTRY CLUB RD. | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.1 | UG/L | 60.4999 | 2022-05-11 | L2 | 0.9 |  | 930 WILLISTON PARK PT. (HLKD) | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 18.9 | UG/L | 80.4999 | 2022-05-11 | L2 | 0.47 |  | 930 WILLISTON PARK PT. (HLKD) | 3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-07-07 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-07-07 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-07-07 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-07-07 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-07-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-07-07 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-07-07 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-07-07 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-07-07 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-07-07 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-07-07 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-07-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-07-07 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-07-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-07-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-07-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-07-07 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-07-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-07-07 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-07-07 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.52 | UG/L | 60.4999 | 2022-08-16 | L3 | 0.98 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.15 | UG/L | 80.4999 | 2022-08-16 | L3 | 0.39 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 39.29 | UG/L | 60.4999 | 2022-08-16 | L4 | 0.98 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.47 | UG/L | 80.4999 | 2022-08-16 | L4 | 0.39 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.31 | UG/L | 60.4999 | 2022-08-16 | L1 | 0.98 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.8 | UG/L | 60.4999 | 2022-08-16 | L2 | 0.98 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.97 | UG/L | 80.4999 | 2022-08-16 | L2 | 0.39 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.8 | UG/L | 80.4999 | 2022-08-16 | L1 | 0.39 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 48.89 | UG/L | 80.4999 | 2022-11-17 | L1 | 0.39 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.92 | UG/L | 60.4999 | 2022-11-17 | L3 | 0.98 |  | RAVEN AVE. L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 63.43 | UG/L | 80.4999 | 2022-11-17 | L3 | 0.39 |  | RAVEN AVE. L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.71 | UG/L | 60.4999 | 2022-11-17 | L4 | 0.98 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 69.7 | UG/L | 80.4999 | 2022-11-17 | L4 | 0.39 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.04 | UG/L | 60.4999 | 2022-11-17 | L1 | 0.98 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.86 | UG/L | 60.4999 | 2022-11-17 | L2 | 0.98 |  | 1057 N. HWY 17-92 (12/22 QTR DISINF BYP RPRT RCVD W/RESULTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.93 | UG/L | 80.4999 | 2022-11-17 | L2 | 0.39 |  | 1057 N. HWY 17-92 (12/22 QTR DISINF BYP RPRT RCVD W/RESULTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.81 | UG/L | 60.4999 | 2023-02-16 | L3 | 0.98 |  | RAVEN AVE L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 50.52 | UG/L | 80.4999 | 2023-02-16 | L3 | 0.39 |  | RAVEN AVE L/S
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.46 | UG/L | 60.4999 | 2023-02-16 | L4 | 0.98 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.76 | UG/L | 80.4999 | 2023-02-16 | L4 | 0.39 |  | 900 NORTH ST.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.43 | UG/L | 60.4999 | 2023-02-16 | L1 | 0.98 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.47 | UG/L | 80.4999 | 2023-02-16 | L1 | 0.39 |  | 235 W. CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.86 | UG/L | 60.4999 | 2023-02-16 | L2 | 0.98 |  | 1057 N. HWY 17-92 (3/23 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 45.66 | UG/L | 80.4999 | 2023-02-16 | L2 | 0.39 |  | 1057 N. HWY 17-92 (3/23 QTR DISINF BYP REPORT RCVD W/RSLTS) HLKD
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.087 | MG/L | 10.4999 | 2023-03-23 | WTP2 | 0.024 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-23 | WTP2 | 0.00025 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1010 | BARIUM | 0.0057 | MG/L | 2.4999 | 2023-03-23 | WTP2 | 0.003 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-23 | WTP2 | 0.00025 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-23 | WTP2 | 0.005 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-03-23 | WTP2 | 0.004 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1025 | FLUORIDE | 0.49 | MG/L | 4.0499 | 2023-03-23 | WTP2 | 0.0099 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-23 | WTP2 | 0.0005 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-23 | WTP2 | 1e-05 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-23 | WTP2 | 0.008 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-23 | WTP2 | 0.0012 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1052 | SODIUM | 13 | MG/L | 160.4999 | 2023-03-23 | WTP2 | 0.8 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-23 | WTP2 | 0.001 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-23 | WTP2 | 0.002 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-23 | WTP2 | 0.00025 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-03-23 | WTP2 | 0.021 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-03-23 | WTP2 | 0.005 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1025 | FLUORIDE | 0.49 | MG/L | 2.0499 | 2023-03-23 | WTP2 | 0.0099 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-23 | WTP2 | 0.0067 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-03-23 | WTP2 | 0.005 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-23 | WTP2 | 0.0005 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1055 | SULFATE | 6.6 | MG/L | 250.4999 | 2023-03-23 | WTP2 | 0.034 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1095 | ZINC | 0 | MG/L | 5.4999 | 2023-03-23 | WTP2 | 0.05 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-03-23 | WTP2 | 5 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2023-03-23 | WTP2 | 1 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.27 | LN(10) |  | 2023-03-23 | WTP2 |  |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-03-23 | WTP2 | 0.32 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 180 | MG/L | 500.4999 | 2023-03-23 | WTP2 | 5 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0.1 |  | 0.5499 | 2023-03-23 | WTP2 | 0.04 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-03-23 | WTP2 | 0.28 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-03-23 | WTP2 | 0.28 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-03-23 | WTP2 | 0.44 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-03-23 | WTP2 | 0.46 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-03-23 | WTP2 | 0.26 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-03-23 | WTP2 | 0.2 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-03-23 | WTP2 | 0.18 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-03-23 | WTP2 | 0.28 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP2 | 0.36 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-03-23 | WTP2 | 0.39 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP2 | 0.23 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-03-23 | WTP2 | 0.26 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP2 | 0.28 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-03-23 | WTP2 | 0.12 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP2 | 0.24 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-03-23 | WTP2 | 0.12 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-03-23 | WTP2 | 0.17 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-03-23 | WTP2 | 0.22 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-03-23 | WTP2 | 0.17 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-03-23 | WTP2 | 0.39 | 0.5499 | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-03-23 | WTP2 | 0.0069 | 0.0149 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP2 | 0.0071 | 0.0249 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-03-23 | WTP2 | 0.0068 | 0.1499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP2 | 0.12 | 1.4999 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-03-23 | WTP2 | 0.9 | 1.4999 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-03-23 | WTP2 | 0.37 | 0.4499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-03-23 | WTP2 | 6 | 9.4999 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-03-23 | WTP2 | 5.9 | 6.4999 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-03-23 | WTP2 | 0.5 | 0.6499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-03-23 | WTP2 | 1.8 | 2.4999 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-03-23 | WTP2 | 0.06 | 0.0749 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-03-23 | WTP2 | 0.5 | 0.6499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-03-23 | WTP2 | 0.09 | 0.1499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-03-23 | WTP2 | 0.18 | 0.2499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-03-23 | WTP2 | 0.019 | 0.1499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-03-23 | WTP2 | 0.51 | 0.9499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP2 | 0.09 | 0.1499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-03-23 | WTP2 | 0.15 | 0.2499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-03-23 | WTP2 | 0.006 | 0.0449 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP2 | 0.0052 | 0.0249 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-03-23 | WTP2 | 0.095 | 0.1499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-03-23 | WTP2 | 0.09 | 0.2499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-03-23 | WTP2 | 0.0063 | 0.1499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP2 | 0.015 | 0.0249 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-03-23 | WTP2 | 0.038 | 0.0449 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-03-23 | WTP2 | 0.093 | 0.1499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP2 | 0.0062 | 0.0249 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-03-23 | WTP2 | 0.0092 | 0.0149 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-03-23 | WTP2 | 0.053 | 0.2499 | WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1010 | BARIUM | 0.0039 | MG/L | 2.4999 | 2023-03-23 | WTP1 | 0.003 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-23 | WTP2 | 0.0034 |  | 1041 J QILIFIED- ACCEPTABLE BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1017 | CHLORIDE | 16 | MG/L | 250.4999 | 2023-03-23 | WTP2 | 0.039 |  | WTP2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.078 | MG/L | 10.4999 | 2023-03-23 | WTP1 | 0.024 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-23 | WTP1 | 0.0034 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-23 | WTP1 | 0.00025 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-23 | WTP1 | 0.00025 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-23 | WTP1 | 0.005 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-03-23 | WTP1 | 0.004 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1025 | FLUORIDE | 0.7 | MG/L | 4.0499 | 2023-03-23 | WTP1 | 0.0099 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2023-03-23 | WTP1 | 0.0005 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2023-03-23 | WTP1 | 1e-05 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2023-03-23 | WTP1 | 0.008 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2023-03-23 | WTP1 | 0.0012 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1052 | SODIUM | 15 | MG/L | 160.4999 | 2023-03-23 | WTP1 | 0.8 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2023-03-23 | WTP1 | 0.001 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2023-03-23 | WTP1 | 2 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2023-03-23 | WTP1 | 0.00025 |  | WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2023-03-23 | WTP1 | 0.021 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1017 | CHLORIDE | 24 | MG/L | 250.4999 | 2023-03-23 | WTP1 | 0.039 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1022 | COPPER | 0 | MG/L | 1.4999 | 2023-03-23 | WTP1 | 0.005 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1025 | FLUORIDE | 0.7 | MG/L | 2.0499 | 2023-03-23 | WTP1 | 0.0099 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1028 | IRON | 0 | MG/L | 0.3499 | 2023-03-23 | WTP1 | 0.0067 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1032 | MANGANESE | 0 | MG/L | 0.0549 | 2023-03-23 | WTP1 | 0.005 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1050 | SILVER | 0 | MG/L | 0.1499 | 2023-03-23 | WTP1 | 0.0005 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1055 | SULFATE | 3.1 | MG/L | 250.4999 | 2023-03-23 | WTP1 | 0.034 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1095 | ZINC | 0.053 | MG/L | 5.4999 | 2023-03-23 | WTP1 | 0.05 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1905 | COLOR | 10 | COLOR UNITS | 15.4999 | 2023-03-23 | WTP1 | 5 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1920 | ODOR THRESHOLD | 1 |  | 3.4999 | 2023-03-23 | WTP1 | 1 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1925 | pH (LAB) (6.5 to 8.5) | 7.25 | LN(10) |  | 2023-03-23 | WTP1 |  |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 1930 | TOTAL DISSOLVED SOLIDS | 160 | MG/L | 500.4999 | 2023-03-23 | WTP1 | 5 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SEC | 2905 | FOAMING AGENTS | 0.088 |  | 0.5499 | 2023-03-23 | WTP1 | 0.04 |  | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-03-23 | WTP1 | 0.28 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-03-23 | WTP1 | 0.32 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-03-23 | WTP1 | 0.28 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-03-23 | WTP1 | 0.44 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-03-23 | WTP1 | 0.46 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-03-23 | WTP1 | 0.26 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-03-23 | WTP1 | 0.2 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-03-23 | WTP1 | 0.18 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-03-23 | WTP1 | 0.28 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP1 | 0.36 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-03-23 | WTP1 | 0.39 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP1 | 0.23 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-03-23 | WTP1 | 0.26 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP1 | 0.28 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-03-23 | WTP1 | 0.12 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP1 | 0.24 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-03-23 | WTP1 | 0.12 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-03-23 | WTP1 | 0.17 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-03-23 | WTP1 | 0.22 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-03-23 | WTP1 | 0.17 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-03-23 | WTP1 | 0.39 | 0.5499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-03-23 | WTP1 | 0.0073 | 0.0149 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-03-23 | WTP1 | 0.9 | 1.4999 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP1 | 0.0075 | 0.0249 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-03-23 | WTP1 | 0.0072 | 0.1499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP1 | 0.13 | 1.4999 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-03-23 | WTP1 | 0.37 | 0.4499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-03-23 | WTP1 | 6 | 9.4999 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-03-23 | WTP1 | 5.9 | 6.4999 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-03-23 | WTP1 | 0.5 | 0.6499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-03-23 | WTP1 | 1.8 | 2.4999 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-03-23 | WTP1 | 0.06 | 0.0749 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-03-23 | WTP1 | 0.5 | 0.6499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-03-23 | WTP1 | 0.09 | 0.1499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-03-23 | WTP1 | 0.18 | 0.2499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-03-23 | WTP1 | 0.02 | 0.1499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-03-23 | WTP1 | 0.51 | 0.9499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-03-23 | WTP1 | 0.09 | 0.1499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-03-23 | WTP1 | 0.15 | 0.2499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-03-23 | WTP1 | 0.0063 | 0.0449 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP1 | 0.0055 | 0.0249 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-03-23 | WTP1 | 0.095 | 0.1499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-03-23 | WTP1 | 0.09 | 0.2499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-03-23 | WTP1 | 0.0066 | 0.1499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP1 | 0.015 | 0.0249 | WTP1
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.72 | LN(10) |  | 2024-10-09 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2024-10-09 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.06 | LN(10) |  | 2024-10-09 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-10-09 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.94 | LN(10) |  | 2024-10-09 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2024-10-09 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2024-10-09 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.5 |  |  | 2024-10-09 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2024-10-09 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.9 |  |  | 2024-10-09 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2024-10-09 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.3 |  |  | 2024-10-09 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.73 | LN(10) |  | 2024-10-23 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2024-10-23 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2024-10-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2024-10-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2024-10-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2024-10-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.59 | MG/L |  | 2024-10-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.1 |  |  | 2024-10-23 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2024-10-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2024-10-23 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2024-10-23 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.2 |  |  | 2024-10-23 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.24 | UG/L | 60.4999 | 2024-11-04 | L3 | 0.98 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 42.95 | UG/L | 80.4999 | 2024-11-04 | L3 | 0.39 |  | CWP2STG1 7603 CITRUS AVE., WINTER PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.64 | UG/L | 60.4999 | 2024-11-04 | L4 | 0.98 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 31.15 | UG/L | 80.4999 | 2024-11-04 | L4 | 0.39 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.64 | UG/L | 60.4999 | 2024-11-04 | L1 | 0.98 |  | CWP4 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 29.23 | UG/L | 80.4999 | 2024-11-04 | L1 | 0.39 |  | CWP4 1817 DOVER RD.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.21 | UG/L | 60.4999 | 2024-11-04 | L2 | 0.98 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 43.16 | UG/L | 80.4999 | 2024-11-04 | L2 | 0.39 |  | CWP5 261 LYMAN RD. (NOT DR.)
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.67 | LN(10) |  | 2024-11-06 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2024-11-06 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-11-06 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2024-11-06 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2024-11-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2024-11-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2024-11-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 25.1 |  |  | 2024-11-06 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2024-11-06 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.8 |  |  | 2024-11-06 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2024-11-06 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.4 |  |  | 2024-11-06 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.75 | LN(10) |  | 2024-11-19 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2024-11-19 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2024-11-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2024-11-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2024-11-19 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2024-11-19 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2024-11-19 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.6 |  |  | 2024-11-19 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2024-11-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.7 |  |  | 2024-11-19 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2024-11-19 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.8 |  |  | 2024-11-19 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-12-04 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-12-04 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.14 | LN(10) |  | 2024-12-04 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2024-12-04 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2024-12-04 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 126 | MG/L |  | 2024-12-04 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2024-12-04 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 22.8 |  |  | 2024-12-04 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2024-12-04 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23 |  |  | 2024-12-04 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.74 | MG/L |  | 2024-12-04 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 22.8 |  |  | 2024-12-04 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-12-18 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-12-18 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.09 | LN(10) |  | 2024-12-18 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2024-12-18 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.7 | LN(10) |  | 2024-12-18 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2024-12-18 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2024-12-18 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24 |  |  | 2024-12-18 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-12-18 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.1 |  |  | 2024-12-18 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.81 | MG/L |  | 2024-12-18 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24 |  |  | 2024-12-18 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2024-12-26 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2024-12-26 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.09 | LN(10) |  | 2024-12-26 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2024-12-26 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.83 | LN(10) |  | 2024-12-26 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2024-12-26 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-12-26 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.4 |  |  | 2024-12-26 | WTP1 |  |  | HOWELL PARK
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2024-12-26 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 24.2 |  |  | 2024-12-26 | WTP2 |  |  | NORTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2024-12-26 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1996 | TEMPERATURE (Degrees C.) | 23.4 |  |  | 2024-12-26 | WTP3 |  |  | SOUTH PLANT
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2025-01-01 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2025-01-01 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-01-01 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2025-01-01 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.13 | LN(10) |  | 2025-01-01 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2025-01-01 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2025-01-08 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.06 | LN(10) |  | 2025-01-08 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2025-01-08 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2025-01-08 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-01-08 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2025-01-08 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.75 | MG/L |  | 2025-01-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.76 | MG/L |  | 2025-01-01 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2025-01-01 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-01-01 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2025-01-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2025-01-08 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2025-01-15 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2025-01-15 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 1111 | MG/L |  | 2025-01-15 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.71 | MG/L |  | 2025-01-15 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.12 | LN(10) |  | 2025-01-15 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2025-01-15 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2025-01-15 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2025-01-15 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2025-01-15 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2025-01-22 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.04 | LN(10) |  | 2025-01-22 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2025-01-22 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2025-01-22 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1924 | pH (FIELD) | 8.14 | LN(10) |  | 2025-01-22 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2025-01-22 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.72 | MG/L |  | 2025-01-22 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.88 | LN(10) |  | 2025-01-22 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-01-22 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-01-29 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2025-01-29 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1929 | ALKALINITY - CARBONATE | 107 | MG/L | 0 | 2025-01-29 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.086 | MG/L | 10.4999 | 2025-01-29 | WTP2 | 0.024 |  | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-29 | WTP2 |  |  | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.2 | MG/L | 10.4999 | 2025-01-29 | WTP3 | 0.024 |  | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-29 | WTP3 |  |  | POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | INOR | 1040 | NITRATE | 0.091 | MG/L | 10.4999 | 2025-01-29 | WTP1 | 0.024 |  | DIST - POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-01-29 | WTP1 |  |  | DIST - POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2025-01-29 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.12 | LN(10) |  | 2025-01-29 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2025-01-29 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.7 | MG/L |  | 2025-01-29 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-01-29 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2025-01-29 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-01-29 | WTP2 | 0.27 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-01-29 | WTP2 | 0.39 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-01-29 | WTP2 | 0.33 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-01-29 | WTP2 | 0.29 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-01-29 | WTP2 | 0.22 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.25 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.21 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.24 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-01-29 | WTP2 | 0.29 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.26 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.14 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.27 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.42 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.36 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-01-29 | WTP2 | 0.26 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-01-29 | WTP2 | 0.33 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-01-29 | WTP2 | 0.31 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.25 | 0.5499 | NORTH PLANT WELL 1
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-01-29 | WTP2 | 0.27 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-01-29 | WTP2 | 0.39 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-01-29 | WTP2 | 0.33 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-01-29 | WTP2 | 0.29 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-01-29 | WTP2 | 0.22 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.21 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.24 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-01-29 | WTP2 | 0.29 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.25 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.26 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.14 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.27 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.42 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.36 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-01-29 | WTP2 | 0.26 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-01-29 | WTP2 | 0.33 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-01-29 | WTP2 | 0.31 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.25 | 0.5499 | NORTH PLANT WELL 2
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-01-29 | WTP2 | 0.27 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.44 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-01-29 | WTP2 | 0.39 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-01-29 | WTP2 | 0.33 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-01-29 | WTP2 | 0.29 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-01-29 | WTP2 | 0.22 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.21 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.24 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-01-29 | WTP2 | 0.29 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.25 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.26 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.14 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-01-29 | WTP2 | 0.27 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-01-29 | WTP2 | 0.42 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.36 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-01-29 | WTP2 | 0.26 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-01-29 | WTP2 | 0.33 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-01-29 | WTP2 | 0.31 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | R | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-01-29 | WTP2 | 0.25 | 0.5499 | NORTH PLANT WELL 3
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.31 | UG/L | 60.4999 | 2025-02-03 | L5 | 0.98 |  | CWP2STG1 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 50.88 | UG/L | 80.4999 | 2025-02-03 | L5 | 0.44 |  | CWP2STG1 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.2 | UG/L | 60.4999 | 2025-02-03 | L4 | 0.98 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 40.57 | UG/L | 80.4999 | 2025-02-03 | L4 | 0.44 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.79 | UG/L | 60.4999 | 2025-02-03 | L6 | 0.98 |  | CWP4 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 37.26 | UG/L | 80.4999 | 2025-02-03 | L6 | 0.44 |  | CWP4 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.49 | UG/L | 60.4999 | 2025-02-03 | L7 | 0.98 |  | CWP5 170 LYMAN ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 55.21 | UG/L | 80.4999 | 2025-02-03 | L7 | 0.44 |  | CWP5 170 LYMAN ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2025-02-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2025-02-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-02-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-02-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2025-02-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2025-02-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2025-02-12 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2025-02-12 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2025-02-12 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2025-02-12 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.12 | LN(10) |  | 2025-02-12 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2025-02-12 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2025-02-12 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.74 | LN(10) |  | 2025-02-12 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2025-02-12 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2025-02-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2025-02-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2025-02-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2025-02-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-02-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2025-02-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2025-02-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.8 | LN(10) |  | 2025-02-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2025-02-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2025-02-26 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2025-02-26 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2025-02-26 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-02-26 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.12 | LN(10) |  | 2025-02-26 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2025-02-26 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2025-02-26 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.77 | LN(10) |  | 2025-02-26 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2025-02-26 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2025-03-05 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2025-03-05 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2025-03-05 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2025-03-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2025-03-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-03-05 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2025-03-12 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2025-03-12 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-03-12 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-03-12 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2025-03-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2025-03-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 106 | MG/L |  | 2025-03-05 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2025-03-12 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2025-03-12 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2025-03-12 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2025-03-12 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2025-03-12 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-03-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2025-03-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-03-19 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2025-03-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.14 | LN(10) |  | 2025-03-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-03-19 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2025-03-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2025-03-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2025-03-19 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2025-03-26 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2025-03-26 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-03-26 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-03-26 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-03-26 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-03-26 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2025-03-26 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.86 | LN(10) |  | 2025-03-26 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2025-03-26 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2025-04-02 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2025-04-02 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-04-02 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2025-04-02 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.12 | LN(10) |  | 2025-04-02 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2025-04-02 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2025-04-02 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2025-04-02 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2025-04-02 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-04-03 | WTP2 | 0.44 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-04-03 | WTP2 | 0.27 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-04-03 | WTP2 | 0.44 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-04-03 | WTP2 | 0.44 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-04-03 | WTP2 | 0.39 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-04-03 | WTP2 | 0.33 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-04-03 | WTP2 | 0.29 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-04-03 | WTP2 | 0.22 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-04-03 | WTP2 | 0.24 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-04-03 | WTP2 | 0.29 | 0.5499 | NORTH WELL POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-03-23 | WTP1 | 0.038 | 0.0449 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-03-23 | WTP1 | 0.098 | 0.1499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-03-23 | WTP1 | 0.0061 | 0.0249 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-03-23 | WTP1 | 0.0091 | 0.0149 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-03-23 | WTP1 | 0.056 | 0.2499 | WTP1
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.63 | UG/L | 60.4999 | 2023-05-17 | L3 | 0.98 |  | RAVEN AVE- J QUALIFIER- ACCEPTED BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.06 | UG/L | 60.4999 | 2023-05-17 | L4 | 0.98 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 75.59 | UG/L | 80.4999 | 2023-05-17 | L4 | 0.39 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.8 | UG/L | 60.4999 | 2023-05-17 | L1 | 0.98 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 57.59 | UG/L | 80.4999 | 2023-05-17 | L1 | 0.39 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.79 | UG/L | 60.4999 | 2023-05-17 | L2 | 0.98 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 74.83 | UG/L | 80.4999 | 2023-05-17 | L2 | 0.39 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 74.88 | UG/L | 80.4999 | 2023-05-17 | L3 | 0.39 |  | RAVEN AVE- J QUALIFIER- ACCEPTED BASED ON QA/QC
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-07-24 | WTP1 |  | 1.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-07-24 | WTP1 |  | 0.0149 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP1 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-07-24 | WTP1 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-07-24 | WTP1 |  | 1.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-07-24 | WTP1 |  | 0.4499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-07-24 | WTP1 |  | 9.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-07-24 | WTP1 |  | 6.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-07-24 | WTP1 |  | 0.6499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-07-24 | WTP1 |  | 2.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-07-24 | WTP1 |  | 0.0749 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-07-24 | WTP1 |  | 0.6499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-07-24 | WTP1 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-07-24 | WTP1 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-07-24 | WTP1 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-07-24 | WTP1 |  | 0.9499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-07-24 | WTP1 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-07-24 | WTP1 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-07-24 | WTP1 |  | 0.0449 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP1 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-07-24 | WTP1 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-07-24 | WTP1 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-07-24 | WTP1 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP1 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-07-24 | WTP1 |  | 0.0449 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-07-24 | WTP1 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP1 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-24 | WTP1 |  | 0.0149 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-07-24 | WTP1 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2023-07-24 | WTP2 |  | 0.0149 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP2 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2023-07-24 | WTP2 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2023-07-24 | WTP2 |  | 1.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-07-24 | WTP2 |  | 1.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2023-07-24 | WTP2 |  | 0.4499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2023-07-24 | WTP2 |  | 9.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2023-07-24 | WTP2 |  | 6.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2023-07-24 | WTP2 |  | 0.6499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2023-07-24 | WTP2 |  | 2.4999 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2023-07-24 | WTP2 |  | 0.0749 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2023-07-24 | WTP2 |  | 0.6499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2023-07-24 | WTP2 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2023-07-24 | WTP2 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2023-07-24 | WTP2 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2023-07-24 | WTP2 |  | 0.9499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2023-07-24 | WTP2 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2023-07-24 | WTP2 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2023-07-24 | WTP2 |  | 0.0449 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP2 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-07-24 | WTP2 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2023-07-24 | WTP2 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2023-07-24 | WTP2 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP2 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2023-07-24 | WTP2 |  | 0.0449 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2023-07-24 | WTP2 |  | 0.1499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2023-07-24 | WTP2 |  | 0.0249 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2023-07-24 | WTP2 |  | 0.0149 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2023-07-24 | WTP2 |  | 0.2499 | POE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.75 | UG/L | 60.4999 | 2023-08-18 | L3 | 0.98 |  | L3- RAVEN AVE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 61.18 | UG/L | 80.4999 | 2023-08-18 | L3 | 0.39 |  | L3- RAVEN AVE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 33.76 | UG/L | 60.4999 | 2023-08-18 | L4 | 0.98 |  | L4- 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 70.7 | UG/L | 80.4999 | 2023-08-18 | L4 | 0.39 |  | L4- 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.93 | UG/L | 60.4999 | 2023-08-18 | L1 | 0.98 |  | L1-W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.53 | UG/L | 80.4999 | 2023-08-18 | L1 | 0.39 |  | L1-W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.41 | UG/L | 60.4999 | 2023-08-18 | L2 | 26.41 |  | L2- 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 51.29 | UG/L | 80.4999 | 2023-08-18 | L2 | 0.39 |  | L2- 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 38.42 | UG/L | 60.4999 | 2023-11-20 | L3 | 0.98 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 53.3 | UG/L | 80.4999 | 2023-11-20 | L3 | 0.39 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 40.33 | UG/L | 60.4999 | 2023-11-20 | L4 | 0.98 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.29 | UG/L | 80.4999 | 2023-11-20 | L4 | 0.39 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 41.02 | UG/L | 60.4999 | 2023-11-20 | L1 | 0.98 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 46.5 | UG/L | 80.4999 | 2023-11-20 | L1 | 0.39 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 47.53 | UG/L | 60.4999 | 2023-11-20 | L2 | 0.98 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.54 | UG/L | 80.4999 | 2023-11-20 | L2 | 0.39 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.61 | UG/L | 60.4999 | 2024-02-19 | L3 | 0.98 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 50.54 | UG/L | 80.4999 | 2024-02-19 | L3 | 0.39 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.71 | UG/L | 60.4999 | 2024-02-19 | L4 | 0.98 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 59.66 | UG/L | 80.4999 | 2024-02-19 | L4 | 0.39 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.6 | UG/L | 60.4999 | 2024-02-19 | L1 | 0.98 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 42.63 | UG/L | 80.4999 | 2024-02-19 | L1 | 0.39 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.74 | UG/L | 60.4999 | 2024-02-19 | L2 | 0.98 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 52.78 | UG/L | 80.4999 | 2024-02-19 | L2 | 0.39 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.14 | UG/L | 60.4999 | 2024-05-17 | L3 | 0.98 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 60.03 | UG/L | 80.4999 | 2024-05-17 | L3 | 0.39 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.74 | UG/L | 60.4999 | 2024-05-17 | L4 | 0.98 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.53 | UG/L | 80.4999 | 2024-05-17 | L4 | 0.39 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.02 | UG/L | 60.4999 | 2024-05-17 | L1 | 0.98 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.58 | UG/L | 80.4999 | 2024-05-17 | L1 | 0.39 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.23 | UG/L | 60.4999 | 2024-05-17 | L2 | 0.98 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 52.84 | UG/L | 80.4999 | 2024-05-17 | L2 | 0.39 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.65 | UG/L | 60.4999 | 2024-08-15 | L3 | 0.89 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 57.18 | UG/L | 80.4999 | 2024-08-15 | L3 | 0.39 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.21 | UG/L | 60.4999 | 2024-08-15 | L4 | 0.89 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 64.5 | UG/L | 80.4999 | 2024-08-15 | L4 | 0.39 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.13 | UG/L | 60.4999 | 2024-08-15 | L1 | 0.89 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 40.33 | UG/L | 80.4999 | 2024-08-15 | L1 | 0.39 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.69 | UG/L | 60.4999 | 2024-08-15 | L2 | 0.89 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 53.06 | UG/L | 80.4999 | 2024-08-15 | L2 | 0.39 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-16 | WTP1 |  |  | WP1 POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-16 | WTP1 |  |  | WP1 POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2024-10-16 | WTP2 |  |  | WP2 POE
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-10-16 | WTP2 |  |  | WP2 POE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 18.99 | UG/L | 60.4999 | 2024-11-15 | L3 | 0.89 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 44.83 | UG/L | 80.4999 | 2024-11-15 | L3 | 0.44 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.24 | UG/L | 60.4999 | 2024-11-15 | L4 | 0.89 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 55.53 | UG/L | 80.4999 | 2024-11-15 | L4 | 0.44 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 17.87 | UG/L | 60.4999 | 2024-11-15 | L1 | 0.89 |  | 235 W CHURCH AVE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 35.12 | UG/L | 80.4999 | 2024-11-15 | L1 | 0.44 |  | 235 W CHURCH AVE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.32 | UG/L | 60.4999 | 2024-11-15 | L2 | 0.89 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 44.25 | UG/L | 80.4999 | 2024-11-15 | L2 | 0.44 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 56.44 | UG/L | 80.4999 | 2025-02-19 | L3 | 0.44 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.71 | UG/L | 60.4999 | 2025-02-19 | L4 | 0.98 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 65.84 | UG/L | 80.4999 | 2025-02-19 | L4 | 0.44 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.76 | UG/L | 60.4999 | 2025-02-19 | L1 | 0.98 |  | 235 W CHURCH AVE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 41.9 | UG/L | 80.4999 | 2025-02-19 | L1 | 0.44 |  | 235 W CHURCH AVE
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.51 | UG/L | 60.4999 | 2025-02-19 | L2 | 0.98 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 48.23 | UG/L | 80.4999 | 2025-02-19 | L2 | 0.44 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 16.91 | UG/L | 60.4999 | 2025-05-20 | L1 | 0.98 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.72 | UG/L | 60.4999 | 2025-02-19 | L3 | 0.98 |  | RAVEN AVE LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.72 | UG/L | 60.4999 | 2025-05-20 | L3 | 0.98 |  | RAVEN AV LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 62.81 | UG/L | 80.4999 | 2025-05-20 | L3 | 0.44 |  | RAVEN AV LS
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.93 | UG/L | 60.4999 | 2025-05-20 | L4 | 0.98 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.55 | UG/L | 80.4999 | 2025-05-20 | L4 | 0.44 |  | 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.56 | UG/L | 80.4999 | 2025-05-20 | L1 | 0.44 |  | 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 20.92 | UG/L | 60.4999 | 2025-05-20 | L2 | 0.98 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 54.94 | UG/L | 80.4999 | 2025-05-20 | L2 | 0.44 |  | 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.89 | UG/L | 60.4999 | 2025-08-19 | L3 | 0.98 |  | RAVEN AVE - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 70.19 | UG/L | 80.4999 | 2025-08-19 | L3 | 0.44 |  | RAVEN AVE - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.08 | UG/L | 60.4999 | 2025-08-19 | L4 | 0.98 |  | NORTH ST - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 77.63 | UG/L | 80.4999 | 2025-08-19 | L4 | 0.44 |  | NORTH ST - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.16 | UG/L | 60.4999 | 2025-08-19 | L1 | 0.98 |  | CHURCH AVE - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 43.14 | UG/L | 80.4999 | 2025-08-19 | L1 | 0.44 |  | CHURCH AVE - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.58 | UG/L | 60.4999 | 2025-08-19 | L2 | 0.98 |  | N HWY 17-92 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 66.94 | UG/L | 80.4999 | 2025-08-19 | L2 | 0.44 |  | N HWY 17-92 - TTHM SUBCONTRACTED TO E82535; HAA5 SUBCONTRACTED TO E84589
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.063 | MG/L | 10.4999 | 2025-10-24 | WTP1 | 0.024 |  | POE- WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-24 | WTP1 |  |  | POE- WTP 1
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1040 | NITRATE | 0.068 | MG/L | 10.4999 | 2025-10-24 | WTP2 | 0.024 |  | POE - WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-10-24 | WTP2 |  |  | POE - WTP 2
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 70.16 | UG/L | 80.4999 | 2025-11-19 | L4 | 0.44 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.82 | UG/L | 60.4999 | 2025-11-19 | L3 | 0.98 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 64.07 | UG/L | 80.4999 | 2025-11-19 | L3 | 0.44 |  | ST1-1 801 RAVEN AVE.=LIFT STATION
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.99 | UG/L | 60.4999 | 2025-11-19 | L4 | 0.98 |  | ST1-2 900 NORTH ST
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.99 | UG/L | 60.4999 | 2025-11-19 | L1 | 0.98 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 52.25 | UG/L | 80.4999 | 2025-11-19 | L1 | 0.44 |  | SM-2 235 W CHURCH AVE.
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 27.74 | UG/L | 60.4999 | 2025-11-19 | L2 | 0.98 |  | SM-4 1057 N HWY 17-92
3590202 | LONGWOOD, CITY OF (2 WPS) | D | DBP | 2950 | TOTAL THMS | 70.58 | UG/L | 80.4999 | 2025-11-19 | L2 | 0.44 |  | SM-4 1057 N HWY 17-92
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-04-03 | WTP2 | 0.25 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-04-03 | WTP2 | 0.26 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-04-03 | WTP2 | 0.14 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-03 | WTP2 | 0.27 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-04-03 | WTP2 | 0.42 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-03 | WTP2 | 0.36 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-04-03 | WTP2 | 0.26 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-04-03 | WTP2 | 0.33 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-04-03 | WTP2 | 0.33 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-04-03 | WTP2 | 0.31 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-04-03 | WTP2 | 0.25 | 0.5499 | NORTH WELL POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-04-10 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1924 | pH (FIELD) | 8.02 | LN(10) |  | 2025-04-10 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-04-10 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2025-04-10 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.13 | LN(10) |  | 2025-04-10 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-04-10 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2025-04-10 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-04-10 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2025-04-10 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-04-16 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2025-04-16 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2025-04-16 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2025-04-16 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.14 | LN(10) |  | 2025-04-16 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-04-16 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2025-04-16 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2025-04-16 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2025-04-16 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-04-23 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.01 | LN(10) |  | 2025-04-23 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-04-23 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.68 | MG/L |  | 2025-04-23 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.09 | LN(10) |  | 2025-04-23 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 115 | MG/L |  | 2025-04-23 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2025-04-23 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.9 | LN(10) |  | 2025-04-23 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2025-04-23 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2025-04-30 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2025-04-30 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2025-04-30 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2025-04-30 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.08 | LN(10) |  | 2025-04-30 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 117 | MG/L |  | 2025-04-30 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2025-04-30 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2025-04-30 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-04-30 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 28.21 | UG/L | 60.4999 | 2025-05-01 | L5 | 0.98 |  | CWP2STG1 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.85 | UG/L | 80.4999 | 2025-05-01 | L5 | 0.44 |  | CWP2STG1 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 24.37 | UG/L | 60.4999 | 2025-05-01 | L4 | 0.98 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 39.45 | UG/L | 80.4999 | 2025-05-01 | L4 | 0.44 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.73 | UG/L | 60.4999 | 2025-05-01 | L6 | 0.98 |  | CWP4 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 33.9 | UG/L | 80.4999 | 2025-05-01 | L6 | 0.44 |  | CWP4 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 21.72 | UG/L | 60.4999 | 2025-05-01 | L7 | 0.98 |  | CWP5 170 LYMAN ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 51.86 | UG/L | 80.4999 | 2025-05-01 | L7 | 0.44 |  | CWP5 170 LYMAN ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1040 | NITRATE | 0.064 | MG/L | 10.4999 | 2025-05-01 | WTP1 | 0.024 |  | HOWELL PARK POE - NN
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-05-01 | WTP1 | 0.0034 |  | HOWELL PARK POE - NN
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2025-05-07 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2025-05-07 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-05-07 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.63 | MG/L |  | 2025-05-07 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2025-05-07 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2025-05-07 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.57 | MG/L |  | 2025-05-07 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.87 | LN(10) |  | 2025-05-07 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2025-05-07 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-05-14 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2025-05-14 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2025-05-14 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-05-14 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.07 | LN(10) |  | 2025-05-14 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 121 | MG/L |  | 2025-05-14 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2025-05-14 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2025-05-14 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-05-14 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.61 | MG/L |  | 2025-05-21 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2025-05-21 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 119 | MG/L |  | 2025-05-21 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.65 | MG/L |  | 2025-05-21 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.11 | LN(10) |  | 2025-05-21 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 116 | MG/L |  | 2025-05-21 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1044 | ORTHOPHOSPHATE | 0.59 | MG/L |  | 2025-05-21 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2025-05-21 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | WQP | 1927 | TOTAL ALKALINITY | 120 | MG/L |  | 2025-05-21 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2025-05-28 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2025-05-28 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 113 | MG/L |  | 2025-05-28 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.59 | MG/L |  | 2025-05-28 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.07 | LN(10) |  | 2025-05-28 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 107 | MG/L |  | 2025-05-28 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2025-05-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.84 | LN(10) |  | 2025-05-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 110 | MG/L |  | 2025-05-28 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.64 | MG/L |  | 2025-06-04 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2025-06-04 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-06-04 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.59 | MG/L |  | 2025-06-04 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.08 | LN(10) |  | 2025-06-04 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2025-06-04 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.67 | MG/L |  | 2025-06-04 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.91 | LN(10) |  | 2025-06-04 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2025-06-04 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.6 | MG/L |  | 2025-06-11 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2025-06-11 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 102 | MG/L |  | 2025-06-11 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.56 | MG/L |  | 2025-06-11 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.1 | LN(10) |  | 2025-06-11 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 118 | MG/L |  | 2025-06-11 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2025-06-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2025-06-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2025-06-11 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.59 | MG/L |  | 2025-06-18 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.99 | LN(10) |  | 2025-06-18 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 108 | MG/L |  | 2025-06-18 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.57 | MG/L |  | 2025-06-18 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.12 | LN(10) |  | 2025-06-18 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 114 | MG/L |  | 2025-06-18 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.69 | MG/L |  | 2025-06-18 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.92 | LN(10) |  | 2025-06-18 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 105 | MG/L |  | 2025-06-18 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.66 | MG/L |  | 2025-06-25 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.98 | LN(10) |  | 2025-06-25 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 109 | MG/L |  | 2025-06-25 | WTP1 |  |  | HOWELL PARK WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.62 | MG/L |  | 2025-06-25 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 8.09 | LN(10) |  | 2025-06-25 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 112 | MG/L |  | 2025-06-25 | WTP2 |  |  | NORTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1044 | ORTHOPHOSPHATE | 0.58 | MG/L |  | 2025-06-25 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1924 | pH (FIELD) | 7.89 | LN(10) |  | 2025-06-25 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | WQP | 1927 | TOTAL ALKALINITY | 111 | MG/L |  | 2025-06-25 | WTP3 |  |  | SOUTH WP
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 38.77 | UG/L | 80.4999 | 2025-08-04 | L4 | 0.44 |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 26.56 | UG/L | 60.4999 | 2025-08-04 | L5 | 0.98 |  | 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 56.41 | UG/L | 80.4999 | 2025-08-04 | L5 | 0.44 |  | 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.41 | UG/L | 60.4999 | 2025-08-04 | L4 | 0.98 |  | 5401 LAKE HOWELL RD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.66 | UG/L | 60.4999 | 2025-08-04 | L6 | 0.98 |  | 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 27.16 | UG/L | 80.4999 | 2025-08-04 | L6 | 0.44 |  | 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.43 | UG/L | 60.4999 | 2025-08-04 | L7 | 0.98 |  | 170 LYMAN ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 52.76 | UG/L | 80.4999 | 2025-08-04 | L7 | 0.44 |  | 170 LYMAN ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-09-04 | WTP2 | 0 | 1.4999 | NORTH WP NORTH PLANT POE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 46.45 | UG/L | 60.4999 | 2025-11-04 | L5 | 0.98 |  | CWP2STG1 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 55.46 | UG/L | 80.4999 | 2025-11-04 | L5 | 0.44 |  | CWP2STG1 7601 CITRUS AVE
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 15.35 | UG/L | 60.4999 | 2025-11-04 | L4 | 0.98 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 38.28 | UG/L | 80.4999 | 2025-11-04 | L4 | 0.44 |  | CWP6 5401 LAKE HOWELL RD. (NOT DR.),W.P.
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 13.91 | UG/L | 60.4999 | 2025-11-04 | L6 | 0.98 |  | CWP4 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 34.54 | UG/L | 80.4999 | 2025-11-04 | L6 | 0.44 |  | CWP4 700 SR 436
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 29.48 | UG/L | 60.4999 | 2025-11-04 | L7 | 0.98 |  | CWP5 170 LYMAN ROAD
3590159 | CASSELBERRY, CITY OF (3 WPS) | D | DBP | 2950 | TOTAL THMS | 70.69 | UG/L | 80.4999 | 2025-11-04 | L7 | 0.44 |  | CWP5 170 LYMAN ROAD
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-08-03 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-08-03 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-08-03 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-08-03 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-08-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-08-03 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-08-03 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-08-03 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-08-03 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-08-03 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-08-03 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-08-03 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-08-03 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-08-03 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-08-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-08-03 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-08-03 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-08-03 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-08-03 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-08-03 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.6 | UG/L | 60.4999 | 2022-08-10 | L4 | 0.9 |  | LKM-28 419 PALM CREST LANE TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 27.5 | UG/L | 80.4999 | 2022-08-10 | L4 | 0.47 |  | LKM-28 419 PALM CREST LANE TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.3 | UG/L | 60.4999 | 2022-08-10 | L1 | 0.9 |  | LKM-33 3580 N. HWY 17-19 TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 17.1 | UG/L | 80.4999 | 2022-08-10 | L1 | 0.47 |  | LKM-33 3580 N. HWY 17-19 TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.6 | UG/L | 60.4999 | 2022-08-10 | L3 | 0.9 |  | LKM-32 455 N. COUNTRY CLUB TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 25.5 | UG/L | 80.4999 | 2022-08-10 | L3 | 0.47 |  | LKM-32 455 N. COUNTRY CLUB TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.5 | UG/L | 60.4999 | 2022-08-10 | L2 | 0.9 |  | LKM-51 930 WILLISTON PARK POINT TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 23.1 | UG/L | 80.4999 | 2022-08-10 | L2 | 0.47 |  | LKM-51 930 WILLISTON PARK POINT TTHM HAA5 | 3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-09-07 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-09-07 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-09-07 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-09-07 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-09-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-09-07 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-09-07 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-09-07 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-09-07 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-09-07 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-09-07 | AAA | 0.17 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-09-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-09-07 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-09-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-09-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-09-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-09-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-09-07 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-09-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-09-07 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-09-07 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-10-05 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-10-05 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-10-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-10-05 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-10-05 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-10-05 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-10-05 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-10-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-10-05 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-10-05 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-10-05 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-10-05 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-11-02 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-11-02 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-11-02 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-11-02 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-11-02 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-11-02 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-11-02 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-11-02 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-11-02 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-11-02 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-11-02 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-11-02 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-11-02 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-11-02 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-11-02 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-11-02 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-11-02 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-11-02 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 7.4 | UG/L | 60.4999 | 2022-11-08 | L4 |  |  | LKM-28 419 PALM CREST LN HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 28.8 | UG/L | 80.4999 | 2022-11-08 | L4 |  |  | LKM-28 419 PALM CREST LN HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 5.1 | UG/L | 60.4999 | 2022-11-08 | L1 |  |  | LKM-33 3580 N HWY 17 HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 19.5 | UG/L | 80.4999 | 2022-11-08 | L1 |  |  | LKM-33 3580 N HWY 17 HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.3 | UG/L | 60.4999 | 2022-11-08 | L3 |  |  | LKM-32 455 N COUNTRY CLUB RD HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 24.3 | UG/L | 80.4999 | 2022-11-08 | L3 |  |  | LKM-32 455 N COUNTRY CLUB RD HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 6.6 | UG/L | 60.4999 | 2022-11-08 | L2 |  |  | LKM-51 930 WILLISTON PARK POINT HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | D | DBP | 2950 | TOTAL THMS | 26.4 | UG/L | 80.4999 | 2022-11-08 | L2 |  |  | LKM-51 930 WILLISTON PARK POINT HAA5 TTHM | 3
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-12-07 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-12-07 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2022-12-07 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-12-07 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-12-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-12-07 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-12-07 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-12-07 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-12-07 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-12-07 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-12-07 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-12-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-12-07 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-12-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-12-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-12-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-12-07 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-12-07 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-12-07 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2022-12-07 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-12-07 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-01-04 | AAA |  | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-02-08 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-02-08 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-02-08 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-02-08 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-02-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-02-08 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-02-08 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-02-08 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-02-08 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-02-08 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-02-08 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-02-08 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-02-08 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-02-08 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-02-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-02-08 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-02-08 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-02-08 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-02-08 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-02-08 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THESE POE RESULTS NEED TO BE ENTERED, SEE FULL LAB REPORT IN OCULUS)
3590201 | LAKE MARY, CITY OF | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-03-01 | AAA | 0.35 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-03-01 | AAA | 0.33 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-03-01 | AAA | 0.11 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2023-03-01 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2023-03-01 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2023-03-01 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2023-03-01 | AAA | 0.12 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2023-03-01 | AAA | 0.29 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2023-03-01 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2023-03-01 | AAA | 0.3 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2023-03-01 | AAA | 0.27 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2023-03-01 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2023-03-01 | AAA | 0.44 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-01 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2023-03-01 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2023-03-01 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1040 | NITRATE | 0.018 | MG/L | 10.4999 | 2021-01-19 | AAA
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2021-01-19 | AAA
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-02-09 | AAA |  | 1.4999
3590443 | GENEVA ELEMENTARY SCHOOL | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 22.74 | UG/L | 60.4999 | 2021-02-09 | L2 |  |  | REQUIRED ANNUAL SAMPLING IN AUG. ESI INDICATES "OPERATOR GOT A LITTLE CONFUSED AND TOOK DBPS" (ATR) | 3
3590443 | GENEVA ELEMENTARY SCHOOL | S | DBP | 2950 | TOTAL THMS | 33.97 | UG/L | 80.4999 | 2021-02-09 | L2 | 0.39 |  | REQUIRED ANNUAL SAMPLING IN AUG. ESI INDICATES "OPERATOR GOT A LITTLE CONFUSED AND TOOK DBPS" (ATR) | 3
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2021-04-22 | AAA |  | 1.4999
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 1.1 | UG/L | 249.9999 | 2021-07-22 | AAA |  | 1.4999
3590443 | GENEVA ELEMENTARY SCHOOL | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 25.09 | UG/L | 60.4999 | 2021-08-04 | L2 |  |  |  | 3
3590443 | GENEVA ELEMENTARY SCHOOL | D | DBP | 2950 | TOTAL THMS | 31.49 | UG/L | 80.4999 | 2021-08-04 | L2 |  |  |  | 3
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-01-20 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-01-20 | AAA |  |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0.56 | UG/L | 249.9999 | 2022-04-14 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-04-14 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-04-14 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2022-04-14 | AAA |  | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-04-14 | AAA |  | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-04-14 | AAA |  | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1040 | NITRATE | 0 | MG/L | 10.4999 | 2022-06-09 | AAA | 0.025
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2022-06-09 | AAA | 0.025
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2022-06-09 | AAA | 0.0005
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2022-06-09 | AAA | 0.0062
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2022-06-09 | AAA | 0.00067
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2022-06-09 | AAA | 0.0026
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2022-06-09 | AAA | 0.005
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1025 | FLUORIDE | 0.064 | MG/L | 4.0499 | 2022-06-09 | AAA | 0.015
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2022-06-09 | AAA | 0.00022
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2022-06-09 | AAA | 9e-05
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2022-06-09 | AAA | 0.002
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2022-06-09 | AAA | 0.00083
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1052 | SODIUM | 17.1 | MG/L | 160.4999 | 2022-06-09 | AAA | 0.59
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2022-06-09 | AAA | 0.00083
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2022-06-09 | AAA | 0.00058
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2022-06-09 | AAA | 0.00021
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2022-06-09 | AAA | 0.44 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2022-06-09 | AAA | 0.35 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2022-06-09 | AAA | 0.33 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 7.1 | UG/L | 10499.9999 | 2022-06-09 | AAA | 0.11 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2022-06-09 | AAA | 0.26 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2022-06-09 | AAA | 0.3 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2022-06-09 | AAA | 0.12 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2022-06-09 | AAA | 0.29 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2022-06-09 | AAA | 0.27 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2022-06-09 | AAA | 0.3 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2022-06-09 | AAA | 0.27 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2022-06-09 | AAA | 0.28 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2022-06-09 | AAA | 0.44 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-06-09 | AAA | 0.26 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2022-06-09 | AAA | 0.28 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2022-06-09 | AAA | 0.26 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2022-06-09 | AAA | 0.26 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2022-06-09 | AAA | 0.4 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2022-06-09 | AAA | 0.28 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 2.1 | UG/L | 749.9999 | 2022-06-09 | AAA | 0.23 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2022-06-09 | AAA | 0.2 | 0.5499 | VOC (XYLENES 7.1 & ETH 2.1, ABOVE RDL OF 0.5)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2022-06-09 | AAA | 0.0023 | 0.0149 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2022-06-09 | AAA | 0.0027 | 0.0249 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2022-06-09 | AAA | 0.023 | 0.1499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2022-06-09 | AAA | 0.67 | 1.4999 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 1.1 | UG/L | 249.9999 | 2022-06-09 | AAA | 0.49 | 1.4999 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2022-06-09 | AAA | 0.16 | 0.4499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2022-06-09 | AAA | 0.36 | 0.6499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2022-06-09 | AAA | 0.46 | 2.4999 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2022-06-09 | AAA | 0.039 | 0.0749 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2022-06-09 | AAA | 0.46 | 0.6499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2022-06-09 | AAA | 0.04 | 0.1499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2022-06-09 | AAA | 0.16 | 0.2499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2022-06-09 | AAA | 0.024 | 0.1499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2022-06-09 | AAA | 0.59 | 0.9499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2022-06-09 | AAA | 0.014 | 0.1499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2022-06-09 | AAA | 0.029 | 0.2499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2022-06-09 | AAA | 0.013 | 0.0449 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2022-06-09 | AAA | 0.003 | 0.0249 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0.31 | UG/L | 74.9999 | 2022-06-09 | AAA | 0.096 | 0.1499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2022-06-09 | AAA | 0.053 | 0.2499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2022-06-09 | AAA | 0.014 | 0.1499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2022-06-09 | AAA | 0.019 | 0.0249 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2022-06-09 | AAA | 0.014 | 0.0449 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2022-06-09 | AAA | 0.044 | 0.1499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2022-06-09 | AAA | 0.0065 | 0.0249 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2022-06-09 | AAA | 0.0076 | 0.0149 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2022-07-14 | AAA |  | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 31.52 | UG/L | 60.4999 | 2022-08-09 | L2 | 0.98 |  | BLDG 5 ROOM 509 (HLKD) | 3
3590443 | GENEVA ELEMENTARY SCHOOL | D | DBP | 2950 | TOTAL THMS | 76.9 | UG/L | 80.4999 | 2022-08-09 | L2 | 0.39 |  | BLDG 5 ROOM 509 (HLKD) | 3
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2022-09-07 | AAA | 4.2 | 6.4999
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-01-03 | AAA |  | 1.4999 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-01-03 | AAA |  | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-05-08 | AAA | 0.48 | 0.5499 | 5-8-23 XY+ETH (HLKD)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-05-08 | AAA | 0.33 | 0.5499 | 5-8-23 XY+ETH (HLKD)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2023-05-16 | AAA | 0.48 | 0.5499 | 5-16-23 XY+ ETH (HLKD)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-05-16 | AAA | 0.33 | 0.5499 | 5-16-23 XY+ ETH (HLKD)
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 8.7 | UG/L | 10499.9999 | 2023-07-25 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 1.8 | UG/L | 749.9999 | 2023-07-25 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008 POE
3590443 | GENEVA ELEMENTARY SCHOOL | D | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 23.14 | UG/L | 60.4999 | 2023-08-02 | L2 | 0.98 |  | BLDG 5 ROOM 509 | 3
3590443 | GENEVA ELEMENTARY SCHOOL | D | DBP | 2950 | TOTAL THMS | 34.62 | UG/L | 80.4999 | 2023-08-02 | L2 | 0.39 |  | BLDG 5 ROOM 509 | 3
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2023-10-02 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2023-10-02 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-10-02 | AAA |  | 1.4999 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-10-02 | AAA |  | 0.1499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-01-09 | AAA |  | 1.4999 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-01-09 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-01-09 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-01-09 | AAA |  | 0.1499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-04-02 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-04-02 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-04-04 | AAA |  | 0.1499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | S | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2024-12-12 | AAA | 0.9 | 1.4999 | DATE CORRECTED. TAKEN 4TH Q
3590443 | GENEVA ELEMENTARY SCHOOL | S | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2024-12-12 | AAA | 0.095 | 0.1499 | DATE CORRECTED. TAKEN 4TH Q
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1040 | NITRATE | 0.088 | MG/L | 10.4999 | 2024-12-31 | AAA | 0.024 |  | 2024 INORGANICS
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2024-12-31 | AAA | 0.0034 |  | 2024 INORGANICS
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2024-12-31 | AAA | 0.48 | 0.5499 | Q4 2024 2955 & 2992
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2024-12-31 | AAA | 0.45 | 0.5499 | Q4 2024 2955 & 2992
3590443 | GENEVA ELEMENTARY SCHOOL | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 0 | UG/L | 60.4999 | 2024-12-31 | L2 | 0.98 |  | LATE. DUE 3RD Q 2024. SAMPLED 4TH Q | 3
3590443 | GENEVA ELEMENTARY SCHOOL | S | DBP | 2950 | TOTAL THMS | 0 | UG/L | 80.4999 | 2024-12-31 | L2 | 0.44 |  | LATE. DUE 3RD Q 2024. SAMPLED 4TH Q | 3
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-04-04 | AAA |  | 0.5499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-05-01 | AAA |  | 0.1499 | POE
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1040 | NITRATE | 0.068 | MG/L | 10.4999 | 2025-09-19 | AAA | 0.024 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2025-09-19 | AAA | 0.0034 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1005 | ARSENIC | 0.0004 | MG/L | 0.0104 | 2025-09-19 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1010 | BARIUM | 0.02 | MG/L | 2.4999 | 2025-09-19 | AAA | 0.003 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2025-09-19 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2025-09-19 | AAA | 0.005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1024 | CYANIDE | 0.011 | MG/L | 0.2499 | 2025-09-19 | AAA | 0.0002 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1025 | FLUORIDE | 0 | MG/L | 4.0499 | 2025-09-19 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1030 | LEAD | 0 | MG/L | 0.0154 | 2025-09-19 | AAA | 0.0005 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1035 | MERCURY | 0 | MG/L | 0.0024 | 2025-09-19 | AAA | 3e-05 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1036 | NICKEL | 0 | MG/L | 0.1499 | 2025-09-19 | AAA | 0.008 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1045 | SELENIUM | 0 | MG/L | 0.0549 | 2025-09-19 | AAA | 0.0012 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1052 | SODIUM | 17 | MG/L | 160.4999 | 2025-09-19 | AAA | 0.8 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1074 | ANTIMONY | 0 | MG/L | 0.0065 | 2025-09-19 | AAA | 0.001 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1075 | BERYLLIUM | 0 | MG/L | 0.0045 | 2025-09-19 | AAA | 0.002 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1085 | THALLIUM | 0 | MG/L | 0.0025 | 2025-09-19 | AAA | 0.00025 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SEC | 1002 | ALUMINUM | 0 | MG/L | 0.2499 | 2025-09-19 | AAA | 0.0099 |  | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2378 | 1,2,4-TRICHLOROBENZENE | 0 | UG/L | 74.9999 | 2025-09-19 | AAA | 0.5 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2380 | CIS-1,2-DICHLOROETHYLENE | 0 | UG/L | 74.9999 | 2025-09-19 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2955 | TOT XYLENE | 0 | UG/L | 10499.9999 | 2025-09-19 | AAA | 0.48 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2964 | DICHLOROMETHANE | 0 | UG/L | 5.4999 | 2025-09-19 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2968 | 1,2-DICHLOROBENZENE | 0 | UG/L | 649.9999 | 2025-09-19 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2969 | P-DICHLOROBENZENE | 0 | UG/L | 75.4999 | 2025-09-19 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2976 | VINYL CHLORIDE | 0 | UG/L | 1.4999 | 2025-09-19 | AAA | 0.28 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2977 | 1,1-DICHLOROETHENE | 0 | UG/L | 7.4999 | 2025-09-19 | AAA | 0.4 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2979 | TRANS-1,2-DICHLOROETHENE | 0 | UG/L | 149.9999 | 2025-09-19 | AAA | 0.41 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2980 | 1,2-DICHLOROETHANE | 0 | UG/L | 3.4999 | 2025-09-19 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2981 | 1,1,1-TRICHLOROETHANE | 0 | UG/L | 249.9999 | 2025-09-19 | AAA | 0.32 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2982 | CARBON TETRACHLORIDE | 0 | UG/L | 3.4999 | 2025-09-19 | AAA | 0.36 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2983 | 1,2-DICHLOROPROPANE | 0 | UG/L | 5.4999 | 2025-09-19 | AAA | 0.33 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2984 | TRICHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-09-19 | AAA | 0.25 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2985 | 1,1,2-TRICHLOROETHANE | 0 | UG/L | 5.4999 | 2025-09-19 | AAA | 0.44 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2987 | TETRACHLOROETHYLENE | 0 | UG/L | 3.4999 | 2025-09-19 | AAA | 0.49 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2025-09-19 | AAA | 0.37 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2025-09-19 | AAA | 0.42 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2025-09-19 | AAA | 0.46 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2025-09-19 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2025-09-19 | AAA | 0.45 | 0.5499 | LOCATION CODE SET BY PWS - 03/10/2008
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2005 | ENDRIN | 0 | UG/L | 2.4999 | 2025-09-19 | AAA | 0.0069 | 0.0149 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2010 | LINDANE | 0 | UG/L | 0.2499 | 2025-09-19 | AAA | 0.0071 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2015 | METHOXYCLOR | 0 | UG/L | 44.9999 | 2025-09-19 | AAA | 0.0068 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2020 | TOXAPHENE | 0 | UG/L | 3.4999 | 2025-09-19 | AAA | 0.12 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2025-09-19 | AAA | 0.9 | 1.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2032 | DIQUAT | 0 | UG/L | 24.9999 | 2025-09-19 | AAA | 0.31 | 0.4499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2033 | ENDOTHALL | 0 | UG/L | 149.9999 | 2025-09-19 | AAA | 6 | 9.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2034 | GLYPHOSATE | 0 | UG/L | 749.9999 | 2025-09-19 | AAA | 5.9 | 6.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2035 | DI(2-ETHYLHEXYL)ADIPATE | 0 | UG/L | 449.9999 | 2025-09-19 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2036 | OXAMYL (VYDATE) | 0 | UG/L | 249.9999 | 2025-09-19 | AAA | 1.8 | 2.4999 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2037 | SIMAZINE | 0 | UG/L | 4.4999 | 2025-09-19 | AAA | 0.06 | 0.0749 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2039 | DI(2-ETHYLHEXYL)PHTHALATE | 0 | UG/L | 6.4999 | 2025-09-19 | AAA | 0.5 | 0.6499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2040 | PICLORAM | 0 | UG/L | 549.9999 | 2025-09-19 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2041 | DINOSEB | 0 | UG/L | 7.4999 | 2025-09-19 | AAA | 0.18 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2042 | HEXACHLOROCYCLOPENTADIENE | 0 | UG/L | 54.9999 | 2025-09-19 | AAA | 0.019 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2046 | CARBOFURAN | 0 | UG/L | 44.9999 | 2025-09-19 | AAA | 0.67 | 0.9499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2050 | ATRAZINE | 0 | UG/L | 3.4999 | 2025-09-19 | AAA | 0.09 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2051 | ALACHLOR (LASSO) | 0 | UG/L | 2.4999 | 2025-09-19 | AAA | 0.15 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2065 | HEPTACHLOR | 0 | UG/L | 0.4499 | 2025-09-19 | AAA | 0.006 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2067 | HEPTACHLOR EPOXIDE | 0 | UG/L | 0.2499 | 2025-09-19 | AAA | 0.0052 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2025-09-19 | AAA | 0.095 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2110 | 2,4,5-TP (Silvex) | 0 | UG/L | 54.9999 | 2025-09-19 | AAA | 0.09 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2274 | HEXACHLOROBENZENE | 0 | UG/L | 1.4999 | 2025-09-19 | AAA | 0.0063 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2306 | BENZO(A)PYRENE | 0 | UG/L | 0.2499 | 2025-09-19 | AAA | 0.015 | 0.0249 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2326 | PENTACHLOROPHENOL | 0 | UG/L | 1.4999 | 2025-09-19 | AAA | 0.038 | 0.0449 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2383 | POLYCHLORINATED BIPHENYL (PCB) | 0 | UG/L | 0.5499 | 2025-09-19 | AAA | 0.093 | 0.1499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2025-09-19 | AAA | 0.053 | 0.2499 | LOCATION CODE SET BY PWS - 03/10/2008- 2931, 2946 Q QUALIFIERS
3590443 | GENEVA ELEMENTARY SCHOOL | S | DBP | 2456 | TOTAL HALOACETIC ACIDS (HAA5) | 19.75 | UG/L | 60.4999 | 2025-09-30 | L2 | 0.98 |  | JULY SAMPLE FOR COMPLIANCE J QUALIFIED--RESAMPLED SEPT MOVED TO QUARTERLY | 3
3590443 | GENEVA ELEMENTARY SCHOOL | S | DBP | 2950 | TOTAL THMS | 31.26 | UG/L | 80.4999 | 2025-09-30 | L2 | 0.44 |  | JULY SAMPLE FOR COMPLIANCE J QUALIFIED--RESAMPLED SEPT MOVED TO QUARTERLY | 3
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2931 | DIBROMOCHLOROPROPANE | 0 | UG/L | 0.2499 | 2025-11-03 | AAA |  | 0.0249 | POE - GEN ELEM
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2946 | ETHYLENE DIBROMIDE | 0 | UG/L | 0.0249 | 2025-11-03 | AAA |  | 0.0149 | POE - GEN ELEM
3590201 | LAKE MARY, CITY OF | N | VOC | 2989 | CHLOROBENZENE | 0 | UG/L | 149.9999 | 2023-03-01 | AAA | 0.26 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2990 | BENZENE | 0 | UG/L | 1.4999 | 2023-03-01 | AAA | 0.4 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2991 | TOLUENE | 0 | UG/L | 1499.9999 | 2023-03-01 | AAA | 0.28 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2992 | ETHYLBENZENE | 0 | UG/L | 749.9999 | 2023-03-01 | AAA | 0.23 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | VOC | 2996 | STYRENE | 0 | UG/L | 149.9999 | 2023-03-01 | AAA | 0.2 | 0.5499 | LKM 7 POE SPECIAL VOC MONITORING (ONLY THE POE RESULTS NEED TO BE ENTERED)
3590201 | LAKE MARY, CITY OF | N | INOR | 1040 | NITRATE | 0.16 | MG/L | 10.4999 | 2023-03-01 | AAA | 0.025
3590201 | LAKE MARY, CITY OF | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-03-01 | AAA | 0.025
3590201 | LAKE MARY, CITY OF | N | INOR | 1005 | ARSENIC | 0 | MG/L | 0.0104 | 2023-03-01 | AAA | 0.0005
3590201 | LAKE MARY, CITY OF | N | INOR | 1010 | BARIUM | 0.01 | MG/L | 2.4999 | 2023-03-01 | AAA | 0.0024
3590201 | LAKE MARY, CITY OF | N | INOR | 1015 | CADMIUM | 0 | MG/L | 0.0055 | 2023-03-01 | AAA | 0.00067
3590201 | LAKE MARY, CITY OF | N | INOR | 1020 | CHROMIUM | 0 | MG/L | 0.1499 | 2023-03-01 | AAA | 0.0026
3590201 | LAKE MARY, CITY OF | N | INOR | 1024 | CYANIDE | 0 | MG/L | 0.2499 | 2023-03-01 | AAA | 0.005
3590201 | LAKE MARY, CITY OF | N | INOR | 1025 | FLUORIDE | 0.59 | MG/L | 4.0499 | 2023-03-01 | AAA | 0.015
3590201 | LAKE MARY, CITY OF | N | INOR | 1052 | SODIUM | 10.3 | MG/L | 160.4999 | 2023-03-01 | AAA | 0.59
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2959 | CHLORDANE | 0 | UG/L | 2.4999 | 2022-06-09 | AAA | 0.035 | 0.2499 | 27 OF 29 TESTED (NO ENDO OR GLY. DAL 1.1) 2,4-D IS 0.31 WITH J QUALIFIER, > RDL OF 0.1, RESULT IS ENT'D FOR NOW, CAN DELETE IF UNACCEPTABLE (QC PAGES, PG 22 OF 39, MS/MSD 105/138% RECOVERY)
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1040 | NITRATE | 0.11 | MG/L | 10.4999 | 2023-01-03 | AAA
3590443 | GENEVA ELEMENTARY SCHOOL | N | INOR | 1041 | NITRITE | 0 | MG/L | 1.4999 | 2023-01-03 | AAA
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-04-04 | AAA | 0.095 | 0.1499
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-04-04 | AAA | 0.9 | 1.4999
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2031 | DALAPON | 0 | UG/L | 249.9999 | 2023-07-05 | AAA | 0.9 | 1.4999
3590443 | GENEVA ELEMENTARY SCHOOL | N | SOC | 2105 | 2,4-D | 0 | UG/L | 74.9999 | 2023-07-05 | AAA | 0.95 | 0.1499