## Sheet1
SORT | CATEGORY | VIOLATION CODE | ASSOCIATED RULES | QUESTION | SIGNIF | REEVALUATION | RULE CAT
1 | Underground | 6001 | 62-761.100(3) | No reasonable access provided. | Minor | Inspection | 62-761
2 | Underground | 6002 | 62-761.350(1), 62-761.350(1)(c), 62-761.350(1)(d), 62-761.350(3)(b)2, 62-761.350(5)(a), 62-761.350(5)(b), 62-761.350(5)(c), 62-761.350(7) | Operator Training records not available. | Minor | Review | 62-761
3 | Underground | 6003 | 62-761.400(1)(b), 62-761.400(2), 62-761.400(2)(a), 62-761.400(3), 62-761.400(3)(a), 62-761.400(3)(b), 62-761.400(3)(c) | Registration Form not submitted for a new system, change in service, closure, owner change, or discovery of unregistered facility. | Minor | Review | 62-761
4 | Underground | 6004 | 62-761.400(1)(c), 62-761.400(2)(b) | For Installation or Closure, Certified Contractors Form not submitted. | Minor | Review | 62-761
5 | Underground | 6005 | 62-761.400(4), 62-761.400(4)(a), 62-761.400(4)(b), 62-761.400(4)(c), 62-761.400(4)(d), 62-761.400(4)(e), 62-761.400(4)(f) | Registration fees not paid (not receiving fuel). | Minor | Review | 62-761
6 | Underground | 6006 | 62-761.400(5) | Placard not displayed (or available upon request). | Minor | Review | 62-761
7 | Underground | 6007 | 62-761.400(7), 62-761.400(7)(a), 62-761.400(7)(b) | Owner, operator, or supplier deposited motor fuel into storage tank without current valid registration placard. | SNC-A | NCLI | 62-761
8 | Underground | 6008 | 62-761.405(1), 62-761.405(1)(a), 62-761.405(1)(b), 62-761.405(1)(c), 62-761.405(2), 62-761.405(2)(a), 62-761.405(2)(b), 62-761.405(2)(c), 62-761.405(2)(d) | For installation, closure, or change in service status, notification not received in a timely manner. | Minor | NCLI | 62-761
9 | Underground | 6009 | 62-761.405(3) | Incident Notification Form (INF) not received in a timely manner. | Minor | NCLI | 62-761
10 | Underground | 6010 | 62-761.405(4) | Discharge Notification Form (DRF) not received in a timely manner. | SNC-B | NCLI | 62-761
11 | Underground | 6011 | 62-761.420(2) | No financial responsibility instrument or expired instrument for < 180 days. | SNC-B | Review | 62-761
12 | Underground | 6012 | 62-761.420(2) | No financial responsibility instrument or expired instrument for > 180 days. | SNC-A | Review | 62-761
13 | Underground | 6013 | 62-761.420(3), 62-761.420(4), 62-761.420(8) | Appropriate paperwork for financial responsibility improperly completed or maintained. | Minor | Review | 62-761
14 | Underground | 6014 | 62-761.430(2) | Incident investigation not initiated within 24-hours (or by next business day) to determine if discharge occurred. | SNC-B | NCLI | 62-761
15 | Underground | 6015 | 62-761.430(4), 62-761.430(5) | Incident investigation not completed within 14 days, and/or no DRF or written confirmation received at the end of the 14-day investigation period. | Minor | Review | 62-761
16 | Underground | 6016 | 62-761.430(6) | Removal of regulated substance from a release into secondary containment not initiated within three days and completed within 30 days of discovery. | SNC-B | Inspection | 62-761
17 | Underground | 6017 | 62-761.430(8) | All incident records, including test results not kept until storage tank system closure. | Minor | NCLI | 62-761
18 | Underground | 6018 | 62-761.440(2) | Discharge not reported within 24-hours, or by next business day. | SNC-B | NCLI | 62-761
19 | Underground | 6019 | 62-761.440(3) | Analyticals not submitted with 24 -hours or next business day. OVA readings are not considered confirmation of discharge. | Minor | Review | 62-761
20 | Underground | 6020 | 62-761.440(6), 62-761.440(6)(a), 62-761.440(6)(b), 62-761.440(6)(c), 62-761.440(6)(d), 62-761.440(6)(e), 62-761.440(6)(f), 62-761.440(6)(g) | Actions not taken immediately to contain, remove, and abate the discharge. | SNC-A | Inspection | 62-761
21 | Underground | 6021 | 62-761.500(1), 62-761.500(1)(b)1, 62-761.500(1)(b)1.a, 62-761.500(1)(b)1.b, 62-761.500(1)(b)1.c | Failure of secondary containment to meet standards including: impervious spill containment, liners, allowing for release detection, allow for monitoring point, and hydrant pit secondary containment. | SNC-B | Inspection | 62-761
22 | Underground | 6022 | 62-761.500(1)(b)2, 62-761.500(1)(c)1 | Cathodic protection test station/method and operation does not meet standards. Or, secondary containment interferes with the cathodic protection system. | SNC-B | Inspection | 62-761
23 | Underground | 6023 | 62-761.500(1)(b)3, 62-761.500(3)(e) | Secondary containment or integral piping not installed to allow for monitoring point. | Minor | Inspection | 62-761
24 | Underground | 6024 | 62-761.500(1)(b)4, 62-761.500(1)(b)5, 62-761.500(1)(b)6, 62-761.500(1)(b)7 | Integrity test not performed on storage tank, integral piping, single-walled spill containment system, double-walled spill containment system, or doubled-walled sump prior to placing into service. | Minor | Review | 62-761
25 | Underground | 6025 | 62-761.500(1)(c)3, 62-761.500(3)(i) | Field installed cathodic protection or corrosion protection system with vapor corrosion inhibitors not installed by or under direction of a Corrosion Professional. | Minor | Inspection | 62-761
26 | Underground | 6026 | 62-761.500(1)(c)4 | Corrosion protection not provided for former single-walled storage tank upgraded to secondary containment by installation of field-fabricated primary storage tank. | SNC-B | Inspection | 62-761
27 | Underground | 6027 | 62-761.500(1)(c)5 | Supplemental anodes are not installed in accordance with guidelines. | Minor | Inspection | 62-761
28 | Underground | 6028 | 62-761.500(1)(d) | The primary and secondary wall linings are not compatible with the regulated substance. | SNC-B | Review | 62-761
29 | Underground | 6029 | 62-761.500(1)(e) | Any component(s) of the storage tank system not installed according to manufacturer's instructions. | Minor | Inspection | 62-761
30 | Underground | 6030 | 62-761.500(1)(f), 62-761.500(1)(f)1, 62-761.500(1)(f)2, 62-761.500(1)(f)3, 62-761.500(1)(f)4, 62-761.500(1)(f)5 | Any component(s) of storage tank system not installed according to reference standards. | SNC-B | Inspection | 62-761
31 | Underground | 6031 | 62-761.500(1)(g), 62-761.500(1)(g)1, 62-761.500(1)(g)2 | Any component(s) of storage tank system not installed according to manufacturer's specification. | SNC-B | Inspection | 62-761
32 | Underground | 6032 | 62-761.500(1)(h) | Work not performed by a Certified Contractor. | SNC-B | Review | 62-761
33 | Underground | 6033 | 62-761.500(1)(i) | Survey of ground contact and underground components not conducted or maintained. | Minor | Review | 62-761
34 | Underground | 6034 | 62-761.500(2), 62-761.500(2)(a), 62-761.500(2)(b), 62-761.500(2)(c), 62-761.500(2)(c)1, 62-761.500(2)(c)2, 62-761.500(2)(c)3, 62-761.500(2)(c)4, 62-761.500(2)(d), 62-761.500(2)(e), 62-761.500(2)(f), 62-761.500(2)(g) | Storage tanks not installed according to manufacturer's instructions or reference standards. | SNC-B | Inspection | 62-761
35 | Underground | 6035 | 62-761.500(2)(h), 62-761.500(2)(h)1, 62-761.500(2)(h)2, 62-761.500(2)(h)3 | Underground tank relocation requirements not met, or reused tanks not properly recertified. | SNC-B | Inspection | 62-761
36 | Underground | 6036 | 62-761.500(3), 62-761.500(3)(a), 62-761.500(3)(b), 62-761.500(3)(c) | Integral piping not installed to standards or installed without secondary containment. | SNC-B | Inspection | 62-761
37 | Underground | 6037 | 62-761.500(3)(d), 62-761.500(3)(d)1, 62-761.500(3)(d)2, 62-761.500(3)(d)3, 62-761.500(3)(d)4, 62-761.500(3)(d)5 | Piping in contact with soil not installed to standards. | SNC-B | Inspection | 62-761
38 | Underground | 6038 | 62-761.500(3)(f) | Shear valve not installed properly. | SNC-B | Inspection | 62-761
39 | Underground | 6039 | 62-761.500(3)(g) | Small diameter piping with gravity head not properly installed or meeting standards. | Minor | Inspection | 62-761
40 | Underground | 6040 | 62-761.500(3)(h) | Pressurized integral piping connected to dispensers not installed with leak detection method. | SNC-B | Inspection | 62-761
41 | Underground | 6041 | 62-761.500(3)(j) | Piping not meeting the Bulk Product Piping Requirements | Minor | Review | 62-761
42 | Underground | 6042 | 62-761.500(4)(a) | Storage tank system not installed with a spill containment system at each tank fill connection. Does not meet performance requirements. | SNC-B | Inspection | 62-761
43 | Underground | 6043 | 62-761.500(4)(b) | Fillbox covers not marked according to requirements. | Minor | Inspection | 62-761
44 | Underground | 6044 | 62-761.500(4)(c) | Single-walled spill containment systems not installed to allow for release detection. | Minor | Inspection | 62-761
45 | Underground | 6045 | 62-761.500(4)(d) | Double-walled spill containment system does not allow for interstitial monitoring. | Minor | Inspection | 62-761
46 | Underground | 6046 | 62-761.500(5)(a) | Dispensers not installed and maintained according to standards. | Minor | Inspection | 62-761
47 | Underground | 6047 | 62-761.500(5)(b) | Dispensers not installed with a dispenser sump. | SNC-B | Inspection | 62-761
48 | Underground | 6048 | 62-761.500(5)(c) | Dispenser sumps not installed to allow for release detection. | SNC-B | Inspection | 62-761
49 | Underground | 6049 | 62-761.500(6)(a) | Piping sumps not meeting performance requirements. | SNC-B | Inspection | 62-761
50 | Underground | 6050 | 62-761.500(6)(b) | Piping sumps not installed to allow for release detection. | SNC-B | Inspection | 62-761
51 | Underground | 6051 | 62-761.500(7)(a) | Overfill prevention not provided or properly functioning. | SNC-B | Inspection | 62-761
52 | Underground | 6052 | 62-761.500(7)(b), 62-761.500(7)(b)1, 62-761.500(7)(b)2, 62-761.500(7)(b)3 | Overfill that shuts off/restricts flow or triggers alarm not provided. | SNC-B | Inspection | 62-761
53 | Underground | 6053 | 62-761.500(7)(c), 62-761.500(7)(c)1, 62-761.500(7)(c)2, 62-761.500(7)(d) | Primary overfill protection not provided, registered, or tested as required. | Minor | Review | 62-761
54 | Underground | 6054 | 62-761.500(7)(e) | Tanks filled without mated tight fill adaptor connection filled beyond 95 percent capacity. | SNC-B | Review | 62-761
55 | Underground | 6055 | 62-761.600(1), 62-761.600(1)(a), 62-761.600(1)(b), 62-761.600(1)(c), 62-761.600(1)(i) | Cannot detect a release from any portion of the system. (Including Emergency power generator storage tank systems installed prior to rule do not meet release detection requirements by October 13, 2018.) | SNC-A | Inspection | 62-761
56 | Underground | 6056 | 62-761.600(1)(d), 62-761.600(1)(e), 62-761.600(1)(g) | Release detection not tested or visually inspected once a month or problems found during the visual inspections not recorded. | SNC-B | Review | 62-761
57 | Underground | 6057 | 62-761.600(1)(f), 62-761.600(1)(f)1 | Release detection not installed, operated, and maintained per manufacturer's instructions and standards. | SNC-B | Inspection | 62-761
58 | Underground | 6058 | 62-761.600(1)(f)2 | Electronic and mechanical release detection devices not registered with the department. | Minor | Review | 62-761
59 | Underground | 6059 | 62-761.600(1)(h) | Release detection shall be constructed and installed so that groundwater, rainfall, or soil moisture will not render the release detection method used inoperable. | SNC-B | Inspection | 62-761
60 | Underground | 6060 | 62-761.600(2), 62-761.600(2)(a), 62-761.600(2)(a)1, 62-761.600(2)(a)2, 62-761.600(2)(a)3, 62-761.600(2)(a)4, 62-761.600(2)(a)5, 62-761.600(2)(a)6, 62-761.600(2)(a)6.a, 62-761.600(2)(a)6.b, 62-761.600(2)(a)7, 62-761.600(2)(a)8 | Release detection methods do not meet monitoring requirements. | SNC-B | Inspection | 62-761
61 | Underground | 6061 | 62-761.600(3), 62-761.600(3)(a), 62-761.600(3)(b), 62-761.600(3)(b)1, 62-761.600(3)(b)2, 62-761.600(3)(b)3 | Release detection devices for integral piping do not meet general standards. | SNC-B | Review | 62-761
62 | Underground | 6062 | 62-761.600(4) | Release detection devices not tested annually. | Minor | Review | 62-761
63 | Underground | 6063 | 62-761.700(1), 62-761.700(1)(a), 62-761.700(1)(a)1, 62-761.700(1)(a)2 | Not repaired or isolated component or piping which has not caused a discharge or release. | SNC-B | Inspection | 62-761
64 | Underground | 6064 | 62-761.700(1), 62-761.700(1)(a), 62-761.700(1)(a)1, 62-761.700(1)(a)2 | Not repaired or isolated component or piping which has cause a discharge or release. | SNC-A | Inspection | 62-761
65 | Underground | 6065 | 62-761.700(1)(b), 62-761.700(1)(b)1, 62-761.700(1)(b)2, 62-761.700(1)(b)3 | Damaged system not taken out of service or out of operation until repair is made. | SNC-B | Inspection | 62-761
66 | Underground | 6066 | 62-761.700(1)(c), 62-761.700(1)(c)1, 62-761.700(1)(c)2 | Not repaired per applicable standards. | Minor | Inspection | 62-761
67 | Underground | 6067 | 62-761.700(1)(d) | Integrity test not completed before being placed into operation or service. | Minor | Inspection | 62-761
68 | Underground | 6068 | 62-761.700(1)(e) | Storage tank system not closed within 90 days in accordance with subsection. | SNC-B | Inspection | 62-761
69 | Underground | 6069 | 62-761.700(2), 62-761.700(2)(a), 62-761.700(2)(b), 62-761.700(2)(b)1, 62-761.700(2)(b)2 | Cathodic protection not operated and maintained to provide continuous protection. System not inspected 6 months after installation or repair. Cathodic protection system not inspected in accordance with NACE International Standards. Impressed current system not inspected every 2 months. | Minor | Review | 62-761
70 | Underground | 6070 | 62-761.700(2)(c) | Records for operation of impressed current systems not complete. | Minor | Review | 62-761
71 | Underground | 6071 | 62-761.700(2)(d), 62-761.700(2)(d)1, 62-761.700(2)(d)2 | Cathodic protection systems that do not meet requirements not repaired in 90 days or storage tank system closed. | Minor | Inspection | 62-761
72 | Underground | 6072 | 62-761.700(3), 62-761.700(3)(a), 62-761.700(3)(a)1, 62-761.700(3)(a)1.a, 62-761.700(3)(a)1.b, 62-761.700(3)(a)1.c, 62-761.700(3)(a)1.d, 62-761.700(3)(a)1.e, 62-761.700(3)(a)1.f, 62-761.700(3)(a)1.g, 62-761.700(3)(a)2 | Integrity testing of secondary containment systems and interstitial spaces not performed per schedule. | Minor | Inspection | 62-761
73 | Underground | 6073 | 62-761.700(3)(b), 62-761.700(3)(b)1, 62-761.700(3)(b)2 | Spill containment, dispenser liners, and piping sumps not accessible. Water or regulated substances not removed. | Minor | Review | 62-761
74 | Underground | 6074 | 62-761.710(1), 62-761.710(2), 62-761.710(2)(a), 62-761.710(2)(b), 62-761.710(2)(c), 62-761.710(2)(d), 62-761.710(3), 62-761.710(3)(a), 62-761.710(3)(b), 62-761.710(3)(c), 62-761.710(3)(d), 62-761.710(3)(e), 62-761.710(3)(f), 62-761.710(3)(g), 62-761.710(3)(h), 62-761.710(3)(i) | Improper maintenance of records. Records requring to be maintained for 3 years or for the life of the system not kept by facility. Records not provided within 5 business days. | Minor | Review | 62-761
75 | Underground | 6075 | 62-761.710(4) | Records of current training certificates for designated Class A, B, and C operators shall be maintained for as long as the operators are designated for that facility not kept. | Minor | Review | 62-761
76 | Underground | 6076 | 62-761.800(1), 62-761.800(1)(b), 62-761.800(1)(b)1, 62-761.800(1)(b)2, 62-761.800(1)(b)3, 62-761.800(1)(b)4, 62-761.800(1)(b)5, 62-761.800(1)(b)6 | Requirements not met for out-of-service systems. | Minor | Inspection | 62-761
77 | Underground | 6077 | 62-761.800(1)(c), 62-761.800(1)(d)4 | Out of service storage tank systems not tested annually for operability or interstice and liquid level not monitored annually. | Minor | Inspection | 62-761
78 | Underground | 6078 | 62-761.800(1)(e) | Storage tanks systems with secondary containment designated out of service greater than 10 years. | SNC-B | Review | 62-761
79 | Underground | 6079 | 62-761.800(2), 62-761.800(2)(a), 62-761.800(2)(a)1, 62-761.800(2)(a)2, 62-761.800(2)(a)3 | USTs not closed with 90 days of discovery, or not meeting requirements, unable to be repaired or no FR. | SNC-B | Inspection | 62-761
80 | Underground | 6080 | 62-761.800(2)(b), 62-761.800(2)(b)1, 62-761.800(2)(b)2, 62-761.800(2)(b)3, 62-761.800(2)(b)4, 62-761.800(2)(b)5, 62-761.800(2)(b)6 | Storage tank system closure requirements not met that did not result in a discharge. | SNC-B | Inspection | 62-761
81 | Underground | 6081 | 62-761.800(2)(b), 62-761.800(2)(b)1, 62-761.800(2)(b)2, 62-761.800(2)(b)3, 62-761.800(2)(b)4, 62-761.800(2)(b)5, 62-761.800(2)(b)6 | Storage tank system closure requirements not met that resulted in a discharge. | SNC-A | Inspection | 62-761
82 | Underground | 6082 | 62-761.800(3), 62-761.800(3)(a), 62-761.800(3)(a)1, 62-761.800(3)(a)2, 62-761.800(3)(a)3, 62-761.800(3)(a)4, 62-761.800(3)(a)5, 62-761.800(3)(a)6 | Closure Integrity Report and Evaluation not completed and submitted in a timely fashion. | Minor | Review | 62-761
83 | Underground | 6083 | 62-761.800(3)(b) | Closure assessment, sampling not performed and submitted within 60 days. | SNC-B | Review | 62-761
84 | Underground | 6084 | 62-761.800(3)(c), 62-761.800(3)(c)1, 62-761.800(3)(c)2, 62-761.800(3)(c)3 | Closure assessment not performed or properly completed. | SNC-B | Review | 62-761
85 | Underground | 6085 | 62-761.850(1), 62-761.850(1)(a), 62-761.850(1)(b), 62-761.850(1)(b)1, 62-761.850(1)(b)2, 62-761.850(1)(b)3, 62-761.850(1)(b)4, 62-761.850(1)(b)5, 62-761.850(1)(b)6, 62-761.850(1)(b)7, 62-761.850(1)(c), 62-761.850(1)(c)1, 62-761.850(1)(c)2, 62-761.850(1)(d), 62-761.850(1)(e), 62-761.850(1)(f) | Facility not in compliance with Alternate Procedure. | Minor | Review | 62-761
86 | Underground | 6086 | 62-761.850(2), 62-761.850(2)(a), 62-761.850(2)(b), 62-761.850(2)(c), 62-761.850(2)(e), 62-761.850(2)(f), 62-761.850(2)(f)1, 62-761.850(2)(f)2, 62-761.850(2)(f)3, 62-761.850(2)(f)4, 62-761.850(2)(f)5, 62-761.850(2)(f)6, 62-761.850(2)(g), 62-761.850(2)(h), 62-761.850(2)(i), 62-761.850(2)(j), 62-761.850(2)(j)1, 62-761.850(2)(j)2, 62-761.850(2)(j)3 | Equipment not registered with DEP before installation or use. | Minor | Review | 62-761